## GSP
Area | Grid Supply Point Name | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification
Scotland | Abernethy | 9.33 / 17.5 | 56.3398 | -3.2941 | NO 20095 17132 | 60 | 77.82 | 11.5 | 38.1 | 263.063 | 0 |  | Constrained | Subject to Transmission Assesment | October 2024 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Alness | 16.81 / 31.5 | 57.7082 | -4.2745 | NH 64573 70990 | 120 | 45 | 7.5 | 35.1 | 267.076 | 0 |  | Constrained | Reinforcement of the 2nd 275kV Beauly-Loch Buidhe circuit and Loch Buidhe-Dounreay 275kV reconductoring and construction of large 275/132kV substation near Fyrish |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Arbroath | 9.73 / 17.4 | 56.5638 | -2.6195 | NO 62026 41488 | 45 | 40 | 9.3 | 30.9 | 159.536 | 0 |  | Constrained | Subject to Transmission Assesment | October 2028 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Ardmore | 5.21 / 25 | 57.5545 | -6.6452688 | NG 22240 61110 | 45 | 30.4 | 9.1 | 33.9 | 87.53 | 0 |  | Constrained | Construct new 132kV busbar substation near Dunvegan and a new 150km 132kV wood pole line back to Fort Augustus substation. | December 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Beauly | 11.6 / 17.5 | 57.4684 | -4.491 | NH 50697 44752 | 45 | 0 | 7.4 | 31.4 | 124.4275 | 0 |  | Constrained | Beauly busbar reinforcement - Subject to Transmisson Assesment | October 2023 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Boat of Garten | 9.22 / 25 | 57.2536 | -3.7319 | NH 95609 19427 | 60 | 1 | 8.2 | 27.9 | 140.109 | 0 |  | Constrained | Construct a new 275/132kV substation near Tomatin and reinforce the Beauly-Knocknagael-Boat of Garten 132kV towerline circuits | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Braco | 17.2 / 25 | 56.2622 | -3.947 | NN 79499 09453 | 120 | 74.9 | 16.3 | 42.4 | 339.203 | 0 |  | Constrained | Subject to Transmission Assesment | October 2029 | Constrained | Reinforce OHL to reduce circuit constraints on 4L5 Reinforce OHL to reduce circuit constraints on 3L5 | March 2023 | Yes | No | None Known | 132 / 33 | Red
Scotland | Bridge of Dun | 8.11 / 31.5 | 56.7204 | -2.5568 | NO 66018 58883 | 60 | 0.182 | 8 | 26.5 | 129.283 | 0 |  | Constrained | Extend Fetteresso 275/132kV substation to include a second 275/132kV transformer and 132kV and 275kV busbar and construct a 10km 132kV double circuit wood pole line to connect to the existing Fiddes Substation | October 2028 | Constrained | Reinforce the existing circuit between Bridge of Dun - Logie Pert | March 2023 | Yes | No | None Known | 132 / 33 | Red
Scotland | Broadford | 3.26 / 17.5 | 57.2482 | -5.9361 | NG 62656 24360 | 30 | 3.389 | 3.5 | 12.2 | 13.967 | 19.533 |  | Constrained | Construct new 132kV busbar substation near Dunvegan and a new 150km 132kV wood pole line back to Fort Augustus substation. | December 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Brora | 5.4 / 13.1 | 58.0199 | -3.8749 | NC 89341 04957 | 45 | 0.06 | 2.9 | 8.8 | 77.994 | -30.094 |  | Constrained |  | April 2023 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Burghmuir | 8.96 / 25 | 56.3966 | -3.4879 | NO 08257 23702 | 90 | 0 | 13.3 | 45 | 184.885 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Carradale | 9.1 / 25 | 55.5902 | -5.5027 | NR 79379 38527 | 120 | 53.1 | 5.1 | 23.7 | 459.709 | 0 |  | Constrained | Construct North Argyll 275/132kV Substation, 275kV double circuit tower line to Dalmally Substation and reinforce existing Inveraray-Crossaig 132kV towerline circuit | April 2022 | Constrained | Submarine Cable Replacement - Carradale/Arran Submarine Cable replacement - Carradale North Arran | March 2023 | Yes | No | None Known | 132 / 33 | Red
Scotland | Cassley | 3.85 / 25 | 58.1876 | -4.7293 | NC 39642 25338 | 30 | 0 | 0.4 | 1.9 | 66.435 | 0 |  | Constrained | Reinforcement of the 2nd 275kV Beauly-Loch Buidhe circuit and Loch Buidhe-Dounreay 275kV reconductoring. Lairg Loch-Buidhe 132kV RF | August 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Ceannacroc | NA | 57.154 | -4.9371 | NH 22442 10847 | 30 | 50 | 0.6 | 3.6 | 25.198 | 5.402 |  | Constrained | Fort Augustus 400/275kV redevelopment | December 2022 | Constrained |  |  | Yes | No | None Known | 132 / 11 | Red
Scotland | Charleston | 10.64 / 17.5 | 56.4746 | -3.0452 | NO 35713 31875 | 90 | 0.132 | 7.3 | 23.8 | 231.9808 | 0 |  | Constrained |  | April 2023 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Clachan | 29.88 / 40 | 56.2775 | -4.9216 | NN 19218 13284 | 60 | 0 | 2.1 | 5.9 | 51.085 | 11.015 |  | Constrained | Construct North Argyll 275/132kV Substation, 275kV double circuit tower line to Dalmally Substation and reinforce existing Inveraray-Taynuilt 132kV towerline circuit | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 11 | Red
Scotland | Clayhills | 11.32 / 17.5 | 57.1401 | -2.0986 | NJ 94129 05470 | 60 | 0 | 9.2 | 32.7 | 1.325 | 67.875 |  | Unconstrained | Subject to Transmission Assesment |  | Unconstrained |  |  | Yes | No | None Known | 132 / 33 | Green
Scotland | Coupar Angus | 12.76 / 25 | 56.5385 | -3.2734 | NO 21788 39221 | 120 | 96.9 | 6.4 | 25 | 394.663 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Craigiebuckler | NA | 57.1311 | -2.1539 | NJ 90783 04476 | 30 | 0 | 6.7 | 23.4 | 72.495 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Dounreay | NA | 58.5761 | -3.7537 | NC 98112 66674 | 90 | 76.9 | 3.7 | 8 | 297.25 | 0 |  | Constrained | Reinforcement of the 2nd 275kV Beauly-Loch Buidhe circuit and Loch Buidhe-Dounreay 275kV reconductoring | August 2025 | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Dudhope | 11.62 / 25 | 56.4632 | -2.9783 | NO 39813 30549 | 60 | 0 | 11.1 | 44.7 | 43.6168 | 27.4832 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 132 / 33 | Green
Scotland | Dunoon | 11.08 / 13.1 | 55.9757 | -4.9479 | NS 16156 79776 | 45 | 3.5 | 6 | 23.2 | 135.384 | 0 |  | Constrained | GSP Reinforcement project | October 2026 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Dunvegan | 6.97 / 25 | 57.4332 | -6.5404659 | NG 27600 47200 | 60 | 0 | 3.5 | 8.6 | 157.84 | 0 |  | Constrained | Construct new 132kV busbar substation near Dunvegan and a new 150km 132kV wood pole line back to Fort Augustus substation. | October 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Dyce | 11.56 / 13.1 | 57.2157 | -2.19 | NJ 88624 13904 | 60 | 0 | 8.1 | 43.5 | 223.868 | 0 |  | Constrained | Kintore to Dyce 132kv reconductoring |  | Constrained | Dyce - Kingseat 33kV Circuit Reinforcement - Increase in circuit capacity of 12.4 MVA Circuit Reinforcement Dyce North - Increase in circuit capacity | February 2022 | Yes | No | None Known | 132 / 33 | Red
Scotland | Elgin | 9.29 / 25 | 57.6649 | -3.3216 | NJ 21254 64662 | 90 | 30 | 12.8 | 47.7 | 154.662 | 0 |  | Constrained | Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the transmission circuits away from Keith to Blackhillock substation and increasing the supergrid capacity at Blackhillock substation and reconductoring the | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Fasnakyle | 18.02 / 25 | 57.3295 | -4.7931 | NH 31948 29998 | 120 | 49.4 | 0.06 | 0.63 | 146.775 | -26.715 |  | Unconstrained |  |  | Constrained |  |  | Yes | No | None Known | 275 / 33 | Red
Scotland | Fiddes | 10.62 / 25 | 56.9246 | -2.302 | NO 81714 81519 | 90 | 69.34 | 3.9 | 19.8 | 192.775 | 0 |  | Constrained | Extend Fetteresso 400/132kV substation to include a second 400/132kV transformer and 132kV and 400kV busbar, and construct a 10km 132kV double circuit wood pole line to connect to the existing Fiddes Substation | October 2028 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Fort Augustus | 3.2 / 25 | 57.1365 | -4.7175 | NH 35643 08347 | 45 | 0 | 1.5 | 5 | 69.803 | 0 |  | Constrained | GSP reinforcement | December 2022 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Fort William | 11.07 / 25 | 56.8209 | -5.0783 | NN 12232 74158 | 120 | 0 | 5.6 | 65.7 | 120.316 | 0 |  | Constrained | 132kV Tower line Upgrade between Fort William - Fort Augustus substation, Fort William Grid Transformer upgrades |  | Constrained | Carnoch 33kV CB Replacement - Increase in make and break fault ratings Glenfinnan-Lochailort 33kV Reinforcement - Increase in circuit capacity of 9 MVA Corran Narrows Sub Sea Cable Replacement" A&W Glenfinnan - Lochailort Reinforce network to reduce voltage issues under n-1 conditions | March 2023 | Yes | No | None Known | 132 / 33 | Red
Scotland | Fraserburgh | 8.86 / 25 | 57.6862 | -2.0241 | NJ 98662 66267 | 45 | 49.599 | 6 | 19.4 | 159.86 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Glenagnes | NA | 56.4618 | -2.9967 | NO 38678 30404 | 60 | 0 | 1.9 | 9 | 3.045 | 58.855 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 132 / 33 | Green
Scotland | Grudie Bridge | NA | 57.6194 | -4.8313 | NH 30998 62352 | 90 | 49.9 | 1.2 | 9.9 | 63.953 | 27.247 |  | Constrained | Beauly busbar reinforcement | October 2023 | Constrained | Aultbea - Ullapool OHL/Cable | March 2022 | Yes | No | None Known | 132 / 33 | Red
Scotland | Inverness | 15.3 / 25 | 57.4538 | -4.2467 | NH 65293 42620 | 90 | 0 | 20.7 | 63.2 | 171.833 | -61.133 |  | Constrained |  |  | Constrained | Establish a new Primary at Longman Switching Station with two 12/24MVA transformers in order to share load currently distributed between Waterloo Place, Raigmore and Culloden | March 2023 | Yes | No | None Known | 132 / 33 | Red
Scotland | Keith | 11.7 / 17.5 | 57.5408 | -2.9385 | NJ 43916 50464 | 90 | 0.1 | 13.3 | 50.5 | 432.987 | 0 |  | Constrained | Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the transmission circuits away from Keith to Blackhillock substation and increasing the supergrid capacity at Blackhillock substation and reconductoring the | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Killin | 11.55 / 25 | 56.4771 | -4.3295 | NN 56618 34099 | 45 | 2.2 | 0.24 | 4 | 92.92 | -47.68 |  | Constrained | GSP reinforcement | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Kinlochleven | 5.29 / 8 | 56.7146 | -4.9543 | NN 19285 62002 | 45 | 0 | 1.2 | 3.4 | 44.379 | 1.821 |  | Constrained | 132kV Tower line Upgrade between Fort William - Fort Augustus substations. |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Kintore | 17.27 / 25 | 57.2186 | -2.3815 | NJ 77060 14275 | 120 | 36.8 | 15.6 | 67.2 | 374.048 | 0 |  | Constrained |  | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Lairg | 6.51 / 20 | 58.0306 | -4.3928 | NC 58798 07111 | 90 | 50 | 0.5 | 1.9 | 84.135 | 6.365 |  | Constrained | Reinforcement of the 2nd 275kV Beauly-Loch Buidhe circuit and Loch Buidhe-Dounreay 275kV reconductoring. Lairg Loch-Buidhe 132kV RF | August 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Lunanhead | 10.75 / 25 | 56.6542 | -2.8656 | NO 47028 51715 | 90 | 62.4 | 8.4 | 62.2 | 289.68 | 0 |  | Constrained | GSP Reinforcement | June 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Lyndhurst | 11.14 / 17.5 | 56.4811 | -3.0174 | NO 37434 32575 | 60 | 20.066 | 6.8 | 25 | 100.41 | -33.61 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | MacDuff | 11.33 / 13.1 | 57.6641 | -2.4984 | NJ 70363 63908 | 90 | 0.067 | 3.6 | 21.8 | 271.615 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Milton of Craigie | 11.46 / 17.5 | 56.4754 | -2.9247 | NO 43137 31857 | 60 | 99.8 | 13.6 | 47.9 | 145.145 | -71.545 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Mybster | 10.78 / 25 | 58.4463 | -3.4244 | ND 16953 51766 | 60 | 0 | 3 | 10.3 | 442.873 | 0 |  | Constrained | Reinforcement of the 2nd 275kV Beauly-Loch Buidhe circuit and Loch Buidhe-Dounreay 275kV reconductoring | August 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Nairn | 9.3 / 25 | 57.5767 | -3.8483 | NH 89567 55574 | 60 | 50 | 8.8 | 31.3 | 211.967 | 0 |  | Constrained | Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the transmission circuits away from Keith to Blackhillock substation and increasing the supergrid capacity at Blackhillock substation and reconductoring the | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Persley | 11.08 / 26.2 | 57.1742 | -2.1381 | NJ 91751 09273 | 90 | 0 | 9.9 | 43.1 | 142.508 | -42.608 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Peterhead Grange | NA | 57.5087 | -1.8058 | NK 11738 46516 | 45 | 0.199 | 8.1 | 24.4 | 151.945 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Peterhead Shell | 11.17 / 18.4 | 57.4745 | -1.8007 | NK 12055 42712 | 15 | 0 | 2.2 | 8.6 | 0 | 17.2 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 132 / 11 | Green
Scotland | Port Ann | 9.88 / 25 | 56.0283 | -5.3567 | NR 90938 86799 | 30 | 112.3 | 3.2 | 21.5 | 189.454 | 0 |  | Constrained | Construct North Argyll 275/132kV Substation, 275kV double circuit tower line to Dalmally Substation and reinforce existing Inveraray-Taynuilt 132kV towerline circuit. Port Ann GSP reinforcement. | October 2026 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Quoich | NA | 57.0627 | -5.1235 | NH 10703 01181 | 30 | 0 | 0.07 | 0.12 | 3.85 | 26.22 |  | Constrained | Construct new 132kV busbar substation near Dunvegan and a new 150km 132kV wood pole line back to Fort Augustus substation. | December 2025 | Constrained |  |  | Yes | No | None Known | 132 / 11 | Red
Scotland | Rannoch | NA | 56.6932 | -4.4008 | NN 53072 58298 | 90 | 20 | 0.25 | 2 | 62.79 | 27.46 |  | Constrained | Subject to Transmission Assesment | October 2022 | Constrained |  |  | Yes | No | None Known | 132 / 11 | Red
Scotland | Redmoss | 11.94 / 17.5 | 57.1084 | -2.0916 | NJ 94551 01947 | 60 | 0.239 | 11.9 | 45.7 | 150.17 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Shin | NA | 57.9435 | -4.4132 | NH 57246 97463 | 90 | 0 | 0.6 | 2.2 | 277.886 | 0 |  | Constrained | Reinforcement of the 2nd 275kV Beauly-Loch Buidhe circuit and Loch Buidhe-Dounreay 275kV reconductoring | October 2024 | Constrained |  |  | Yes | No | None Known | 132 / 11 | Red
Scotland | Sloy | NA | 56.2451 | -4.7304 | NN 30906 09190 | 50 | 0 | 0.01 | 2.9 | 79.997 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 11 | Red
Scotland | St Fillans | NA | 56.3955 | -4.1236 | NN 69020 24601 | 25 | 0 | 0.5 | 1.9 | 24.23 | 1.27 |  | Unconstrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Stornoway | 3.64 / 25 | 58.2034 | -6.3737 | NB 43147 32182 | 30 | 0 |  |  | 129.605 | 0 |  | Constrained | Subsea Cable from Stornoway to Beauly | March 2027 | Constrained | Stornoway to Barvas 33kV Circuit Reinforcement | December 2022 | Yes | No | None Known | 33 / 33 | Red
Scotland | Strathleven | NA | 55.960875 | -4.5616133 | NS 40190 77170 | 60 | 0.5 |  |  | 54.648 | 5.352 |  | Constrained | To be advised by Scottish Power |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Strichen | 10.73 / 16 | 57.5861 | -2.0698 | NJ 95925 55119 | 90 | 25.479 | 1.1 | 16.6 | 230.463 | 0 |  | Constrained | Subject to Transmission Assesment |  | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Tarland | 6.86 / 25 | 57.1519 | -2.7873 | NJ 52468 07060 | 30 | 0 | 4.5 | 20.3 | 73.035 | 0 |  | Constrained | Subject to Transmission Assesment | October 2028 | Constrained | A new Primary transformer to be established between Aboyne and Ballater | March 2023 | Yes | No | None Known | 132 / 33 | Red
Scotland | Taynuilt | 10.97 / 25 | 56.4301 | -5.2141 | NN 01911 31063 | 90 | 0 | 6.3 | 33.8 | 124.929 | 0 |  | Constrained | Construct North Argyll 275/132kV Substation, 275kV double circuit tower line to Dalmally Substation and reinforce existing Inveraray-Taynuilt 132kV towerline circuit | October 2028 | Constrained | 33kV Busbar reinforcement 33kV OHL Taynuilt - Tullich Reinforcement Taynuilt to Tullich Reinforcemet of 33kV lines to improve voltage due to load demand | December 2022 | Yes | No | None Known | 132 / 33 | Red
Scotland | Thurso | 12.02 / 17.5 | 58.574 | -3.5117 | ND 12180 66102 | 120 | 28.05 | 7 | 41.4 | 335.645 | 0 |  | Constrained | Reinforcement of the 2nd 275kV Beauly-Loch Buidhe circuit and Loch Buidhe-Dounreay 275kV reconductoring | August 2025 | Constrained | Replace the existing submarine cables between Mainland Orkney to Hoy North and Mainland Orkney to Hoy Central | March 2022 | Yes | No | None Known | 132 / 33 | Red
Scotland | Tummel Bridge | NA | 56.7072 | -4.0292 | NN 75868 59115 | 21 | 0 | 3.9 | 13.8 | 55.902 | 0 |  | Constrained | Subject to Transmission Assesment | October 2025 | Constrained |  |  | Yes | No | None Known | 132 / 33 | Red
Scotland | Willowdale | 11.64 / 17.5 | 57.1538 | -2.0972 | NJ 94217 06996 | 60 | 0 | 10.1 | 36.4 | 2.725 | 67.375 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 132 / 33 | Green
Scotland | Woodhill | NA | 57.1543 | -2.1462 | NJ 91252 07055 | 90 | 0 | 10.5 | 33.4 | 3.274 | 97.226 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 132 / 33 | Green

## BSP
Area | Bulk Supply Point Name | GSP Parent | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate Rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification

## PS
Area | Primary Substation Name | GSP Parent | BSP Parent | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate Rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification
Scotland | Abernethy | Abernethy |  | 1.8 / 13.1 | 56.3398 | -3.2942 | NO 20094 17132 | 6.3 | 0 | 0.028 | 1.509 | 1.479 | 1.019 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Balbeggie | Abernethy |  | 2.65 / 25 | 56.4514 | -3.3401 | NO 17499 29606 | 6.25 | 0 | 0.62 | 3.89 | 1.10539 | 2.98 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Bridge of Earn | Abernethy |  | 6.59 / 25 | 56.3443 | -3.4035 | NO 13343 17764 | 8 | 0 | 0.56 | 3.28 | 0.8 | 7.76 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Errol | Abernethy |  | 5.25 / 13.1 | 56.3933 | -3.2456 | NO 23206 23038 | 5.0 | 0 | 1.04 | 4.55 | 0.45 | 5.59 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Glendevon | Abernethy |  | 1.86 / 13.1 | 56.2069 | -3.612 | NO 00101 02760 | 8 | 0 | 0.16 | 1.7 | 1.632 | 6.528 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Milnathort | Abernethy |  | 5.66 / 13.1 | 56.23 | -3.4226 | NO 11900 05074 | 15 | 0 | 2.6936 | 11.0491 | 2.442 | 15.2516 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Perth Harbour | Abernethy |  | 6.77 / 13.1 | 56.3825 | -3.4276 | NO 11948 22049 | 15 | 0 | 2.8691 | 11.2868 | 0.2 | 17.6691 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Rumbling Bridge | Abernethy |  | NA | 56.1822 | -3.5804 | NT 02000 99967 | 2.0 | 0 | 0 | 0 |  | 2 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Scone | Abernethy |  | 5.67 / 13.1 | 56.4139 | -3.389 | NO 14401 25495 | 15 | 0 | 1.0697 | 4.09 | 0.1 | 15.9697 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Balaldie | Alness |  | 1.82 / 18.4 | 57.7928 | -3.9022 | NH 87017 79720 | 4.0 | 0 | 0.6 | 2.45 | 0.1 | 2.15 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Contullich | Alness |  | NA | 57.704 | -4.2865 | NN 59226 32752 | 0.1 | 0 | 0.01 | 0.05 | 0 | 0.11 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Crosshills | Alness |  | 7.9 / 13.1 | 57.701 | -4.259 | NH 65470 70156 | 15 | 0 | 1.6911 | 6.9293 | 0.096 | 16.5951 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Glastullich | Alness |  | 3.16 / 26.2 | 57.7618 | -4.0436 | NH 78509 76508 | 8 | 0 | 0.23322 | 1.754 | .9 | 7.3332 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Invergordon | Alness |  | 7.4 / 13.1 | 57.6938 | -4.1699 | NH 70756 69177 | 15 | 0 | 0.28238 | 12.0315 | 6.95 | 8.3324 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Nigg | Alness |  | 2.45 / 13.1 | 57.7016 | -4.0238 | NH 79490 69773 | 15 | 0 | 0.02 | 0.684 | 0 | 15.02 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Peddieston | Alness |  | 2.31 / 18.4 | 57.6452 | -4.1093 | NH 74198 63656 | 2.5 | 0 | 0.334 | 1.781 | 0 | 2.834 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Tain | Alness |  | 5.03 / 13.1 | 57.8062 | -4.0618 | NH 77578 81489 | 15 | 0 | 1.49 | 7.8544 | 0.08 | 16.41 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Carnoustie | Arbroath |  | 6.02 / 13.1 | 56.5086 | -2.7225 | NO 55631 35403 | 10.0 | 0 | 2.0597 | 8.0034 | 0.74 | 11.3197 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Charles Avenue | Arbroath |  | 7.7 / 13.1 | 56.5604 | -2.6043 | NO 62954 41097 | 10 | 0 | 2.2443 | 10.5122 | 0.385 | 11.8593 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Elliot Depot | Arbroath |  | 4.38 / 13.1 | 56.5539 | -2.6157 | NO 62251 40381 | 15 | 0 | 1.5467 | 5.9439 | 1.05 | 15.4967 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Hume Street | Arbroath |  | 7.63 / 13.1 | 56.5612 | -2.5862 | NO 64067 41180 | 24 | 0 | 2.0422 | 9.4459 | 0.345 | 25.6972 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Redford | Arbroath |  | 3.9 / 13.1 | 56.5862 | -2.7199 | NO 55879 44046 | 5.0 | 0 | 0.70427 | 3.0846 | 2.444 | 4.7043 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Aird | Ardmore |  | 1.94 / 13.1 | 57.4611 | -7.3525 | NF 79163 53853 | 8 | 0 | 0.827 | 2.8403 | 0 | 5.9867 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Clachan | Ardmore |  | 0.98 / 25 | 57.5569 | -7.3214 | NF 81863 64360 | 2.5 | 0 | 0.51988 | 2.0854 | 0 | 3.0199 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Drimore | Ardmore |  | 1.16 / 18.4 | 57.3364 | -7.3641 | NF 77377 40049 | 2.5 | 0 | 0.32584 | 1.1705 | 0 | 2.8258 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Loch Carnan | Ardmore |  | 4.46 / 13.1 | 57.3645 | -7.2707 | NF 83230 42735 | 8 | 0 | 0.125 | 0.513 | 0 | 8.125 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Pollachar | Ardmore |  | 1.48 / 13.1 | 57.1064 | -7.3688 | NF 75073 14513 | 2.5 | 0 | 0.71256 | 2.8196 | 0.9 | 2.3126 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Stockinish | Ardmore |  | 0.77 / 17.5 | 57.8454 | -6.8311 | NG 13447 94222 | 1.0 | 0 | 0.10987 | 0.84932 | 0.2 | 1.1099 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Tarbert, Harris | Ardmore |  | 2.23 / 18.4 | 57.8996 | -6.8073 | NB 15289 00157 | 2.5 | 0 | 0.23941 | 1.7848 | 3.1 | 2.7394 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Aigas | Beauly |  | 0.41 / 13.1 | 57.4287 | -4.5772 | NH 45362 40529 | 0.5 | 0 | 0.08 | 0.295 | 0 | 0.285 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Blackstand | Beauly |  | NA | 57.6039 | -4.1598 | NH 71036 59151 | 6.0 | 0 | 0.61 | 2.6369 | 0 | 6.61 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Conon Bridge | Beauly |  | 5.32 / 20 | 57.5662 | -4.4258 | NH 54996 55499 | 6.25 | 0 | 0.58578 | 3.2603 | 0.2 | 6.6358 | 50 | Constrained |  |  | Constrained | Conon Bridge Transformer Replacement - Increase in transformer capacity of 0.05 MVA | March 2022 | Yes | No | None Known | 33 / 11 | Green
Scotland | Dingwall | Beauly |  | 6.27 / 13.1 | 57.6034 | -4.4457 | NH 53956 59680 | 15 | 0 | 1.2 | 12.3585 | 3.67 | 12.53 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kiltarlity | Beauly |  | 3.48 / 18.4 | 57.437 | -4.496 | NH 50271 41265 | 6.0 | 0 | 0.239 | 1.262 | 0.5 | 5.739 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Marybank | Beauly |  | NA | 57.5496 | -4.5625 | NH 46749 53948 | 2.5 | 0 | 0.263 | 1.43 | 0 | 2.763 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Muir of Ord | Beauly |  | 7.45 / 13.1 | 57.5032 | -4.4479 | NH 53420 48534 | 15 | 0 | 2.748 | 7 | 0.1 | 17.648 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Muirend | Beauly |  | NA | 57.5588 | -4.2663 | NH 64508 54337 | 6.0 | 0 | 0.47381 | 2.6572 | 0 | 6.4738 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | North Kessock | Beauly |  | 1.4 / 13.1 | 57.5062 | -4.2547 | NH 65004 48461 | 2.5 | 0 | 0.20912 | 1.3972 | 0 | 2.7091 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Aviemore | Boat of Garten |  | 7.14 / 13.1 | 57.1801 | -3.8237 | NH 89856 11394 | 24 | 0 | 1.95 | 9.831 | 0 | 16.119 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Ballindalloch | Boat of Garten |  | 3.02 / 20 | 57.3951 | -3.3447 | NJ 19279 34652 | 15 | 0 | 1.1352 | 3.5 | 0 | 12.6352 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Boat of Garten | Boat of Garten |  | 7.39 / 13.1 | 57.2536 | -3.7319 | NH 95609 19427 | 5.0 | 0 | 0.57059 | 3.4 | 0 | 5.5706 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dalwhinnie | Boat of Garten |  | 0.68 / 13.1 | 56.9332 | -4.2413 | NN 63711 84671 | 1.0 | 0 | 0.26507 | 0.81276 | 0.5 | 0.76507 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Grantown | Boat of Garten |  | 5.84 / 13.1 | 57.3172 | -3.601 | NJ 03670 26311 | 15 | 0 | 1.0749 | 5.9807 | 0 | 16.0749 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kingussie | Boat of Garten |  | 4.54 / 13.1 | 57.0779 | -4.0567 | NH 75429 00426 | 15 | 0 | 0.94963 | 5.6002 | 0.74 | 15.2096 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Tomatin | Boat of Garten |  | 1.24 / 12.5 | 57.342 | -4.0103 | NH 79106 29734 | 2.0 | 0 | 0.1017 | 0.72556 | 0.092 | 2.1017 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Callander | Braco |  | 3.84 / 13.1 | 56.2365 | -4.212 | NN 62995 07081 | 8 | 0 | 0.70631 | 5.5411 | 2.984 | 5.7223 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Crieff | Braco |  | 5.21 / 13.1 | 56.3775 | -3.8536 | NN 85626 22119 | 15 | 0 | 1.842 | 10.561 | 2.834 | 14.008 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dunblane | Braco |  | 6.37 / 13.1 | 56.1908 | -3.969 | NN 77907 01544 | 12.5 | 0 | 2.3797 | 10.4293 | 0.65 | 14.2297 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Forteviot | Braco |  | 2.44 / 12 | 56.3455 | -3.546 | NO 04539 18092 | 4.0 | 0 | 0.252 | 2.8 | 0.204 | 4.048 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Gleneagles | Braco |  | 6.18 / 7.9 | 56.2843 | -3.7536 | NN 91540 11582 | 15 | 0 | 3.7147 | 10.8105 | 0.2 | 18.5147 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kippen | Braco |  | 4.2 / 13.1 | 56.1346 | -4.1517 | NS 66376 95628 | 8 | 0 | 0.662 | 4.4483 | 0.99 | 7.672 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Brechin | Bridge of Dun |  | 5.8 / 25 | 56.7272 | -2.639 | NO 60998 59682 | 12.5 | 0 | 1.759 | 7.59 | 2.55 | 11.709 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Bridge of Dun | Bridge of Dun |  | 1.7 / 13.1 | 56.7204 | -2.5568 | NO 66018 58883 | 2.5 | 0 | 0.18611 | 1.13 | 0.68 | 2.0061 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Glaxo | Bridge of Dun |  | 4.7 / 18 | 56.7078 | -2.4528 | NO 72377 57431 | 10.0 | 0 | 0.26 | 2.56 | 0 | 10.26 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Inchbare | Bridge of Dun |  | 1.24 / 7.9 | 56.7783 | -2.645 | NO 60684 65379 | 2.5 | 0 | 0.32862 | 1.2995 | 0.255 | 2.5736 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Logie Pert | Bridge of Dun |  | 2.64 / 20 | 56.7703 | -2.529 | NO 67764 64427 | 5.0 | 0 | 0.0054704 | 1.1254 | 0.09 | 4.9155 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Mill Road | Bridge of Dun |  | 5.96 / 13.1 | 56.71 | -2.4701 | NO 71317 57683 | 12.5 | 0 | 2.1405 | 8.0492 | 0.211 | 14.4295 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Montrose North | Bridge of Dun |  | 6.42 / 13.1 | 56.7224 | -2.4718 | NO 71226 59070 | 15 | 0 | 2.4816 | 10.4316 | 0.11 | 17.3716 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | St Cyrus | Bridge of Dun |  | 3.83 / 16 | 56.7811 | -2.4126 | NO 74889 65577 | 8 | 0 | 0.14837 | 1.87 | 4.305 | 7.6184 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Achintee | Broadford |  | NA | 57.4162 | -5.4323 | NG 93973 41406 | 2.5 | 0 | 0.08 | 0.08 | 0 | 2.5 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Broadford | Broadford |  | NA | 57.2482 | -5.9361 | NG 62656 24360 | 6.5 | 0 | 0.52093 | 1.686 | 1.7 | 5.3209 | 100 | Constrained |  |  | Constrained | 2no 200A Voltage Regulator to alleviate voltage constraints | May 2022 | Yes | No | None Known | 33 / 11 | Green
Scotland | Kishorn Hill | Broadford |  | NA | 57.4063 | -5.5258 | NG 88304 40591 | 2.0 | 0 | 0.40606 | 1.3518 | 0.45 | 1.9561 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Kyle | Broadford |  | NA | 57.281 | -5.7098 | NG 76499 27247 | 5.0 | 0 | 0.76854 | 2.5157 | 0 | 5.7685 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lower Ollach | Broadford |  | NA | 57.3554 | -6.1375 | NG 51241 37001 | 1.0 | 0 | 0.1641 | 0.59625 | 0 | 1.1641 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Nostie Bridge | Broadford |  | 1.87 / 13.1 | 57.2852 | -5.5656 | NG 85209 27252 | 8 | 0 | 0.55 | 3.77 | 3 | 5.55 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Shieldaig | Broadford |  | 0.71 / 13.1 | 57.5076 | -5.6469 | NG 81637 52250 | 1.0 | 0 | 0.23 | 0.921 | 0.09 | 0.33 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Skulamus | Broadford |  | 2.91 / 18.4 | 57.2326 | -5.8809 | NG 65881 22438 | 4.0 | 0 | 0.558 | 2.5776 | 0 | 4.558 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Brora | Brora |  | 4.96 / 13.1 | 58.0138 | -3.8553 | NC 90482 04236 | 5.0 | 0 | 0.59058 | 2.7436 | 0.294 | 5.2966 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dornoch | Brora |  | 2.3 / 13.1 | 57.8828 | -4.03 | NH 79721 89953 | 8 | 0 | 2.0857 | 3.7095 | 0 | 10.0857 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Golspie | Brora |  | 2.16 / 18.4 | 57.976 | -3.9799 | NC 82996 00240 | 4.0 | 0 | 0.52383 | 2.2017 | 0.05 | 4.4738 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Helmsdale | Brora |  | 1.81 / 13.1 | 58.1165 | -3.6588 | ND 02372 15376 | 2.5 | 0 | 0.14879 | 1.23 | 0.9 | 1.7488 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Burghmuir | Burghmuir |  | 7.59 / 13.1 | 56.3966 | -3.4879 | NO 08256 23702 | 12.5 | 0 | 2.8 | 11.54 | 0 | 15.3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Goodlyburn | Burghmuir |  | 7.47 / 13.1 | 56.4049 | -3.4586 | NO 10084 24586 | 12.5 | 0 | 2.304 | 9.8431 | 0 | 14.804 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Inveralmond | Burghmuir |  | 6.5/25 | 56.4156 | -3.4811 | NO 08721 25807 | 24 | 0 | 0.69 | 4.6 | 0 | 24 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Redgorton | Burghmuir |  | 6.76 / 13.1 | 56.4428 | -3.4995 | NO 07650 28860 | 15 | 0 | 1.082 | 7.81 | 1.3 | 14.782 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Thimblerow | Burghmuir |  | 7.78 / 13.1 | 56.3978 | -3.4377 | NO 11356 23764 | 30 | 0 | 5.0117 | 18.9213 | 0 | 26.0117 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Balliekine | Carradale |  | 0.81 / 10 | 55.5963 | -5.3794 | NR 87179 38819 | 1.0 | 0 | 0.02 | 0.722 | 0.5 | 0.298 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Ballure | Carradale |  | NA | 55.689 | -5.6381 | NR 71425 49944 | 2.5 | 0 | 0.296 | 1.184 | 1.155 | 1.612 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Brodick | Carradale |  | 4.14 / 25 | 55.5724 | -5.1426 | NS 01976 35459 | 8 | 0 | 1.0995 | 7.543 | 0.7 | 8.3995 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Campbeltown | Carradale |  | 5.34 / 13.1 | 55.4272 | -5.6127 | NR 71509 20746 | 15 | 0 | 2.3066 | 7.9345 | 2.8 | 14.5066 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Claonaig | Carradale |  | NA | 55.7545 | -5.3973 | NR 86915 56467 | 0.2 | 0 | 0.03 | 0.187 | 0 | 0.23 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Dippen | Carradale |  | 0.84 / 5.2 | 55.5822 | -5.4917 | NR 80026 37592 | 1.0 | 0 | 0.3 | 0.877 | 0 | 1.3 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Machrie | Carradale |  | NA | 55.5532 | -5.3295 | NR 90092 33864 | 2.5 | 0 | 0.30503 | 2.0177 | 0.053 | 2.752 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | West Parkfergus | Carradale |  | 2.43 / 18.4 | 55.4265 | -5.6979 | NR 66116 20950 | 8 | 0 | 0.023735 | 1.0839 | 0 | 8.0237 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Whiting Bay | Carradale |  | NA | 55.4909 | -5.1013 | NS 04169 26277 | 4.0 | 0 | 0.12948 | 2.4407 | 0.1 | 4.1295 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Overscaig | Cassley |  | NA | 58.1881 | -4.7281 | NC 39711 25382 | 0.1 | 0 | 0.01 | 0.041 | 0 | 0.11 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Rhiconich | Cassley |  | 1.32 / 18.4 | 58.4297 | -4.9893 | NC 25554 52924 | 2.5 | 0 | 0.50329 | 1.8917 | 0 | 3.0033 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Drumnadrochit | Ceannacroc |  | NA | 57.3343 | -4.4884 | NH 50306 29824 | 6.0 | 0 | 0.364 | 3.6711 | 0 | 6.364 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Charleston | Charleston |  | 7.85 / 13.1 | 56.4741 | -3.0448 | NO 35734 31818 | 10.0 | 0 | 1.502 | 5.968 | 0 | 11.502 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Gourdie | Charleston |  | 3.83 / 13.1 | 56.4774 | -3.0638 | NO 34573 32203 | 5.0 | 0 | 0.64112 | 2.836 | 0 | 5.6411 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Menzieshill | Charleston |  | 8.6 / 13.1 | 56.467 | -3.0417 | NO 35918 31022 | 15 | 0 | 3.523 | 14.093 | 0.108 | 18.415 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Ninewells | Charleston |  | 7.66 / 20 | 56.4634 | -3.0541 | NO 35148 30641 | 15 | 0 | 2.1378 | 6.2121 | 0.25 | 16.8878 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Butterbridge | Clachan |  | NA | 56.2475 | -4.9179 | NN 19306 09936 | 0.15 | 0 | 0.005 | 0.02 | 0 | 0.155 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Douglas Pier | Clachan |  | 1.07 / 13.1 | 56.1549 | -4.9094 | NS 19396 99616 | 2.5 | 0 | 0.512 | 2.047 | 0.646 | 2.366 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Inveraray | Clachan |  | 1.11 / 25 | 56.2418 | -5.081 | NN 09172 09746 | 2.5 | 0 | 0.42256 | 2.0328 | 0 | 2.9226 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Lochgoilhead | Clachan |  | 1.06 / 18.4 | 56.1754 | -4.8987 | NN 20159 01862 | 1.5 | 0 | 0.065658 | 0.56592 | 1.35 | 0.21566 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Strachur | Clachan |  | 0.65 / 13.1 | 56.1648 | -5.0829 | NN 08672 01180 | 1.0 | 0 | 0.049927 | 0.93263 | 1 | 1.0499 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Balnagask | Clayhills |  | 4.65 / 13.1 | 57.138 | -2.0668 | NJ 96055 05234 | 23 | 0 | 1.998 | 8.072 | 1 | 16.926 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Clayhills | Clayhills |  | 8.32 / 13.1 | 57.1405 | -2.1 | NJ 94047 05518 | 24 | 0 | 5.096 | 17.562 | 0.15 | 28.946 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Commerce Street | Clayhills |  | 8.2 / 25 | 57.1474 | -2.0873 | NJ 94816 06282 | 23 | 0 | 4.776 | 15.562 | 0 | 27.776 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Craiginches | Clayhills |  | NA | 57.1277 | -2.0893 | NJ 94694 04089 | 12.5 | 0 | 3.0453 | 12.9745 | 0 | 15.5453 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Alyth | Coupar Angus |  | 4.7 / 13.1 | 56.6204 | -3.247 | NO 23579 48311 | 5.0 | 0 | 0.78201 | 3.1514 | 0.25 | 2.6307 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Blairgowrie | Coupar Angus |  | 6.9 / 13.1 | 56.5858 | -3.3246 | NO 18741 44551 | 23 | 0 | 2.4161 | 9.2207 | 0.475 | 24.9411 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Caputh | Coupar Angus |  | 5.41 / 20 | 56.5456 | -3.4771 | NO 09277 40265 | 15 | 0 | 1.264 | 6.67 | 1.25 | 15.014 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Coupar Angus | Coupar Angus |  | 7.87 / 13.1 | 56.5384 | -3.2735 | NO 21784 39212 | 8.4 | 0 | 1.692 | 6.493 | 1.23 | 8.862 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dalrulzion | Coupar Angus |  | 2.43 / 25 | 56.707 | -3.4145 | NO 13498 58153 | 2.5 | 0 | 0.35087 | 1.9085 | 0.5 | 2.3509 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Leoch | Coupar Angus |  | 3.04 / 13.1 | 56.5143 | -3.0425 | NO 35945 36287 | 5.0 | 0 | 0.242 | 2.9856 | 2.2 | 3.042 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Craigiebuckler | Craigiebuckler |  | 7.64 / 13.1 | 57.1315 | -2.154 | NJ 90775 04519 | 24 | 0 | 0.831 | 3.58 | 0.25 | 24.581 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Craigton Cults | Craigiebuckler |  | 7.92 / 18.4 | 57.1217 | -2.1801 | NJ 89195 03438 | 10.0 | 0 | 2.175 | 9.502 | 0.8 | 11.375 | 50 | Unconstrained |  |  | Unconstrained | Replace existing 10MVA units with 7.5/15MVA units | February 2023 | Yes | No | None Known | 33 / 11 | Green
Scotland | Culter | Craigiebuckler |  | 3.43 / 25 | 57.0987 | -2.2656 | NJ 84009 00884 | 12.5 | 0 | 2.73 | 10.917 | 0.5 | 14.73 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Ruthrieston | Craigiebuckler |  | 7.81 / 21.9 | 57.1274 | -2.1243 | NJ 92574 04060 | 24 | 0 | 2.92 | 9.9 | 0 | 25.92 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Constable Street | Dudhope |  | 8.19 / 20 | 56.4658 | -2.9607 | NO 40903 30821 | 30 | 0 | 8.2274 | 13.7751 | 0.25 | 37.9774 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Rosebank Street | Dudhope |  | 8.34 / 13.1 | 56.4686 | -2.9764 | NO 39943 31150 | 46 | 0 | 3 | 19.6 | 0 | 49 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Bruchag | Dunoon |  | 3.66 / 13.1 | 55.7712 | -5.0087 | NS 11372 57191 | 5.0 | 0 | 0.42015 | 3.9865 | 0.22 | 5.2001 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Colintraive | Dunoon |  | NA | 55.926 | -5.1514 | NS 03209 74814 | 0.3 | 0 | 0.0059 | 0.232 | 0.35 | 0 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Dunoon | Dunoon |  | 7.69 / 13.1 | 55.9559 | -4.9307 | NS 17135 77531 | 24 | 0 | 1.7762 | 8.0326 | 0.056 | 25.7202 | 50 | Constrained |  |  | Constrained | Installation of NERs at the primary and cable overlay | October 2021 | Yes | No | None Known | 33 / 11 | Green
Scotland | Glendaruel | Dunoon |  | NA | 56.0333 | -5.2167 | NN 03067 59147 | 0.3 | 0 | 0.0695 | 0.278 | 0.0046 | 0.3649 |  | Constrained |  |  | Constrained | Glendaruel Primary Tx Replacement | July 2022 | Yes | No | None Known | 33 / 11 | Red
Scotland | Innellan | Dunoon |  | 3.04 / 13.1 | 55.8954 | -4.9582 | NS 15129 70875 | 6.25 | 0 | 0.18783 | 1.1283 | 0 | 6.4378 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kames | Dunoon |  | 1.15 / 13.1 | 55.8911 | -5.259 | NR 96305 71237 | 2.5 | 0 | 0.078 | 0.751 | 0.075 | 2.503 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Newton | Dunoon |  | NA | 56.1403 | -5.1411 | NS 04939 98621 | 0.2 | 0 | 0.39 | 0.626 | 0 | 0.59 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Otter Ferry | Dunoon |  | 1.34 / 18.4 | 56.0107 | -5.3165 | NR 93352 84713 | 2.5 | 0 | 0.069762 | 0.85618 | 0.25 | 2.3198 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Rothesay | Dunoon |  | 4.74 / 13.1 | 55.837 | -5.0575 | NS 08636 64647 | 24 | 0 | 1.2061 | 4.8132 | 0.7 | 25.2061 | 50 | Constrained |  |  | Constrained | Rothesay 11kV Board Replacement - Increase in make and break fault ratings | March 2022 | Yes | No | None Known | 33 / 11 | Green
Scotland | Sandbank | Dunoon |  | 7.45 / 13.1 | 55.9898 | -4.9631 | NS 15274 81386 | 8 | 0 | 0.788 | 3.855 | 0.85 | 8.688 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Drynoch | Dunvegan |  | NA | 57.2986 | -6.2999 | NG 41080 31292 | 2.5 | 0 | 0.949 | 1.905 | 0.93 | 2.519 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Dunvegan | Dunvegan |  | 2.35 / 20 | 57.4327 | -6.5397 | NG 27646 47150 | 6.0 | 0 | 0.422 | 2.2758 | 0 | 6.422 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Portree | Dunvegan |  | 2.86 / 13.1 | 57.4217 | -6.1973 | NG 48102 44602 | 15 | 0 | 3.6249 | 10.172 | 0 | 18.6249 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Uig | Dunvegan |  | 0.87 / 13.1 | 57.5941 | -6.3674 | NG 39131 64412 | 2.5 | 0 | 0.33771 | 1.2688 | 0.09 | 2.8377 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Balmedie | Dyce |  | 3.32 / 16 | 57.2583 | -2.0755 | NJ 95546 18627 | 8 | 0 | 0.68507 | 3.5514 | 0.3 | 5.1337 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dyce North | Dyce |  | 8.1 / 13.1 | 57.205 | -2.1822 | NJ 89092 12705 | 24 | 0 | 4.824 | 20.407 | 0.622 | 28.202 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Ellon | Dyce |  | 6.01 / 13.1 | 57.3609 | -2.0763 | NJ 95510 30054 | 12.5 | 0 | 2.7625 | 11.9579 | 0 | 15.2625 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kingseat | Dyce |  | 5.59 / 25 | 57.2679 | -2.175 | NJ 89545 19709 | 5.0 | 0 | 1.22 | 4.66 | 1.7 | 4.52 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Ashgrove | Elgin |  | 3.88 / 13.1 | 57.6424 | -3.3006 | NJ 22458 62130 | 12.5 | 0 | 1.3086 | 8.6055 | 0 | 5.2031 | 100 | Constrained |  |  | Constrained | Replace existing transformer with a 12/24MVA unit and install a 2nd 12/24 MVA transformer | March 2023 | Yes | No | None Known | 33 / 11 | Green
Scotland | Bilbohal | Elgin |  | 4.03 / 13.1 | 57.637 | -3.3285 | NJ 20782 61556 | 24 | 0 | 1.3755 | 4.5541 | 0 | 25.3755 | 100 | Constrained |  |  | Constrained | Install a second 12/24MVA transformer | March 2023 | Yes | No | None Known | 33 / 11 | Green
Scotland | Burghead | Elgin |  | 6.1 / 13.1 | 57.7003 | -3.467 | NJ 12666 68781 | 15 | 0 | 1.9022 | 7.2092 | 0 | 16.9022 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Cumming Street | Elgin |  | 7.94 / 13.1 | 57.6501 | -3.3162 | NJ 21542 63007 | 23 | 0 | 2.9082 | 13.1865 | 0 | 25.9082 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Elgin | Elgin |  | 7.73 / 13.1 | 57.6649 | -3.3215 | NJ 21256 64664 | 10.0 | 0 | 0.58305 | 4.1378 | 0.5 | 10.0831 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Fochabers | Elgin |  | 3.15 / 13.1 | 57.6217 | -3.1093 | NC 94318 95432 | 15 | 0 | 1.878 | 6.9995 | 0.04 | 16.838 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kinloss | Elgin |  | 3.15 / 13.1 | 57.6359 | -3.5644 | NJ 06695 61740 | 15 | 0 | 0.68501 | 3.4239 | 2.398 | 13.287 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lhanbryde | Elgin |  | 5.02 / 20 | 57.6389 | -3.2086 | NJ 27940 61640 | 5.0 | 0 | 0.23754 | 1.7966 | 0.25 | 4.9875 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Lossiemouth | Elgin |  | 6.54 / 13.1 | 57.7125 | -3.2906 | NJ 23203 69923 | 15 | 0 | 2.3126 | 6.726 | 0 | 17.3126 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Fasnakyle | Fasnakyle |  | 0.83 / 16 | 57.3295 | -4.7931 | NH 31948 29998 | 1.0 | 0 | 0.159 | 0.632 | 0.1 | 1.059 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Edzell | Fiddes |  | 2.61 / 16 | 56.8247 | -2.5996 | NO 63500 70513 | 8 | 0 | 0.42737 | 2.9062 | 0.55 | 7.8774 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Inverbervie | Fiddes |  | 4.55 / 16 | 56.8475 | -2.2828 | NO 82850 72935 | 8 | 0 | 1.51 | 4.62 | 4.7 | 4.81 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Laurencekirk | Fiddes |  | 4.18 / 25 | 56.8298 | -2.4782 | NO 70915 71028 | 15 | 0 | 1.088 | 5.4644 | 2.39 | 3.698 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Stonehaven | Fiddes |  | 7.22 / 25 | 56.9618 | -2.2334 | NO 85903 85641 | 24 | 0 | 1.615 | 10.7348 | 4.15 | 24.815 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Aberchalder | Fort Augustus |  | NA | 57.0931 | -4.744 | NH 33843 03575 | 0.2 | 0 | 0.0167 | 0.067 | 0 | 0.1497 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Bunoich | Fort Augustus |  | NA | 57.1491 | -4.685 | NH 37662 09672 | 2 | 0 | 0.042825 | 0.35034 | 0 | 2.0428 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Glen Laogh | Fort Augustus |  | NA | 57.0668 | -4.8479 | NH 27430 00910 | 0.1 | 0 | 0.005 | 0.01 | 0 | 0.105 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Glendoe | Fort Augustus |  | 3.25 / 25 | 57.143 | -4.6449 | NH 40060 08894 | 15 | 0 | 0.009 | 0.992 | 0 | 15.009 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Invergarry | Fort Augustus |  | 0.73 / 5.2 | 57.0685 | -4.8079 | NH 29862 01000 | 0.5 | 0 | 0.2 | 0.546 | 0.499 | 0.201 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Markethill | Fort Augustus |  | NA | 57.1371 | -4.6871 | NH 37481 08337 | 1.0 | 0 | 0.051937 | 0.22183 | 0 | 1.0519 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Annat | Fort William |  | 4.16 / 25 | 56.8426 | -5.1421 | NN 08452 76751 | 5.0 | 0 | 0.66826 | 3.7832 | 0.25 | 1.8851 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Arisaig | Fort William |  | 0.99 / 13.1 | 56.9119 | -5.8363 | NM 66564 86619 | 2.5 | 0 | 0.10815 | 0.78991 | 0 | 1.8182 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Corran | Fort William |  | 1.4 / 13.1 | 56.7179 | -5.2282 | NN 02545 63126 | 2.5 | 0 | 0.42 | 1.54 | 0.25 | 2.67 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Glensanda | Fort William |  | 3.67 / 25 | 56.5708 | -5.5392 | NM 82677 47699 | 15 | 0 | 0.481 | 4.989 | 0 | 15.481 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Glenuig | Fort William |  | NA | 56.8271 | -5.8168 | NM 67224 77119 | 0.1 | 0 | 0.0155 | 0.062 | 0 | 0.1155 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Inverlochy | Fort William |  | 8.36 / 25 | 56.8281 | -5.0884 | NN 11653 74987 | 15 | 0 | 2.8032 | 10.395 | 6.763 | 11.0402 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kingairloch | Fort William |  | NA | 56.6483 | -5.6405 | NM 76917 56652 | 0.1 | 0 | 0.015 | 0.06 | 0.1 | 0.015 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Kinlochmoidart | Fort William |  | NA | 56.7841 | -5.7439 | NM 71407 72091 | 0.1 | 0 | 0.03 | 0.122 | 1.45 | 0 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Liddesdale | Fort William |  | NA | 56.6743 | -5.6234 | NM 78116 59480 | 0.1 | 0 | 0.005 | 0.02 | 0 | 0.105 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Lochaline | Fort William |  | NA | 56.5435 | -5.7765 | NM 67939 45444 | 6.5 | 0 | 0.095 | 0.447 | 0.87 | 5.725 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Mallaig | Fort William |  | 1.61 / 13.1 | 56.9859 | -5.8263 | NM 67637 94811 | 8 | 0 | 0.19119 | 1.7521 | 0.8 | 7.3912 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Pinegrove | Fort William |  | 7.51 / 13.1 | 56.8148 | -5.1062 | NN 10496 73556 | 10.0 | 0 | 1.7277 | 6.4108 | 0 | 11.7277 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Poor House | Fort William |  | NA | 56.7668 | -5.7363 | NM 71766 70148 | 0.1 | 0 | 0.007 | 0.03 | 0 | 0.107 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Rahoy | Fort William |  | NA | 56.5782 | -5.7526 | NM 69621 49222 | 0.1 | 0 | 0.01 | 0.048 | 0.3 | 0.11 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Salen, Mull | Fort William |  | 2.06 / 13.1 | 56.724 | -5.7773 | NM 69002 65519 | 2.5 | 0 | 0.47 | 3.7 | 0.665 | 2.48 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Shona Beag | Fort William |  | NA | 56.8023 | -5.8151 | NM 67173 74363 | 0.1 | 0 | 0.012 | 0.047 | 0 | 0.112 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Strontian | Fort William |  | 1.28 / 13.1 | 56.6981 | -5.5701 | NM 81521 61955 | 2.5 | 0 | 0.033994 | 0.80365 | 0.1 | 2.534 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Fraserburgh | Fraserburgh |  | 10.46 / 25 | 57.6865 | -2.0242 | NH 51502 69028 | 40 | 0 | 5.5734 | 20.6135 | 3.6 | 41.9734 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Overgate | Glenagnes |  | NA | 56.4597 | -2.9747 | NO 40033 30155 | 42 | 0 | 8.14 | 21.05 | 3 | 47.14 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Walton | Glenagnes |  | NA | 56.4612 | -2.9916 | NO 38995 30333 | 24 | 0 | 1.374 | 6.7297 | 0.045 | 25.374 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Achiltibuie | Grudie Bridge |  | 0.62 / 8 | 58.0307 | -5.3615 | NC 01618 09557 | 1.0 | 0 | 0.10938 | 0.57229 | 0.42 | 0.53709 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Aultbea | Grudie Bridge |  | 1.48 / 25 | 57.8388 | -5.5823 | NG 87458 88885 | 6.0 | 0 | 0.37733 | 1.7604 | 3.645 | 4.617 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Conon Falls | Grudie Bridge |  | NA | 57.5795 | -4.6986 | NH 38745 57593 | 0.5 | 0 | 0.08 | 0.317 | 0 | 0.58 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Drumrunie | Grudie Bridge |  | NA | 57.999 | -5.1038 | NC 16664 05298 | 0.15 | 0 | 0.0875 | 0.35 | 0 | 0.2375 |  | Constrained |  |  | Constrained | Transformer replacement | March 2024 | Yes | No | None Known | 33 / 11 | Red
Scotland | Garbat Forest | Grudie Bridge |  | NA | 57.6737 | -4.6635 | NH 41255 67993 | 0.1 | 0 | 0.005 | 0.01 | 0 | 0.105 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Inverbroom | Grudie Bridge |  | NA | 57.8144 | -5.0674 | NH 17885 84667 | 0.1 | 0 | 0.0585 | 0.234 | 0 | 0.1585 |  | Constrained |  |  | Constrained | Transformer replacement | March 2024 | Yes | No | None Known | 33 / 11 | Red
Scotland | Kerry Falls | Grudie Bridge |  | NA | 57.6851 | -5.6434 | NG 82909 71978 | 6.0 | 0 | 0.58 | 2.335 | 3.2 | 3.38 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Kinlochewe | Grudie Bridge |  | NA | 57.608 | -5.2871 | NH 03723 62321 | 1.0 | 0 | 0.238 | 0.953 | 0.5 | 0.738 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Letterewe | Grudie Bridge |  | NA | 57.6731 | -5.4637 | NG 93546 70082 | 0.1 | 0 | 0.0015 | 0.006 | 0.1 | 0.0015 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Loch Glascarnoch | Grudie Bridge |  | NA | 57.7061 | -4.8276 | NH 31620 71996 | 0.5 | 0 | 0.005 | 0.01 | 0.3 | 0.205 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Lochcarron | Grudie Bridge |  | NA | 57.4191 | -5.4664 | NG 91944 41839 | 2.5 | 0 | 0.08 | 0.08 | 0 | 2.5 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Lochinver | Grudie Bridge |  | 0.8 / 13.1 | 58.1479 | -5.2383 | NC 09516 22243 | 2.5 | 0 | 0.541 | 2.165 | 0.24 | 2.801 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Minor Grudie | Grudie Bridge |  | NA | 57.6195 | -4.832 | NH 30954 62371 | 0.1 | 0 | 0.005 | 0.02 | 0 | 0.105 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Ullapool | Grudie Bridge |  | 1.16 / 18.4 | 57.9014 | -5.1569 | NH 13018 94588 | 6 | 0 | 0.56964 | 2.596 | 0.1 | 6.5696 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Culloden | Inverness |  | 7.52 / 13.1 | 57.4814 | -4.1492 | NH 71240 45502 | 15 | 0 | 2.9608 | 11.2219 | 0.12 | 17.8408 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dalneigh | Inverness |  | 4.66 / 13.1 | 57.4749 | -4.2435 | NH 65564 44955 | 24 | 0 | 2.2375 | 10.0808 | 0 | 26.2375 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Errogie | Inverness |  | 1.24 / 25 | 57.2734 | -4.3787 | NH 56674 22810 | 0.2 | 0 | 0.05 | 0.209 | 1.25 | 0 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Foyers | Inverness |  | 1.13 / 18.4 | 57.2553 | -4.4925 | NH 49740 21044 | 5.0 | 0 | 0.11 | 0.434 | 0 | 5.11 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Hilton | Inverness |  | 8.37 / 13.1 | 57.4602 | -4.2132 | NH 67326 43262 | 24 | 0 | 2.0527 | 11.2026 | 0 | 26.0527 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Inverarnie | Inverness |  | 1.46 / 13.1 | 57.3862 | -4.1837 | NH 68830 34971 | 2.5 | 0 | 0.029712 | 0.90216 | 0.5 | 2.0297 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Inverness | Inverness |  | 8.54 / 13.1 | 57.4539 | -4.2466 | NH 65302 42625 | 10.0 | 0 | 2.2883 | 7.8002 | 0.43 | 11.8583 | 50 | Unconstrained |  |  | Unconstrained | Replace existing 10MVA units with 7.5/15MVA units | March 2023 | Yes | No | None Known | 33 / 11 | Green
Scotland | Raigmore | Inverness |  | 8.48 / 13.1 | 57.4733 | -4.1956 | NH 68427 44693 | 24 | 0 | 4.5017 | 15.1319 | 0 | 28.5017 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Waterloo Place | Inverness |  | 8.59 / 18.4 | 57.4827 | -4.2317 | NH 66301 45800 | 23 | 0 | 3.4693 | 15.8234 | 0 | 26.4693 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Aberlour | Keith |  | 4.07 / 13.1 | 57.452 | -3.2546 | NJ 24809 40878 | 5.0 | 0 | 1.2822 | 4.7746 | 0.5 | 1.5075 | 50 | Constrained |  |  | Constrained | Aberlour 33kV Circuit Breaker Repalcement - Increase in make and break fault ratings | November 2023 | Yes | No | None Known | 33 / 11 | Amber
Scotland | Buckie | Keith |  | 4.66 / 13.1 | 57.6695 | -2.9523 | NJ 43291 64802 | 24 | 0 | 2.5275 | 10.6649 | 1.5 | 25.0275 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Cullen | Keith |  | 2.71 / 20 | 57.6725 | -2.8133 | NJ 51590 65032 | 5.0 | 0 | 0.5489 | 2.5963 | 0.5 | 5.0489 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dufftown | Keith |  | 4.02 / 13.1 | 57.4427 | -3.1335 | NJ 32060 39722 | 5.0 | 0 | 1.7107 | 4.8687 | 0 | 6.7107 | 50 | Constrained |  |  | Constrained | Dufftown 33kV Circuit Breaker Repalcement - Increase in make and break fault ratings | January 2024 | Yes | No | None Known | 33 / 11 | Green
Scotland | Huntly | Keith |  | 5.39 / 13.1 | 57.4408 | -2.7886 | NJ 52762 39217 | 15 | 0 | 1.5442 | 6.4314 | 2.05 | 14.4942 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Insch | Keith |  | 2.99 / 13.1 | 57.3469 | -2.6148 | NJ 63100 28651 | 7.0 | 0 | 1.0839 | 6.99 | 0.09 | 7.9939 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Keith | Keith |  | 7.53 / 13.1 | 57.5403 | -2.9383 | NJ 43925 50405 | 15 | 0 | 1.54 | 6.5 | 1.98 | 14.56 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Limehillocks | Keith |  | 1.72 / 12.5 | 57.5439 | -2.802 | NJ 52093 50703 | 2.5 | 0 | 0.14183 | 1.6511 | 2.409 | 0.23283 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Marnoch | Keith |  | 4.26 / 13.1 | 57.5655 | -2.6376 | NJ 61955 53001 | 5.0 | 0 | 0.3866 | 2.6973 | 5.178 | 0.2086 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Rothes | Keith |  | 4.16 / 13.1 | 57.5316 | -3.2057 | NJ 27901 49693 | 5.0 | 0 | 1.0401 | 4.4564 | 0 | 6.0401 | 50 | Constrained |  |  | Constrained | Rothes 11kV & 33kV Switchgear Replacement - Increase in make and break fault ratings | March 2024 | Yes | No | None Known | 33 / 11 | Green
Scotland | Cashlie | Killin |  | NA | 56.5475 | -4.4299 | NN 50711 42144 | 1.0 | 0 | 0 | 0.222 | 0.275 | 0.725 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Coshieville | Killin |  | NA | 56.6139 | -4.0026 | NN 77193 48683 | 2.5 | 0 | 0.16058 | 1.9412 | 1.3 | 1.3606 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Killin Town | Killin |  | 1.69 / 13.1 | 56.4643 | -4.3237 | NN 56931 32662 | 2.5 | 0 | 0.21707 | 1.07 | .1 | 2.6171 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Kingshouse | Killin |  | NA | 56.6482 | -4.8345 | NN 26312 54302 | 0.3 | 0 | 0 | 0.03 | 0 | 0.3 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Loch Lubnaig | Killin |  | NA | 56.2951 | -4.3049 | NN 57455 13800 | 0.1 | 0 | 0 | 0.03 | 0 | 0.1 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Lochearnhead | Killin |  | 1.97 / 13.1 | 56.3887 | -4.2893 | NN 58766 24177 | 4.0 | 0 | 0.20004 | 1.4458 | 2.35 | 1.85 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Wester Drummond | Killin |  | NA | 56.5775 | -4.0827 | NN 72155 44784 | 0.1 | 0 | 0.02 | 0.081 | 0 | 0.12 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Glencoe | Kinlochleven |  | 2.72 / 13.1 | 56.6824 | -5.0927 | NN 10658 58797 | 6.25 | 0 | 0.35569 | 2.4004 | 0.5 | 6.1057 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kinlochleven | Kinlochleven |  | NA | 56.7146 | -4.9543 | NN 19285 62002 | 2.5 | 0 | 0.27489 | 1.39 | 7.1 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Banchory | Kintore |  | 5.55 / 25 | 57.0567 | -2.5084 | NO 69262 96297 | 14.0 | 0 | 2.4349 | 11.338 | 0.1 | 5.0968 | 50 | Constrained |  |  | Constrained | Reinforcement of network and instalation of 150A 2no Tank Regulator to alleviate voltage constraints | March 2023 | Yes | No | None Known | 33 / 11 | Green
Scotland | Fyvie | Kintore |  | 6.21 / 12.5 | 57.4285 | -2.3887 | NJ 76759 37635 | 5.0 | 0 | 0.5 | 5.3 | 7.95 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Inverurie | Kintore |  | 10.52 / 25 | 57.2852 | -2.4053 | NJ 75665 21688 | 28 | 0 | 4.48 | 15.4 | 1.84 | 30.64 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kemnay | Kintore |  | 6.58 / 13.1 | 57.2412 | -2.446 | NJ 73180 16804 | 15 | 0 | 0.60869 | 3.5882 | 0 | 15.6087 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Methlick | Kintore |  | 3.38 / 13.1 | 57.4216 | -2.2458 | NJ 85339 36835 | 5.0 | 0 | 0.25372 | 2.17 | 4.026 | 1.2277 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Midmar | Kintore |  | 2.34 / 21 | 57.1517 | -2.5264 | NJ 68253 06875 | 5.0 | 0 | 0.26872 | 2.9508 | 3.975 | 1.2937 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Oldmeldrum | Kintore |  | 4.5 / 13.1 | 57.3364 | -2.3063 | NJ 81659 27360 | 8 | 0 | 0.77248 | 5.47 | 2.6 | 6.1725 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Park | Kintore |  | 3.34 / 20 | 57.0854 | -2.3463 | NO 79107 99434 | 6.0 | 0 | 0.42 | 2.2807 | 0 | 6.42 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Skene | Kintore |  | 7.49 / 25 | 57.149 | -2.2958 | NJ 82203 06495 | 30 | 0 | 3.1402 | 14.8545 | 0.45 | 32.6902 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Torryburn | Kintore |  | 9.43 / 13.1 | 57.2311 | -2.3473 | NJ 79129 15653 | 24 | 0 | 1.8944 | 9.7513 | 8.65 | 17.7944 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lairg | Lairg |  | 1.71 / 13.1 | 58.0306 | -4.3928 | NC 58798 07111 | 2.5 | 0 | 0.23 | 1.45 | 0.1 | 2.63 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Torboll | Lairg |  | NA | 57.9745 | -4.1019 | NC 75779 00296 | 0.1 | 0 | 0 | 0.02 | 0 | 0.1 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Tressady | Lairg |  | NA | 58.0034 | -4.1923 | NC 70537 03678 | 0.5 | 0 | 0.18 | 0.71 | 0.045 | 0.68 |  | Constrained |  |  | Constrained | Transformer replacement | March 2024 | Yes | No | None Known | 33 / 11 | Red
Scotland | Friokheim | Lunanhead |  | 2.84 / 16 | 56.6339 | -2.6727 | NO 58834 49317 | 5.0 | 0 | 0.79761 | 3.4336 | 3.59 | 2.2076 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Inverarity | Lunanhead |  | 1.69 / 13.1 | 56.5864 | -2.9044 | NO 44549 44200 | 5.0 | 0 | 0.072908 | 0.77015 | 0.7 | 4.3729 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Lochside | Lunanhead |  | 8.01 / 20 | 56.6435 | -2.896 | NO 45151 50548 | 24 | 0 | 4.9037 | 15.379 | 0.08 | 28.8237 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lunanhead | Lunanhead |  | 8.22 / 13.1 | 56.6544 | -2.8654 | NO 47042 51733 | 10.0 | 0 | 1.663 | 11.47 | 10.54 | 1.123 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Maryton | Lunanhead |  | 6.44 / 13.1 | 56.6655 | -2.9935 | NO 39206 53075 | 15 | 0 | 1.1123 | 7.2081 | 2.206 | 13.9063 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lochee | Lyndhurst |  | 7.79 / 13.1 | 56.4708 | -3.0069 | NO 38065 31416 | 23 | 0 | 1.02 | 6.36 | 0 | 24.02 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lyndhurst | Lyndhurst |  | 7.87 / 20 | 56.4811 | -3.0174 | NO 37434 32575 | 10.0 | 0 | 1.207 | 5.4574 | 0 | 11.207 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | MacAlpine Road | Lyndhurst |  | 7.84 / 13.1 | 56.4912 | -3.0079 | NO 38034 33691 | 15 | 0 | 1.86 | 7.84 | 0.424 | 16.436 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | West Kirkton | Lyndhurst |  | 7.84 / 13.1 | 56.4923 | -2.9891 | NO 39194 33796 | 23 | 0 | 1.6384 | 9.9495 | 0.1 | 24.5384 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | MacDuff | MacDuff |  | NA | 57.6641 | -2.4984 | NJ 70363 63908 | 24 | 0 | 2.2294 | 10.4797 | 77.28 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Portsoy | MacDuff |  | NA | 57.6733 | -2.6976 | NJ 58491 65037 | 5.0 | 0 | 0.48047 | 2.1258 | 1.543 | 3.9375 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Turriff | MacDuff |  | NA | 57.5417 | -2.4626 | NJ 72407 50271 | 15 | 0 | 1.8843 | 11.1 | 11.268 | 10.8813 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Ashludie | Milton of Craigie |  | 6.44 / 13.1 | 56.4916 | -2.8263 | NO 49222 33584 | 10.0 | 0 | 2.4484 | 9.5671 | 2.06 | 2.8812 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Baldovie | Milton of Craigie |  | 8.59 / 13.1 | 56.4782 | -2.89 | NO 45279 32147 | 24 | 0 | 1.9213 | 13.2204 | 4.429 | 12.7009 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Broughty Ferry | Milton of Craigie |  | 7.97 / 13.1 | 56.4659 | -2.8673 | NO 46658 30758 | 10.0 | 0 | 1.92 | 8.56 | 0.05 | 11.87 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Edzell Street | Milton of Craigie |  | 4.21 / 13.1 | 56.4778 | -2.8604 | NO 47103 32070 | 10.0 | 0 | 0.42737 | 2.9062 | 0 | 10.4274 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Longhaugh | Milton of Craigie |  | 7.87 / 13.1 | 56.4927 | -2.9311 | NO 42768 33789 | 23 | 0 | 2.1607 | 8.8257 | 6.098 | 19.0627 | 50 | Unconstrained |  |  | Unconstrained | Transformer replacement | March 2023 | Yes | No | None Known | 33 / 11 | Green
Scotland | Milton of Craigie | Milton of Craigie |  | 8.8 / 18.4 | 56.4754 | -2.9247 | NO 43137 31857 | 24 | 0 | 0.3386 | 10.3498 | 8.7 | 15.6386 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Old Craigie Road | Milton of Craigie |  | 7.78 / 13.1 | 56.4777 | -2.9407 | NO 42156 32130 | 10.0 | 0 | 1.9377 | 7.0806 | 0 | 11.9377 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Bettyhill | Mybster |  | NA | 58.5237 | -4.2208 | NC 70763 61645 | 2.5 | 0 | 0.1818 | 0.89867 | 0.09 | 2.5918 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Coldbackie | Mybster |  | NA | 58.5026 | -4.3667 | NC 62182 59590 | 2.5 | 0 | 0.16254 | 0.76313 | 0.181 | 2.4815 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Latheron | Mybster |  | 2.15 / 18.4 | 58.284 | -3.3672 | ND 19924 33627 | 6.25 | 0 | 0.58979 | 2.1329 | 3.677 | 3.1628 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Melvich | Mybster |  | NA | 58.5522 | -3.9169 | NC 88547 64274 | 1.0 | 0 | 0.1266 | 0.92996 | 0 | 1.1266 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Wick | Mybster |  | 5.63 / 13.1 | 58.4421 | -3.1051 | ND 35583 50947 | 24 | 0 | 2.3077 | 9.0469 | 2.116 | 24.7377 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Arderseir | Nairn |  | 4.85 / 13.1 | 57.5773 | -4.0004 | NH 80475 55905 | 5.0 | 0 | 0.47562 | 2.2675 | 0 | 3.2082 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Dalcross | Nairn |  | 6.9 / 12.5 | 57.5398 | -4.0675 | NH 76333 51847 | 15 | 0 | 4.6514 | 8.1914 | 1.474 | 18.1774 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Forres | Nairn |  | 5.58 / 13.1 | 57.6144 | -3.6193 | NJ 03362 59425 | 15 | 0 | 2.2869 | 9.2098 | 0.925 | 16.3619 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lethen | Nairn |  | 1.58 / 18.4 | 57.5344 | -3.8004 | NH 92307 50795 | 2.5 | 0 | 0.36408 | 1.4292 | 0.191 | 2.6731 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Nairn Central | Nairn |  | 7.78 / 13.1 | 57.5829 | -3.8665 | NH 88496 56295 | 15 | 0 | 1.9961 | 10.2091 | 0 | 16.9961 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Bridge of Don | Persley |  | 8.85 / 13.1 | 57.1824 | -2.0987 | NJ 94130 10184 | 24 | 0 | 2.9122 | 16.3113 | 3.86 | 23.0522 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Haudagain | Persley |  | 7.91 / 13.1 | 57.1723 | -2.1435 | NJ 91425 09066 | 23 | 0 | 1.9511 | 7.0296 | 8.1 | 16.8511 | 50 | Unconstrained |  |  | Unconstrained | Upgrade existing transformers to 12/24 units | May 2022 | Yes | No | None Known | 33 / 11 | Green
Scotland | Northfield | Persley |  | 7.66 / 13.1 | 57.166 | -2.1549 | NJ 90728 08364 | 15 | 0 | 0.80776 | 5.6648 | 0 | 15.8078 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | St Machar | Persley |  | 8.16 / 18.4 | 57.1637 | -2.1077 | NJ 93584 08102 | 24 | 0 | 1.4551 | 8.52 | 2.135 | 23.4051 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Stoneywood Mills T3 | Persley |  | NA | 57.1904 | -2.1789 | NJ 89285 11082 | 1 | 0 | 1 | 14.376 | 0 | 0 |  | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Stoneywood T1 T2 | Persley |  | 7.91 / 18.4 | 57.1904 | -2.1789 | NJ 89285 11082 | 24 | 0 | 1.956 | 10.67 | 12 | 13.956 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Whitestripes | Persley |  | 7.88 / 13.1 | 57.1902 | -2.1199 | NJ 92850 11054 | 15 | 0 | 1.5731 | 7.334 | 0.164 | 16.4091 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Peterhead Grange | Peterhead Grange |  | 9.73 / 13.1 | 57.5087 | -1.8058 | NK 11738 46516 | 24 | 0 | 3.3594 | 14.0875 | 0.85 | 26.5094 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Boddam | Peterhead Shell |  | NA | 57.4727 | -1.7979 | NK 12219 42512 | 15 | 0 | 1.2842 | 6.5249 | 0 | 16.2842 | 100 | Unconstrained |  |  | Unconstrained | Reinforcment of underground cable | August 2022 | Yes | No | None Known | 33 / 11 | Green
Scotland | Arigh-na-Brodaig | Port Ann |  | NA | 55.9184 | -5.4287 | NR 85849 74792 | 0.1 | 0 | 0.01 | 0.07 | 0 | 0.04 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Bowmore | Port Ann |  | 2.31 / 13.1 | 55.7608 | -6.2733 | NR 32021 60211 | 8 | 0 | 0.69133 | 3.1094 | 6.445 | 2.2463 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Crinan | Port Ann |  | 1.09 / 8 | 56.073 | -5.5426 | NR 79620 92347 | 1.0 | 0 | 0.25 | 1.05 | 1 | 0.25 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Furnace Quarry | Port Ann |  | 1.39 / 13.1 | 56.1517 | -5.1767 | NS 02783 99996 | 2.5 | 0 | 0 | 0.37 | 0 | 2.5 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Inverneil | Port Ann |  | 1.53 / 18.4 | 55.9698 | -5.4502 | NR 84790 80580 | 2.5 | 0 | 0.012254 | 1.5285 | 0.66 | 1.8523 | 100 | Constrained |  |  | Constrained | Inverneil Primary Transformer Replacement | March 2023 | Yes | No | None Known | 33 / 11 | Amber
Scotland | Lochgilphead | Port Ann |  | 7.36 / 13.1 | 56.0403 | -5.4356 | NR 86092 88371 | 8 | 0 | 0.61 | 9.57 | 33.891 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Lussagiven | Port Ann |  | NA | 56.0156 | -5.7967 | NR 63461 86798 | 0.1 | 0 | 0.01 | 0.036 | 0 | 0.11 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Port Askaig | Port Ann |  | NA | 55.8434 | -6.1216 | NR 42082 68818 | 2.5 | 0 | 0.37517 | 1.2211 | 0.05 | 2.8252 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Port Ellen | Port Ann |  | 1.05 / 18.4 | 55.6315 | -6.1886 | NR 36459 45513 | 4.0 | 0 | 0.67 | 2.68 | 0.33 | 4.34 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Stonefield | Port Ann |  | NA | 55.9061 | -5.4213 | NR 86244 73400 | 0.3 | 0 | 0.001 | 0.03 | 0 | 0.301 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Tarbert, Jura | Port Ann |  | NA | 55.9726 | -5.8391 | NR 60552 82166 | 0.2 | 0 | 0.01 | 0.04 | 1.45 | 0.21 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Tarbert, Loch Fyne | Port Ann |  | 2.09 / 25 | 55.8618 | -5.4212 | NR 86003 68479 | 6.0 | 0 | 0.42 | 3.196 | 1.55 | 4.87 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Quoich | Quoich |  | NA | 57.0695 | -5.1077 | NH 11700 01900 | 1 | 0 | 0 | 0 | 3.45 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Blackmount | Rannoch |  | NA | 56.5338 | -4.7647 | NN 30077 41404 | 0.1 | 0 | 0.01 | 0.04 | 0 | 0.11 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Bridge of Gaur | Rannoch |  | 0.42 / 6 | 56.6877 | -4.4395 | NN 50676 57767 | 1.0 | 0 | 0.04 | 0.46 | 0.45 | 0.59 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Glen Etive | Rannoch |  | NA | 56.6533 | -4.8424 | NN 25850 54886 | 0.3 | 0 | 0.05 | 0.04 | 0 | 0.35 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Tyndrum | Rannoch |  | 1.31 / 20 | 56.4402 | -4.7122 | NN 32894 30860 | 2.5 | 0 | 0.23 | 1.88 | 1.35 | 1.38 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Kincorth | Redmoss |  | 8.05 / 13.1 | 57.1202 | -2.0934 | NJ 94445 03252 | 12.5 | 0 | 2.7567 | 11.7448 | 0 | 15.2567 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Newtonhill | Redmoss |  | 6.37 / 13.1 | 57.0339 | -2.1633 | NO 90190 93653 | 15 | 0 | 3.1803 | 12.5817 | 2.9 | 15.2803 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Redmoss | Redmoss |  | 10.46 / 25 | 57.1082 | -2.0914 | NJ 94562 01919 | 24 | 0 | 5 | 17.9429 | 0.088 | 29 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Gledfield | Shin |  | 1.61 / 18.4 | 57.8846 | -4.3818 | NH 58876 90837 | 2.5 | 0 | 0.29474 | 1.5778 | 0 | 2.7947 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Shin | Shin |  | NA | 57.9435 | -4.4132 | NH 57246 97463 | 2.5 | 0 | 0.1 | 0.39 | 0 | 2.6 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Sloy | Sloy |  | NA | 56.2511 | -4.7117 | NN 32095 09816 | 8 | 0 | 0.66 | 3.55 | 7.307 | 7.665 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Comrie | St Fillans |  | NA | 56.378 | -3.9952 | NN 76887 22417 | 0.1 | 0 | 0.008 | 0.03 | 0 | 0.108 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Dalchonzie | St Fillans |  | 2.32 / 25 | 56.3728 | -4.0404 | NN 74079 21921 | 6.0 | 0 | 0.35809 | 2.0356 | 0 | 6.3581 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Arnish | Stornoway |  | 4.68 / 25 | 58.1873 | -6.3861 | NB 42300 30440 | 5.0 | 0 | 0.002 | 0.02 | 0 | 4.982 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Barvas | Stornoway |  | 2.01 / 18.4 | 58.3485 | -6.5205 | NB 35613 48891 | 2 | 0 | 0.36917 | 2.8003 | 0.33 | 2.0392 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Battery Point | Stornoway |  | 9.73 / 13.1 | 58.2034 | -6.3737 | NB 43147 32182 | 16 | 0 | 2.7558 | 13.467 | 3.455 | 15.3008 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Callanish | Stornoway |  | 1.71 / 18.4 | 58.2028 | -6.7332 | NB 22040 33554 | 2.5 | 0 | 0.33302 | 2.1861 | 1.4 | 1.433 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Coll | Stornoway |  | 1.75 / 13.1 | 58.2775 | -6.3083 | NB 47510 40182 | 6.0 | 0 | 0.091712 | 2.0277 | 0.9 | 5.1917 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Gisla | Stornoway |  | 0.75 / 25 | 58.1278 | -6.8796 | NB 12846 25823 | 1.0 | 0 | 0.2 | 0.65 | 0.7 | 0.5 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Harris Grid | Stornoway |  | NA | 57.8456 | -6.8303 | NG 13495 94249 | 30.0 | 0 | 0 | 0 | 0 | 30 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Laxay | Stornoway |  | 1.36 / 18.4 | 58.1058 | -6.5269 | NB 33424 21925 | 2.5 | 0 | 0.25539 | 1.6878 | 0.05 | 2.7054 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Maaruig | Stornoway |  | NA | 57.9574 | -6.7494 | NB 19162 06332 | 0.2 | 0 | 0.02 | 0.1 | 0 | 0.22 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Stornoway Grid | Stornoway |  | NA | 58.2033 | -6.4228 | NB 40261 32368 | 30.0 | 0 | 0 | 0 | 4.5 | 25.5 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Aberfoyle | Strathleven |  | 2.92 / 13.1 | 56.1673 | -4.3655 | NS 53215 99705 | 3.5 | 0 | 0.47664 | 2.8755 | 1.6 | 1.1011 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Blairlinnans | Strathleven |  | 1.56 / 13.1 | 56.0324 | -4.558 | NS 40709 85121 | 2.5 | 0 | 0.044786 | 0.336 | 0.2 | 2.3448 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Drymen | Strathleven |  | 3.07 / 13.1 | 56.061 | -4.4349 | NS 48494 88026 | 6.0 | 0 | 0.58465 | 2.676 | 1.15 | 5.4347 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kepculloch | Strathleven |  | 5.05 / 13.1 | 56.0948 | -4.3506 | NS 53864 91598 | 6.25 | 0 | 0.82375 | 3.6738 | 1.09 | 5.9838 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Killearn | Strathleven |  | 2.98 / 13.1 | 56.0505 | -4.3889 | NS 51313 86758 | 6.25 | 0 | 0.41637 | 1.9924 | 0.1 | 6.5664 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Hatton | Strichen |  | 3.96 / 13.1 | 57.4264 | -1.8944 | NK 06441 37348 | 5.0 | 0 | 0.67214 | 3.0998 | 0.61 | 5.0621 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Maud | Strichen |  | 6.15 / 13.1 | 57.5175 | -2.1264 | NJ 92528 47491 | 8 | 0 | 0.42 | 3.37 | 2.525 | 5.895 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Mintlaw | Strichen |  | 6.95 / 13.1 | 57.5281 | -1.9867 | NK 00897 48662 | 15 | 0 | 1 | 6.9 | 3.713 | 12.287 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | New Pitsligo | Strichen |  | 3.02 / 13.1 | 57.5836 | -2.1935 | NJ 88529 54853 | 2.5 | 0 | 0.042255 | 1.9719 | 2.88 | 0 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Strichen | Strichen |  | 9.06 / 13.1 | 57.5863 | -2.0702 | NJ 95900 55137 | 15 | 0 | 0.011518 | 3.1334 | 9.088 | 10.2115 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Aboyne | Tarland |  | 5.06 / 25 | 57.077 | -2.7926 | NO 52048 98716 | 15 | 0 | 1.1641 | 6.9324 | 0.211 | 9.2318 | 50 | Unconstrained |  |  | Unconstrained | Establish a new 8MVA 33/11kV primary in the Ruthven area | March 2023 | Yes | No | None Known | 33 / 11 | Green
Scotland | Ballater | Tarland |  | 4.38 / 16 | 57.061 | -3.0315 | NO 37542 97131 | 15 | 0 | 1.2 | 6.4 | 0.235 | 9.8 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Mossat | Tarland |  | 2.11 / 13.1 | 57.2667 | -2.8726 | NJ 47470 19897 | 2.5 | 0 | 0.25 | 1.8 | 0.225 | 2.525 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Strathdon | Tarland |  | 1.28 / 13.1 | 57.1936 | -3.0384 | NJ 37343 11904 | 2.5 | 0 | 0.115 | 0.901 | 0.165 | 2.45 | 100 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Whitehouse | Tarland |  | 3.98 / 13.1 | 57.2246 | -2.6366 | NJ 61658 15058 | 8 | 0 | 0.91309 | 5.2447 | 2.35 | 8.9131 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Barcaldine | Taynuilt |  | 3.08 / 18.4 | 56.5274 | -5.3127 | NM 96356 42181 | 5.0 | 0 | 0.48536 | 3.5671 | 2.807 | 2.6784 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Bonawe | Taynuilt |  | NA | 56.4506 | -5.2279 | NN 01166 33385 | 0.5 | 0 | 0 | 0.12 | 0 | 0.5 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Connel | Taynuilt |  | 3.45 / 13.1 | 56.4515 | -5.3895 | NM 91213 33970 | 8 | 0 | 0.22523 | 1.5582 | 0.1 | 8.1252 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Dalmally | Taynuilt |  | NA | 56.3985 | -4.9905 | NN 15538 26930 | 0.8 | 0 | 0.06 | 0.644 | 0 | 0.86 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Dervaig (incl Tiree) | Taynuilt |  | NA | 56.582 | -6.1959 | NM 42441 51227 | 8 | 0 | 0.15535 | 3.6947 | 2.8 | 5.3554 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Eredine | Taynuilt |  | NA | 56.2335 | -5.2745 | NM 97142 09376 | 0.2 | 0 | 0.01 | 0.12 | 0 | 0.21 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Kenmore | Taynuilt |  | NA | 56.4561 | -5.242 | NN 00325 34042 | 0.5 | 0 | 0.1 | 0.315 | 0.95 | 0 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Kerrera | Taynuilt |  | NA | 56.3939 | -5.5282 | NM 82340 27997 | 0.3 | 0 | 0.01 | 0.11 | 0 | 0.31 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Kilchrenan | Taynuilt |  | 0.81 / 13.1 | 56.3659 | -5.183 | NN 03495 23835 | 1.0 | 0 | 0.05607 | 0.73525 | 0.35 | 0.70607 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Kilmelford | Taynuilt |  | 1.66 / 25 | 56.2731 | -5.4894 | NM 84056 14437 | 2.5 | 0 | 0.3999 | 2 | 2.85 | 0.049898 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Kilninver | Taynuilt |  | 1.46 / 8 | 56.3427 | -5.512 | NM 83049 22251 | 2.5 | 0 | 0.48 | 1.86 | 0.885 | 2.095 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Kinloch | Taynuilt |  | 0.89 / 13.1 | 56.3722 | -6.0103 | NM 52465 27215 | 2.5 | 0 | 0.30105 | 1.4 | 0 | 2.8011 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Lochdonhead | Taynuilt |  | 0.76 / 18.4 | 56.4445 | -5.6861 | NM 72902 34134 | 1.0 | 0 | 0.3 | 1.15 | 0 | 1.3 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Oban | Taynuilt |  | 6.17 / 20 | 56.4075 | -5.4759 | NM 85643 29338 | 24 | 0 | 7.456 | 13.9578 | 0 | 31.456 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Salen, Acharacle | Taynuilt |  | 1.24 / 13.1 | 56.5148 | -5.9475 | NM 57252 42849 | 2.5 | 0 | 0.053 | 2.11 | 1.23 | 0 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Scammadale | Taynuilt |  | NA | 56.3198 | -5.4912 | NM 84207 19638 | 0.1 | 0 | 0.02 | 0.081 | 0 | 0.12 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Taynuilt | Taynuilt |  | NA | 56.4302 | -5.215 | NN 01856 31079 | 2.5 | 0 | 0.20973 | 1.3991 | 0 | 1.9097 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Tiroran Bridge | Taynuilt |  | NA | 56.3838 | -6.0731 | NM 48666 28729 | 0.1 | 0 | 0.01 | 0.063 | 0 | 0.11 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Burgar Hill | Thurso |  | 3.28 / 13.1 | 59.1165 | -3.1467 | HY 34441 26078 | 8 | 0 | 0.11731 | 1.92 | 6.3 | 1.8173 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Eday | Thurso |  | 0.74 / 13.1 | 59.1852 | -2.7658 | HY 56341 33422 | 1.0 | 0 | 0.01 | 0.21434 | 4.9 | 0 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Flotta | Thurso |  | 2.8 / 13.1 | 58.8333 | -3.1273 | NC 94318 95432 | 8 | 0 | 0.001 | 0.15 | 2 | 6.001 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Forss | Thurso |  | NA | 58.5993 | -3.6774 | ND 02614 69148 | 2.5 | 0 | 0.04832 | 0.60966 | 2.32 | 0.22832 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Halkirk | Thurso |  | 1.66 / 13.1 | 58.5035 | -3.4904 | ND 13246 58223 | 2.5 | 0 | 0.49222 | 2.0788 | 0.9 | 2.0922 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Hastigrow | Thurso |  | 2.5 / 18.4 | 58.5289 | -3.2625 | ND 26576 60773 | 5.0 | 0 | 0.547 | 2.8452 | 0 | 5.547 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Kirkwall | Thurso |  | NA | 58.9824 | -2.9643 | HY 44669 10987 | 24 | 0 | 3.2 | 15.7 | 4.12 | 23.08 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Lyness | Thurso |  | 0.73 / 18.4 | 58.8334 | -3.2082 | ND 30350 94625 | 1.0 | 0 | 0.072414 | 0.72857 | 0.9 | 0.17241 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Mount Pleasant | Thurso |  | 7.26 / 13.1 | 58.5897 | -3.5033 | ND 12706 67832 | 15 | 0 | 1.0196 | 4.9695 | 0 | 16.0196 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | North Hoy | Thurso |  | NA | 58.9038 | -3.2917 | HY 25681 02549 | 0.15 | 0 | 0.05 | 0.117 | 0 | 0.2 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Ormlie | Thurso |  | 7.23 / 18.4 | 58.5855 | -3.5367 | ND 10757 67408 | 15 | 0 | 1.376 | 6.4933 | 0.955 | 15.421 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Rousay | Thurso |  | 1.64 / 13.1 | 59.1582 | -2.9831 | HY 43876 30573 | 1.0 | 0 | 0.02 | 0.3 | 0.9 | 0.12 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Sanday | Thurso |  | 0.71 / 13.1 | 59.207 | -2.6814 | HY 61184 35797 | 1.0 | 0 | 0.080062 | 0.76798 | 0 | 1.0801 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Shapinsay | Thurso |  | 0.74 / 18.4 | 59.0382 | -2.9024 | HY 48313 17148 | 1.0 | 0 | 0.046 | 0.50821 | 0.9 | 0.146 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | St Mary's | Thurso |  | 2.55 / 13.1 | 58.8966 | -2.9221 | HY 46965 01396 | 4.0 | 0 | 0.7 | 2.8 | 1.88 | 2.9 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Stromness | Thurso |  | NA | 58.9744 | -3.2892 | HY 25978 10409 | 8 | 0 | 1.4734 | 5.3009 | 8.2 | 1.5734 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Stronsay | Thurso |  | 0.7 / 13.1 | 59.1285 | -2.6211 | HY 64548 27016 | 1.0 | 0 | 0.010025 | 0.45101 | 0 | 1.01 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Westray | Thurso |  | 1.78 / 25 | 59.2384 | -2.8744 | HY 50213 39413 | 1.0 | 0 | 0.29 | 1.6 | 3.7 | 0 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Aberfeldy | Tummel Bridge |  | 4.09 / 13.1 | 56.6176 | -3.8774 | NN 84889 48876 | 8 | 0 | 0.86684 | 4.96 | 2.449 | 3.9068 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Bonskeid | Tummel Bridge |  | 2.28 / 13.1 | 56.7248 | -3.7842 | NN 90919 60658 | 5.0 | 0 | 0.80954 | 3.8743 | 0.1 | 5.7095 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Calvine | Tummel Bridge |  | NA | 56.7636 | -3.9616 | NN 80186 65270 | 2.5 | 0 | 0.94922 | 1.2279 | 0.52 | 2.9292 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Fincastle | Tummel Bridge |  | NA | 56.7285 | -3.8324 | NN 87976 61147 | 0.1 | 0 | 0.05 | 0.042 | 0 | 0.15 |  | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Kinloch Rannoch | Tummel Bridge |  | NA | 56.6989 | -4.1911 | NN 65927 58500 | 2.5 | 0 | 0.15719 | 1.2313 | 2.05 | 0.60719 | 100 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Red
Scotland | Pitlochry | Tummel Bridge |  | 3.7 / 13.1 | 56.7109 | -3.7045 | NN 95756 58991 | 6.25 | 0 | 0.47644 | 4.6 | 1.489 | 5.2374 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Tummel Bridge | Tummel Bridge |  | NA | 56.7069 | -4.0286 | NN 75906 59080 | 2.5 | 0 | 0.097 | 0.69101 | 0 | 1.847 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | None Known | 33 / 11 | Amber
Scotland | Denburn | Willowdale |  | 8.32 / 18.4 | 57.1479 | -2.1093 | NJ 93484 06342 | 21 | 0 | 4.1066 | 14.6493 | 0 | 25.1066 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Greyfriars | Willowdale |  | 8.21 / 13.1 | 57.1545 | -2.0954 | NJ 94327 07070 | 12.5 | 0 | 1.6556 | 9.5446 | 0 | 14.1556 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Hayton | Willowdale |  | 7.92 / 13.1 | 57.171 | -2.1215 | NJ 92753 08909 | 23 | 0 | 1.5321 | 6.7293 | 1.63 | 22.9021 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | St Nicholas | Willowdale |  | 8.16 / 21.9 | 57.1519 | -2.1051 | NJ 93737 06782 | 12.5 | 0 | 3.1946 | 11.3958 | 0 | 15.6946 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Queens Lane North | Woodhill |  | 7.95 / 18.4 | 57.1432 | -2.1301 | NJ 92224 05823 | 12.5 | 0 | 2.65 | 13.94 | 0 | 15.15 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Springhill | Woodhill |  | 8.1 / 13.1 | 57.1486 | -2.1694 | NJ 89850 06421 | 21 | 0 | 3.2528 | 14.1106 | 0.3 | 23.9528 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green
Scotland | Woodhill | Woodhill |  | 8.31 / 13.1 | 57.1543 | -2.1461 | NJ 91259 07053 | 24 | 0 | 4.5543 | 15.2393 | 1.258 | 28.2913 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None Known | 33 / 11 | Green

## Contracted Generation
Area | Project Name | GSP Parent | BSP Parent | PS Parent | Technology Type | Voltage (kV) | Status | Contracted Capacity (MVA) | Expected Connection Date
Scotland | Abernethy Project 01 | Abernethy |  |  | Wind | 33kV | Connected | 9.949
Scotland | Abernethy Project 02 | Abernethy |  |  | BioGas | 33kV | Connected | 4.4
Scotland | Abernethy Project 03 |  |  | Errol | Wind | 11kV | Connected | 0.45
Scotland | Abernethy Project 04 |  |  | Glendevon | Hydro | 11kV | Connected | 0.434
Scotland | Abernethy Project 05 |  |  | Glendevon | Hydro | LV | Connected | 0.297
Scotland | Abernethy Project 06 |  |  | Milnathort | Wind | LV | Connected | 0.2
Scotland | Abernethy Project 07 |  |  | Milnathort | P.V. | LV | Connected | 0.122
Scotland | Abernethy Project 08 |  |  | Abernethy | Hydro | LV | Connected | 0.1
Scotland | Abernethy Project 09 | Abernethy |  |  | P.V. | LV | Contracted | 9.9 | May 2022
Scotland | Abernethy Project 10 | Abernethy |  |  | P.V. | LV | Connected | 9.9
Scotland | Abernethy Project 11 | Abernethy |  |  | P.V. | LV | Contracted | 9.9 | May 2022
Scotland | Abernethy Project 12 |  |  | Milnathort | BioGas | LV | Connected | 0.8
Scotland | Abernethy Project 13 |  |  | Milnathort | Wind | LV | Connected | 0.8
Scotland | Abernethy Project 14 |  |  | Milnathort | Wind | LV | Connected | 0.5
Scotland | Abernethy Project 15 |  |  | Milnathort | Hydro | 11kV | Connected | 0.5
Scotland | Abernethy Project 16 |  |  | Balbeggie | Wind | 33kV | Connected | 0.5
Scotland | Abernethy Project 17 | Abernethy |  |  | Hydro | 33kV | Connected | 0.316
Scotland | Abernethy Project 18 | Abernethy |  |  | P.V. | 33kV | Connected | 0.25
Scotland | Abernethy Project 19 | Abernethy |  |  | Wind | 11kV | Connected | 0.18
Scotland | Abernethy Project 20 |  |  | Perth Harbour | CHP | LV | Connected | 0
Scotland | Abernethy Project 21 |  |  | Milnathort | P.V. | 33kV | Connected | 0.05
Scotland | Abernethy Project 22 | Abernethy |  |  | Other | 33kV | Contracted | 30 | October 2022
Scotland | Abernethy Project 23 | Abernethy |  |  | Other | LV | Contracted | 19 | March 2022
Scotland | Abernethy Project 24 |  |  | Errol | P.V. | 33kV | Connected | 0.02
Scotland | Abernethy Project 25 | Abernethy |  |  | Wind | LV | Connected | 7.05
Scotland | Abernethy Project 26 |  |  | Glendevon | Hydro | LV | Connected | 0.075
Scotland | Abernethy Project 27 |  |  | Glendevon | Photovoltaic | LV | Connected | 0.05
Scotland | Abernethy Project 28 |  |  | Milnathort | Photovoltaic | 33kV | Contracted | 0.06 | March 2022
Scotland | Abernethy Project 29 | Abernethy |  |  | Wind | LV | Contracted | 2.35 | October 2022
Scotland | Abernethy Project 30 |  |  | Glendevon | Photovoltaic | LV | Contracted | 0.11 | March 2022
Scotland | Abernethy Project 31 | Abernethy |  |  | Battery | 33kV | Contracted | 49.9 | May 2025
Scotland | Abernethy Project 32 | Abernethy |  |  | Battery | 33kV | Contracted | 15 | December 2024
Scotland | Abernethy Project 33 | Abernethy |  |  | Battery | 33kV | Contracted | 30 | Jan 26
Scotland | Abernethy Project 34 | Abernethy |  |  | Biomass | 33kV | Contracted | 9.9 | October 26
Scotland | Abernethy Project 35 | Abernethy |  |  | Battery | 33kV | Contracted | 50 | Jan 27
Scotland | Alness Project 01 | Alness |  |  | Wind | 33kV | Connected | 32
Scotland | Alness Project 02 | Alness |  |  | Wind | 33kV | Connected | 29
Scotland | Alness Project 03 | Alness |  |  | Wind | 33kV | Connected | 18.5
Scotland | Alness Project 04 | Alness |  |  | Biomass | 11kV | Connected | 4.95
Scotland | Alness Project 05 |  |  | Invergordon | Wind | 33kV | Connected | 4.8
Scotland | Alness Project 06 | Alness |  |  | Wind | 33kV | Connected | 4.6
Scotland | Alness Project 07 | Alness |  |  | Hydro | 33kV | Connected | 4
Scotland | Alness Project 08 | Alness |  |  | Biomass | 11kV | Connected | 2
Scotland | Alness Project 09 |  |  | Invergordon | Wind | LV | Connected | 0.1
Scotland | Alness Project 10 |  |  | Balaldie | Other | 11kV | Connected | 0.08
Scotland | Alness Project 11 |  |  | Tain | Wind | 11kV | Connected | 0.57
Scotland | Alness Project 12 |  |  | Tain | Wind | 11kV | Connected | 0.33
Scotland | Alness Project 13 |  |  | Glastullich | Hydro | 11kV | Connected | 0.096
Scotland | Alness Project 14 |  |  | Glastullich | Wind | 33kV | Connected | 30
Scotland | Alness Project 15 | Alness |  |  | Photovoltaic | LV | Connected | 0.05
Scotland | Alness Project 16 |  |  | Invergordon | Photovoltaic | LV | Connected | 0.05
Scotland | Alness Project 17 |  |  | Tain | Photovoltaic | LV | Connected | 0.05
Scotland | Alness Project 18 | Alness |  |  | Wind | 33kV | Contracted | 36 | March 2024
Scotland | Alness Project 19 | Alness |  |  | Battery | 33kV | Contracted | 50 | November 2025
Scotland | Alness Project 20 | Alness |  |  | Battery | 33kV | Contracted | 49.9 | December 2025
Scotland | Arbroath Project 01 | Arbroath |  |  | Wind | 11kV | Connected | 0.33
Scotland | Arbroath Project 02 |  |  | Redford | P.V. | LV | Connected | 0.26
Scotland | Arbroath Project 03 |  |  | Charles Avenue | Wind | 11kV | Connected | 0.225
Scotland | Arbroath Project 04 |  |  | Redford | P.V. | LV | Connected | 0.24
Scotland | Arbroath Project 05 |  |  | Carnoustie | P.V. | LV | Connected | 0.158
Scotland | Arbroath Project 06 |  |  | Redford | BioGas | 11kV | Connected | 0.15
Scotland | Arbroath Project 07 |  |  | Elliot Depot | Gas | LV | Connected | 0.125
Scotland | Arbroath Project 08 |  |  | Charles Avenue | Wind | LV | Connected | 0.1
Scotland | Arbroath Project 09 |  |  | Hume Street | Wind | LV | Connected | 0.1
Scotland | Arbroath Project 10 |  |  | Redford | P.V. | LV | Connected | 0.081
Scotland | Arbroath Project 11 |  |  | Redford | P.V. | 11kV | Connected | 0.08
Scotland | Arbroath Project 12 |  |  | Hume Street | P.V. | LV | Connected | 0.065
Scotland | Arbroath Project 13 |  |  | Hume Street | P.V. | 33kV | Connected | 5
Scotland | Arbroath Project 14 | Arbroath |  |  | P.V. | 33kV | Connected | 9.5
Scotland | Arbroath Project 15 | Arbroath |  |  | Wind | 11kV | Connected | 0.5
Scotland | Arbroath Project 16 |  |  | Redford | AD | 33kV | Connected | 0.499
Scotland | Arbroath Project 17 | Arbroath |  |  | P.V. | LV | Connected | 0.05
Scotland | Arbroath Project 18 |  |  | Redford | P.V. | 33kV | Connected | 4.99
Scotland | Arbroath Project 19 | Arbroath |  |  | P.V. | LV | Connected | 0.15
Scotland | Arbroath Project 20 |  |  | Hume Street | P.V. | LV | Connected | 0.05
Scotland | Arbroath Project 21 |  |  | Carnoustie | P.V. | LV | Connected | 0.05
Scotland | Arbroath Project 22 |  |  | Redford | AD | LV | Connected | 0.5
Scotland | Arbroath Project 23 |  |  | Elliot Depot | CHP | LV | Contracted | 0.05 | March 2022
Scotland | Arbroath Project 24 |  |  | Carnoustie | Photovoltaic | LV | Connected | 0.035
Scotland | Arbroath Project 25 |  |  | Hume Street | Photovoltaic | LV | Connected | 0.305
Scotland | Arbroath Project 26 |  |  | Elliot Depot | Battery | 33kV | Contracted | 35 | October 2026
Scotland | Arbroath Project 27 | Arbroath |  |  | Photovoltaic | LV | Connected | 0.129
Scotland | Arbroath Project 28 | Arbroath |  |  | Photovoltaic | LV | Contracted | 0.065 | August 2022
Scotland | Arbroath Project 29 | Arbroath |  |  | Photovoltaic | LV | Contracted | 0.01 | August 2022
Scotland | Arbroath Project 30 | Arbroath |  |  | Photovoltaic | 11kV | Contracted | 9.9 | September 2024
Scotland | Arbroath Project 31 | Arbroath |  |  | Photovoltaic | LV | Contracted | 0.18 | August 2022
Scotland | Arbroath Project 32 | Arbroath |  |  | Battery | 33kV | Contracted | 11 | October 2025
Scotland | Arbroath Project 33 | Arbroath |  |  | Battery | 33kV | Contracted | 50 | September 2026
Scotland | Arbroath Project 34 | Arbroath |  |  | Other | 33kV | Contracted | 9.49 | August 2025
Scotland | Arbroath Project 35 | Arbroath |  |  | Photovoltaic | 11kV | Contracted | 0.12 | January 2023
Scotland | Arbroath Project 36 | Arbroath |  |  | Photovoltaic | 11kV | Contracted | 0.049 | May 23
Scotland | Arbroath Project 37 | Arbroath |  |  | Battery | 33kV | Contracted | 20 | March 26
Scotland | Ardmore Project 01 | Ardmore |  |  | Standby Diesel | 33kV | Connected | 11.8
Scotland | Ardmore Project 02 | Ardmore |  |  | Wind | 33kV | Connected | 7.5
Scotland | Ardmore Project 03 | Ardmore |  |  | Standby Diesel | 11kV | Connected | 2
Scotland | Ardmore Project 04 |  |  | Pollachar | Wind | 11kV | Connected | 0.9
Scotland | Ardmore Project 05 |  |  | Pollachar | Wind | 11kV | Connected | 0.9
Scotland | Ardmore Project 06 |  |  | Aird | Wind | 33kV | Contracted | 6.9 | October 2025
Scotland | Ardmore Project 07 | Ardmore |  |  | Wind | 11kV | Connected | 1.8
Scotland | Ardmore Project 08 | Ardmore |  |  | Wind | LV | Connected | 0.33
Scotland | Ardmore Project 09 | Ardmore |  |  | Battery | 33kV | Contracted | 25 | October 2024
Scotland | Ardmore Project 10 | Ardmore |  |  | Battery | 33kV | Contracted | 30.4 | December 2026
Scotland | Beauly Project 01 |  |  | Loch Carnan | Hydro | 11kV | Connected | 0.92
Scotland | Beauly Project 02 |  |  | Dingwall | Wind | LV | Connected | 0.9
Scotland | Beauly Project 03 | Beauly |  |  | Wind | LV | Connected | 0.9
Scotland | Beauly Project 04 | Beauly |  |  | Hydro | LV | Connected | 0.7
Scotland | Beauly Project 05 | Beauly |  |  | Wind | LV | Connected | 0.7
Scotland | Beauly Project 06 | Beauly |  |  | Hydro | 11kV | Connected | 0.63
Scotland | Beauly Project 07 |  |  | Dingwall | Wind | 11kV | Connected | 0.5
Scotland | Beauly Project 08 |  |  | Dingwall | Hydro | 33kV | Connected | 0.4
Scotland | Beauly Project 09 | Beauly |  |  | Hydro | 33kV | Connected | 0.3
Scotland | Beauly Project 10 | Beauly |  |  | Wind | 11kV | Connected | 0.25
Scotland | Beauly Project 11 |  |  | Dingwall | Hydro | LV | Connected | 0.2
Scotland | Beauly Project 12 | Beauly |  |  | Hydro | LV | Connected | 0.1
Scotland | Beauly Project 13 |  |  | Dingwall | Hydro | LV | Connected | 0.1
Scotland | Beauly Project 14 | Beauly |  |  | Hydro | LV | Connected | 0.1
Scotland | Beauly Project 15 |  |  | Conon Falls | Hydro | 33kV | Connected | 0.1
Scotland | Beauly Project 16 | Beauly |  |  | Hydro | LV | Connected | 0.1
Scotland | Beauly Project 17 |  |  | Conon Falls | Wind | LV | Connected | 0.09
Scotland | Beauly Project 18 |  |  | Dingwall | Hydro | 33kV | Connected | 15
Scotland | Beauly Project 19 | Beauly |  |  | Hydro | LV | Connected | 0.1
Scotland | Beauly Project 20 |  |  | Muir of Ord | Hydro | 11kV | Connected | 0.9
Scotland | Beauly Project 21 |  |  | Dingwall | Wind | 11kV | Connected | 0.4
Scotland | Beauly Project 22 | Beauly |  |  | Hydro | LV | Connected | 0.28
Scotland | Beauly Project 23 |  |  | Dingwall | Hydro | LV | Connected | 0.2
Scotland | Beauly Project 24 |  |  | Conon Bridge | P.V. | LV | Connected | 0.0185
Scotland | Beauly Project 25 |  |  | Dingwall | Hydro | LV | Connected | 0.099
Scotland | Beauly Project 26 |  |  | Dingwall | P.V. | LV | Connected | 0.15
Scotland | Beauly Project 27 | Beauly |  |  | Battery | 33kV | Contracted | 49.9 | April 2023
Scotland | Beauly Project 28 | Beauly |  |  | PV | LV | Contracted | 0.49 | October 23
Scotland | Beauly Project 29 | Beauly |  |  | Battery | 33kV | Contracted | 49.9 | May 26
Scotland | Boat of Garten Project 01 | Boat of Garten |  |  | Hydro | 33kV | Connected | 2.6
Scotland | Boat of Garten Project 02 | Boat of Garten |  |  | Hydro | 33kV | Connected | 1.25
Scotland | Boat of Garten Project 03 | Boat of Garten |  |  | Wind | 11kV | Connected | 0.65
Scotland | Boat of Garten Project 04 |  |  | Kingussie | Other | LV | Connected | 0.09
Scotland | Boat of Garten Project 05 |  |  | Kingussie | Hydro | LV | Connected | 0.1
Scotland | Boat of Garten Project 06 | Boat of Garten |  |  | Hydro | 33kV | Connected | 5
Scotland | Boat of Garten Project 07 | Boat of Garten |  |  | CHP | LV | Connected | 0.249
Scotland | Boat of Garten Project 08 |  |  | Grantown | Wind | 33kV | Connected | 39.1
Scotland | Boat of Garten Project 09 | Boat of Garten |  |  | Photovoltaic | LV | Connected | 0.105
Scotland | Boat of Garten Project 10 |  |  | Kingussie | Photovoltaic | LV | Connected | 0.165
Scotland | Boat of Garten Project 11 | Boat of Garten |  |  | Wind | 11kV | Contracted | 0.9 | March 2022
Scotland | Boat of Garten Project 12 | Boat of Garten |  |  | Battery | 33kV | Contracted | 49.9 | October 2023
Scotland | Boat of Garten Project 13 | Boat of Garten |  |  | Wind | 33kV | Contracted | 40 | March 2025
Scotland | Braco Project 01 | Braco |  |  | Wind | 33kV | Connected | 74
Scotland | Braco Project 02 | Braco |  |  | Hydro | 11kV | Connected | 2
Scotland | Braco Project 03 |  |  | Crieff | Hydro | LV | Connected | 0.35
Scotland | Braco Project 04 |  |  | Callander | Hydro | LV | Connected | 0.5
Scotland | Braco Project 05 |  |  | Callander | Wind | LV | Connected | 0.33
Scotland | Braco Project 06 | Braco |  |  | P.V. | LV | Connected | 0.204
Scotland | Braco Project 07 |  |  | Forteviot | Wind | LV | Connected | 0.2
Scotland | Braco Project 08 |  |  | Gleneagles | Hydro | LV | Connected | 0.15
Scotland | Braco Project 09 |  |  | Dunblane | Hydro | LV | Connected | 0.15
Scotland | Braco Project 10 |  |  | Crieff | Wind | LV | Connected | 0.09
Scotland | Braco Project 11 |  |  | Kippen | CHP | LV | Connected | 0.084
Scotland | Braco Project 12 |  |  | Crieff | Wind | 33kV | Contracted | 8 | May 2022
Scotland | Braco Project 13 | Braco |  |  | Hydro | 11kV | Connected | 1
Scotland | Braco Project 14 |  |  | Callander | Hydro | LV | Connected | 0.5
Scotland | Braco Project 15 | Braco |  |  | Hydro | LV | Connected | 0.5
Scotland | Braco Project 16 |  |  | Callander | Hydro | LV | Connected | 0.095
Scotland | Braco Project 17 |  |  | Crieff | Hydro | LV | Connected | 0.384
Scotland | Braco Project 18 |  |  | Callander | Hydro | LV | Connected | 0.1
Scotland | Braco Project 19 |  |  | Callander | Wind | 11kV | Contracted | 0.5 | November 2022
Scotland | Braco Project 20 |  |  | Dunblane | CHP | LV | Connected | 0.1
Scotland | Braco Project 21 |  |  | Crieff | Other | 33kV | Contracted | 9.999 | March 2022
Scotland | Braco Project 22 | Braco |  |  | Photovoltaic | 33kV | Contracted | 9.9 | December 2023
Scotland | Braco Project 23 | Braco |  |  | Other | LV | Connected | 0.05
Scotland | Braco Project 24 |  |  | Crieff | Photovoltaic | 33kV | Contracted | 9.9 | September 2022
Scotland | Braco Project 25 | Braco |  |  | Battery | 33kV | Contracted | 49.9 | June 2022
Scotland | Braco Project 26 | Braco |  |  | Photovoltaic | LV | Contracted | 0.117 | March 2022
Scotland | Braco Project 27 | Braco |  |  | Photovoltaic | LV | Contracted | 0.075 | March 2022
Scotland | Braco Project 28 | Braco |  |  | Wind | 33kV | Contracted | 45 | May 2024
Scotland | Braco Project 29 | Braco |  |  | Battery | 33kV | Contracted | 50 | October 2023
Scotland | Braco Project 30 | Braco |  |  | Battery | 33kV | Contracted | 49.9 | May 2024
Scotland | Braco Project 31 | Braco |  |  | CHP | 11kV | Contracted | 0.125 | June 23
Scotland | Braco Project 32 | Braco |  |  | Battery | 33kV | Contracted | 25 | Jan 26
Scotland | Bridge of Dun Project 01 | Bridge of Dun |  |  | Wind | 33kV | Connected | 13.5
Scotland | Bridge of Dun Project 02 | Bridge of Dun |  |  | Wind | 33kV | Connected | 3.5
Scotland | Bridge of Dun Project 03 | Bridge of Dun |  |  | Wind | LV | Connected | 0.8
Scotland | Bridge of Dun Project 04 | Bridge of Dun |  |  | Wind | 11kV | Connected | 0.5
Scotland | Bridge of Dun Project 05 |  |  | Bridge of Dun | Wind | 11kV | Connected | 0.5
Scotland | Bridge of Dun Project 06 |  |  | Brechin | Wind | 11kV | Connected | 0.225
Scotland | Bridge of Dun Project 07 |  |  | St Cyrus | Wind | 11kV | Connected | 0.225
Scotland | Bridge of Dun Project 08 |  |  | St Cyrus | P.V. | LV | Connected | 0.211
Scotland | Bridge of Dun Project 09 |  |  | Mill Road | Wind | LV | Connected | 0.1
Scotland | Bridge of Dun Project 10 |  |  | Brechin | Wind | LV | Connected | 0.1
Scotland | Bridge of Dun Project 11 |  |  | Brechin | Wind | LV | Connected | 0.08
Scotland | Bridge of Dun Project 12 |  |  | St Cyrus | Wind | LV | Connected | 0.08
Scotland | Bridge of Dun Project 13 |  |  | Bridge of Dun | CHP | LV | Connected | 0.07
Scotland | Bridge of Dun Project 14 |  |  | Inchbare | Hydro | LV | Connected | 0.1
Scotland | Bridge of Dun Project 15 |  |  | Bridge of Dun | P.V. | LV | Connected | 0.09
Scotland | Bridge of Dun Project 16 |  |  | Logie Pert | Wind | 33kV | Connected | 0.8
Scotland | Bridge of Dun Project 17 | Bridge of Dun |  |  | Wind | 11kV | Connected | 0.8
Scotland | Bridge of Dun Project 18 |  |  | St Cyrus | Wind | 11kV | Connected | 0.8
Scotland | Bridge of Dun Project 19 |  |  | St Cyrus | Wind | LV | Connected | 0.8
Scotland | Bridge of Dun Project 20 |  |  | Brechin | Wind | LV | Connected | 0.5
Scotland | Bridge of Dun Project 21 | Bridge of Dun |  |  | Wind | 11kV | Connected | 0.5
Scotland | Bridge of Dun Project 22 |  |  | St Cyrus | Wind | 11kV | Connected | 0.45
Scotland | Bridge of Dun Project 23 |  |  | St Cyrus | Wind | 11kV | Connected | 0.45
Scotland | Bridge of Dun Project 24 |  |  | St Cyrus | Wind | 11kV | Connected | 0.225
Scotland | Bridge of Dun Project 25 |  |  | St Cyrus | Wind | LV | Connected | 0.11
Scotland | Bridge of Dun Project 26 |  |  | Montrose North | Wind | 11kV | Connected | 0.1
Scotland | Bridge of Dun Project 27 |  |  | Brechin | Hydro | LV | Connected | 0.1
Scotland | Bridge of Dun Project 28 |  |  | Inchbare | Hydro | LV | Connected | 0.085
Scotland | Bridge of Dun Project 29 |  |  | Inchbare | Wind | 11kV | Connected | 0.05
Scotland | Bridge of Dun Project 30 |  |  | St Cyrus | Wind | LV | Connected | 0.05
Scotland | Bridge of Dun Project 31 |  |  | St Cyrus | P.V. | LV | Connected | 0.05
Scotland | Bridge of Dun Project 32 |  |  | Bridge of Dun | Other | LV | Connected | 0.02
Scotland | Bridge of Dun Project 33 |  |  | Montrose North | Hydro | LV | Connected | 0.06
Scotland | Bridge of Dun Project 34 |  |  | Inchbare | P.V. | LV | Connected | 0.05
Scotland | Bridge of Dun Project 35 | Bridge of Dun |  |  | Biogas | LV | Connected | 0.05
Scotland | Bridge of Dun Project 36 |  |  | Logie Pert | P.V. | 33kV | Contracted | 9.99 | October 2024
Scotland | Bridge of Dun Project 37 | Bridge of Dun |  |  | P.V. | LV | Connected | 0.05
Scotland | Bridge of Dun Project 38 |  |  | Montrose North | P.V. | LV | Connected | 0.1
Scotland | Bridge of Dun Project 39 | Bridge of Dun |  |  | Battery | 33kV | Contracted | 49.9 | Jan 2024
Scotland | Bridge of Dun Project 40 | Bridge of Dun |  |  | P.V. | LV | Contracted | 0.112 | August 2022
Scotland | Bridge of Dun Project 41 | Bridge of Dun |  |  | P.V. | 33kV | Contracted | 18 | November 2024
Scotland | Bridge of Dun Project 42 | Bridge of Dun |  |  | Battery | 33kV | Contracted | 25 | October 2025
Scotland | Broadford Project 01 |  |  | Broadford | Hydro | 11kV | Connected | 1.2
Scotland | Broadford Project 02 |  |  | Nostie Bridge | Hydro | 11kV | Connected | 0.95
Scotland | Broadford Project 03 |  |  | Broadford | Hydro | 11kV | Connected | 0.45
Scotland | Broadford Project 04 |  |  | Kishorn Hill | Hydro | LV | Connected | 0.1
Scotland | Broadford Project 05 |  |  | Nostie Bridge | Hydro | 11kV | Connected | 0.09
Scotland | Broadford Project 06 |  |  | Shieldaig | Hydro | 33kV | Contracted | 1.99 | December 2025
Scotland | Broadford Project 07 | Broadford |  |  | Hydro | LV | Connected | 0.05
Scotland | Broadford Project 08 |  |  | Nostie Bridge | Hydro | 11kV | Contracted | 0.137 | December 2025
Scotland | Broadford Project 09 |  |  |  | Wind | 33kV | Contracted | 9 | March 2026
Scotland | Brora Project 01 | Brora |  |  | Hydro | LV | Connected | 0.5
Scotland | Brora Project 02 |  |  | Golspie | Hydro | LV | Connected | 0.1
Scotland | Brora Project 03 |  |  | Brora | Hydro | LV | Connected | 0.099
Scotland | Brora Project 04 |  |  | Brora | Hydro | LV | Connected | 0.095
Scotland | Brora Project 05 |  |  | Brora | Wind | 33kV | Contracted | 27.2 | April 2023
Scotland | Brora Project 06 | Brora |  |  | Battery | 33kV | Contracted | 50 | March 2026
Scotland | Burghmuir Project 01 |  |  | Redgorton | Hydro | 11kV | Connected | 1
Scotland | Burghmuir Project 02 |  |  | Redgorton | Hydro | 11kV | Connected | 0.1
Scotland | Burghmuir Project 03 |  |  | Redgorton | Hydro | LV | Connected | 0.1
Scotland | Burghmuir Project 04 |  |  | Redgorton | Hydro | LV | Connected | 0.1
Scotland | Burghmuir Project 05 |  |  | Redgorton | P.V. | 11kV | Connected | 0.101
Scotland | Burghmuir Project 06 |  |  | Burghmuir | P.V. | LV | Connected | 0.05
Scotland | Burghmuir Project 07 |  |  | Inveralmond | Photovoltaic | LV | Contracted | 0.178 | March 2022
Scotland | Burghmuir Project 08 |  |  | Burghmuir | Photovoltaic | LV | Connected | 0.075
Scotland | Burghmuir Project 09 |  |  | Burghmuir | Battery | 33kV | Contracted | 49.9 | December 2022
Scotland | Burghmuir Project 10 | Burghmuir |  |  | Photovoltaic | LV | Contracted | 0.152 | March 2022
Scotland | Burghmuir Project 11 |  |  | Burghmuir | CHP | LV | Contracted | 0.18 | March 2022
Scotland | Burghmuir Project 12 |  |  | Burghmuir | Other | 11kV | Contracted | 1.366 | March 2022
Scotland | Burghmuir Project 13 | Burghmuir |  |  | Battery | 33kV | Contracted | 29.99 | December 2022
Scotland | Burghmuir Project 14 | Burghmuir |  |  | PV | 33kV | Contracted | 49.9 | January 2025
Scotland | Burghmuir Project 15 | Burghmuir |  |  | CHP | 11kV | Contracted | 0.199 | February 2023
Scotland | Burghmuir Project 16 | Burghmuir |  |  | P.V. | LV | Contracted | 0.1 | August 2022
Scotland | Burghmuir Project 17 | Burghmuir |  |  | P.V. | 11kV | Contracted | 1.24 | April 2025
Scotland | Burghmuir Project 18 | Burghmuir |  |  | Battery | 33kV | Contracted | 50 | October 2026
Scotland | Burghmuir Project 19 | Burghmuir |  |  | PV | 11kV | Contracted | 0.154 | Nov 25
Scotland | Carradale Project 01 | Carradale |  |  | Wind | 33kV | Connected | 38
Scotland | Carradale Project 02 | Carradale |  |  | Wind | 33kV | Connected | 30
Scotland | Carradale Project 03 | Carradale |  |  | Wind | 33kV | Connected | 15
Scotland | Carradale Project 04 | Carradale |  |  | Wind | 33kV | Connected | 12.75
Scotland | Carradale Project 05 | Carradale |  |  | Wind | 33kV | Connected | 5.7
Scotland | Carradale Project 06 | Carradale |  |  | Wind | 33kV | Connected | 5
Scotland | Carradale Project 07 | Carradale |  |  | Hydro | 11kV | Connected | 2.4
Scotland | Carradale Project 08 |  |  | Campbeltown | Wind | 11kV | Connected | 0.675
Scotland | Carradale Project 09 |  |  | Ballure | Hydro | 11kV | Connected | 0.5
Scotland | Carradale Project 10 |  |  | Balliekine | Wind | 11kV | Connected | 0.225
Scotland | Carradale Project 11 |  |  | Ballure | Hydro | LV | Connected | 0.2
Scotland | Carradale Project 12 | Carradale |  |  | Wind | 33kV | Contracted | 35 | April 2023
Scotland | Carradale Project 13 | Carradale |  |  | Wind | 33kV | Connected | 6.9
Scotland | Carradale Project 14 | Carradale |  |  | Hydro | LV | Connected | 0.5
Scotland | Carradale Project 15 |  |  | Brodick | Wind | LV | Connected | 0.114
Scotland | Carradale Project 16 | Carradale |  |  | Wind | 11kV | Connected | 0.105
Scotland | Carradale Project 17 |  |  | Ballure | Hydro | LV | Connected | 0.1
Scotland | Carradale Project 18 | Carradale |  |  | Wind | LV | Connected | 0.05
Scotland | Carradale Project 19 |  |  | Campbeltown | Hydro | LV | Connected | 0.1
Scotland | Carradale Project 20 |  |  | Whiting Bay | Wind | LV | Connected | 0.1
Scotland | Carradale Project 21 |  |  | Campbeltown | Hydro | 33kV | Connected | 0.1
Scotland | Carradale Project 22 | Carradale |  |  | Hydro | LV | Connected | 0.24
Scotland | Carradale Project 23 |  |  | Campbeltown | Hydro | LV | Contracted | 0.1 | October 2022
Scotland | Carradale Project 24 |  |  | Campbeltown | Wind | 33kV | Contracted | 50 | October 2022
Scotland | Carradale Project 25 | Carradale |  |  | Wind | 33kV | Contracted | 47.6 | April 2025
Scotland | Carradale Project 26 | Carradale |  |  | PV | LV | Connected | 0.25
Scotland | Carradale Project 27 | Carradale |  |  | Wind | 33kV | Contracted | 50 | October 2026
Scotland | Carradale Project 28 | Carradale |  |  | Wind | 33kV | Contracted | 26 | July 2024
Scotland | Carradale Project 29 | Carradale |  |  | Wind | 33kV | Contracted | 72.6 | December 2024
Scotland | Carradale Project 30 | Carradale |  |  | Wind | 33kV | Contracted | 59.4 | August 2025
Scotland | Cassley Project 01 | Cassley |  |  | Hydro | 33kV | Connected | 10
Scotland | Cassley Project 02 | Cassley |  |  | Hydro | 33kV | Connected | 4.5
Scotland | Cassley Project 03 | Cassley |  |  | Hydro | LV | Connected | 0.75
Scotland | Cassley Project 04 | Cassley |  |  | Hydro | LV | Connected | 0.6
Scotland | Cassley Project 05 | Cassley |  |  | Hydro | 33kV | Connected | 0.45
Scotland | Cassley Project 06 | Cassley |  |  | Hydro | LV | Connected | 0.15
Scotland | Cassley Project 07 | Cassley |  |  | Hydro | LV | Connected | 0.1
Scotland | Cassley Project 08 | Cassley |  |  | Hydro | LV | Connected | 0.09
Scotland | Cassley Project 09 | Cassley |  |  | Hydro | 33kV | Contracted | 0.2 | January 2022
Scotland | Cassley Project 10 | Cassley |  |  | Hydro | 11kV | Connected | 0.095
Scotland | Cassley Project 11 | Cassley |  |  | Wind | 33kv | Contracted | 49.5 | Feb 2025
Scotland | Ceannacroc Project 01 | Cassley |  |  | Hydro | 11kV | Connected | 20
Scotland | Ceannacroc Project 02 | Ceannacroc |  |  | Hydro | LV | Connected | 0.7
Scotland | Ceannacroc Project 03 | Ceannacroc |  |  | Hydro | LV | Connected | 0.6
Scotland | Ceannacroc Project 04 | Ceannacroc |  |  | Hydro | LV | Connected | 0.45
Scotland | Ceannacroc Project 05 | Ceannacroc |  |  | Hydro | LV | Connected | 0.3
Scotland | Ceannacroc Project 06 | Ceannacroc |  |  | Hydro | LV | Connected | 0.2
Scotland | Ceannacroc Project 07 | Ceannacroc |  |  | Hydro | 33kV | Connected | 1.75
Scotland | Ceannacroc Project 08 | Ceannacroc |  |  | Hydro | LV | Connected | 0.55
Scotland | Ceannacroc Project 09 | Ceannacroc |  |  | Hydro | LV | Connected | 0.55
Scotland | Ceannacroc Project 10 | Ceannacroc |  |  | Hydro | LV | Connected | 0.098
Scotland | Charleston Project 01 |  |  | Menzieshill | Wind | LV | Connected | 0.084
Scotland | Charleston Project 02 |  |  | Menzieshill | P.V. | LV | Connected | 0.017
Scotland | Charleston Project 03 |  |  | Menzieshill | P.V. | 11kV | Connected | 0.25
Scotland | Charleston Project 04 |  |  | Menzieshill | Other | 11kV | Connected | 0.95
Scotland | Charleston Project 05 |  |  | Menzieshill | P.V. | LV | Connected | 0.187
Scotland | Charleston Project 06 |  |  | Ninewells | CHP | LV | Connected | 0.089
Scotland | Charleston Project 07 |  |  | Gourdie | P.V. | LV | Connected | 0.062
Scotland | Charleston Project 08 |  |  | Ninewells | Other | LV | Connected | 0.084
Scotland | Charleston Project 09 |  |  | Menzieshill | Battery | 33kV | Contracted | 49.9 | March 2022
Scotland | Charleston Project 10 | Charleston |  |  | Photovoltaic | LV | Connected | 0.158
Scotland | Charleston Project 11 | Charleston |  |  | Photovoltaic | 33kV | Contracted | 49.9 | April 2023
Scotland | Charleston Project 12 | Charleston |  |  | Battery | 33kV | Contracted | 49.9 | April 2025
Scotland | Charleston Project 13 | Charleston |  |  | PV | LV | Contracted | 0.0828 | July 2022
Scotland | Charleston Project 14 | Charleston |  |  | PV | LV | Contracted | 0.117 | July 2022
Scotland | Charleston Project 15 | Charleston |  |  | P.V. | LV | Contracted | 0.75 | November 2024
Scotland | Charleston Project 16 | Charleston |  |  | P.V. | 33kV | Contracted | 20 | May 2025
Scotland | Charleston Project 17 | Charleston |  |  | other | 33kV | Contracted | 9.95 | May 25
Scotland | Charleston Project 18 | Charleston |  |  | Battery | 33kV | Contracted | 49.5 | Oct 25
Scotland | Clachan Project 01 | Clachan |  |  | Hydro | 33kV | Connected | 40
Scotland | Clachan Project 02 | Clachan |  |  | Hydro | 11kV | Connected | 6
Scotland | Clachan Project 03 | Clachan |  |  | Hydro | LV | Connected | 0.96
Scotland | Clachan Project 04 | Clachan |  |  | Hydro | LV | Connected | 0.415
Scotland | Clachan Project 05 |  |  | Douglas Pier | Hydro | 11kV | Connected | 1.35
Scotland | Clachan Project 06 |  |  | Lochgoilhead | Hydro | 11kV | Contracted | 0.5 | March 2022
Scotland | Clachan Project 07 | Clachan |  |  | Hydro | LV | Connected | 0.4
Scotland | Clachan Project 08 | Clachan |  |  | Hydro | LV | Connected | 0.13
Scotland | Clachan Project 09 | Clachan |  |  | Hydro | LV | Connected | 0.1
Scotland | Clachan Project 10 | Clachan |  |  | Hydro | 11kV | Connected | 0.99
Scotland | Clachan Project 11 | Clachan |  |  | Hydro | 11kV | Contracted | 0.19 | October 2022
Scotland | Clachan Project 12 | Clachan |  |  | Photovoltaic | LV | Contracted | 0.05 | August 2022
Scotland | Clayhills Project 01 |  |  | Douglas Pier | BioGas | 11kV | Connected | 1
Scotland | Clayhills Project 02 | Clayhills |  |  | P.V. | 11kV | Connected | 0.15
Scotland | Clayhills Project 03 | Clayhills |  |  | P.V. | LV | Contracted | 0.175 | 2022-08-01
Scotland | Coupar Angus Project 01 | Coupar Angus |  |  | Wind | 33kV | Connected | 32
Scotland | Coupar Angus Project 02 | Coupar Angus |  |  | Wind | 33kV | Connected | 6.4
Scotland | Coupar Angus Project 03 | Coupar Angus |  |  | Wind | 11kV | Connected | 0.8
Scotland | Coupar Angus Project 04 |  |  | Leoch | Hydro | LV | Connected | 0.7
Scotland | Coupar Angus Project 05 |  |  | Caputh | Wind | 11kV | Connected | 0.5
Scotland | Coupar Angus Project 06 |  |  | Coupar Angus | Wind | 11kV | Connected | 0.375
Scotland | Coupar Angus Project 07 |  |  | Blairgowrie | Wind | 11kV | Connected | 0.225
Scotland | Coupar Angus Project 08 |  |  | Leoch | Wind | 11kV | Connected | 0.225
Scotland | Coupar Angus Project 09 |  |  | Leoch | P.V. | LV | Connected | 0.18
Scotland | Coupar Angus Project 10 |  |  | Coupar Angus | Hydro | LV | Connected | 0.15
Scotland | Coupar Angus Project 11 |  |  | Dalrulzion | Hydro | LV | Connected | 0.1
Scotland | Coupar Angus Project 12 |  |  | Blairgowrie | Hydro | LV | Connected | 0.1
Scotland | Coupar Angus Project 13 |  |  | Caputh | Hydro | LV | Connected | 0.1
Scotland | Coupar Angus Project 14 |  |  | Caputh | Wind | LV | Connected | 0.1
Scotland | Coupar Angus Project 15 |  |  | Caputh | Wind | LV | Connected | 0.1
Scotland | Coupar Angus Project 16 |  |  | Dalrulzion | Wind | LV | Connected | 0.1
Scotland | Coupar Angus Project 17 |  |  | Leoch | Wind | LV | Connected | 0.05
Scotland | Coupar Angus Project 18 |  |  | Leoch | Wind | 33kV | Connected | 14.35
Scotland | Coupar Angus Project 19 | Coupar Angus |  |  | Wind | 33kV | Connected | 9.2
Scotland | Coupar Angus Project 20 | Coupar Angus |  |  | Wind | 11kV | Connected | 0.5
Scotland | Coupar Angus Project 21 |  |  | Leoch | Wind | 11kV | Connected | 0.3
Scotland | Coupar Angus Project 22 |  |  | Leoch | Hydro | LV | Connected | 0.25
Scotland | Coupar Angus Project 23 |  |  | Caputh | Wind | LV | Connected | 0.25
Scotland | Coupar Angus Project 24 |  |  | Alyth | P.V. | LV | Connected | 0.05
Scotland | Coupar Angus Project 25 |  |  | Coupar Angus | Hydro | LV | Connected | 0.12
Scotland | Coupar Angus Project 26 |  |  | Dalrulzion | P.V. | LV | Connected | 0.07
Scotland | Coupar Angus Project 27 |  |  | Coupar Angus | CHP | LV | Connected | 0.075
Scotland | Coupar Angus Project 28 |  |  | Leoch | P.V. | LV | Connected | 0.08
Scotland | Coupar Angus Project 29 |  |  | Coupar Angus | CHP | LV | Connected | 0.098
Scotland | Coupar Angus Project 30 |  |  | Coupar Angus | Other | 33kV | Contracted | 40 | March 2022
Scotland | Coupar Angus Project 31 | Coupar Angus |  |  | CHP | LV | Connected | 0.05
Scotland | Coupar Angus Project 32 |  |  | Leoch | Photovoltaic | LV | connected | 0.375
Scotland | Coupar Angus Project 33 |  |  | Coupar Angus | CHP | LV | Connected | 0.245
Scotland | Coupar Angus Project 34 |  |  | Coupar Angus | Battery | LV | Connected | 0.015
Scotland | Coupar Angus Project 35 | Coupar Angus |  |  | Photovoltaic | 33kV | Contracted | 49.9 | March 2023
Scotland | Coupar Angus Project 36 | Coupar Angus |  |  | Wind | 11kV | Contracted | 8.5 | April 2024
Scotland | Coupar Angus Project 37 | Coupar Angus |  |  | Photovoltaic | 33kV | Contracted | 49.9 | September 2024
Scotland | Coupar Angus Project 38 | Coupar Angus |  |  | Photovoltaic | 33kV | Contracted | 49.9 | September 2024
Scotland | Coupar Angus Project 39 | Coupar Angus |  |  | Battery | 33kV | Contracted | 16 | March 2023
Scotland | Coupar Angus Project 40 | Coupar Angus |  |  | P.V. | 11kV | Contracted | 1.215 | October 2025
Scotland | Coupar Angus Project 41 | Coupar Angus |  |  | P.V. | 11kV | Contracted | 0.21 | August 2022
Scotland | Coupar Angus Project 42 | Coupar Angus |  |  | P.V. | 33kV | Contracted | 10 | May 2025
Scotland | Coupar Angus Project 43 | Coupar Angus |  |  | P.V. | LV | Contracted | 0.105 | May 2023
Scotland | Coupar Angus Project 44 | Coupar Angus |  |  | P.V. | LV | Contracted | 0.9 | October 2022
Scotland | Coupar Angus Project 45 | Coupar Angus |  |  | Wind | 33kV | Contracted | 49.9 | Oct 26
Scotland | Coupar Angus Project 46 | Coupar Angus |  |  | Battery | 33kV | Contracted | 49.9 | Dec 26
Scotland | Craigiebuckler Project 01 | Craigiebuckler |  |  | Wind | 11kV | Connected | 0.8
Scotland | Craigiebuckler Project 02 |  |  | Craigton Cults | P.V. | 11kV | Connected | 0.05
Scotland | Craigiebuckler Project 03 |  |  | Craigiebuckler | Wind | 11kV | Connected | 0.5
Scotland | Craigiebuckler Project 04 |  |  | Culter | CHP | LV | Connected | 0.015
Scotland | Craigiebuckler Project 05 | Craigiebuckler |  |  | P.V. | LV | Contracted | 0.2 | June 2023
Scotland | Craigiebuckler Project 06 | Craigiebuckler |  |  | P.V. | 33kV | Contracted | 35 | September 2024
Scotland | Craigiebuckler Project 07 | Craigiebuckler |  |  | Battery | 33kV | Contracted | 35 | January 2024
Scotland | Craigiebuckler Project 08 | Craigiebuckler |  |  | P.V. | LV | Contracted | 0.93 | September 2023
Scotland | Dounreay Project 01 | Dounreay |  |  | Wind | 33kV | Contracted | 1.5 | March 2022
Scotland | Dounreay Project 02 | Dounreay |  |  | Wind | 33kV | Connected | 5
Scotland | Dounreay Project 03 | Dounreay |  |  | Wind | 33kV | Connected | 52.7
Scotland | Dounreay Project 04 | Dounreay |  |  | Wind | 33kV | Connected | 5.29
Scotland | Dounreay Project 05 | Dounreay |  |  | Wind | 11kV | Connected | 2.32
Scotland | Dounreay Project 06 |  |  | Forss | Wind | 33kV | Contracted | 1 | March 2022
Scotland | Dounreay Project 07 | Dounreay |  |  | Hydro | LV | Connected | 0.09
Scotland | Dounreay Project 08 |  |  | Bettyhill | Wind | 33kV | Contracted | 9.8 | August 2025
Scotland | Dounreay Project 09 | Dounreay |  |  | Wind | 33kV | Contracted | 0.85 | October 2024
Scotland | Dounreay Project 10 | Dounreay |  |  | Wind | 33kV | Contracted | 49.9 | October 2024
Scotland | Dounreay Project 11 | Dounreay |  |  | Wind | 33kV | Contracted | 48 | October 2024
Scotland | Dounreay Project 12 | Dounreay |  |  | Wind | 33kV | Contracted | 9.9 | August 2025
Scotland | Dounreay Project 13 | Dounreay |  |  | Battery | 33kV | Contracted | 34 | Jan 2026
Scotland | Dounreay Project 14 | Dounreay |  |  | Battery | 33kV | Contracted | 49.9 | November 2027
Scotland | Dounreay Project 15 | Dounreay |  |  | Wind | 33kV | Contracted | 27 | Aug 26
Scotland | Dudhope Project 01 |  |  | Constable Street | CHP | LV | Connected | 0.15
Scotland | Dudhope Project 02 |  |  | Constable Street | P.V. | LV | Connected | 0.1
Scotland | Dudhope Project 03 |  |  | Constable Street | Other | LV | Connected | 0.06
Scotland | Dudhope Project 04 |  |  | Constable Street | Other | LV | Connected | 0.097
Scotland | Dudhope Project 05 |  |  | Constable Street | Other | LV | Contracted | 0.1 | March 2022
Scotland | Dudhope Project 06 |  |  | Constable Street | Photovoltaic | LV | Connected | 0.05
Scotland | Dudhope Project 07 |  |  | Constable Street | CHP | LV | Connected | 3
Scotland | Dudhope Project 08 |  |  | Constable Street | P.V. | LV | Contracted | 0.077 | January 2022
Scotland | Dudhope Project 09 |  |  |  | P.V. | LV | Contracted | 0.0828 | December 2022
Scotland | Dudhope Project 10 |  |  |  | Battery | 33kV | Contracted | 39.9 | November 2024
Scotland | Dunoon Project 01 | Dunoon |  |  | Wind | 33kV | Connected | 29
Scotland | Dunoon Project 02 | Dunoon |  |  | Hydro | 33kV | Connected | 7.8
Scotland | Dunoon Project 03 | Dunoon |  |  | Wind | LV | Connected | 0.9
Scotland | Dunoon Project 04 | Dunoon |  |  | Hydro | LV | Connected | 0.1
Scotland | Dunoon Project 05 |  |  | Sandbank | Hydro | LV | Connected | 0.1
Scotland | Dunoon Project 06 |  |  | Otter Ferry | Hydro | 11kV | Connected | 0.55
Scotland | Dunoon Project 07 |  |  | Sandbank | Hydro | LV | Connected | 0.225
Scotland | Dunoon Project 08 | Dunoon |  |  | Hydro | LV | Connected | 0.35
Scotland | Dunoon Project 09 |  |  | Colintraive | Hydro | LV | Connected | 0.3
Scotland | Dunoon Project 10 | Dunoon |  |  | Hydro | LV | Connected | 0.1
Scotland | Dunoon Project 11 |  |  | Dunoon | Hydro | LV | Connected | 0.1
Scotland | Dunoon Project 12 |  |  | Dunoon | Hydro | LV | Connected | 0.09
Scotland | Dunoon Project 13 |  |  | Otter Ferry | Hydro | 11kV | Connected | 0.075
Scotland | Dunoon Project 14 | Dunoon |  |  | Hydro | LV | Connected | 0.06
Scotland | Dunoon Project 15 |  |  | Otter Ferry | P.V. | LV | Connected | 0.056
Scotland | Dunoon Project 16 |  |  | Otter Ferry | P.V. | LV | Connected | 0.2
Scotland | Dunoon Project 17 |  |  | Dunoon | Hydro | 11kV | Connected | 0.135
Scotland | Dunoon Project 18 |  |  | Sandbank | Hydro | LV | Connected | 0.1
Scotland | Dunoon Project 19 | Dunoon |  |  | Hydro | 33kV | Connected | 0.048
Scotland | Dunoon Project 20 | Dunoon |  |  | Hydro | 11kV | Connected | 0.199
Scotland | Dunoon Project 21 | Dunoon |  |  | P.V. | 11kV | Connected | 0.086
Scotland | Dunoon Project 22 | Dunoon |  |  | Hydro | 11kV | Connected | 0.19
Scotland | Dunoon Project 23 | Dunoon |  |  | Hydro | 11kV | Connected | 0.1
Scotland | Dunoon Project 24 | Dunoon |  |  | Hydro | 11kV | Contracted | 0.095 | March 2022
Scotland | Dunoon Project 25 | Dunoon |  |  | Hydro | 11kV | Contracted | 0.075 | March 2022
Scotland | Dunoon Project 26 | Dunoon |  |  | Hydro | 11kV | Contracted | 0.45 | January 2022
Scotland | Dunoon Project 27 | Dunoon |  |  | Wind | 33kV | Contracted | 44 | October 2024
Scotland | Dunoon Project 28 | Dunoon |  |  | Battery | 33kV | Contracted | 49.9 | June 2025
Scotland | Dunvegan Project 01 | Dunvegan |  |  | Wind | 33kV | Connected | 21
Scotland | Dunvegan Project 02 | Dunvegan |  |  | Wind | 33kV | Connected | 7
Scotland | Dunvegan Project 03 | Dunvegan |  |  | Other | 33kV | Connected | 1.9
Scotland | Dunvegan Project 04 | Dunvegan |  |  | Wind | 33kV | Contracted | 6.9 | December 2025
Scotland | Dunvegan Project 05 | Dunvegan |  |  | Wind | LV | Connected | 0.09
Scotland | Dunvegan Project 06 | Dunvegan |  |  | Hydro | LV | Connected | 0.09
Scotland | Dunvegan Project 07 |  |  | Drynoch | Wind | 11kV | Contracted | 0.9 | March 2022
Scotland | Dunvegan Project 08 |  |  | Dunvegan | Wind | 33kV | Contracted | 25 | March 2022
Scotland | Dunvegan Project 09 | Dunvegan |  |  | Wind | 33kV | Contracted | 2.3 | March 2022
Scotland | Dunvegan Project 10 | Dunvegan |  |  | Wind | 33kV | Contracted | 40.8 | October 2024
Scotland | Dunvegan Project 11 | Dunvegan |  |  | Wind | 33kV | Contracted | 45 | October 2024
Scotland | Dunvegan Project 12 | Dunvegan |  |  | Wind | 33kV | Contracted | 6.1 | December 2025
Scotland | Dunvegan Project 13 |  |  | Drynoch | Wind | 11kV | Connected | 0.33
Scotland | Dunvegan Project 14 |  |  | Drynoch | Wind | 11kV | Connected | 0.33
Scotland | Dunvegan Project 15 |  |  | Drynoch | Hydro | 11kV | Connected | 0.1
Scotland | Dyce Project 01 | Dyce |  |  | Wind | 33kV | Connected | 9.9
Scotland | Dyce Project 02 | Dyce |  |  | Wind | 33kV | Connected | 7.5
Scotland | Dyce Project 03 | Dyce |  |  | Wind | 11kV | Connected | 0.9
Scotland | Dyce Project 04 |  |  | Kingseat | Wind | 11kV | Connected | 0.8
Scotland | Dyce Project 05 |  |  | Kingseat | Wind | LV | Connected | 0.45
Scotland | Dyce Project 06 | Dyce |  |  | P.V. | 11kV | Connected | 0.075
Scotland | Dyce Project 07 |  |  | Dyce North | BioGas | LV | Connected | 0.4
Scotland | Dyce Project 08 |  |  | Dyce North | Wind | LV | Connected | 0.147
Scotland | Dyce Project 09 |  |  | Dyce North | P.V. | 11kV | Connected | 0
Scotland | Dyce Project 10 | Dyce |  |  | P.V. | LV | Connected | 0.069
Scotland | Dyce Project 11 | Dyce |  |  | Other | 11kV | Connected | 3.2
Scotland | Dyce Project 12 |  |  | Dyce North | CHP | 11kV | Connected | 0.18
Scotland | Dyce Project 13 |  |  | Dyce North | Gas | 11kV | Connected | 0.2
Scotland | Dyce Project 14 | Dyce |  |  | Battery | 33kV | Contracted | 30 | March 2022
Scotland | Dyce Project 15 | Dyce |  |  | Biomass | 11kV | Connected | 0.499
Scotland | Dyce Project 16 |  |  | Dyce North | CHP | 11kV | Connected | 0.62
Scotland | Dyce Project 17 | Dyce |  |  | Photovoltaic | 11kV | Connected | 0.2
Scotland | Dyce Project 18 | Dyce |  |  | Battery | 33kV | Contracted | 20.622 | March 2024
Scotland | Dyce Project 19 | Dyce |  |  | P.V. | 33kV | Contracted | 45 | July 2024
Scotland | Dyce Project 20 | Dyce |  |  | P.V. | LV | Contracted | 0.176 | June 2022
Scotland | Dyce Project 21 | Dyce |  |  | P.V. | LV | Contracted | 0.08 | June 2022
Scotland | Dyce Project 22 | Dyce |  |  | P.V. | 33kV | Contracted | 20 | April 2025
Scotland | Dyce Project 23 | Dyce |  |  | Battery | 33kV | Contracted | 49.9 | May 2025
Scotland | Dyce Project 23 | Dyce |  |  | Battery | 33kV | Contracted | 32.95 | March 2026
Scotland | Elgin Project 01 | Elgin |  |  | Wind | 11kV | Connected | 0.975
Scotland | Elgin Project 02 |  |  | Kinloss | P.V. | 33kV | Contracted | 49.9 | October 2022
Scotland | Elgin Project 03 | Elgin |  |  | Photovoltaic | 33kV | Contracted | 20 | October 2022
Scotland | Elgin Project 04 | Elgin |  |  | Other | 11kV | Connected | 0.999
Scotland | Elgin Project 05 |  |  | Kinloss | CHP | LV | Connected | 0.25
Scotland | Elgin Project 06 |  |  | Kinloss | P.V. | LV | Connected | 0.05
Scotland | Elgin Project 07 |  |  | Elgin | P.V. | LV | Connected | 0.05
Scotland | Elgin Project 08 |  |  | Elgin | P.V. | LV | Connected | 0.05
Scotland | Elgin Project 09 |  |  | Elgin | CHP | LV | Connected | 0.05
Scotland | Elgin Project 10 |  |  | Kinloss | Wind | 33kV | Contracted | 23 | October 2022
Scotland | Elgin Project 11 | Elgin |  |  | BioGas | 11kV | Connected | 0.499
Scotland | Elgin Project 12 | Elgin |  |  | Other | LV | Contracted | 8 | October 2022
Scotland | Elgin Project 13 |  |  | Kinloss | Photovoltaic | LV | Connected | 0.12
Scotland | Elgin Project 14 |  |  | Kinloss | CHP | LV | Connected | 0.21
Scotland | Elgin Project 15 | Elgin |  |  | Photovoltaic | LV | Contracted | 0.2 | March 2022
Scotland | Elgin Project 16 | Keith |  |  | CHP | LV | Contracted | 0.06 | October 2022
Scotland | Elgin Project 17 | Keith |  |  | PV | LV | Contracted | 0.199
Scotland | Elgin Project 18 | Keith |  |  | PV | LV | Contracted | 0.05 | January 2022
Scotland | Elgin Project 19 | Elgin |  |  | Battery | 33kV | contracted | 50 | August 2025
Scotland | Fasnakyle Project 01 | Fasnakyle |  |  | Wind | 33kV | Connected | 9.95
Scotland | Fasnakyle Project 02 | Fasnakyle |  |  | Hydro | 33kV | Connected | 2.5
Scotland | Fasnakyle Project 03 | Fasnakyle |  |  | Hydro | 33kV | Connected | 0.1
Scotland | Fasnakyle Project 04 | Fasnakyle |  |  | Hydro | LV | Connected | 3.7
Scotland | Fasnakyle Project 05 | Fasnakyle |  |  | Wind | 33kV | Connected | 1.55
Scotland | Fasnakyle Project 06 | Fasnakyle |  |  | Hydro | 33kV | Connected | 0.5
Scotland | Fasnakyle Project 07 | Fasnakyle |  |  | Hydro | LV | Connected | 0.5
Scotland | Fasnakyle Project 08 | Fasnakyle |  |  | Hydro | LV | Connected | 0.485
Scotland | Fasnakyle Project 09 | Fasnakyle |  |  | Wind | LV | Connected | 0.1
Scotland | Fasnakyle Project 10 | Fasnakyle |  |  | Hydro | LV | Connected | 0.015
Scotland | Fasnakyle Project 11 | Fasnakyle |  |  | Hydro | LV | Contracted | 0.05 | March 2022
Scotland | Fasnakyle Project 12 | Fasnakyle |  |  | Hydro | 33kV | Connected | 1.425
Scotland | Fasnakyle Project 13 | Fasnakyle |  |  | Hydro | 33kV | Connected | 7.5
Scotland | Fasnakyle Project 14 | Fasnakyle |  |  | Hydro | 33kV | Connected | 23
Scotland | Fasnakyle Project 15 | Fasnakyle |  |  | Hydro | 33kV | Connected | 23
Scotland | Fasnakyle Project 16 | Fasnakyle |  |  | Hydro | 33kV | Connected | 23
Scotland | Fasnakyle Project 17 | Fasnakyle |  |  | Battery | 33kV | Contracted | 49.4 | October 26
Scotland | Fiddes Project 01 | Fiddes |  |  | Wind | 33kV | Connected | 25
Scotland | Fiddes Project 02 | Fiddes |  |  | Wind | 33kV | Connected | 9.9
Scotland | Fiddes Project 03 | Fiddes |  |  | Wind | 33kV | Connected | 6.9
Scotland | Fiddes Project 04 | Fiddes |  |  | Wind | 33kV | Connected | 4.99
Scotland | Fiddes Project 05 | Fiddes |  |  | Wind | 33kV | Connected | 4.6
Scotland | Fiddes Project 06 | Fiddes |  |  | Wind | 33kV | Connected | 3.9
Scotland | Fiddes Project 07 | Fiddes |  |  | Wind | 33kV | Connected | 3
Scotland | Fiddes Project 08 | Fiddes |  |  | Wind | 11kV | Connected | 0.9
Scotland | Fiddes Project 09 |  |  | Laurencekirk | Wind | 11kV | Connected | 0.8
Scotland | Fiddes Project 10 |  |  | Stonehaven | Wind | 11kV | Connected | 0.8
Scotland | Fiddes Project 11 |  |  | Stonehaven | Wind | LV | Connected | 0.8
Scotland | Fiddes Project 12 | Fiddes |  |  | Wind | 11kV | Connected | 0.5
Scotland | Fiddes Project 13 |  |  | Edzell | Wind | 11kV | Connected | 0.45
Scotland | Fiddes Project 14 |  |  | Inverbervie | Wind | LV | Connected | 0.45
Scotland | Fiddes Project 15 |  |  | Inverbervie | Wind | LV | Connected | 0.45
Scotland | Fiddes Project 16 | Fiddes |  |  | Biodiesel | LV | Connected | 0.14
Scotland | Fiddes Project 17 |  |  | Laurencekirk | Wind | LV | Connected | 0.1
Scotland | Fiddes Project 18 |  |  | Laurencekirk | Wind | LV | Connected | 0.1
Scotland | Fiddes Project 19 |  |  | Laurencekirk | Wind | LV | Connected | 0.1
Scotland | Fiddes Project 20 |  |  | Laurencekirk | Wind | LV | Connected | 0.05
Scotland | Fiddes Project 21 |  |  | Laurencekirk | P.V. | LV | Connected | 0.05
Scotland | Fiddes Project 22 |  |  | Laurencekirk | Wind | 33kV | Connected | 7.5
Scotland | Fiddes Project 23 | Fiddes |  |  | Wind | 11kV | Connected | 0.05
Scotland | Fiddes Project 24 |  |  | Inverbervie | Wind | LV | Connected | 0.5
Scotland | Fiddes Project 25 |  |  | Inverbervie | Wind | 11kV | Connected | 0.5
Scotland | Fiddes Project 26 |  |  | Inverbervie | Wind | 11kV | Connected | 0.8
Scotland | Fiddes Project 27 |  |  | Stonehaven | Wind | 11kV | Connected | 0.5
Scotland | Fiddes Project 28 |  |  | Stonehaven | Wind | 11kV | Connected | 0.5
Scotland | Fiddes Project 29 |  |  | Inverbervie | Wind | LV | Connected | 0.5
Scotland | Fiddes Project 30 |  |  | Stonehaven | Wind | 11kV | Connected | 0.5
Scotland | Fiddes Project 31 |  |  | Laurencekirk | Wind | LV | Connected | 0.5
Scotland | Fiddes Project 32 | Fiddes |  |  | Wind | 11kV | Connected | 0.45
Scotland | Fiddes Project 33 |  |  | Stonehaven | Wind | 11kV | Connected | 0.45
Scotland | Fiddes Project 34 |  |  | Inverbervie | Wind | 11kV | Connected | 0.3
Scotland | Fiddes Project 35 |  |  | Stonehaven | Wind | 11kV | Connected | 0.2
Scotland | Fiddes Project 36 |  |  | Inverbervie | P.V. | LV | Connected | 0.05
Scotland | Fiddes Project 37 |  |  | Laurencekirk | P.V. | LV | Connected | 0.05
Scotland | Fiddes Project 38 |  |  | Edzell | Wind | 33kV | Connected | 4.6
Scotland | Fiddes Project 39 | Fiddes |  |  | Wind | 11kV | Contracted | 0.05 | March 2022
Scotland | Fiddes Project 40 |  |  | Inverbervie | Wind | 33kV | Connected | 0.5
Scotland | Fiddes Project 41 | Fiddes |  |  | P.V. | LV | Connected | 0.05
Scotland | Fiddes Project 42 |  |  | Inverbervie | P.V. | LV | Connected | 0.05
Scotland | Fiddes Project 43 |  |  | Laurencekirk | CHP | LV | Connected | 0.05
Scotland | Fiddes Project 44 |  |  | Laurencekirk | CHP | 11kV | Connected | 0.9
Scotland | Fiddes Project 45 |  |  | Inverbervie | CHP | LV | Connected | 0.05
Scotland | Fiddes Project 46 | Fiddes |  |  | CHP | LV | Connected | 0.045
Scotland | Fiddes Project 47 | Fiddes |  |  | Other | LV | Connected | 0.05
Scotland | Fiddes Project 48 | Fiddes |  |  | CHP | 11kV | Connected | 0
Scotland | Fiddes Project 49 | Fiddes |  |  | Battery | 33kV | Contracted | 30 | March 2024
Scotland | Fiddes Project 50 | Fiddes |  |  | Battery | 33kV | Contracted | 49.9 | October 2023
Scotland | Fiddes Project 51 | Fiddes |  |  | Wind | 33kV | Contracted | 9.2 | October 2028
Scotland | Fiddes Project 52 | Fiddes |  |  | P.V. | 33kV | Contracted | 20 | October 2028
Scotland | Fort Augustus Project 01 | Fort Augustus |  |  | Hydro | 33kV | Connected | 0.95
Scotland | Fort Augustus Project 02 | Fort Augustus |  |  | Hydro | 33kV | Connected | 0.9
Scotland | Fort Augustus Project 03 | Fort Augustus |  |  | Hydro | 33kV | Connected | 0.3
Scotland | Fort Augustus Project 04 | Fort Augustus |  |  | Hydro | 33kV | Connected | 0.315
Scotland | Fort Augustus Project 05 | Fort Augustus |  |  | Hydro | LV | Connected | 0.15
Scotland | Fort Augustus Project 06 | Fort Augustus |  |  | Hydro | 33kV | Connected | 2.05
Scotland | Fort Augustus Project 07 | Fort Augustus |  |  | Hydro | 11kV | Connected | 1.99
Scotland | Fort Augustus Project 08 |  |  | Drumnadrochit | Hydro | 33kV | Connected | 1.35
Scotland | Fort Augustus Project 09 | Fort Augustus |  |  | Hydro | LV | Connected | 0.99
Scotland | Fort Augustus Project 10 | Fort Augustus |  |  | Hydro | LV | Connected | 0.85
Scotland | Fort Augustus Project 11 | Fort Augustus |  |  | Hydro | LV | Connected | 0.5
Scotland | Fort Augustus Project 12 | Fort Augustus |  |  | Hydro | LV | Connected | 0.36
Scotland | Fort Augustus Project 13 | Fort Augustus |  |  | Hydro | LV | Connected | 0.499
Scotland | Fort Augustus Project 14 |  |  | Invergarry | Hydro | 11kV | Connected | 0.45
Scotland | Fort Augustus Project 15 |  |  | Invergarry | Hydro | 11kV | Connected | 0.7
Scotland | Fort Augustus Project 16 | Fort Augustus |  |  | Hydro | LV | Connected | 0.35
Scotland | Fort Augustus Project 17 | Fort Augustus |  |  | Hydro | LV | Connected | 0.999
Scotland | Fort Augustus Project 18 | Fort Augustus |  |  | Hydro | 33kV | Connected | 0.1
Scotland | Fort Augustus Project 19 | Fort Augustus |  |  | Hydro | LV | Connected | 3
Scotland | Fort Augustus Project 20 | Fort Augustus |  |  | Hydro | 33kV | Connected | 0.55
Scotland | Fort Augustus Project 21 | Fort Augustus |  |  | Battery | 33kV | Contracted | 49.9 | June 2022
Scotland | Fort Augustus Project 22 | Fort Augustus |  |  | Hydro | 33kV | Contracted | 0.5 | March 2022
Scotland | Fort Augustus Project 23 | Fort Augustus |  |  | Hydro | 33kV | Contracted | 0.05 | March 2022
Scotland | Fort Augustus Project 24 | Fort Augustus |  |  | Hydro | 33kV | Connected | 2
Scotland | Fort William Project 01 | Fort William |  |  | Hydro | 33kV | Connected | 4.2
Scotland | Fort William Project 02 | Fort William |  |  | Hydro | 11kV | Connected | 3.5
Scotland | Fort William Project 03 | Fort William |  |  | Hydro | 33kV | Connected | 2.34
Scotland | Fort William Project 04 | Fort William |  |  | Hydro | 11kV | Connected | 1.8
Scotland | Fort William Project 05 |  |  | Inverlochy | Hydro | LV | Connected | 1.35
Scotland | Fort William Project 06 | Fort William |  |  | Hydro | 33kV | Connected | 1.35
Scotland | Fort William Project 07 | Fort William |  |  | Hydro | LV | Connected | 0.95
Scotland | Fort William Project 08 |  |  | Kinlochmoidart | Hydro | LV | Connected | 0.95
Scotland | Fort William Project 09 | Fort William |  |  | Hydro | LV | Connected | 0.9
Scotland | Fort William Project 10 | Fort William |  |  | Hydro | 33kV | Connected | 0.83
Scotland | Fort William Project 11 | Fort William |  |  | Hydro | LV | Connected | 0.8
Scotland | Fort William Project 12 | Fort William |  |  | Hydro | 11kV | Connected | 0.8
Scotland | Fort William Project 13 |  |  | Mallaig | Hydro | 11kV | Connected | 0.66
Scotland | Fort William Project 14 |  |  | Salen, Mull | Hydro | 33kV | Connected | 0.65
Scotland | Fort William Project 15 | Fort William |  |  | Hydro | 11kV | Connected | 0.5
Scotland | Fort William Project 16 |  |  | Kinlochmoidart | Hydro | LV | Connected | 0.496
Scotland | Fort William Project 17 | Fort William |  |  | Hydro | LV | Connected | 0.45
Scotland | Fort William Project 18 | Fort William |  |  | Hydro | 11kV | Connected | 0.4
Scotland | Fort William Project 19 |  |  | Lochaline | Wind | 11kV | Connected | 0.33
Scotland | Fort William Project 20 |  |  | Salen, Mull | Hydro | LV | Connected | 0.25
Scotland | Fort William Project 21 |  |  | Corran | Hydro | LV | Connected | 0.14
Scotland | Fort William Project 22 |  |  | Salen, Mull | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 23 | Fort William |  |  | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 24 |  |  | Inverlochy | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 25 |  |  | Salen, Mull | Hydro | LV | Connected | 0.05
Scotland | Fort William Project 26 | Fort William |  |  | Hydro | 33kV | Connected | 5.7
Scotland | Fort William Project 27 | Fort William |  |  | Hydro | 33kV | Connected | 2
Scotland | Fort William Project 28 | Fort William |  |  | Hydro | 11kV | Connected | 1.1
Scotland | Fort William Project 29 |  |  | Inverlochy | Hydro | LV | Connected | 0.099
Scotland | Fort William Project 30 | Fort William |  |  | Hydro | LV | Connected | 0.95
Scotland | Fort William Project 31 | Fort William |  |  | Hydro | LV | Connected | 0.75
Scotland | Fort William Project 32 | Fort William |  |  | Hydro | LV | Connected | 0.6
Scotland | Fort William Project 33 | Fort William |  |  | Hydro | LV | Connected | 0.5
Scotland | Fort William Project 34 | Fort William |  |  | Hydro | LV | Connected | 0.5
Scotland | Fort William Project 35 | Fort William |  |  | Wind | LV | Connected | 0.4
Scotland | Fort William Project 36 | Fort William |  |  | Hydro | LV | Connected | 0.4
Scotland | Fort William Project 37 | Fort William |  |  | Hydro | LV | Connected | 0.3
Scotland | Fort William Project 38 | Fort William |  |  | Hydro | LV | Connected | 0.3
Scotland | Fort William Project 39 |  |  | Rahoy | Hydro | LV | Connected | 0.262
Scotland | Fort William Project 40 | Fort William |  |  | Hydro | 11kV | Connected | 0.25
Scotland | Fort William Project 41 |  |  | Annat | Hydro | LV | Connected | 0.15
Scotland | Fort William Project 42 | Fort William |  |  | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 43 |  |  | Strontian | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 44 |  |  | Kingairloch | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 45 | Fort William |  |  | Hydro | LV | Connected | 0.075
Scotland | Fort William Project 46 | Fort William |  |  | Hydro | LV | Connected | 0.049
Scotland | Fort William Project 47 | Fort William |  |  | Hydro | 33kV | Connected | 1
Scotland | Fort William Project 48 | Fort William |  |  | Hydro | 11kV | Connected | 1.75
Scotland | Fort William Project 49 | Fort William |  |  | Hydro | LV | Connected | 0.9
Scotland | Fort William Project 50 | Fort William |  |  | Hydro | LV | Connected | 0.8
Scotland | Fort William Project 51 | Fort William |  |  | Hydro | LV | Connected | 0.5
Scotland | Fort William Project 52 | Fort William |  |  | Hydro | 33kV | Connected | 0.25
Scotland | Fort William Project 53 |  |  | Inverlochy | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 54 | Fort William |  |  | Hydro | 33kV | Connected | 3
Scotland | Fort William Project 55 | Fort William |  |  | Hydro | 33kV | Connected | 0.1
Scotland | Fort William Project 56 | Fort William |  |  | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 57 | Fort William |  |  | Hydro | LV | Connected | 0.95
Scotland | Fort William Project 58 | Fort William |  |  | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 59 | Fort William |  |  | Hydro | 33kV | Connected | 18.1
Scotland | Fort William Project 60 | Fort William |  |  | CHP | LV | Connected | 0.1
Scotland | Fort William Project 61 |  |  | Salen, Mull | Hydro | 33kV | connected | 1.1
Scotland | Fort William Project 62 | Fort William |  |  | Hydro | LV | Connected | 0.1
Scotland | Fort William Project 63 | Fort William |  |  | Hydro | LV | connected | 0.5
Scotland | Fort William Project 64 | Fort William |  |  | Photovoltaic | LV | connected | 0.085
Scotland | Fort William Project 65 | Fort William |  |  | Hydro | 33kV | Contracted | 52 | March 2022
Scotland | Fort William Project 66 | Fort William |  |  | Wind | 11kV | Connected | 0.1
Scotland | Fraserburgh Project 01 |  |  | Lochaline | Wind | 33kV | Connected | 1.6
Scotland | Fraserburgh Project 02 |  |  | Fraserburgh | Wind | LV | Connected | 0.09
Scotland | Fraserburgh Project 03 |  |  | Fraserburgh | Wind | LV | Connected | 0.09
Scotland | Fraserburgh Project 04 |  |  | Fraserburgh | Wind | 11kV | Connected | 0.9
Scotland | Fraserburgh Project 05 |  |  | Fraserburgh | Wind | 11kV | Connected | 0.4
Scotland | Fraserburgh Project 06 |  |  | Fraserburgh | Wind | LV | Connected | 0.33
Scotland | Fraserburgh Project 07 |  |  | Fraserburgh | Wind | LV | Connected | 0.1
Scotland | Fraserburgh Project 08 |  |  | Fraserburgh | Wind | LV | Connected | 0.09
Scotland | Fraserburgh Project 09 |  |  | Fraserburgh | CHP | 33kV | Contracted | 35 | October 2023
Scotland | Fraserburgh Project 10 |  |  | Fraserburgh | Other | 33kV | Contracted | 25 | March 2022
Scotland | Fraserburgh Project 11 |  |  | Fraserburgh | Photovoltaic | LV | Contracted | 0.85 | March 2022
Scotland | Fraserburgh Project 12 |  |  | Fraserburgh | P.V. | LV | Contracted | 0.15 | January 2022
Scotland | Fraserburgh Project 13 |  |  | Fraserburgh | P.V. | LV | Contracted | 0.15 | August 2022
Scotland | Fraserburgh Project 14 |  |  | Fraserburgh | P.V. | 11kV | Contracted | 0.11 | December 2022
Scotland | Fraserburgh Project 15 |  |  | Fraserburgh | Battery | 33kV | Contracted | 50 | March 2025
Scotland | Fraserburgh Project 16 |  |  | Fraserburgh | Battery | 33kV | Contracted | 45 | October 2023
Scotland | Glenagnes Project 01 |  |  | Overgate | CHP | 11kV | Connected | 3
Scotland | Glenagnes Project 02 |  |  | Overgate | Wind | LV | Connected | 0.045
Scotland | Grudie Bridge Project 01 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 3
Scotland | Grudie Bridge Project 02 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 2.5
Scotland | Grudie Bridge Project 03 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 2
Scotland | Grudie Bridge Project 04 | Grudie Bridge |  |  | Hydro | 11kV | Connected | 1.2
Scotland | Grudie Bridge Project 05 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 1
Scotland | Grudie Bridge Project 06 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.815
Scotland | Grudie Bridge Project 07 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.15
Scotland | Grudie Bridge Project 08 |  |  | Kerry Falls | Hydro | 11kV | Connected | 0.24
Scotland | Grudie Bridge Project 09 |  |  | Lochinver | Hydro | LV | Connected | 0.1
Scotland | Grudie Bridge Project 10 |  |  | Ullapool | Hydro | 33kV | Connected | 2.4
Scotland | Grudie Bridge Project 11 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 1
Scotland | Grudie Bridge Project 12 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 2
Scotland | Grudie Bridge Project 13 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 1.5
Scotland | Grudie Bridge Project 14 | Grudie Bridge |  |  | Hydro | 11kV | Connected | 1.5
Scotland | Grudie Bridge Project 15 |  |  | Kerry Falls | Hydro | LV | Connected | 1.35
Scotland | Grudie Bridge Project 16 | Grudie Bridge |  |  | Hydro | LV | Connected | 1.2
Scotland | Grudie Bridge Project 17 | Grudie Bridge |  |  | Hydro | LV | Connected | 1.195
Scotland | Grudie Bridge Project 18 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.999
Scotland | Grudie Bridge Project 19 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.5
Scotland | Grudie Bridge Project 20 |  |  | Kinlochewe | Hydro | LV | Connected | 0.5
Scotland | Grudie Bridge Project 21 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.5
Scotland | Grudie Bridge Project 22 | Grudie Bridge |  |  | Hydro | 11kV | Connected | 0.42
Scotland | Grudie Bridge Project 23 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.4
Scotland | Grudie Bridge Project 24 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.5
Scotland | Grudie Bridge Project 25 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.25
Scotland | Grudie Bridge Project 26 |  |  | Kerry Falls | Hydro | LV | Connected | 0.1
Scotland | Grudie Bridge Project 27 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.1
Scotland | Grudie Bridge Project 28 |  |  | Letterewe | Hydro | LV | Connected | 0.096
Scotland | Grudie Bridge Project 29 |  |  | Aultbea | Hydro | LV | Connected | 0.05
Scotland | Grudie Bridge Project 30 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.099
Scotland | Grudie Bridge Project 31 |  |  | Aultbea | Hydro | 11kV | Connected | 1.3
Scotland | Grudie Bridge Project 32 |  |  | Kerry Falls | Hydro | 11kV | Connected | 0.3
Scotland | Grudie Bridge Project 33 |  |  | Loch Glascarnoch | Hydro | 33kV | Connected | 3.5
Scotland | Grudie Bridge Project 34 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.5
Scotland | Grudie Bridge Project 35 | Grudie Bridge |  |  | Hydro | 33kV | Contracted | 2 | June 2025
Scotland | Grudie Bridge Project 36 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 0.1
Scotland | Grudie Bridge Project 37 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.1
Scotland | Grudie Bridge Project 38 | Grudie Bridge |  |  | Hydro | 11kV | Connected | 0.08
Scotland | Grudie Bridge Project 39 |  |  | Achiltibuie | Hydro | LV | Connected | 0.1
Scotland | Grudie Bridge Project 40 |  |  | Aultbea | P.V. | 33kV | Contracted | 0.999 | June 2023
Scotland | Grudie Bridge Project 41 | Grudie Bridge |  |  | Hydro | LV | Connected | 0
Scotland | Grudie Bridge Project 42 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.5
Scotland | Grudie Bridge Project 43 | Grudie Bridge |  |  | Wind | 11kv | Connected | 0.5
Scotland | Grudie Bridge Project 44 |  |  | Achiltibuie | Hydro | LV | Connected | 0.1
Scotland | Grudie Bridge Project 45 | Grudie Bridge |  |  | Hydro | LV | Connected | 0.05
Scotland | Grudie Bridge Project 46 | Grudie Bridge |  |  | Hydro | 11kV | Contracted | 0.5 | March 2022
Scotland | Grudie Bridge Project 47 | Grudie Bridge |  |  | Hydro | 33kV | Connected | 1.5
Scotland | Grudie Bridge Project 48 | Grudie Bridge |  |  | Hydro | 11kV | Connected | 2
Scotland | Grudie Bridge Project 49 | Grudie Bridge |  |  | Hydro | 33kV | Contracted | 0.5 | March 2022
Scotland | Grudie Bridge Project 50 | Grudie Bridge |  |  | Wind | 33kV | Connected | 21.66
Scotland | Inverness Project 01 | Inverness |  |  | Hydro | 33kV | Connected | 5
Scotland | Inverness Project 02 | Inverness |  |  | Hydro | 11kV | Connected | 0.75
Scotland | Inverness Project 03 |  |  | Errogie | Wind | 11kV | Connected | 0.5
Scotland | Inverness Project 04 |  |  | Errogie | CHP | LV | Connected | 0.23
Scotland | Inverness Project 05 |  |  | Inverness | CHP | LV | Connected | 0.12
Scotland | Inverness Project 06 |  |  | Culloden | Wind | 33kV | Connected | 60
Scotland | Inverness Project 07 | Inverness |  |  | Hydro | 11kV | Connected | 0.5
Scotland | Inverness Project 08 |  |  | Inverarnie | Hydro | LV | Connected | 0.5
Scotland | Inverness Project 09 | Inverness |  |  | Hydro | LV | Connected | 0.2
Scotland | Inverness Project 10 |  |  | Inverness | Gas | 11kV | Connected | 0.24
Scotland | Inverness Project 11 |  |  | Culloden | CHP | LV | Connected | 0
Scotland | Inverness Project 12 |  |  | Hilton | Gas | 11kV | Contracted | 1.2 | March 2022
Scotland | Inverness Project 13 | Inverness |  |  | Hydro | LV | Contracted | 0.1 | March 2022
Scotland | Inverness Project 14 | Inverness |  |  | Photovoltaic | LV | Connected | 0.08
Scotland | Inverness Project 15 | Inverness |  |  | Photovoltaic | LV | Connected | 0.2
Scotland | Inverness Project 16 | Inverness |  |  | Photovoltaic | LV | Contracted | 0.165 | March 2022
Scotland | Inverness Project 17 | Inverness |  |  | Photovoltaic | LV | Contracted | 0.148 | March 2022
Scotland | Inverness Project 18 | Inverness |  |  | Battery | 33kV | Contracted | 49.9 | December 2025
Scotland | Inverness Project 19 | Inverness |  |  | Battery | 33kV | Contracted | 52 | July 26
Scotland | Keith Project 01 | Keith |  |  | Wind | 33kV | Connected | 12.25
Scotland | Keith Project 02 | Keith |  |  | Biomass | 33kV | Connected | 4.999
Scotland | Keith Project 03 | Keith |  |  | Wind | 33kV | Connected | 4.6
Scotland | Keith Project 04 | Keith |  |  | Wind | 33kV | Connected | 4.6
Scotland | Keith Project 05 | Keith |  |  | Biomass | 33kV | Connected | 3
Scotland | Keith Project 06 | Keith |  |  | Wind | 11kV | Connected | 2.4
Scotland | Keith Project 07 |  |  | Marnoch | BioGas | 11kV | Connected | 1
Scotland | Keith Project 08 |  |  | Buckie | Wind | 33kV | Connected | 0.85
Scotland | Keith Project 09 | Keith |  |  | Wind | 11kV | Connected | 0.225
Scotland | Keith Project 10 |  |  | Marnoch | Wind | 11kV | Connected | 0.2
Scotland | Keith Project 11 |  |  | Marnoch | Wind | LV | Connected | 0.09
Scotland | Keith Project 12 |  |  | Insch | Wind | 33kV | Connected | 14.1
Scotland | Keith Project 13 | Keith |  |  | Wind | 33kV | Connected | 9.99
Scotland | Keith Project 14 | Keith |  |  | CHP | 33kV | Connected | 9.9
Scotland | Keith Project 15 | Keith |  |  | Wind | 33kV | Connected | 6
Scotland | Keith Project 16 | Keith |  |  | CHP | 33kV | Connected | 5.1
Scotland | Keith Project 17 | Keith |  |  | Wind | 33kV | Connected | 1.6
Scotland | Keith Project 18 | Keith |  |  | Wind | 11kV | Connected | 0.8
Scotland | Keith Project 19 |  |  | Marnoch | Wind | 11kV | Connected | 0.8
Scotland | Keith Project 20 |  |  | Limehillocks | Wind | 33kV | Connected | 0.8
Scotland | Keith Project 21 | Keith |  |  | Wind | 11kV | Connected | 0.5
Scotland | Keith Project 22 |  |  | Marnoch | Wind | LV | Connected | 0.5
Scotland | Keith Project 23 | Keith |  |  | AD | 11kV | Connected | 0.5
Scotland | Keith Project 24 |  |  | Aberlour | Wind | 11kV | Connected | 0.5
Scotland | Keith Project 25 |  |  | Keith | Wind | 11kV | Connected | 0.5
Scotland | Keith Project 26 |  |  | Cullen | Wind | 11kV | Connected | 0.5
Scotland | Keith Project 27 |  |  | Keith | Wind | 11kV | Connected | 0.5
Scotland | Keith Project 28 | Keith |  |  | Wind | 11kV | Connected | 0.5
Scotland | Keith Project 29 |  |  | Huntly | Wind | 11kV | Connected | 0.45
Scotland | Keith Project 30 |  |  | Marnoch | Wind | 33kV | Connected | 0.45
Scotland | Keith Project 31 | Keith |  |  | Wind | 11kV | Connected | 0.3
Scotland | Keith Project 32 |  |  | Limehillocks | Wind | 11kV | Connected | 0.225
Scotland | Keith Project 33 |  |  | Marnoch | Hydro | 11kV | Connected | 0.056
Scotland | Keith Project 34 |  |  | Limehillocks | Wind | 11kV | Connected | 0.025
Scotland | Keith Project 35 |  |  | Marnoch | Wind | LV | Connected | 0.5
Scotland | Keith Project 36 |  |  | Huntly | Wind | LV | Connected | 0.18
Scotland | Keith Project 37 |  |  | Keith | Wind | LV | Connected | 0.053
Scotland | Keith Project 38 | Keith |  |  | BioGas | LV | Connected | 0.05
Scotland | Keith Project 39 |  |  | Dufftown | Wind | 33kV | Connected | 48.3
Scotland | Keith Project 40 | Keith |  |  | Wind | 33kV | Contracted | 15 | August 2023
Scotland | Keith Project 41 | Keith |  |  | Wind | 33kV | Contracted | 1.05 | October 2022
Scotland | Keith Project 42 | Keith |  |  | Wind | 33kV | Contracted | 4.3 | October 2022
Scotland | Keith Project 43 | Keith |  |  | Battery | 33kV | Contracted | 9.9 | October 2022
Scotland | Keith Project 44 | Keith |  |  | Gas | 33kV | Connected | 0.001
Scotland | Keith Project 45 | Keith |  |  | Wind | 33kV | Contracted | 36 | October 2022
Scotland | Keith Project 46 | Keith |  |  | Wind | 33kV | Contracted | 4.7 | August 2023
Scotland | Keith Project 47 | Keith |  |  | Wind | 33kV | Contracted | 14 | March 2022
Scotland | Keith Project 48 | Keith |  |  | Gas | 11kV | Contracted | 0.199 | September 2022
Scotland | Keith Project 49 | Keith |  |  | Wind | 11kV | Connected | 0.8
Scotland | Keith Project 50 | Keith |  |  | Wind | LV | Connected | 0.05
Scotland | Keith Project 51 | Keith |  |  | Wind | LV | Connected | 0.05
Scotland | Keith Project 52 | Keith |  |  | Wind | 33kV | Connected | 13
Scotland | Keith Project 53 | Keith |  |  | CHP | LV | Contracted | 0.199 | October 2022
Scotland | Keith Project 54 | Keith |  |  | Photovoltaic | LV | Connected | 0.04
Scotland | Keith Project 55 | Keith |  |  | Battery | 33kV | Contracted | 49 | October 2023
Scotland | Keith Project 56 | Keith |  |  | Battery | 33kV | Contracted | 49.5 | June 2024
Scotland | Keith Project 57 | Keith |  |  | CHP | LV | Contracted | 0.05 | January 2022
Scotland | Keith Project 58 | Keith |  |  | Other | 11kV | Contracted | 1.065 | March 2024
Scotland | Keith Project 59 | Keith |  |  | Wind | 33kV | Contracted | 46.2 | November 2024
Scotland | Keith Project 60 | Keith |  |  | Battery | 33kV | Contracted | 49.99 | January 2025
Scotland | Killin Project 01 | Killin |  |  | Hydro | 33kV | Connected | 11.6
Scotland | Killin Project 02 | Killin |  |  | Hydro | 33kV | Connected | 4.2
Scotland | Killin Project 03 | Killin |  |  | Hydro | 33kV | Connected | 2.1
Scotland | Killin Project 04 | Killin |  |  | Hydro | LV | Connected | 1
Scotland | Killin Project 05 | Killin |  |  | Hydro | LV | Connected | 1
Scotland | Killin Project 06 | Killin |  |  | Hydro | LV | Connected | 0.95
Scotland | Killin Project 07 | Killin |  |  | Hydro | LV | Connected | 0.9
Scotland | Killin Project 08 | Killin |  |  | Hydro | LV | Connected | 0.81
Scotland | Killin Project 09 | Killin |  |  | Hydro | 11kV | Connected | 0.7
Scotland | Killin Project 10 |  |  | Lochearnhead | Hydro | LV | Connected | 0.6
Scotland | Killin Project 11 | Killin |  |  | Hydro | 33kV | Connected | 0.5
Scotland | Killin Project 12 | Killin |  |  | Hydro | LV | Connected | 0.45
Scotland | Killin Project 13 | Killin |  |  | Hydro | LV | Connected | 0.2
Scotland | Killin Project 14 | Killin |  |  | Hydro | LV | Connected | 0.1
Scotland | Killin Project 15 |  |  | Lochearnhead | Hydro | LV | Connected | 0.1
Scotland | Killin Project 16 |  |  | Lochearnhead | Hydro | LV | Connected | 0.1
Scotland | Killin Project 17 | Killin |  |  | Biomass | 33kV | Connected | 5.6
Scotland | Killin Project 18 | Killin |  |  | Hydro | 11kV | Connected | 1.5
Scotland | Killin Project 19 | Killin |  |  | Hydro | LV | Connected | 0.85
Scotland | Killin Project 20 | Killin |  |  | Hydro | LV | Connected | 0.75
Scotland | Killin Project 21 |  |  | Lochearnhead | Hydro | LV | Connected | 0.5
Scotland | Killin Project 22 | Killin |  |  | Hydro | 11kV | Connected | 0.4
Scotland | Killin Project 23 | Killin |  |  | Hydro | 11kV | Connected | 0.1
Scotland | Killin Project 24 |  |  | Lochearnhead | Hydro | LV | Connected | 0.1
Scotland | Killin Project 25 | Killin |  |  | Hydro | LV | Connected | 0.1
Scotland | Killin Project 26 |  |  | Killin Town | Hydro | 11kV | Connected | 0.1
Scotland | Killin Project 27 | Killin |  |  | Hydro | 33kV | Contracted | 2.2 | August 2022
Scotland | Killin Project 28 | Killin |  |  | Hydro | 11kV | Connected | 2
Scotland | Killin Project 29 | Killin |  |  | Hydro | LV | Connected | 1.2
Scotland | Killin Project 30 | Killin |  |  | Hydro | 11kV | Connected | 0.8
Scotland | Killin Project 31 | Killin |  |  | Hydro | 11kV | Connected | 0.6
Scotland | Killin Project 32 |  |  | Lochearnhead | Wind | LV | Connected | 0.15
Scotland | Killin Project 33 | Killin |  |  | Hydro | LV | Connected | 0.1
Scotland | Killin Project 34 | Killin |  |  | Hydro | LV | Connected | 0.1
Scotland | Killin Project 35 | Killin |  |  | Hydro | LV | Connected | 0.1
Scotland | Killin Project 36 | Killin |  |  | Hydro | LV | Connected | 0.06
Scotland | Killin Project 37 | Killin |  |  | Hydro | LV | Connected | 0.09
Scotland | Killin Project 38 | Killin |  |  | Hydro | LV | Contracted | 0.09 | January 2022
Scotland | Killin Project 39 | Killin |  |  | Hydro | LV | Connected | 0.2
Scotland | Killin Project 40 | Killin |  |  | Hydro | LV | Contracted | 0.42 | March 2022
Scotland | Killin Project 41 |  |  | Lochearnhead | Hydro | LV | Connected | 0.1
Scotland | Killin Project 42 |  |  |  | Battery | 33kV | Contracted | 49.4 | November 2025
Scotland | Kinlochleven Project 01 | Kinlochleven |  |  | Hydro | 33kV | Connected | 20
Scotland | Kinlochleven Project 02 | Kinlochleven |  |  | Hydro | 33kV | Connected | 4
Scotland | Kinlochleven Project 03 | Kinlochleven |  |  | Hydro | 33kV | Connected | 2
Scotland | Kinlochleven Project 04 |  |  | Kinlochleven | Hydro | LV | Contracted | 0.7 | March 2022
Scotland | Kinlochleven Project 05 | Kinlochleven |  |  | Hydro | 33kV | Connected | 0.999
Scotland | Kinlochleven Project 06 | Kinlochleven |  |  | Hydro | 33kV | Connected | 8.5
Scotland | Kinlochleven Project 07 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 1.36 | March 2022
Scotland | Kinlochleven Project 08 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 0.809 | March 2022
Scotland | Kinlochleven Project 09 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 1.047 | March 2022
Scotland | Kinlochleven Project 10 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 0.981 | March 2022
Scotland | Kinlochleven Project 11 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 1.047 | March 2022
Scotland | Kinlochleven Project 12 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 1.36 | March 2022
Scotland | Kinlochleven Project 13 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 0.586 | March 2022
Scotland | Kinlochleven Project 14 |  |  | Kinlochleven | Hydro | 11kV | Contracted | 0.99 | March 2022
Scotland | Kintore Project 01 | Kintore |  |  | Wind | 33kV | Connected | 12.5
Scotland | Kintore Project 02 | Kintore |  |  | Wind | 33kV | Connected | 4.6
Scotland | Kintore Project 03 | Kintore |  |  | Wind | 33kV | Connected | 2.4
Scotland | Kintore Project 04 | Kintore |  |  | Wind | 33kV | Connected | 2.3
Scotland | Kintore Project 05 | Kintore |  |  | Wind | 33kV | Connected | 2.3
Scotland | Kintore Project 06 | Kintore |  |  | Wind | 11kV | Connected | 1.7
Scotland | Kintore Project 07 |  |  | Methlick | Wind | 11kV | Connected | 1.7
Scotland | Kintore Project 08 |  |  | Fyvie | Wind | 11kV | Connected | 1.2
Scotland | Kintore Project 09 |  |  | Fyvie | Wind | 11kV | Connected | 1.2
Scotland | Kintore Project 10 |  |  | Fyvie | Wind | 11kV | Connected | 0.9
Scotland | Kintore Project 11 |  |  | Methlick | Wind | 11kV | Connected | 0.9
Scotland | Kintore Project 12 |  |  | Fyvie | Wind | 11kV | Connected | 0.85
Scotland | Kintore Project 13 |  |  | Fyvie | Wind | 11kV | Connected | 0.85
Scotland | Kintore Project 14 |  |  | Inverurie | Wind | LV | Connected | 0.8
Scotland | Kintore Project 15 |  |  | Oldmeldrum | Wind | 11kV | Connected | 0.8
Scotland | Kintore Project 16 |  |  | Oldmeldrum | Wind | 11kV | Connected | 0.6
Scotland | Kintore Project 17 |  |  | Fyvie | Wind | 11kV | Connected | 0.45
Scotland | Kintore Project 18 |  |  | Torryburn | Wind | LV | Connected | 0.45
Scotland | Kintore Project 19 | Kintore |  |  | Wind | 11kV | Connected | 0.45
Scotland | Kintore Project 20 |  |  | Skene | Wind | 11kV | Connected | 0.45
Scotland | Kintore Project 21 |  |  | Midmar | Wind | 11kV | Connected | 0.225
Scotland | Kintore Project 22 |  |  | Inverurie | Wind | 11kV | Connected | 0.225
Scotland | Kintore Project 23 |  |  | Inverurie | P.V. | LV | Connected | 0.15
Scotland | Kintore Project 24 |  |  | Torryburn | CHP | 11kV | Connected | 0.1
Scotland | Kintore Project 25 |  |  | Banchory | Wind | LV | Connected | 0.09
Scotland | Kintore Project 26 |  |  | Inverurie | Wind | LV | Connected | 0.073
Scotland | Kintore Project 27 |  |  | Methlick | Wind | LV | Connected | 0.053
Scotland | Kintore Project 28 |  |  | Methlick | P.V. | LV | Connected | 0.05
Scotland | Kintore Project 29 |  |  | Oldmeldrum | P.V. | LV | Connected | 0.05
Scotland | Kintore Project 30 |  |  | Torryburn | Wind | LV | Connected | 0.045
Scotland | Kintore Project 31 |  |  | Insch | Wind | 33kV | Connected | 6.9
Scotland | Kintore Project 32 | Kintore |  |  | Wind | 33kV | Connected | 2.4
Scotland | Kintore Project 33 |  |  | Midmar | Wind | 33kV | Connected | 2.3
Scotland | Kintore Project 34 | Kintore |  |  | Wind | 11kV | Connected | 0.8
Scotland | Kintore Project 35 |  |  | Oldmeldrum | Wind | 11kV | Connected | 0.5
Scotland | Kintore Project 36 |  |  | Fyvie | Wind | 11kV | Connected | 0.5
Scotland | Kintore Project 37 |  |  | Fyvie | Wind | 11kV | Connected | 0.5
Scotland | Kintore Project 38 |  |  | Methlick | Wind | 11kV | Connected | 0.5
Scotland | Kintore Project 39 |  |  | Fyvie | Wind | 11kV | Connected | 0.45
Scotland | Kintore Project 40 |  |  | Midmar | Wind | 11kV | Connected | 0.45
Scotland | Kintore Project 41 |  |  | Midmar | Wind | LV | Connected | 0.33
Scotland | Kintore Project 42 | Kintore |  |  | Wind | LV | Connected | 0.33
Scotland | Kintore Project 43 | Kintore |  |  | Wind | 11kV | Connected | 0.225
Scotland | Kintore Project 44 |  |  | Inverurie | Wind | 11kV | Connected | 0.225
Scotland | Kintore Project 45 |  |  | Midmar | Wind | LV | Connected | 0.18
Scotland | Kintore Project 46 |  |  | Insch | P.V. | 33kV | Contracted | 8.75 | March 2022
Scotland | Kintore Project 47 | Kintore |  |  | CHP | LV | Connected | 0.05
Scotland | Kintore Project 48 |  |  | Insch | P.V. | LV | Connected | 0.25
Scotland | Kintore Project 49 |  |  | Torryburn | Waste | 11kV | Connected | 0.5
Scotland | Kintore Project 50 |  |  | Torryburn | P.V. | 11kV | Connected | 0.05
Scotland | Kintore Project 51 | Kintore |  |  | Other | LV | Connected | 0.05
Scotland | Kintore Project 52 | Kintore |  |  | Wind | 11kV | Contracted | 1.5 | March 2022
Scotland | Kintore Project 53 | Kintore |  |  | P.V. | 11kV | Connected | 0.15
Scotland | Kintore Project 54 | Kintore |  |  | Battery | 33kV | Contracted | 49.9 | March 2022
Scotland | Kintore Project 55 | Kintore |  |  | Photovoltaic | LV | Connected | 0.14
Scotland | Kintore Project 56 | Kintore |  |  | CHP | LV | Connected | 0.02
Scotland | Kintore Project 57 | Kintore |  |  | Wind | 33kV | Connected | 13
Scotland | Kintore Project 58 | Kintore |  |  | Wind | 11kV | Connected | 0.08
Scotland | Kintore Project 59 | Kintore |  |  | Other | 33kV | Contracted | 40 | July 2023
Scotland | Kintore Project 60 | Kintore |  |  | Battery | 33kV | Contracted | 49.9 | August 2024
Scotland | Kintore Project 61 | Kintore |  |  | Battery | 33kV | Contracted | 50 | August 2023
Scotland | Kintore Project 62 | Kintore |  |  | Battery | 33kV | Contracted | 49.9 | January 2024
Scotland | Kintore Project 63 | Kintore |  |  | Battery | 33kV | Contracted | 49.9 | March 2023
Scotland | Kintore Project 64 | Kintore |  |  | P.V. | LV | Contracted | 0.11 | June 2022
Scotland | Kintore Project 65 | Kintore |  |  | P.V. | LV | Contracted | 0.167 | December 2022
Scotland | Kintore Project 66 | Kintore |  |  | P.V. | LV | Contracted | 0.08 | December 2022
Scotland | Kintore Project 67 | Kintore |  |  | Wind | 33kV | Contracted | 4.5 | Jan 25
Scotland | Lairg Project 01 | Lairg |  |  | Wind | 33kV | Connected | 38
Scotland | Lairg Project 02 | Lairg |  |  | Wind | 33kV | Connected | 4.99
Scotland | Lairg Project 03 | Lairg |  |  | Hydro | 33kV | Connected | 3.7
Scotland | Lairg Project 04 | Lairg |  |  | Hydro | LV | Connected | 0.1
Scotland | Lairg Project 05 | Lairg |  |  | Wind | 33kV | Connected | 2.5
Scotland | Lairg Project 06 | Lairg |  |  | Hydro | LV | Connected | 0.045
Scotland | Lairg Project 07 | Lairg |  |  | Wind | 33kV | Contracted | 34.8 | August 2024
Scotland | Lunanhead Project 01 | Lunanhead |  |  | BioGas | 11kV | Connected | 2
Scotland | Lunanhead Project 02 |  |  | Lunanhead | Biomass | LV | Connected | 1
Scotland | Lunanhead Project 03 |  |  | Friokheim | Wind | 33kV | Connected | 0.5
Scotland | Lunanhead Project 04 |  |  | Lunanhead | Wind | 11kV | Connected | 0.5
Scotland | Lunanhead Project 05 |  |  | Friokheim | Wind | LV | Connected | 0.45
Scotland | Lunanhead Project 06 |  |  | Maryton | Hydro | 11kV | Connected | 0.45
Scotland | Lunanhead Project 07 |  |  | Maryton | Wind | 11kV | Connected | 0.45
Scotland | Lunanhead Project 08 |  |  | Inverarity | Wind | 33kV | Connected | 0.33
Scotland | Lunanhead Project 09 |  |  | Lunanhead | Hydro | LV | Connected | 0.3
Scotland | Lunanhead Project 10 |  |  | Maryton | Wind | LV | Connected | 0.25
Scotland | Lunanhead Project 11 |  |  | Inverarity | Hydro | LV | Connected | 0.23
Scotland | Lunanhead Project 12 |  |  | Maryton | P.V. | LV | Connected | 0.1
Scotland | Lunanhead Project 13 |  |  | Lunanhead | Hydro | LV | Connected | 0.1
Scotland | Lunanhead Project 14 |  |  | Lunanhead | Wind | LV | Connected | 0.1
Scotland | Lunanhead Project 15 |  |  | Maryton | Wind | 11kV | Connected | 0.1
Scotland | Lunanhead Project 16 |  |  | Lunanhead | Wind | LV | Connected | 0.1
Scotland | Lunanhead Project 17 |  |  | Lunanhead | P.V. | LV | Connected | 0.1
Scotland | Lunanhead Project 18 |  |  | Lunanhead | Wind | LV | Connected | 0.09
Scotland | Lunanhead Project 19 |  |  | Friokheim | Wind | LV | Connected | 0.09
Scotland | Lunanhead Project 20 |  |  | Maryton | Wind | LV | Connected | 0.08
Scotland | Lunanhead Project 21 |  |  | Lochside | Wind | LV | Connected | 0.08
Scotland | Lunanhead Project 22 | Lunanhead |  |  | Wind | LV | Connected | 0.07
Scotland | Lunanhead Project 23 |  |  | Lunanhead | Wind | 11kV | Connected | 0.5
Scotland | Lunanhead Project 24 |  |  | Friokheim | Wind | 11kV | Connected | 0.5
Scotland | Lunanhead Project 25 |  |  | Lunanhead | Wind | 11kV | Connected | 0.5
Scotland | Lunanhead Project 26 |  |  | Lunanhead | P.V. | LV | Connected | 0.136
Scotland | Lunanhead Project 27 |  |  | Maryton | Wind | LV | Connected | 0.1
Scotland | Lunanhead Project 28 |  |  | Friokheim | Hydro | LV | Connected | 0.1
Scotland | Lunanhead Project 29 |  |  | Maryton | P.V. | 33kV | Connected | 5
Scotland | Lunanhead Project 30 | Lunanhead |  |  | P.V. | 33kV | Contracted | 5 | March 2022
Scotland | Lunanhead Project 31 | Lunanhead |  |  | P.V. | 33kV | Contracted | 5 | March 2022
Scotland | Lunanhead Project 32 | Lunanhead |  |  | P.V. | LV | Connected | 0.05
Scotland | Lunanhead Project 33 |  |  | Friokheim | P.V. | LV | Connected | 0.05
Scotland | Lunanhead Project 34 |  |  | Lunanhead | P.V. | LV | Connected | 0.04
Scotland | Lunanhead Project 35 |  |  | Friokheim | Other | 33kV | Contracted | 9.999 | March 2022
Scotland | Lunanhead Project 36 | Lunanhead |  |  | Photovoltaic | 33kV | Connected | 0.15
Scotland | Lunanhead Project 37 | Lunanhead |  |  | Battery | 33kV | Contracted | 49.99 | June 2022
Scotland | Lunanhead Project 38 | Lunanhead |  |  | Photovoltaic | 33kV | Contracted | 30 | October 2022
Scotland | Lunanhead Project 39 | Lunanhead |  |  | Photovoltaic | 33kV | Contracted | 5 | October 2022
Scotland | Lunanhead Project 40 | Lunanhead |  |  | Battery | 33kV | Contracted | 22 | January 2022
Scotland | Lunanhead Project 41 | Lunanhead |  |  | Photovoltaic | 33kV | Contracted | 0.18 | May 2023
Scotland | Lunanhead Project 42 | Lunanhead |  |  | P.V. | 33kV | Contracted | 29.8 | October 2022
Scotland | Lunanhead Project 43 | Lunanhead |  |  | Other | 33kV | Contracted | 34.375 | August 2024
Scotland | Lunanhead Project 44 | Lunanhead |  |  | PV | LV | Contracted | 0.16 | October 2022
Scotland | Lunanhead Project 45 | Lunanhead |  |  | Battery | 33kV | Contracted | 30 | Jan 25
Scotland | Lunanhead Project 46 | Lunanhead |  |  | PV | LV | Contracted | 0.18 | May 2025
Scotland | Lunanhead Project 47 | Lunanhead |  |  | Battery | 33kV | Contracted | 49.9 | August 2025
Scotland | Lunanhead Project 48 | Lunanhead |  |  | PV | 11kV | Contracted | 0.1 | May 2025
Scotland | Lunanhead Project 49 | Lunanhead |  |  | P.V. | 11kV | Contracted | 3.4 | December 2023
Scotland | Lyndhurst Project 01 | Lyndhurst |  |  | Hydro | LV | Connected | 0.2
Scotland | Lyndhurst Project 02 |  |  | West Kirkton | P.V. | 11kV | Connected | 0.1
Scotland | Lyndhurst Project 03 |  |  | MacAlpine Road | P.V. | LV | Connected | 0.224
Scotland | Lyndhurst Project 04 | Lyndhurst |  |  | CHP | LV | Connected | 0.086
Scotland | Lyndhurst Project 05 | Lyndhurst |  |  | Battery | 33kV | Contracted | 49.9 | March 2022
Scotland | Lyndhurst Project 06 | Lyndhurst |  |  | Battery | 33kV | Contracted | 49.9 | November 2025
Scotland | Macduff Project 01 | MacDuff |  |  | Wind | 33kV | Connected | 14.3
Scotland | Macduff Project 02 |  |  | MacDuff | Wind | 33kV | Connected | 7
Scotland | Macduff Project 03 |  |  | MacDuff | Wind | 33kV | Connected | 4.6
Scotland | Macduff Project 04 |  |  | MacDuff | Wind | 33kV | Connected | 2.4
Scotland | Macduff Project 05 |  |  | MacDuff | Wind | LV | Connected | 2.3
Scotland | Macduff Project 06 |  |  | Turriff | Wind | 33kV | Connected | 2.3
Scotland | Macduff Project 07 |  |  | MacDuff | Wind | 11kV | Connected | 2.3
Scotland | Macduff Project 08 |  |  | Turriff | Wind | 11kV | Connected | 2
Scotland | Macduff Project 09 |  |  | Portsoy | Wind | 11kV | Connected | 0.9
Scotland | Macduff Project 10 |  |  | MacDuff | Wind | 11kV | Connected | 0.9
Scotland | Macduff Project 11 |  |  | MacDuff | Wind | 11kV | Connected | 0.9
Scotland | Macduff Project 12 |  |  | Turriff | Wind | 11kV | Connected | 0.85
Scotland | Macduff Project 13 |  |  | MacDuff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 14 |  |  | MacDuff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 15 |  |  | Turriff | Wind | LV | Connected | 0.8
Scotland | Macduff Project 16 |  |  | MacDuff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 17 |  |  | Turriff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 18 |  |  | Turriff | BioGas | LV | Connected | 0.5
Scotland | Macduff Project 19 |  |  | Turriff | Wind | 11kV | Connected | 0.5
Scotland | Macduff Project 20 |  |  | Turriff | Wind | LV | Connected | 0.2
Scotland | Macduff Project 21 |  |  | Turriff | Wind | LV | Connected | 0.053
Scotland | Macduff Project 22 |  |  | Turriff | Wind | 33kV | Connected | 0.04
Scotland | Macduff Project 23 |  |  | MacDuff | Wind | 33kV | Connected | 6.9
Scotland | Macduff Project 24 |  |  | MacDuff | Wind | 33kV | Connected | 4.6
Scotland | Macduff Project 25 |  |  | MacDuff | Wind | 11kV | Contracted | 4.6 | March 2022
Scotland | Macduff Project 26 |  |  | MacDuff | Wind | 33kV | Connected | 1.65
Scotland | Macduff Project 27 |  |  | MacDuff | Wind | 11kV | Connected | 2.4
Scotland | Macduff Project 28 |  |  | MacDuff | Wind | 11kV | Contracted | 2.3 | March 2022
Scotland | Macduff Project 29 |  |  | MacDuff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 30 |  |  | MacDuff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 31 |  |  | Turriff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 32 | MacDuff |  |  | Wind | 11kV | Connected | 0.5
Scotland | Macduff Project 33 | MacDuff |  |  | Wind | 11kV | Connected | 0.45
Scotland | Macduff Project 34 |  |  | Turriff | Wind | LV | Connected | 0.45
Scotland | Macduff Project 35 |  |  | MacDuff | Wind | 11kV | Connected | 0.45
Scotland | Macduff Project 36 |  |  | MacDuff | Wind | 11kV | Connected | 0.33
Scotland | Macduff Project 37 |  |  | Turriff | Wind | LV | Connected | 0.3
Scotland | Macduff Project 38 |  |  | MacDuff | Wind | 11kV | Connected | 0.225
Scotland | Macduff Project 39 |  |  | Turriff | Wind | 11kV | Connected | 0.225
Scotland | Macduff Project 40 | MacDuff |  |  | Wind | LV | Connected | 0.2
Scotland | Macduff Project 41 |  |  | Portsoy | Wind | LV | Connected | 0.09
Scotland | Macduff Project 42 |  |  | Portsoy | Wind | 33kV | Connected | 0.053
Scotland | Macduff Project 43 |  |  | MacDuff | Wind | LV | Connected | 4.6
Scotland | Macduff Project 44 |  |  | MacDuff | Wind | 11kV | Connected | 0.8
Scotland | Macduff Project 45 | MacDuff |  |  | CHP | 11kV | Connected | 0.199
Scotland | Macduff Project 46 |  |  | MacDuff | Wind | LV | Connected | 0.05
Scotland | Macduff Project 47 |  |  | MacDuff | Wind | 11kV | Connected | 1
Scotland | Macduff Project 48 | MacDuff |  |  | Other | 33kV | Contracted | 20 | October 2022
Scotland | Macduff Project 49 | MacDuff |  |  | Wind | 33kV | Connected | 0.8
Scotland | Macduff Project 50 | MacDuff |  |  | P.V. | 33kV | Contracted | 35 | June 2024
Scotland | Macduff Project 51 | MacDuff |  |  | P.V. | 33kV | Contracted | 35.2 | May 2025
Scotland | Macduff Project 52 | MacDuff |  |  | CHP | 33kV | Contracted | 49.9 | July 2025
Scotland | Macduff Project 53 | MacDuff |  |  | Battery | 33kV | Contracted | 49.9 | OCt 2025
Scotland | Milton of Craigie Project 01 | Milton of Craigie |  |  | Waste | 11kV | Connected | 8.7
Scotland | Milton of Craigie Project 02 |  |  | Baldovie | Wind | 11kV | Connected | 4
Scotland | Milton of Craigie Project 03 |  |  | Ashludie | BioGas | 11kV | Connected | 1
Scotland | Milton of Craigie Project 04 |  |  | Longhaugh | Wind | LV | Connected | 0.5
Scotland | Milton of Craigie Project 05 |  |  | Broughty Ferry | P.V. | LV | Connected | 0.05
Scotland | Milton of Craigie Project 06 |  |  | Ashludie | Other | 11kV | Connected | 0.26
Scotland | Milton of Craigie Project 07 |  |  | Baldovie | P.V. | LV | Connected | 0.15
Scotland | Milton of Craigie Project 08 |  |  | Longhaugh | P.V. | LV | Connected | 0.098
Scotland | Milton of Craigie Project 09 |  |  | Baldovie | P.V. | 11kV | Connected | 0.129
Scotland | Milton of Craigie Project 10 | Milton of Craigie |  |  | P.V. | 11kV | Connected | 0.15
Scotland | Milton of Craigie Project 11 | Milton of Craigie |  |  | Gas | 33kV | Contracted | 22.5 | March 2022
Scotland | Milton of Craigie Project 12 | Milton of Craigie |  |  | Photovoltaic | LV | Connected | 0.057
Scotland | Milton of Craigie Project 13 | Milton of Craigie |  |  | CHP | LV | Connected | 0.152
Scotland | Milton of Craigie Project 14 | Milton of Craigie |  |  | Photovoltaic | 33kV | Connected | 9.999
Scotland | Milton of Craigie Project 15 | Milton of Craigie |  |  | Photovoltaic | 33kV | Contracted | 25 | March 2022
Scotland | Milton of Craigie Project 16 | Milton of Craigie |  |  | Gas | 33kV | Contracted | 22.5 | Nov 25
Scotland | Milton of Craigie Project 17 | Milton of Craigie |  |  | Battery | 33kV | Contracted | 49.9 | Dec 26
Scotland | Mybster Project 01 | Mybster |  |  | Wind | 33kV | Connected | 50
Scotland | Mybster Project 02 | Mybster |  |  | Wind | 33kV | Connected | 48
Scotland | Mybster Project 03 | Mybster |  |  | Wind | 33kV | Connected | 9.9
Scotland | Mybster Project 04 | Mybster |  |  | Wind | 33kV | Connected | 6.9
Scotland | Mybster Project 05 | Mybster |  |  | Wind | 33kV | Connected | 4.99
Scotland | Mybster Project 06 | Mybster |  |  | Wind | 33kV | Connected | 4.2
Scotland | Mybster Project 07 | Mybster |  |  | Wind | 11kV | Connected | 2.5
Scotland | Mybster Project 08 |  |  | Wick | Biomass | 11kV | Connected | 1.566
Scotland | Mybster Project 09 |  |  | Hastigrow | Waste | LV | Connected | 0.5
Scotland | Mybster Project 10 | Mybster |  |  | Hydro | LV | Connected | 0.1
Scotland | Mybster Project 11 |  |  | Latheron | Wind | LV | Connected | 0.09
Scotland | Mybster Project 12 |  |  | Latheron | Wind | 33kV | Connected | 0.017
Scotland | Mybster Project 13 | Mybster |  |  | Wind | 33kV | Connected | 22.5
Scotland | Mybster Project 14 | Mybster |  |  | Wind | 33kV | Connected | 20
Scotland | Mybster Project 15 | Mybster |  |  | Biomass | 11kV | Connected | 0.55
Scotland | Mybster Project 16 | Mybster |  |  | Wind | LV | Connected | 0.18
Scotland | Mybster Project 17 |  |  | Wick | Wind | 33kV | Connected | 22.5
Scotland | Mybster Project 18 | Mybster |  |  | Wind | 33kV | Contracted | 36 | September 2025
Scotland | Mybster Project 19 | Mybster |  |  | Wind | 11kV | Connected | 0.1
Scotland | Mybster Project 20 |  |  | Latheron | Wind | 33kV | Contracted | 58 | October 2022
Scotland | Mybster Project 21 | Mybster |  |  | Wind | 33kV | Contracted | 38 | October 2022
Scotland | Mybster Project 22 | Mybster |  |  | Wind | 33kV | Contracted | 25.2 | April 2023
Scotland | Mybster Project 23 | Mybster |  |  | Wind | 33kV | Contracted | 14.97 | August 2025
Scotland | Mybster Project 24 | Mybster |  |  | Wind | 33kV | Contracted | 55 | March 2023
Scotland | Mybster Project 25 | Mybster |  |  | Wind | LV | Contracted | 0.11 | September 2025
Scotland | Mybster Project 26 | Mybster |  |  | Battery | 33kV | Contracted | 21 | October 27
Scotland | Nairn Project 01 | Nairn |  |  | Wind | LV | Connected | 0.3
Scotland | Nairn Project 02 |  |  | Forres | Wind | LV | Connected | 0.3
Scotland | Nairn Project 03 |  |  | Forres | Wind | LV | Connected | 0.1
Scotland | Nairn Project 04 |  |  | Lethen | Hydro | LV | Connected | 0.093
Scotland | Nairn Project 05 | Nairn |  |  | Other | 11kV | Connected | 0.5
Scotland | Nairn Project 06 |  |  | Dalcross | Biodiesel | 11kV | Connected | 0.499
Scotland | Nairn Project 07 |  |  | Dalcross | AD | 33kV | Connected | 0.25
Scotland | Nairn Project 08 | Nairn |  |  | Other | 33kV | Contracted | 49.9 | March 2023
Scotland | Nairn Project 09 | Nairn |  |  | PV | LV | Contracted | 0.035 | March 2022
Scotland | Nairn Project 10 |  |  | Dalcross | Wind | LV | Contracted | 0.19 | March 2022
Scotland | Nairn Project 11 | Nairn |  |  | Battery | 33kV | Contracted | 49.9 | March 2024
Scotland | Nairn Project 12 | Nairn |  |  | Photovoltaic | 33kV | Contracted | 60 | March 2023
Scotland | Nairn Project 13 | Nairn |  |  | Battery | 33kV | Contracted | 49.9 | August 2025
Scotland | Persley Project 01 | Persley |  |  | CHP | 33kV | Connected | 12
Scotland | Persley Project 02 | Persley |  |  | BioGas | 33kV | Connected | 1.065
Scotland | Persley Project 03 | Persley |  |  | BioGas | 11kV | Connected | 2.1
Scotland | Persley Project 04 |  |  | St Machar | CHP | 11kV | Connected | 1.45
Scotland | Persley Project 05 |  |  | Bridge of Don | BioGas | 11kV | Connected | 1.1
Scotland | Persley Project 06 |  |  | St Machar | CHP | LV | Connected | 0.6
Scotland | Persley Project 07 |  |  | Bridge of Don | Wind | 11kV | Connected | 0.33
Scotland | Persley Project 08 |  |  | Bridge of Don | BioGas | 11kV | Connected | 0.33
Scotland | Persley Project 09 |  |  | Whitestripes | CHP | LV | Connected | 0.1
Scotland | Persley Project 10 |  |  | Whitestripes | P.V. | LV | Connected | 0.064
Scotland | Persley Project 11 |  |  | St Machar | P.V. | LV | Connected | 0.085
Scotland | Persley Project 12 |  |  | Bridge of Don | P.V. | 11kV | Connected | 0.1
Scotland | Persley Project 13 |  |  | Bridge of Don | Photovoltaic | 11kV | Connected | 0.075
Scotland | Persley Project 14 |  |  | Dyce North | CHP | LV | Connected | 0.07
Scotland | Persley Project 15 | Persley |  |  | Photovoltaic | LV | Contracted | 0.029 | March 2022
Scotland | Persley Project 16 | Persley |  |  | Other | 11kV | Contracted | 9.4 | September 2022
Scotland | Persley Project 17 | Persley |  |  | Photovoltaic | 11kV | Contracted | 0.2 | October 2022
Scotland | Persley Project 18 | Persley |  |  | Battery | 33kV | Contracted | 63.3 | April 2025
Scotland | Persley Project 19 | Persley |  |  | P.V. | 11kV | Contracted | 0.11 | November 2022
Scotland | Persley Project 20 | Persley |  |  | Battery | 33kV | Contracted | 50 | November 2025
Scotland | Peterhead Grange Project 01 |  |  | Bridge of Don | Wind | 33kV | Connected | 0.85
Scotland | Peterhead Grange Project 02 | Peterhead Grange |  |  | Wind | 33kV | Contracted | 30 | October 2023
Scotland | Peterhead Grange Project 03 | Peterhead Grange |  |  | P.V. | 33kV | Contracted | 35 | October 2023
Scotland | Peterhead Grange Project 04 |  |  | Lochgilphead | Photovoltaic | LV | Connected | 0.075
Scotland | Peterhead Grange Project 05 |  |  | Lochgilphead | CHP | LV | Connected | 0.05
Scotland | Peterhead Grange Project 06 | Peterhead Grange |  |  | P.V. | LV | Contracted | 0.1 | April 2022
Scotland | Peterhead Grange Project 07 | Peterhead Grange |  |  | P.V. | 11kV | Contracted | 0.77 | June 2022
Scotland | Peterhead Grange Project 08 | Peterhead Grange |  |  | Other | 33kV | Contracted | 35 | September 2022
Scotland | Peterhead Grange Project 09 | Peterhead Grange |  |  | Photovoltaic | 11kV | Contracted | 0.1 | October 2022
Scotland | Peterhead Grange Project 10 | Peterhead Grange |  |  | Battery | 33kV | Contracted | 50 | October 2025
Scotland | Port Ann Project 01 | Port Ann |  |  | Wind | 11kV | Connected | 9.95
Scotland | Port Ann Project 02 |  |  | Bowmore | Standby Diesel | 33kV | Connected | 6.2
Scotland | Port Ann Project 03 | Port Ann |  |  | Hydro | LV | Connected | 6
Scotland | Port Ann Project 04 |  |  | Lochgilphead | Hydro | 11kV | Connected | 1.05
Scotland | Port Ann Project 05 |  |  | Tarbert, Loch Fyne | Hydro | 11kV | Connected | 0.9
Scotland | Port Ann Project 06 |  |  | Inverneil | Hydro | LV | Connected | 0.55
Scotland | Port Ann Project 07 |  |  | Crinan | Hydro | 11kV | Connected | 0.5
Scotland | Port Ann Project 08 |  |  | Lochgilphead | Hydro | LV | Connected | 0.5
Scotland | Port Ann Project 09 |  |  | Crinan | Hydro | LV | Connected | 0.5
Scotland | Port Ann Project 10 |  |  | Lochgilphead | Hydro | 11kV | Connected | 0.449
Scotland | Port Ann Project 11 |  |  | Port Ellen | Wind | 11kV | Connected | 0.33
Scotland | Port Ann Project 12 |  |  | Bowmore | Wave | LV | Connected | 0.15
Scotland | Port Ann Project 13 |  |  | Lochgilphead | Hydro | LV | Connected | 0.14
Scotland | Port Ann Project 14 |  |  | Inverneil | Hydro | 11kV | Connected | 0.11
Scotland | Port Ann Project 15 |  |  | Tarbert, Loch Fyne | Hydro | LV | Connected | 0.1
Scotland | Port Ann Project 16 |  |  | Bowmore | P.V. | 33kV | Connected | 0.02
Scotland | Port Ann Project 17 |  |  | Lochgilphead | Wind | 33kV | Connected | 5.9
Scotland | Port Ann Project 18 | Port Ann |  |  | Hydro | 33kV | Connected | 0.55
Scotland | Port Ann Project 19 | Port Ann |  |  | Tidal | 33kV | Contracted | 10 | March 2022
Scotland | Port Ann Project 20 | Port Ann |  |  | Hydro | 11kV | Connected | 1.1
Scotland | Port Ann Project 21 |  |  | Tarbert, Loch Fyne | Hydro | LV | Connected | 0.45
Scotland | Port Ann Project 22 |  |  | Port Askaig | Wind | LV | Connected | 0.05
Scotland | Port Ann Project 23 |  |  | Lochgilphead | Hydro | 33kV | Connected | 0.45
Scotland | Port Ann Project 24 |  |  | Quoich | Hydro | 11kV | Contracted | 0.125 | March 2022
Scotland | Port Ann Project 25 | Port Ann |  |  | Wind | 33kV | Contracted | 50.4 | March 2022
Scotland | Port Ann Project 26 | Port Ann |  |  | Wind | 11kV | Connected | 0.05
Scotland | Port Ann Project 27 | Port Ann |  |  | Gas | 33kV | Contracted | 38.4 | October 2022
Scotland | Port Ann Project 28 | Port Ann |  |  | Hydro | 33kV | Connected | 2.5
Scotland | Port Ann Project 29 | Port Ann |  |  | Hydro | 33kV | Connected | 0.5
Scotland | Port Ann Project 30 | Port Ann |  |  | Hydro | LV | Contracted | 0.03 | September 2022
Scotland | Port Ann Project 31 | Port Ann |  |  | Tidal | 33kV | Contracted | 1.5 | October 2025
Scotland | Port Ann Project 32 | Port Ann |  |  | Wind | 33kV | Contracted | 50 | OCt 2025
Scotland | Quoich Project 01 | Quoich |  |  | Hydro | 11kV | Connected | 3.45
Scotland | Quoich Project 02 | Quoich |  |  | Hydro | 33kV | Connected | 0.4
Scotland | Rannoch Project 01 | Rannoch |  |  | Hydro | 33kV | Connected | 44
Scotland | Rannoch Project 02 | Rannoch |  |  | Hydro | 33kV | Connected | 7.5
Scotland | Rannoch Project 03 | Rannoch |  |  | Hydro | 11kV | Connected | 2.2
Scotland | Rannoch Project 04 |  |  | Tyndrum | Hydro | 11kV | Connected | 0.7
Scotland | Rannoch Project 05 |  |  | Tyndrum | Hydro | LV | Connected | 0.65
Scotland | Rannoch Project 06 | Rannoch |  |  | Hydro | LV | Connected | 0.45
Scotland | Rannoch Project 07 | Rannoch |  |  | Hydro | LV | Connected | 0.45
Scotland | Rannoch Project 08 |  |  | Bridge of Gaur | Hydro | LV | Connected | 0.45
Scotland | Rannoch Project 09 | Rannoch |  |  | Hydro | 33kV | Connected | 0.09
Scotland | Rannoch Project 10 | Rannoch |  |  | Hydro | LV | Connected | 5.5
Scotland | Rannoch Project 11 | Rannoch |  |  | Hydro | 33kV | Connected | 0.8
Scotland | Redmoss Project 01 | Redmoss |  |  | Wind | 33kV | Connected | 9.999
Scotland | Redmoss Project 02 | Redmoss |  |  | Wind | 11kV | Connected | 49.6
Scotland | Redmoss Project 03 |  |  | Newtonhill | Wind | LV | Connected | 2.4
Scotland | Redmoss Project 04 |  |  | Redmoss | P.V. | 11kV | Connected | 0.088
Scotland | Redmoss Project 05 |  |  | Newtonhill | Wind | 11kV | Connected | 0.5
Scotland | Redmoss Project 06 |  |  | Newtonhill | Wind | 33kV | Connected | 0.4
Scotland | Redmoss Project 07 | Redmoss |  |  | Diesel | 33kV | Contracted | 20 | October 2022
Scotland | Redmoss Project 08 | Redmoss |  |  | Other | 33kV | Contracted | 16 | October 2024
Scotland | Redmoss Project 09 | Redmoss |  |  | Photovoltaic | LV | Contracted | 0.233 | March 2022
Scotland | Redmoss Project 10 | Redmoss |  |  | Photovoltaic | LV | Connected | 0.05
Scotland | Redmoss Project 11 | Redmoss |  |  | Photovoltaic | LV | Contracted | 0.3 | July 2022
Scotland | Redmoss Project 12 | Redmoss |  |  | Battery | 33kV | Contracted | 50 | April 2024
Scotland | Redmoss Project 13 | Redmoss |  |  | Photovoltaic | 11kV | Contracted | 0.2 | December 2022
Scotland | Redmoss Project 14 | Redmoss |  |  | Photovoltaic | 11kV | Contracted | 0.1 | December 2022
Scotland | Redmoss Project 15 | Redmoss |  |  | P.V. | 11kV | Contracted | 0.3 | December 2022
Scotland | Shin Project 01 | Shin |  |  | Wind | 33kV | Connected | 24.7
Scotland | Shin Project 02 | Shin |  |  | Hydro | LV | Connected | 18.62
Scotland | Shin Project 03 | Shin |  |  | Hydro | 33kV | Connected | 0.481
Scotland | Shin Project 04 | Shin |  |  | Wind | LV | Contracted | 65 | October 2024
Scotland | Shin Project 05 | Shin |  |  | Hydro | 33kV | Connected | 0.499
Scotland | Shin Project 06 | Shin |  |  | Hydro | 11kV | Connected | 0.499
Scotland | Shin Project 07 | Shin |  |  | Battery | 33kV | Contracted | 50 | December 2025
Scotland | Shin Project 08 | Shin |  |  | Hydro | LV | Connected | 0.087
Scotland | Shin Project 09 | Shin |  |  | Wind | 33kV | Contracted | 68 | December 2023
Scotland | Shin Project 10 | Shin |  |  | Battery | 33kV | Contracted | 50 | June 2026
Scotland | Sloy Project 01 | Shin |  |  | Hydro | 11kV | Connected | 2
Scotland | Sloy Project 02 |  |  | Sloy | Hydro | 11kV | Connected | 0.995
Scotland | Sloy Project 03 | Sloy |  |  | Hydro | 11kV | Connected | 2.8
Scotland | Sloy Project 04 |  |  | Sloy | Hydro | 11kV | Connected | 1.3
Scotland | Sloy Project 05 |  |  | Sloy | Hydro | LV | Connected | 0.115
Scotland | Sloy Project 06 |  |  | Sloy | Hydro | 33kV | Connected | 0.19
Scotland | Sloy Project 07 | Sloy |  |  | Hydro | 11kV | Connected | 72.5
Scotland | Sloy Project 08 | Sloy |  |  | Hydro | 11kV | Connected | 0.097
Scotland | St Fillans Project 01 | St Fillans |  |  | Hydro | 33kV | Connected | 4.2
Scotland | St Fillans Project 02 | St Fillans |  |  | Hydro | 33kV | Connected | 3.2
Scotland | St Fillans Project 03 | St Fillans |  |  | Hydro | 33kV | Connected | 16.83
Scotland | Stornoway Project 01 | St Fillans |  |  | Wind | 33kV | Connected | 13.8
Scotland | Stornoway Project 02 | Stornoway |  |  | Wind | 11kV | Connected | 3.9
Scotland | Stornoway Project 03 |  |  | Battery Point | Standby Diesel | 33kV | Connected | 3
Scotland | Stornoway Project 04 | Stornoway |  |  | Wind | 11kV | Connected | 2.7
Scotland | Stornoway Project 05 |  |  | Callanish | Wind | 11kV | Connected | 0.9
Scotland | Stornoway Project 06 |  |  | Coll | Wind | 11kV | Connected | 0.9
Scotland | Stornoway Project 07 |  |  | Gisla | Hydro | LV | Connected | 0.7
Scotland | Stornoway Project 08 |  |  | Battery Point | Wind | LV | Connected | 0.225
Scotland | Stornoway Project 09 |  |  | Battery Point | Gas | 11kV | Connected | 0.15
Scotland | Stornoway Project 10 | Stornoway |  |  | Wind | 33kV | Connected | 0.08
Scotland | Stornoway Project 11 | Stornoway |  |  | Wind | 33kV | Connected | 9
Scotland | Stornoway Project 12 | Stornoway |  |  | Wind | 33kV | Contracted | 4.2
Scotland | Stornoway Project 13 | Stornoway |  |  | Wind | 11kV | Contracted | 0.05 | October 2024
Scotland | Stornoway Project 14 | Stornoway |  |  | Wind | LV | Contracted | 0 | March 2022
Scotland | Stornoway Project 15 |  |  | Battery Point | Wind | 33kV | Contracted | 49.7 | April 2024
Scotland | Stornoway Project 16 | Stornoway |  |  | Wind | 33kV | Contracted | 5 | October 2024
Scotland | Stornoway Project 17 | Stornoway |  |  | Wind | 33kV | Contracted | 6 | October 2024
Scotland | Stornoway Project 18 | Stornoway |  |  | Standby Diesel | 33kV | Connected | 22.3
Scotland | Stornoway Project 19 | Stornoway |  |  | Wind | 33kV | Contracted | 4 | October 2024
Scotland | Stornoway Project 20 | Stornoway |  |  | Wave | 33kV | Contracted | 3 | October 2025
Scotland | Strathleven Project 01 | Strathleven |  |  | BioGas | 11kV | Connected | 2
Scotland | Strathleven Project 02 | Strathleven |  |  | BioGas | 11kV | Connected | 1.065
Scotland | Strathleven Project 03 | Strathleven |  |  | BioGas | 11kV | Connected | 1
Scotland | Strathleven Project 04 |  |  | Kepculloch | Biomass | LV | Connected | 0.5
Scotland | Strathleven Project 05 |  |  | Blairlinnans | P.V. | LV | Connected | 0.2
Scotland | Strathleven Project 06 |  |  | Kepculloch | Wind | 33kV | Connected | 0.09
Scotland | Strathleven Project 07 | Strathleven |  |  | Wind | 33kV | Contracted | 21 | September 2023
Scotland | Strathleven Project 08 | Strathleven |  |  | Wind | 11kV | Connected | 2.5
Scotland | Strathleven Project 09 |  |  | Aberfoyle | Hydro | 33kV | Connected | 1.5
Scotland | Strathleven Project 10 | Strathleven |  |  | Wind | 11kV | Connected | 0.744
Scotland | Strathleven Project 11 | Strathleven |  |  | Wind | 11kV | Connected | 20
Scotland | Strathleven Project 12 | Strathleven |  |  | BioGas | 11kV | Connected | 0.935
Scotland | Strathleven Project 13 |  |  | Drymen | Hydro | 11kV | Connected | 0.5
Scotland | Strathleven Project 14 |  |  | Kepculloch | BioGas | LV | Connected | 0.5
Scotland | Strathleven Project 15 |  |  | Drymen | Hydro | LV | Connected | 0.65
Scotland | Strathleven Project 16 |  |  | Killearn | Hydro | LV | Connected | 0.1
Scotland | Strathleven Project 17 |  |  | Aberfoyle | Hydro | LV | Connected | 0.1
Scotland | Strathleven Project 18 |  |  | Blairlinnans | Wind | LV | Connected | 0.094
Scotland | Strathleven Project 19 |  |  | Drymen | CHP | LV | Connected | 0.049
Scotland | Strathleven Project 20 |  |  | Kepculloch | CHP | LV | Connected | 0.09
Scotland | Strathleven Project 21 |  |  | Drymen | Hydro | 11kV | Contracted | 0.1 | March 2022
Scotland | Strathleven Project 22 |  |  |  | P.V. | 11kV | Contracted | 0.931 | August 2024
Scotland | Strichen Project 01 | Strichen |  |  | BioGas | 33kV | Connected | 3.2
Scotland | Strichen Project 02 | Strichen |  |  | Wind | 33kV | Connected | 2.4
Scotland | Strichen Project 03 | Strichen |  |  | Wind | 11kV | Connected | 2.4
Scotland | Strichen Project 04 |  |  | Strichen | Wind | 33kV | Connected | 2.4
Scotland | Strichen Project 05 | Strichen |  |  | Wind | 11kV | Connected | 2.4
Scotland | Strichen Project 06 |  |  | Mintlaw | Wind | 33kV | Connected | 2.4
Scotland | Strichen Project 07 | Strichen |  |  | Wind | 11kV | Connected | 2.3
Scotland | Strichen Project 08 |  |  | Strichen | Wind | 11kV | Connected | 0.8
Scotland | Strichen Project 09 |  |  | Strichen | Wind | 11kV | Connected | 0.8
Scotland | Strichen Project 10 |  |  | Mintlaw | Wind | 11kV | Connected | 0.8
Scotland | Strichen Project 11 |  |  | Maud | Wind | 11kV | Connected | 0.8
Scotland | Strichen Project 12 |  |  | Strichen | Wind | 11kV | Connected | 0.8
Scotland | Strichen Project 13 |  |  | Strichen | Wind | LV | Connected | 0.8
Scotland | Strichen Project 14 |  |  | Hatton | Wind | 11kV | Connected | 0.45
Scotland | Strichen Project 15 |  |  | Mintlaw | Wind | LV | Connected | 0.45
Scotland | Strichen Project 16 |  |  | Hatton | Wind | LV | Connected | 0.16
Scotland | Strichen Project 17 |  |  | Maud | Wind | 11kV | Connected | 0.1
Scotland | Strichen Project 18 |  |  | New Pitsligo | Wind | LV | Connected | 0.09
Scotland | Strichen Project 19 |  |  | New Pitsligo | Wind | LV | Connected | 0.09
Scotland | Strichen Project 20 |  |  | Maud | Wind | LV | Connected | 0.05
Scotland | Strichen Project 21 |  |  | Maud | Wind | 33kV | Connected | 1.6
Scotland | Strichen Project 22 | Strichen |  |  | Wind | 11kV | Connected | 0.999
Scotland | Strichen Project 23 |  |  | Strichen | Wind | 11kV | Connected | 0.9
Scotland | Strichen Project 24 |  |  | Maud | Wind | LV | Connected | 0.9
Scotland | Strichen Project 25 | Strichen |  |  | Wind | 11kV | Connected | 0.8
Scotland | Strichen Project 26 | Strichen |  |  | Wind | 11kV | Connected | 0.8
Scotland | Strichen Project 27 |  |  | Strichen | Wind | LV | Connected | 0.8
Scotland | Strichen Project 28 |  |  | Strichen | Wind | LV | Connected | 0.8
Scotland | Strichen Project 29 | Strichen |  |  | Wind | LV | Connected | 0.8
Scotland | Strichen Project 30 | Strichen |  |  | Wind | LV | Connected | 0.8
Scotland | Strichen Project 31 | Strichen |  |  | Wind | LV | Connected | 0.8
Scotland | Strichen Project 32 | Strichen |  |  | Wind | LV | Connected | 0.45
Scotland | Strichen Project 33 |  |  | Maud | Wind | LV | Connected | 0.225
Scotland | Strichen Project 34 |  |  | Strichen | Wind | 11kV | Connected | 0.04
Scotland | Strichen Project 35 | Strichen |  |  | Wind | 33kV | Connected | 2.7
Scotland | Strichen Project 36 | Strichen |  |  | Wind | 33kV | Connected | 2.4
Scotland | Strichen Project 37 | Strichen |  |  | Wind | 11kV | Connected | 2.3
Scotland | Strichen Project 38 | Strichen |  |  | Wind | LV | Connected | 0.8
Scotland | Strichen Project 39 |  |  | Strichen | P.V. | LV | Connected | 0.05
Scotland | Strichen Project 40 |  |  | Strichen | Wind | LV | Connected | 0.098
Scotland | Strichen Project 41 |  |  | MacDuff | P.V. | LV | Connected | 0.063
Scotland | Strichen Project 42 |  |  | Maud | CHP | 33kV | Connected | 0.049
Scotland | Strichen Project 43 | Strichen |  |  | Wind | 33kV | Contracted | 0.9 | March 2022
Scotland | Strichen Project 44 | Strichen |  |  | Wind | 33kV | Connected | 0.1
Scotland | Strichen Project 45 | Strichen |  |  | Wind | 33kV | Connected | 0.999
Scotland | Strichen Project 46 | Strichen |  |  | Wind | 33kV | Contracted | 2.3 | March 2022
Scotland | Strichen Project 47 | Strichen |  |  | Wind | 33kV | Contracted | 1.5 | March 2022
Scotland | Strichen Project 48 | Strichen |  |  | P.V. | 33kV | Contracted | 25 | March 2022
Scotland | Strichen Project 49 | Strichen |  |  | Other | 33kV | Contracted | 25 | December 2022
Scotland | Strichen Project 50 | Strichen |  |  | Other | 33kV | Contracted | 10 | December 2022
Scotland | Strichen Project 51 | Strichen |  |  | Photovoltaic | 33kV | Contracted | 27 | December 2022
Scotland | Strichen Project 52 | Strichen |  |  | Wind | 33kV | Contracted | 0.05 | March 2022
Scotland | Strichen Project 53 | Strichen |  |  | Photovoltaic | 33kV | Contracted | 9.5 | November 2023
Scotland | Strichen Project 54 | Strichen |  |  | Battery | 33kV | Contracted | 49.9 | November 2023
Scotland | Strichen Project 55 | Strichen |  |  | Battery | 33kV | Contracted | 25 | February 2024
Scotland | Strichen Project 56 | Strichen |  |  | P.V. | 11kV | Contracted | 9.9 | February 2023
Scotland | Strichen Project 57 | Strichen |  |  | P.V. | LV | Contracted | 0.1 | August 2022
Scotland | Strichen Project 58 | Strichen |  |  | P.V. | LV | Contracted | 0.06 | October 2022
Scotland | Strichen Project 59 | Strichen |  |  | P.V. | LV | Contracted | 0.086 | December 2022
Scotland | Strichen Project 60 | Strichen |  |  | P.V. | LV | Contracted | 0.204 | Feb 24
Scotland | Tarland Project 01 | Tarland |  |  | Wind | 33kV | Connected | 9.949
Scotland | Tarland Project 02 | Tarland |  |  | Wind | 33kV | Connected | 8.45
Scotland | Tarland Project 03 | Tarland |  |  | Wind | LV | Connected | 2.7
Scotland | Tarland Project 04 |  |  | Ballater | Hydro | LV | Connected | 0.1
Scotland | Tarland Project 05 |  |  | Strathdon | Hydro | LV | Connected | 0.085
Scotland | Tarland Project 06 |  |  | Strathdon | Wind | LV | Connected | 0.08
Scotland | Tarland Project 07 |  |  | Whitehouse | Hydro | LV | Connected | 0.05
Scotland | Tarland Project 08 |  |  | Ballater | Hydro | 11kV | Connected | 0.035
Scotland | Tarland Project 09 | Tarland |  |  | Wind | 11kV | Connected | 2.55
Scotland | Tarland Project 10 |  |  | Mossat | Wind | 33kV | Connected | 0.225
Scotland | Tarland Project 11 | Tarland |  |  | Wind | LV | Connected | 2.4
Scotland | Tarland Project 12 |  |  | Ballater | Hydro | LV | Connected | 0.1
Scotland | Tarland Project 13 |  |  | Aboyne | P.V. | LV | Connected | 0.085
Scotland | Tarland Project 14 |  |  | Aboyne | P.V. | LV | Connected | 0.016
Scotland | Tarland Project 15 |  |  | Aboyne | P.V. | 33kV | Connected | 0.11
Scotland | Tarland Project 16 | Tarland |  |  | Hydro | 33kV | Connected | 2
Scotland | Tarland Project 17 | Tarland |  |  | Other | 33kV | Contracted | 20 | March 2022
Scotland | Tarland Project 18 | Tarland |  |  | Wind | 11kV | Connected | 1.7
Scotland | Tarland Project 19 | Tarland |  |  | Wind | 33kV | Contracted | 2.4 | October 2024
Scotland | Tarland Project 20 | Tarland |  |  | Wind | 33kV | Contracted | 20 | October 2025
Scotland | Taynuilt Project 01 | Taynuilt |  |  | Hydro | 33kV | Connected | 25
Scotland | Taynuilt Project 02 | Taynuilt |  |  | Wind | 11kV | Connected | 8
Scotland | Taynuilt Project 03 | Taynuilt |  |  | Standby Diesel | 33kV | Connected | 2.8
Scotland | Taynuilt Project 04 | Taynuilt |  |  | Hydro | 11kV | Connected | 2.5
Scotland | Taynuilt Project 05 |  |  | Kilmelford | Hydro | 33kV | Connected | 2.1
Scotland | Taynuilt Project 06 | Taynuilt |  |  | Hydro | 11kV | Connected | 2
Scotland | Taynuilt Project 07 | Taynuilt |  |  | Hydro | 11kV | Connected | 1.35
Scotland | Taynuilt Project 08 | Taynuilt |  |  | Hydro | 11kV | Connected | 0.95
Scotland | Taynuilt Project 09 |  |  | Kenmore | Hydro | 11kV | Connected | 0.95
Scotland | Taynuilt Project 10 | Taynuilt |  |  | Wind | LV | Connected | 0.9
Scotland | Taynuilt Project 11 | Taynuilt |  |  | Hydro | 11kV | Connected | 0.8
Scotland | Taynuilt Project 12 |  |  | Barcaldine | Hydro | 33kV | Connected | 0.69
Scotland | Taynuilt Project 13 | Taynuilt |  |  | Wind | 11kV | Connected | 0.6
Scotland | Taynuilt Project 14 |  |  | Kilninver | Wind | 11kV | Connected | 0.6
Scotland | Taynuilt Project 15 | Taynuilt |  |  | Hydro | 33kV | Connected | 0.5
Scotland | Taynuilt Project 16 | Taynuilt |  |  | Hydro | 11kV | Connected | 0.475
Scotland | Taynuilt Project 17 |  |  | Barcaldine | Hydro | 11kV | Connected | 0.45
Scotland | Taynuilt Project 18 | Taynuilt |  |  | Hydro | LV | Connected | 0.335
Scotland | Taynuilt Project 19 |  |  | Salen, Acharacle | Hydro | 11kV | Connected | 0.3
Scotland | Taynuilt Project 20 | Taynuilt |  |  | Hydro | 11kV | Connected | 0.199
Scotland | Taynuilt Project 21 |  |  | Salen, Acharacle | Hydro | LV | Connected | 0.19
Scotland | Taynuilt Project 22 | Taynuilt |  |  | Hydro | LV | Connected | 0.11
Scotland | Taynuilt Project 23 |  |  | Kilninver | Wind | LV | Connected | 0.11
Scotland | Taynuilt Project 24 |  |  | Connel | Hydro | LV | Connected | 0.1
Scotland | Taynuilt Project 25 |  |  | Kilninver | Hydro | LV | Connected | 0.1
Scotland | Taynuilt Project 26 |  |  | Barcaldine | Hydro | LV | Connected | 0.1
Scotland | Taynuilt Project 27 | Taynuilt |  |  | Hydro | LV | Connected | 0.08
Scotland | Taynuilt Project 28 | Taynuilt |  |  | Wind | 33kV | Connected | 0.015
Scotland | Taynuilt Project 29 | Taynuilt |  |  | Hydro | 33kV | Connected | 4.5
Scotland | Taynuilt Project 30 | Taynuilt |  |  | Hydro | LV | Connected | 2
Scotland | Taynuilt Project 31 | Taynuilt |  |  | Hydro | 11kV | Connected | 0.75
Scotland | Taynuilt Project 32 |  |  | Barcaldine | Wind | LV | Connected | 0.67
Scotland | Taynuilt Project 33 | Taynuilt |  |  | Hydro | 11kV | Connected | 0.5
Scotland | Taynuilt Project 34 |  |  | Barcaldine | Hydro | 11kV | Connected | 0.5
Scotland | Taynuilt Project 35 | Taynuilt |  |  | Wind | LV | Connected | 0.399
Scotland | Taynuilt Project 36 |  |  | Kilchrenan | Hydro | LV | Connected | 0.35
Scotland | Taynuilt Project 37 |  |  | Kilmelford | Hydro | LV | Connected | 0.25
Scotland | Taynuilt Project 38 | Taynuilt |  |  | Hydro | LV | Connected | 0.185
Scotland | Taynuilt Project 39 | Taynuilt |  |  | Hydro | LV | Connected | 0.1
Scotland | Taynuilt Project 40 | Taynuilt |  |  | Hydro | LV | Connected | 0.1
Scotland | Taynuilt Project 41 | Taynuilt |  |  | Hydro | LV | Connected | 0.096
Scotland | Taynuilt Project 42 | Taynuilt |  |  | Wind | LV | Contracted | 0.075 | March 2022
Scotland | Taynuilt Project 43 | Taynuilt |  |  | Hydro | 11kV | Connected | 0.9
Scotland | Taynuilt Project 44 | Taynuilt |  |  | Wind | 11kV | Connected | 0.9
Scotland | Taynuilt Project 45 | Taynuilt |  |  | Hydro | LV | Connected | 0.4
Scotland | Taynuilt Project 46 | Taynuilt |  |  | Hydro | LV | Connected | 0.25
Scotland | Taynuilt Project 47 | Taynuilt |  |  | Hydro | LV | Connected | 0.1
Scotland | Taynuilt Project 48 |  |  | Salen, Acharacle | Hydro | 33kV | Connected | 0.1
Scotland | Taynuilt Project 49 | Taynuilt |  |  | Wind | LV | Connected | 0.201
Scotland | Taynuilt Project 50 | Taynuilt |  |  | P.V. | LV | Connected | 0.05
Scotland | Taynuilt Project 51 |  |  | Barcaldine | Hydro | 11kV | Contracted | 6.8 | March 2022
Scotland | Taynuilt Project 52 | Taynuilt |  |  | Hydro | 11kV | Contracted | 0.18 | March 2022
Scotland | Taynuilt Project 53 | Taynuilt |  |  | Hydro | 11kV | Contracted | 0.14 | March 2022
Scotland | Taynuilt Project 54 |  |  | Barcaldine | Hydro | 33kV | Contracted | 0.45 | October 2023
Scotland | Taynuilt Project 55 | Taynuilt |  |  | Hydro | 11kV | Contracted | 0.7 | October 2023
Scotland | Taynuilt Project 56 |  |  | Barcaldine | Hydro | 11kV | Connected | 0.034
Scotland | Taynuilt Project 57 |  |  | Kilninver | Hydro | 11kV | Connected | 0.08
Scotland | Taynuilt Project 58 | Taynuilt |  |  | Hydro | LV | Connected | 0.1
Scotland | Taynuilt Project 59 | Taynuilt |  |  | Hydro | 11kV | Contracted | 0.075 | March 2022
Scotland | Taynuilt Project 60 | Taynuilt |  |  | Wind | LV | Connected | 0.05
Scotland | Taynuilt Project 61 | Taynuilt |  |  | Wind | LV | Contracted | 0.01 | March 2022
Scotland | Taynuilt Project 62 | Taynuilt |  |  | P.V. | LV | Contracted | 0.13 | October 2026
Scotland | Taynuilt Project 63 | Taynuilt |  |  | Wind | 33kV | Contracted | 50 | May 2025
Scotland | Taynuilt Project 64 | Taynuilt |  |  | P.V. | 11kV | Contracted | 0.5 | October 2028
Scotland | Thurso Project 01 | Thurso |  |  | Wind | 33kV | Connected | 0.225
Scotland | Thurso Project 02 | Thurso |  |  | Tidal | 33kV | Connected | 14.9
Scotland | Thurso Project 03 | Thurso |  |  | Wind | 33kV | Connected | 9.2
Scotland | Thurso Project 04 | Thurso |  |  | Wind | LV | Connected | 0.1
Scotland | Thurso Project 05 |  |  | Ormlie | Wind | 33kV | Connected | 30
Scotland | Thurso Project 06 | Thurso |  |  | Biomass | 11kV | Connected | 3.5
Scotland | Thurso Project 07 | Thurso |  |  | Gas | 33kV | Connected | 10
Scotland | Thurso Project 08 | Thurso |  |  | Wind | 11kV | Connected | 7.5
Scotland | Thurso Project 09 |  |  | Stromness | Tidal | 33kV | Connected | 7
Scotland | Thurso Project 10 | Thurso |  |  | Wind | 33kV | Connected | 4.99
Scotland | Thurso Project 11 | Thurso |  |  | Wind | 11kV | Connected | 4.5
Scotland | Thurso Project 12 | Thurso |  |  | Tidal | 11kV | Connected | 4
Scotland | Thurso Project 13 |  |  | Burgar Hill | Wind | 33kV | Connected | 4
Scotland | Thurso Project 14 | Thurso |  |  | Wind | 33kV | Connected | 2.7
Scotland | Thurso Project 15 | Thurso |  |  | Wind | 33kV | Connected | 2.45
Scotland | Thurso Project 16 | Thurso |  |  | Wind | 11kV | Connected | 2.3
Scotland | Thurso Project 17 |  |  | Flotta | Wind | 11kV | Connected | 2
Scotland | Thurso Project 18 |  |  | Flotta | Wind | 11kV | Connected | 1.8
Scotland | Thurso Project 19 |  |  | Burgar Hill | Wind | 11kV | Connected | 1.5
Scotland | Thurso Project 20 |  |  | Shapinsay | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 21 |  |  | Eday | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 22 |  |  | Kirkwall | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 23 |  |  | St Mary's | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 24 |  |  | Rousay | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 25 |  |  | Lyness | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 26 |  |  | Kirkwall | Wind | LV | Connected | 0.9
Scotland | Thurso Project 27 | Thurso |  |  | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 28 |  |  | St Mary's | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 29 |  |  | Westray | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 30 |  |  | Stromness | Wind | 11kV | Connected | 0.9
Scotland | Thurso Project 31 |  |  | Westray | Wind | LV | Connected | 0.5
Scotland | Thurso Project 32 | Thurso |  |  | Wind | 11kV | Connected | 0.5
Scotland | Thurso Project 33 |  |  | Westray | Wind | 11kV | Connected | 0.5
Scotland | Thurso Project 34 |  |  | Burgar Hill | Wind | 11kV | Connected | 0.3
Scotland | Thurso Project 35 |  |  | Stromness | Wind | LV | Connected | 0.3
Scotland | Thurso Project 36 |  |  | Kirkwall | Wind | LV | Connected | 0.08
Scotland | Thurso Project 37 |  |  | Kirkwall | Wind | LV | Connected | 0.08
Scotland | Thurso Project 38 |  |  | Kirkwall | Wind | LV | Connected | 0.08
Scotland | Thurso Project 39 | Thurso |  |  | Wind | LV | Connected | 0.5
Scotland | Thurso Project 40 |  |  | Kirkwall | Wind | LV | Connected | 0.08
Scotland | Thurso Project 41 |  |  | St Mary's | Wind | LV | Connected | 0.08
Scotland | Thurso Project 42 |  |  | Kirkwall | Wind | LV | Connected | 0.055
Scotland | Thurso Project 43 |  |  | Halkirk | Wind | 33kV | Contracted | 36 | November 2023
Scotland | Thurso Project 44 | Thurso |  |  | Standby Diesel | 33kV | Connected | 15.5
Scotland | Thurso Project 45 | Thurso |  |  | Photovoltaic | LV | Contracted | 0.11 | August 2025
Scotland | Thurso Project 46 |  |  | Eday | Tidal Stream WAVE power | 11kV | Contracted | 3.2 | March 2022
Scotland | Thurso Project 47 |  |  | Kirkwall | Wind | 11kV | Contracted | 0.9 | October 2023
Scotland | Thurso Project 48 | Thurso |  |  | Wind | 11kV | Contracted | 1.8 | March 2024
Scotland | Thurso Project 49 | Thurso |  |  | Wind | 11kV | Contracted | 1.8 | March 2024
Scotland | Thurso Project 50 |  |  | Kirkwall | CHP | 11kV | Contracted | 0.115 | May 2023
Scotland | Thurso Project 51 | Thurso |  |  | Wind | 11kV | Contracted | 12.2 | September 2025
Scotland | Thurso Project 52 | Thurso |  |  | Other | 33kV | Contracted | 0.3 | April 2023
Scotland | Thurso Project 53 | Thurso |  |  | Wind | 33kV | Contracted | 17.2 | Feb 2025
Scotland | Thurso Project 54 | Thurso |  |  | Wind | 33kV | Contracted | 13 | October 2028
Scotland | Thurso Project 55 | Thurso |  |  | Wind | 33kV | Contracted | 8 | September 2025
Scotland | Thurso Project 56 | Thurso |  |  | Battery | 33kV | Contracted | 49.9 | June 2027
Scotland | Thurso Project 57 | Thurso |  |  | Battery | 33kV | Contracted | 50 | May 2026
Scotland | Tummel Bridge Project 01 | Tummel Bridge |  |  | Hydro | 33kV | Connected | 2
Scotland | Tummel Bridge Project 02 | Tummel Bridge |  |  | Hydro | 11kV | Connected | 2
Scotland | Tummel Bridge Project 03 |  |  | Kinloch Rannoch | Hydro | 11kV | Connected | 1.4
Scotland | Tummel Bridge Project 04 |  |  | Aberfeldy | Hydro | LV | Connected | 0.9
Scotland | Tummel Bridge Project 05 | Tummel Bridge |  |  | Hydro | 11kV | Connected | 0.75
Scotland | Tummel Bridge Project 06 |  |  | Pitlochry | Hydro | LV | Connected | 0.52
Scotland | Tummel Bridge Project 07 |  |  | Coshieville | Hydro | 11kV | Connected | 0.5
Scotland | Tummel Bridge Project 08 |  |  | Pitlochry | Hydro | LV | Connected | 0.47
Scotland | Tummel Bridge Project 09 |  |  | Coshieville | Hydro | 11kV | Connected | 0.45
Scotland | Tummel Bridge Project 10 |  |  | Coshieville | Hydro | LV | Connected | 0.35
Scotland | Tummel Bridge Project 11 |  |  | Pitlochry | Hydro | LV | Connected | 0.24
Scotland | Tummel Bridge Project 12 | Tummel Bridge |  |  | Hydro | LV | Connected | 0.2
Scotland | Tummel Bridge Project 13 |  |  | Calvine | Hydro | LV | Connected | 0.1
Scotland | Tummel Bridge Project 14 |  |  | Coshieville | Hydro | LV | Connected | 0.1
Scotland | Tummel Bridge Project 15 |  |  | Bonskeid | Hydro | 11kV | Connected | 0.1
Scotland | Tummel Bridge Project 16 |  |  | Kinloch Rannoch | Hydro | 11kV | Connected | 0.65
Scotland | Tummel Bridge Project 17 |  |  | Coshieville | Wind | 11kV | Connected | 0.5
Scotland | Tummel Bridge Project 18 | Tummel Bridge |  |  | Hydro | 11kV | Connected | 0.33
Scotland | Tummel Bridge Project 19 |  |  | Pitlochry | Hydro | 11kV | Connected | 0.259
Scotland | Tummel Bridge Project 20 |  |  | Aberfeldy | Hydro | 33kV | Connected | 0.999
Scotland | Tummel Bridge Project 21 | Tummel Bridge |  |  | Hydro | LV | Connected | 0.834
Scotland | Tummel Bridge Project 22 |  |  | Aberfeldy | Hydro | LV | Connected | 0.3
Scotland | Tummel Bridge Project 23 |  |  | Coshieville | Hydro | LV | Connected | 0.3
Scotland | Tummel Bridge Project 24 |  |  | Aberfeldy | Wind | LV | Connected | 0.25
Scotland | Tummel Bridge Project 25 |  |  | Pitlochry | Hydro | 11kV | Connected | 0.17
Scotland | Tummel Bridge Project 26 | Tummel Bridge |  |  | Hydro | LV | Connected | 0.6
Scotland | Tummel Bridge Project 27 | Tummel Bridge |  |  | Hydro | 11kV | Connected | 0.02
Scotland | Tummel Bridge Project 28 | Tummel Bridge |  |  | Hydro | 33kV | Connected | 34
Scotland | Tummel Bridge Project 29 | Tummel Bridge |  |  | Hydro | 33kV | Contracted | 6.46 | October 2024
Scotland | Tummel Bridge Project 30 | Tummel Bridge |  |  | Hydro | 11kV | Contracted | 0.15 | October 2024
Scotland | Willowdale Project 01 |  |  | Hayton | P.V. | 11kV | Connected | 0.245
Scotland | Willowdale Project 02 |  |  | Hayton | CHP | LV | Connected | 0.995
Scotland | Willowdale Project 03 |  |  | Hayton | Hydro | LV | Connected | 0.285
Scotland | Willowdale Project 04 |  |  | Hayton | P.V. | 11kV | Connected | 0.077
Scotland | Willowdale Project 05 |  |  | Hayton | P.V. | 11kV | Connected | 0.028
Scotland | Willowdale Project 06 |  |  | Greyfriars | CHP | LV | Connected | 0.995
Scotland | Willowdale Project 07 |  |  | Greyfriars | PV | LV | Contracted | 0.1 | September 2023
Scotland | Woodhill Project 01 |  |  | Springhill | Gas | LV | Connected | 0.3
Scotland | Woodhill Project 02 |  |  | Woodhill | CHP | LV | Connected | 0.2
Scotland | Woodhill Project 03 |  |  | Woodhill | P.V. | 11kV | Connected | 0.063
Scotland | Woodhill Project 04 |  |  | Woodhill | Other | LV | Connected | 0.995
Scotland | Woodhill Project 05 |  |  | Woodhill | P.V. | 11kV | Connected | 0.147
Scotland | Woodhill Project 06 |  |  | Woodhill | CHP | 33kV | Connected | 0.999
Scotland | Woodhill Project 07 |  |  | Woodhill | CHP | LV | Connected | 0.265
Scotland | Woodhill Project 08 |  |  | Woodhill | P.V. | LV | Contracted | 0.06 | October 2022
Scotland | Woodhill Project 09 |  |  | Woodhill | P.V. | LV | Contracted | 0.145 | March 2023
Scotland | Woodhill Project 10 |  |  | Woodhill | P.V. | LV | Contracted | 0.06 | May 23
Scotland | Woodhill Project 11 |  |  | Woodhill | P.V. | LV | Contracted | 0.04 | Feb 23

## Quoted Jobs
Area | Project Name | GSP Parent | BSP Parent | PS Parent | Technology Type | Capacity (MVA) | Quotation Expiry Date | Contestable Costs | Non-Contestable Costs | Reinforcement Works
Scotland | Abernethy Quoted Job 1 | Abernethy |  |  | Wind | 8 | January 2023 | 2894048.85 | 2507609.23 | 0
Scotland | Abernethy Quoted Job 2 | Abernethy |  |  | Battery | 49.4 | February 2023 | 2336441.47 | 1525997.34 | 0
Scotland | Abernethy Quoted Job 3 | Abernethy |  |  | PV | 20 | February 2023 | 4239271.5 | 782752.44 | 0
Scotland | Abernethy Quoted Job 4 | Abernethy |  |  | PV | 0.14 | February 2023 | 3714.8 | 3714.8 | 0
Scotland | Abernethy Quoted Job 5 | Abernethy |  |  | PV | 0.18 | March 2023 | 1957.23 | 1957.23 | 0
Scotland | Abernethy Quoted Job 6 | Abernethy |  |  | PV | 0.1 | March 2023 | 11655.44 | 11655.44 | 0
Scotland | Alness Quoted Job 1 | Alness |  |  | Battery | 45 | March 2023 | 657059.43 | 306538 | 0
Scotland | Arbroath Quoted Job 1 | Arbroath |  |  | PV | 20 | January 2023 | 3461903.09 | 293598.46 | 0
Scotland | Arbroath Quoted Job 2 | Arbroath |  |  | PV | 20 | January 2023 | 3461903.09 | 293598.46 | 0
Scotland | Ardmore Quoted Job 1 | Ardmore |  |  | Battery | 30.4 | January 2023 | 1258593.67 | 629385.45 | 0
Scotland | Boat of Garten Quoted Job 1 | Boat of Garten |  |  | Wind | 1 | January 2023 | 11367 | 11367 | 0
Scotland | Braco Quoted Job 1 | Braco |  |  | Battery | 49.9 | January 2023 | 993714.71 | 306204.96 | 0
Scotland | Braco Quoted Job 2 | Braco |  |  | Battery | 25 | January 2023 | 0 | 306237.23 | 0
Scotland | Bridge of Dun Quoted Job 1 | Bridge of Dun |  |  | PV | 0.122 | January 2023 | 485 | 485 | 0
Scotland | Bridge of Dun Quoted Job 2 | Bridge of Dun |  |  | PV | 0.06 | February 2023 | 485 | 485 | 0
Scotland | Brora Quoted Job 1 | Brora |  |  | Battery | 0.06 | March 2023 | 665.83 | 600.83 | 0
Scotland | Broadford Quoted Job 1 | Broadford |  |  | PV | 0.1 | January 2023 | 80593.68 | 20001.62 | 0
Scotland | Broadford Quoted Job 4 | Broadford |  |  | PV | 1.79 | February 2023 | 4034207.57 | 24361.14 | 0
Scotland | Broadford Quoted Job 2 | Broadford |  |  | Hydro | 0.999 | February 2023 | 222258.41 | 49515.62 | 0
Scotland | Broadford Quoted Job 3 | Broadford |  |  | Hydro | 0.5 | February 2023 | 166898.6 | 25987.78 | 0
Scotland | Carradale Quoted Job 1 | Carradale |  |  | Wind | 52.8 | January 2023 | 5175816.27 | 303398.82 | 0
Scotland | Carradale Quoted Job 2 | Carradale |  |  | PV | 0.3 | February 2023 | 0 | 114560.31 | 0
Scotland | Ceannacroc Quoted Job 1 | Ceannacroc |  |  | Battery | 50 | March 2023 | 0 | 303396.25 | 0
Scotland | Charleston Quoted Job 1 | Charleston |  |  | PV | 0.132 | February 2023 | 485 | 485 | 0
Scotland | Coupar Angus Quoted Job 1 | Coupar Angus |  |  | PV | 25 | January 2023 | 3408225.31 | 293041.62 | 0
Scotland | Coupar Angus Quoted Job 2 | Coupar Angus |  |  | PV | 22 | February 2023 | 1309631.88 | 293041.62 | 0
Scotland | Coupar Angus Quoted Job 3 | Coupar Angus |  |  | Battery | 49.9 | March 2023 | 2759100.03 | 309989.24 | 0
Scotland | Dounreay Quoted Job 1 | Dounreay |  |  | Battery | 27 | January 2023 | 2227573.75 | 923897.13 | 0
Scotland | Dounreay Quoted Job 2 | Dounreay |  |  | Battery | 49.9 | January 2023 | 3872951.66 | 1082168.97 | 0
Scotland | Dunoon Quoted Job 1 | Dunoon |  |  | Wind | 3.5 | January 2023 | 0 | 95104.18 | 0
Scotland | Elgin Quoted Job 1 | Elgin |  |  | Battery | 30 | February 2023 | 829950.85 | 351527.51 | 0
Scotland | Fasnakyle Quoted Job 1 | Fasnakyle |  |  | Battery | 49.4 | February 2023 | 1819562.84 | 121630.08 | 0
Scotland | Fetterso Quoted Job 1 | Fettereso |  |  | Battery | 50 | March 2023 | 2155045.39 | 333743.39 | 0
Scotland | Fiddes Quoted Job 1 | Fiddes |  |  | PV | 0.15 | January 2023 | 485 | 485 | 0
Scotland | Fiddes Quoted Job 2 | Fiddes |  |  | PV | 12.6 | January 2023 | 5177623.24 | 622215.18 | 0
Scotland | Fiddes Quoted Job 3 | Fiddes |  |  | PV | 6 | January 2023 | 1709347.51 | 1484477.76 | 0
Scotland | Fiddes Quoted Job 4 | Fiddes |  |  | PV | 0.09 | March 2023 | 150127.56 | 150127.56 | 0
Scotland | Fiddes Quoted Job 5 | Fiddes |  |  | Battery | 50 | March 2023 | 2356008.16 | 326384.61 | 0
Scotland | Fiddes Quoted Job 6 | Fiddes |  |  | CHP | 0.5 | March 2023 | 2367 | 2367 | 0
Scotland | Fraserburgh Quote Job 1 | Fraserburgh |  |  | PV | 0.199 | February 2023 | 670 | 670 | 0
Scotland | Fraserburgh Quote Job 2 | Fraserburgh |  |  | Battery | 49.4 | March 2023 | 2475335.67 | 252156.85 | 0
Scotland | Grudie Bridge Quoted Job 1 | Grudie Bridge |  |  | Battery | 49.9 | January 2023 | 3020677.68 | 1499818.28 | 0
Scotland | Keith Quoted Job 1 | Keith |  |  | PV | 0.1 | February 2023 | 485 | 485 | 0
Scotland | Killin Quoted Job 1 | Killin |  |  | Hydro | 2.2 | January 2023 | 291956.99 | 54590.13 | 5600.35
Scotland | Kintore Quoted Job 1 | Kintore |  |  | PV/Battery | 36.8 | January 2023 | 2176641.72 | 803949.44 | 0
Scotland | Lairg Quoted Job 1 | Lairg |  |  | Battery | 50 | March 2023 | 1636522.53 | 984833.23 | 0
Scotland | Lunanhead Quoted Job 1 | Lunanhead |  |  | Wind | 4.8 | February 2023 | 1118447.22 | 138367.95 | 0
Scotland | Lunanhead Quoted Job 2 | Lunanhead |  |  | Battery/Wind | 57.6 | March 2023 | 9119054.11 | 327068.16 | 0
Scotland | Lyndhurst Quoted Job 1 | Lyndhurst |  |  | PV | 0.066 | February 2023 | 485 | 485 | 0
Scotland | Lyndhurst Quoted Job 2 | Lyndhurst |  |  | Battery | 20 | March 2023 | 1095355.32 | 130017.22 | 0
Scotland | Macduff Quoted Job 1 | Macduff |  |  | PV | 0.067 | March 2023 | 485 | 485 | 0
Scotland | Milton of Craigie Quoted Job 1 | Milton of Craigie |  |  | Battery | 49.9 | January 2023 | 1908708.95 | 329633.69 | 0
Scotland | Milton of Craigie Quoted Job 2 | Milton of Craigie |  |  | Battery | 49.9 | January 2023 | 6408762.79 | 329633.69 | 0
Scotland | Nairn Quoted Job 1 | Nairn |  |  | Battery | 50 | February 2023 | 2210182.39 | 849119.58 | 0
Scotland | Peterhead Grange Quoted Job 1 | Peterhead Grange |  |  | PV | 0.199 | February 2023 | 1664 | 1664 | 0
Scotland | Port Ann Quoted Job 1 | Port Ann |  |  | Wind | 62.4 | February 2023 | 30555760.64 | 331744.41 | 0
Scotland | Port Ann Quoted Job 2 | Port Ann |  |  | Battery | 49.9 | January 2023 | 1380117.94 | 299953.73 | 0
Scotland | Rannoch Quoted Job 1 | Rannoch |  |  | Battery | 20 | February 2023 | 623837.66 | 295457.78 | 0
Scotland | Redmoss Quoted Job 1 | Redmoss |  |  | CHP | 0.14 | January 2023 | 122821.43 | 4365.05 | 0
Scotland | Redmoss Quoted Job 2 | Redmoss |  |  | PV | 0.099 | February 2023 | 485 | 485 | 0
Scotland | Strathleven Quoted Job 1 | Strathleven |  |  | PV | 0.5 | February 2023 | 145560.84 | 81120.98 | 0
Scotland | Strichen Quoted Job 1 | Strichen |  |  | PV | 0.085 | February 2023 | 485 | 485 | 0
Scotland | Strichen Quoted Job 2 | Strichen |  |  | PV | 0.095 | February 2023 | 485 | 485 | 0
Scotland | Strichen Quoted Job 3 | Strichen |  |  | PV | 0.199 | February 2023 | 2384 | 2384 | 0
Scotland | Strichen Quoted Job 4 | Strichen |  |  | PV | 0.1 | March 2023 | 485 | 485 | 0
Scotland | Strichen Quoted Job 5 | Strichen |  |  | Battery | 25 | March 2023 | 1000195.8 | 309914.08 | 0
Scotland | Thurso Quoted Job 1 | Thurso |  |  | Tidal | 28 | March 2023 | 10967090.12 | 791559.75 | 0
Scotland | Thurso Quoted Job 2 | Thurso |  |  | PV | 0.05 | March 2023 | 550 | 485 | 0

## RRD_Extract (hidden)
Project Number | Name | Project Code | Status | RAG | Licence Area | Region | NRN Primary | NRN HV Feeder | Planning Brief Number | Investment Manager | Responsible Officer | Design Manager | Construction Manager | 1st Year Of Construction | C0 Cost | Id | Stage | Status | Location
PH003158 | Inverneil Primary Transformer Replacement Inverneil Primary (P) | CV1 - Primary Reinforcement | In Refinement | Green | SSEH | SHEPD South Caledonia | INVERNEIL | INVERNEIL R.M.U. |  | Watson Allen | Tarrant James | Tarrant James | Doherty Jordan | 2022/23 | 377878.64 | 30688 | Stage 3 - Refinement | Added - PS | HERE
PH003138 | SCAL T&C Protection Panels Callander, Mill Rd & Ninewells (P) | CV1 - Primary Reinforcement | In Refinement | Green | SSEH | SHEPD South Caledonia | CALLANDER |  |  | Watson Allen | Brass George | Brass George | Brass George | 2021/22 | 195100 | 30375 | Stage 3 - Refinement | Not Applicable | N/A
PH003126 | Flexible Power North Network (P) | CV1 - Primary Reinforcement | In Refinement | Green | SSEH | SHEPD Central | n/a | N/A |  | MacDonald Chris | MacDonald Chris | MacDonald Chris | Howison Alex | 2020/21 | 102270 | 30237 | Stage 3 - Refinement | Not Applicable | N/A
PH003199 | OPT 3 Motts (S) / Rothienorrman GSP - Methlick Pri Integration Works Aberdeenshire (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | METHLICK | CRIMMOND HILL |  | Taylor Bruce | Wells Rikki | Wells Rikki | Riach Margaret | 2022/23 | 220500 | 30107 | Stage 3 - Refinement | Rothienorrman Integration
PH003198 | OPT 3 Motts (S) / Rothienorrman GSP - Fyvie Pri Integration Works Aberdeenshire (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | FYVIE | BEECH ROW |  | Taylor Bruce | Wells Rikki | Wells Rikki | Riach Margaret | 2021/22 | 170800 | 30106 | Stage 3 - Refinement | Rothienorrman Integration
PH003197 | OPT 3 Motts (S) / Rothienorrman GSP - Insch Pri Integration Works Aberdeenshire (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | INSCH | CHURCH AVENUE |  | Taylor Bruce | Wells Rikki | Wells Rikki | Riach Margaret | 2022/23 | 83300 | 30105 | Stage 3 - Refinement | Rothienorrman Integration
PH003127 | OPT 3 Motts (S) / Rothienorrman GSP - Gordonstown W/F Cabling Aberdeenshire (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | n/a | N/A |  | Taylor Bruce | Wells Rikki | Wells Rikki | Riach Margaret | 2022/23 | 1159200 | 30104 | Stage 3 - Refinement | Rothienorrman Integration
PH003128 | OPT 3 Motts (S) / Rothienorrman GSP - Glens of Foudland W/F Cabling Aberdeenshire (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | n/a | N/A |  | Taylor Bruce | Wells Rikki | Wells Rikki | Riach Margaret | 2022/23 | 2125200 | 30087 | Stage 3 - Refinement | Rothienorrman Integration
PH003027 | A&W Glendaruel Primary Tx Replacement A&W LRE (P) / Opt 3 (S)` | CV1 - Primary Reinforcement | In Refinement | Green | SSEH | SHEPD South Caledonia | GLENDARUEL | WAUKMILL |  | MacDonald Chris | Godwin Richard | Godwin Richard | Doherty Jordan | 2022/23 | 239411.27 | 29307 | Stage 3 - Refinement | Added - PS | HERE
PH002860 | Balmedie Primary Substation Reinforcement P2 Scheme (P) / Opt 3 Jacobs (S) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | BALMEDIE | COCK AND BULL |  | MacDonald Chris | Tarrant James | Tarrant James | Riach Margaret | 2021/22 | 1068195 | 27904 | Stage 3 - Refinement | Added - PS | HERE
PH002864 | Opt 3 Motts (S) / Stornoway to Barvas 33kV Circuit Reinforcement P2 Scheme (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD Highlands and Islands | STORNOWAY GRID | BARVAS MOOR |  | Wong Ken | Wells Rikki | Wells Rikki | MacKinnon Donald | 2023/24 | 4292141 | 27899 | Stage 3 - Refinement | Added - GSP | HERE
PH002846 | Opt 1 PLPC (S) / T&C Dunblane - Braco 4L5 33kV OHL Reinforcement 33kV OHL between Braco & Pole 17 (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD South Caledonia | BRACO GRID | BRAES OF DOUNE No1 |  | MacDonald Chris | Wells Rikki | Wells Rikki | Dickie David | 2021/22 | 408090 | 27867 | Stage 3 - Refinement | Y - GSP | HERE
PH002824 | NRN 305 310 (S) / Coire Na Cloiche 33kV Cable Remedial Works Alness GSP (P) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD Highlands and Islands |  |  |  | Konstantinidis Dimitrios | Jahateh Lesiaty | Jahateh Lesiaty | Morrison Iain | 2021/22 | 179000 | 26990 | Stage 3 - Refinement | Not Applicable | N/A
PH002726 | Opt 3 Motts (S) / Scalloway, Setter Sandwick, Sumburgh 33kV and 11kV Reinforcement Shetland (P) | CV1 - Primary Reinforcement | In Refinement | Amber | SSEH | SHEPD North Caledonia (SHETLAND) | GREMISTA | 1L5 |  | MacDonald Chris | Wells Rikki | Wells Rikki | Priest George | 2023/24 | 2582000 | 26509 | Stage 3 - Refinement | Shetland Heat Map | SHETLAND
PH002729 | Longman Drive Primary Substation Inverness GSP (P) / Opt 3 Jacobs (S) (New Primary S/S 2x24 MVA in Inverness) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD Highlands and Islands | n/a | N/A |  | MacDonald Chris | Dougan Megan | Dougan Megan | Morrison Iain | 2021/22 | 2026000 | 26503 | Stage 3 - Refinement | Y - GSP | HERE
PH002730 | Opt 3 Jacobs (S) / South Elgin Strategy Cumming Street, Ashgrove & Bilbohall (P) (Second TFR at Ashgrove & Bilbohall) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | n/a | N/A |  | MacDonald Chris | Wells Rikki | Wells Rikki | Jarvis Andy | 2023/24 | 2200000 | 26502 | Stage 3 - Refinement | Y - PS | HERE
PH002739 | Aboyne & Ballater 11kV network reinforcement North Caledonia (P) / Opt 3 Motts (S) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD North Caledonia | ABOYNE | CHARLESTON PARK |  | MacDonald Chris | Wells Rikki | Wells Rikki | Jarvis Andy | 2022/23 | 1228244 | 26495 | Stage 3 - Refinement | Y - PS | HERE
PH002866 | Aultbea - Ullapool OHL/Cable Highlands & Islands (P) / Opt 3 Motts (S) | CV1 - Primary Reinforcement | In Refinement | Amber | SSEH | SHEPD Highlands and Islands | GRUDIE BRIDGE | MOIREACH |  | MacDonald Chris | Wells Rikki | Wells Rikki | Shanks John | 2021/22 | 7703273.58 | 24263 | Stage 3 - Refinement | Added - GSP | HERE
PH002581 | Opt 3 Motts (S) / T&C Bridge of Dun - Logie Pert 1L5 33kV reinforcement circuit South Caledonia (P) | CV1 - Primary Reinforcement | In Refinement | Amber | SSEH | SHEPD South Caledonia | BRIDGE OF DUN GRID | LOGIE PERT |  | MacDonald Chris | Wells Rikki | Wells Rikki | Dickie David | 2022/23 | 1531349 | 24258 | Stage 3 - Refinement | Y - GSP | HERE
PH002544 | A&W Taynuilt - Tullich Argyll (P) / Opt 3 Motts (S) (33kV OHL Taynuilt - Tullich Reinforcement) | CV1 - Primary Reinforcement | In Refinement | Red | SSEH | SHEPD South Caledonia | TAYNUILT GRID | BARGUILEAN |  | MacDonald Chris | Wells Rikki | Wells Rikki | Bell Tom | 2021/22 | 2200000 | 23801 | Stage 3 - Refinement | Y - GSP | HERE
PH000897 | A&W Glenfinnan-Lochailort 33kV Reinforcement Fort William (P) / Opt 3 (S) | CV1 - Primary Reinforcement | In Refinement | Amber | SSEH | SHEPD South Caledonia | FORT WILLIAM GRID | INVERLOCHY NO.2 TEED | PH000897 | MacDonald Chris | Wells Rikki | Wells Rikki | MacKechnie Allan | 2021/22 | 913346 | 10759 | Stage 3 - Refinement | Y - GSP | HERE
PH003238 | Harris Ardmore (S) / Western Isles Protection Upgrades H&I (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD Highlands and Islands | HARRIS GRID | GOLDEN ROAD |  | MacDonald Chris | Ross John | Wong Ken | Ross John | 2021/22 | 30000 | 31285 | Stage 4 - Execution | Not Applicable | N/A
PH003136 | SCAL A&W Protection Upgrade Dunoon, Lunanhead & Taynuilt Substations (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD South Caledonia | MILL RD MONTROSE |  |  | Watson Allen | Brass George | Brass George | Brass George | 2021/22 | 40000 | 30387 | Stage 4 - Execution | Not Applicable | N/A
PH003099 | A&W Corran Narrows 33kV North and South Corran (P) / Submarine Cable Repalcement Opt 3 (S) | CV1 - Primary Reinforcement | In Execution | Red | SSEH | SHEPD South Caledonia | FORT WILLIAM GRID | SHEEPFANK |  | Taylor David | Mel Chisholm | Tarrant James | Mel Chisholm | 2020/21 | 4000000 | 29937 | Stage 4 - Execution | Y - GSP | HERE
PH003078 | Brora S/S T1 & T2 AVC Panels Brora (P) / IIS (S) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD Highlands and Islands | BRORA | BRORA OFFICE |  | Black David | Ross John | Wells Rikki | Ross John | 2020/21 | 30000 | 29738 | Stage 4 - Execution | Not Applicable | N/A
PH002987 | T&C Tummel Bridge GSP Intertrip Energisation & Load Flow Monitoring South Caledonia LRE (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD South Caledonia | TUMMEL BRIDGE GRID | TUMMEL/RANNOCH (2L5) |  | Golzadeh Yadaki Ahmad | Brass George | Taylor Gary | Brass George | 2019/20 | 25000 | 29038 | Stage 4 - Execution | Not applicable | N/A
PH002851 | Opt 3 (S) / T&C Laurencekirk 33/11kV Transformer Reinforcement Laurencekirk Primary LRE (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD South Caledonia | LAURENCEKIRK |  |  | Golzadeh Yadaki Ahmad | O'Donnell Michael | Rennie Ruth | O'Donnell Michael | 2020/21 | 800000 | 27878 | Stage 4 - Execution | Added - PS | HERE
PH002802 | Limehillocks P162 to Marnoch 33kV Overhead Enhanced Reinforcement Keith Grid (P) / Opt 3 (S) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD North Caledonia | KEITH GRID |  |  | Ferrell Gavin | Ingram Eddie | Woodrow Ryan | Ingram Eddie | 2021/22 | 44000 | 26738 | Stage 4 - Execution | Added - GSP | HERE
PH002798 | Gremista 696-303 - Scalloway 696-301 33kV Link, IIS Improvement, Shetland, North Caledonia (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD North Caledonia (SHETLAND) | GREMISTA | 3L5 |  | Lamont Christopher | Priest George | Godwin Richard | Priest George | 2020/21 | 966000 | 26679 | Stage 4 - Execution | Shetland Heat Map | SHETLAND
PH002662 | Opt 3 Motts (S) / Rothienorman GSP Integration Works Aberdeenshire (P) | CV1 - Primary Reinforcement | In Execution | Amber | SSEH | SHEPD North Caledonia | n/a | N/A |  | Taylor Bruce | Riach Margaret | Kinninmonth Steven | Riach Margaret | 2019/20 | 768000 | 25188 | Stage 4 - Execution | Rothienorrman Integration (September 2021)
PH002575 | Lochcarron 33/11kV Substation Lochcarron, Wester Ross (P) (New Primary S/S) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD Highlands and Islands | ACHINTEE | ACHINTEE |  | Black David | Brown Gary | Lee Alasdair | Brown Gary | 2019/20 | 934700 | 24774 | Stage 4 - Execution | Added - PS | HERE
PH002621 | Macduff 33kV Transformer + 11kV Switchboard Replacement Macduff Primary Substation (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD North Caledonia | MACDUFF | GELLYHILL TEED |  | Taylor Bruce | Riach Margaret | Kinninmonth Steven | Riach Margaret | 2019/20 | 771800 | 24547 | Stage 4 - Execution | Added - PS | HERE
PH002545 | T&C Thimblerow Primary Perth (P) (Upgrade existing TFRs - 2x30 MVA) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD South Caledonia | THIMBLEROW | BLACKFRIARS |  | Watson Allen | Johnston John | Taylor Gary | Johnston John | 2020/21 | 1508000 | 23799 | Stage 4 - Execution | Added - PS | HERE
PH000867 | Kingseat Primary substation, Aberdeen (S) / Dyce-Kingseat 33kV Cable Reinforcement Dyce Grid Substation, Aberdeen (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD North Caledonia | DYCE GRID |  |  | Taylor Bruce | Riach Margaret | Kinninmonth Steven | Riach Margaret | 2019/20 | 2914842 | 15482 | Stage 4 - Execution | Y - GSP | HERE
PH000901 | A&W Taynuilt 33/11kV S/S Reinforcement Argyll (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD South Caledonia | TAYNUILT |  | PH000901 | Taylor David | Mackintosh Scott | Taylor Gary | Mackintosh Scott | 2020/21 | 501220 | 10758 | Stage 4 - Execution | Added - PS | HERE
PH002164 | Opt 3 (S) / Stockinish 33/11kV T1 Replacement Stockinish Primary substation (P) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD Highlands and Islands | STOCKINISH |  |  | Bogodage Matthew | Brown Gary | Wardlaw Ryan | Brown Gary | 2021/22 | 377900 | 10074 | Stage 4 - Execution | Added - PS | HERE
PH002214 | Beauly Grid 303 33kV Circuit Reinforcement Beauly Grid (P) / Opt 3 (S) | CV1 - Primary Reinforcement | In Execution | Green | SSEH | SHEPD Highlands and Islands | BEAULY GRID | INCHRORY |  | MacDonald Chris | Schofield Paul | Wells Rikki | Schofield Paul | 2021/22 | 654000 | 10000 | Stage 4 - Execution | Y - GSP | HERE