## Contents
SHEPD Network Headroom Report 2022 Summary
Our Network Headroom Report (NHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations up to 2050. SHEPD have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN best view of the future demand and generation needs on our network is aligned to the Customer Transformation scenario. Although the NHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Local Authority Reference | This tab provides information on the local authorities and the Primaries that support those areas
May 2022
Version 1.1

## Key Information
SHEPD Network Headroom Report 2022 Key Information
Our Network Headroom Report (NHR) has been developed to be used in conjunction with our others documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation as per out Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. Alternatively, for single transformer sites the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SHEPD.
May 2022
Version 1.1

## Primary Headroom Dem
Grid Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[5 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050
FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | 0.19291 | 0.19355 | 0.19316 | 0.19224 | 0.18934 | 0.1872 | 0.18385 | 0.17845 | 0.17325 | 0.1698 | 0.15473 | 0.14119 | 0.14186 | 0.14163 | 0.19333 | 0.19345 | 0.19323 | 0.19265 | 0.19126 | 0.18978 | 0.18793 | 0.18539 | 0.18287 | 0.17992 | 0.16885 | 0.15901 | 0.15923 | 0.15912 | 0.17952 | 0.18006 | 0.1797 | 0.17883 | 0.17621 | 0.1743 | 0.17108 | 0.16621 | 0.1615 | 0.15824 | 0.14425 | 0.13338 | 0.13397 | 0.13377
| ABERCHALDER | CT |  |  | 0.1953 | 0.19593 | 0.1952 | 0.1938 | 0.19135 | 0.18824 | 0.18385 | 0.17845 | 0.17325 | 0.17027 | 0.15795 | 0.14977 | 0.14832 | 0.14739 | 0.19418 | 0.19432 | 0.19396 | 0.19322 | 0.19144 | 0.18978 | 0.18793 | 0.18539 | 0.18287 | 0.18112 | 0.17267 | 0.16582 | 0.16526 | 0.16488 | 0.1816 | 0.18223 | 0.1819 | 0.18099 | 0.17783 | 0.17498 | 0.17108 | 0.16621 | 0.1615 | 0.15873 | 0.14702 | 0.1414 | 0.13934 | 0.13803
| ABERCHALDER | LW |  |  | 0.19291 | 0.19355 | 0.19316 | 0.19224 | 0.18934 | 0.1872 | 0.1842 | 0.18105 | 0.1737 | 0.1698 | 0.15473 | 0.14119 | 0.14186 | 0.14163 | 0.19333 | 0.19345 | 0.19323 | 0.19265 | 0.19126 | 0.19035 | 0.18868 | 0.1866 | 0.183 | 0.17992 | 0.16885 | 0.15901 | 0.15923 | 0.15912 | 0.17952 | 0.18006 | 0.1797 | 0.17883 | 0.17621 | 0.1743 | 0.17153 | 0.16859 | 0.16186 | 0.15824 | 0.14425 | 0.13338 | 0.13397 | 0.13377
| ABERCHALDER | ST |  |  | 0.19451 | 0.19432 | 0.19417 | 0.19394 | 0.19345 | 0.1931 | 0.19209 | 0.19185 | 0.19025 | 0.18831 | 0.18023 | 0.1584 | 0.14866 | 0.14664 | 0.19396 | 0.19385 | 0.19375 | 0.19344 | 0.19305 | 0.19281 | 0.19206 | 0.19183 | 0.19088 | 0.18979 | 0.18486 | 0.16928 | 0.16312 | 0.16234 | 0.18093 | 0.18076 | 0.18062 | 0.18036 | 0.17989 | 0.17955 | 0.17857 | 0.17833 | 0.17684 | 0.17505 | 0.16814 | 0.14926 | 0.14022 | 0.13845
| ABERCHALDER | SP |  |  | 0.19429 | 0.19393 | 0.19367 | 0.19328 | 0.19168 | 0.19019 | 0.18812 | 0.1864 | 0.18422 | 0.18076 | 0.1734 | 0.15423 | 0.14666 | 0.14375 | 0.19387 | 0.19371 | 0.19357 | 0.19333 | 0.1927 | 0.1921 | 0.1911 | 0.1904 | 0.1893 | 0.1875 | 0.18368 | 0.17179 | 0.16526 | 0.16358 | 0.18073 | 0.18042 | 0.18019 | 0.17983 | 0.17842 | 0.17711 | 0.17523 | 0.17371 | 0.17173 | 0.16857 | 0.16185 | 0.1439 | 0.13694 | 0.13439
TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | YES | 4.463 | 4.4094 | 4.3118 | 4.1974 | 3.9895 | 3.774 | 3.5207 | 3.2145 | 2.8735 | 2.611 | 1.8948 | 1.1947 | 0.91299 | 0.81396 | 5.3726 | 5.3243 | 5.2507 | 5.1516 | 5.0235 | 4.8977 | 4.7522 | 4.5625 | 4.3639 | 4.1863 | 3.703 | 3.3328 | 3.1932 | 3.1029 | 4.8792 | 4.8334 | 4.7456 | 4.6419 | 4.4661 | 4.2733 | 4.0611 | 3.7929 | 3.5061 | 3.2658 | 2.6004 | 1.9881 | 1.7424 | 1.6555
| ABERFELDY | CT |  |  | 4.4842 | 4.4276 | 4.331 | 4.1974 | 3.9895 | 3.7885 | 3.5584 | 3.2779 | 2.9869 | 2.7404 | 1.9628 | 1.1947 | 0.91299 | 0.81396 | 5.375 | 5.3243 | 5.2507 | 5.1516 | 5.0235 | 4.8977 | 4.7522 | 4.5914 | 4.4244 | 4.2717 | 3.7618 | 3.3328 | 3.1932 | 3.1029 | 4.899 | 4.8347 | 4.7456 | 4.6419 | 4.4661 | 4.2818 | 4.0723 | 3.8515 | 3.6133 | 3.4004 | 2.683 | 1.9881 | 1.7424 | 1.6555
| ABERFELDY | LW |  |  | 4.463 | 4.4094 | 4.3118 | 4.1976 | 3.994 | 3.774 | 3.5207 | 3.2145 | 2.8735 | 2.611 | 1.8948 | 1.3603 | 1.1739 | 1.0683 | 5.3726 | 5.3252 | 5.2536 | 5.1718 | 5.0498 | 4.9139 | 4.7575 | 4.5625 | 4.3639 | 4.1863 | 3.703 | 3.3956 | 3.3267 | 3.2884 | 4.8792 | 4.8334 | 4.7491 | 4.6506 | 4.4695 | 4.2733 | 4.0611 | 3.7929 | 3.5061 | 3.2658 | 2.6004 | 2.1108 | 1.9584 | 1.873
| ABERFELDY | ST |  |  | 4.4994 | 4.4425 | 4.3677 | 4.283 | 4.2107 | 4.1346 | 4.0411 | 3.9398 | 3.8202 | 3.7111 | 3.3471 | 2.6196 | 2.3264 | 2.1606 | 5.3916 | 5.3465 | 5.2892 | 5.2233 | 5.1634 | 5.0876 | 4.9995 | 4.9106 | 4.8102 | 4.719 | 4.416 | 3.9349 | 3.7231 | 3.5972 | 4.9117 | 4.8623 | 4.7917 | 4.7161 | 4.643 | 4.561 | 4.4638 | 4.3683 | 4.2661 | 4.1795 | 3.8573 | 3.1604 | 2.8988 | 2.7646
| ABERFELDY | SP |  |  | 4.5018 | 4.4499 | 4.3773 | 4.3018 | 4.2055 | 4.1087 | 3.9987 | 3.8826 | 3.7515 | 3.618 | 3.2571 | 2.5995 | 2.1522 | 2.0414 | 5.3909 | 5.349 | 5.2921 | 5.2339 | 5.1664 | 5.0965 | 5.0113 | 4.926 | 4.832 | 4.741 | 4.4875 | 4.0242 | 3.6427 | 3.4573 | 4.9139 | 4.8689 | 4.7949 | 4.7233 | 4.6527 | 4.5734 | 4.4786 | 4.3767 | 4.2558 | 4.1341 | 3.8205 | 3.2165 | 2.7889 | 2.6923
STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | 3.219 | 3.1666 | 3.1139 | 3.0471 | 2.866 | 2.6656 | 2.4725 | 2.2653 | 2.0715 | 1.9372 | 1.6105 | 1.5255 | 1.6353 | 1.6025 | 3.7312 | 3.7081 | 3.6869 | 3.6557 | 3.5855 | 3.5112 | 3.4353 | 3.3349 | 3.2383 | 3.1288 | 2.8782 | 2.7888 | 2.8009 | 2.697 | 3.4454 | 3.3995 | 3.3543 | 3.2942 | 3.1448 | 2.9785 | 2.8146 | 2.6272 | 2.4504 | 2.2989 | 1.9409 | 1.8339 | 1.9172 | 1.8927
| ABERFOYLE | CT |  |  | 3.2434 | 3.2127 | 3.1716 | 3.1091 | 2.9143 | 2.7239 | 2.5499 | 2.3827 | 2.2257 | 2.1351 | 1.8323 | 1.611 | 1.6442 | 1.6379 | 3.7343 | 3.7181 | 3.6978 | 3.6594 | 3.5855 | 3.5112 | 3.4424 | 3.3697 | 3.2992 | 3.235 | 2.9909 | 2.8183 | 2.8009 | 2.7623 | 3.464 | 3.4358 | 3.399 | 3.3383 | 3.1758 | 3.0163 | 2.8701 | 2.7252 | 2.5877 | 2.4929 | 2.1549 | 1.9171 | 1.933 | 1.9247
| ABERFOYLE | LW |  |  | 3.219 | 3.1666 | 3.1139 | 3.0471 | 2.866 | 2.6656 | 2.4725 | 2.2653 | 2.0715 | 1.9372 | 1.6105 | 1.5255 | 1.6353 | 1.6025 | 3.7312 | 3.7081 | 3.6869 | 3.6557 | 3.5888 | 3.5131 | 3.4353 | 3.3349 | 3.2383 | 3.1288 | 2.8782 | 2.7888 | 2.8187 | 2.8085 | 3.4454 | 3.3995 | 3.3543 | 3.2942 | 3.1448 | 2.9785 | 2.8146 | 2.6272 | 2.4504 | 2.2989 | 1.9409 | 1.8339 | 1.9172 | 1.8927
| ABERFOYLE | ST |  |  | 3.2533 | 3.2417 | 3.2297 | 3.2111 | 3.1972 | 3.182 | 3.1643 | 3.1402 | 3.108 | 3.0499 | 2.8514 | 2.402 | 2.2495 | 2.1798 | 3.7443 | 3.7375 | 3.7298 | 3.7166 | 3.705 | 3.6906 | 3.6752 | 3.6567 | 3.6345 | 3.5967 | 3.4553 | 3.0802 | 2.9828 | 2.9218 | 3.4754 | 3.4643 | 3.4524 | 3.433 | 3.4175 | 3.3987 | 3.3785 | 3.3526 | 3.3197 | 3.2619 | 3.055 | 2.5512 | 2.4099 | 2.3497
| ABERFOYLE | SP |  |  | 3.2674 | 3.2649 | 3.2617 | 3.2576 | 3.2289 | 3.2036 | 3.173 | 3.1383 | 3.0943 | 3.0324 | 2.7945 | 2.1979 | 1.8041 | 1.6451 | 3.7472 | 3.7437 | 3.7387 | 3.7324 | 3.7175 | 3.7051 | 3.6877 | 3.6671 | 3.6375 | 3.604 | 3.4805 | 3.1009 | 2.8265 | 2.697 | 3.4853 | 3.4815 | 3.4763 | 3.4698 | 3.4435 | 3.4202 | 3.3912 | 3.3577 | 3.3127 | 3.2554 | 3.0385 | 2.4502 | 2.0657 | 1.9345
KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | YES | 1.8894 | 1.8593 | 1.82 | 1.768 | 1.6722 | 1.5745 | 1.4748 | 1.3324 | 1.149 | 1.0082 | 0.59362 | 0.23224 | 0.041968 | -0.033452 | 2.2459 | 2.2283 | 2.2124 | 2.189 | 2.168 | 2.1493 | 2.1324 | 2.1135 | 2.0918 | 2.061 | 1.9539 | 1.8582 | 1.8537 | 1.8492 | 2.0955 | 2.0708 | 2.0486 | 2.0162 | 1.9681 | 1.8884 | 1.8089 | 1.6923 | 1.5267 | 1.3958 | 1.0095 | 0.68872 | 0.52193 | 0.45591
| ABERLOUR | CT |  |  | 1.9247 | 1.9015 | 1.8703 | 1.8134 | 1.7158 | 1.6301 | 1.4895 | 1.3324 | 1.1813 | 1.0624 | 0.65291 | 0.23224 | 0.041968 | -0.033452 | 2.2459 | 2.2283 | 2.2124 | 2.189 | 2.168 | 2.1493 | 2.1324 | 2.1135 | 2.0935 | 2.0699 | 1.989 | 1.902 | 1.8937 | 1.8719 | 2.0955 | 2.0708 | 2.0486 | 2.0162 | 1.9886 | 1.9475 | 1.8321 | 1.6923 | 1.5571 | 1.448 | 1.0676 | 0.68872 | 0.52193 | 0.45591
| ABERLOUR | LW |  |  | 1.8894 | 1.8593 | 1.82 | 1.768 | 1.6722 | 1.5745 | 1.4748 | 1.3492 | 1.149 | 1.0082 | 0.59362 | 0.30426 | 0.20422 | 0.15343 | 2.2483 | 2.2317 | 2.2174 | 2.1982 | 2.1801 | 2.1617 | 2.1443 | 2.1192 | 2.0918 | 2.061 | 1.9539 | 1.8582 | 1.8537 | 1.8492 | 2.0985 | 2.0754 | 2.0556 | 2.0294 | 1.9681 | 1.8884 | 1.8089 | 1.7081 | 1.5267 | 1.3958 | 1.0095 | 0.74936 | 0.66203 | 0.61759
| ABERLOUR | ST |  |  | 1.9203 | 1.8903 | 1.8647 | 1.8348 | 1.8153 | 1.7988 | 1.7773 | 1.7582 | 1.7252 | 1.6784 | 1.4994 | 1.0368 | 0.80612 | 0.67476 | 2.252 | 2.2387 | 2.2277 | 2.2137 | 2.2051 | 2.199 | 2.1909 | 2.1825 | 2.1727 | 2.1597 | 2.1065 | 1.9558 | 1.8861 | 1.8621 | 2.1031 | 2.0838 | 2.0681 | 2.0484 | 2.0373 | 2.0302 | 2.0204 | 2.0099 | 1.9977 | 1.9814 | 1.8375 | 1.3991 | 1.1924 | 1.0763
| ABERLOUR | SP |  |  | 1.9234 | 1.8944 | 1.8723 | 1.8452 | 1.8092 | 1.7808 | 1.7494 | 1.7109 | 1.6635 | 1.6042 | 1.4219 | 0.96016 | 0.67401 | 0.57517 | 2.2525 | 2.2398 | 2.2297 | 2.2175 | 2.2103 | 2.206 | 2.2013 | 2.1947 | 2.1855 | 2.1756 | 2.1443 | 2.0364 | 1.9479 | 1.9161 | 2.104 | 2.0858 | 2.0715 | 2.0543 | 2.0446 | 2.0393 | 2.0332 | 2.004 | 1.9705 | 1.9252 | 1.7773 | 1.3467 | 1.0789 | 0.99074
ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | 1.4289 | 1.3539 | 1.3156 | 1.278 | 1.2635 | 1.2482 | 1.2334 | 1.218 | 1.1993 | 1.1791 | 1.1416 | 1.1071 | 1.103 | 1.0986 | 1.4632 | 1.4064 | 1.3755 | 1.3431 | 1.3212 | 1.2976 | 1.2743 | 1.2496 | 1.2202 | 1.1968 | 1.1479 | 1.1176 | 1.0479 | 0.96729 | 1.2764 | 1.2246 | 1.1922 | 1.1572 | 1.1182 | 1.0792 | 1.0415 | 1.0031 | 0.9593 | 0.93 | 0.86494 | 0.83457 | 0.80922 | 0.80638
| ABERNETHY | CT |  |  | 1.4289 | 1.3539 | 1.3156 | 1.278 | 1.2635 | 1.2482 | 1.2334 | 1.218 | 1.2019 | 1.1836 | 1.1534 | 1.1233 | 1.1181 | 1.1137 | 1.4733 | 1.4155 | 1.3849 | 1.3518 | 1.3276 | 1.3049 | 1.2827 | 1.26 | 1.2364 | 1.214 | 1.1647 | 1.1176 | 1.0962 | 1.0584 | 1.3015 | 1.2484 | 1.219 | 1.185 | 1.1437 | 1.1065 | 1.07 | 1.0343 | 0.99854 | 0.97131 | 0.91 | 0.86022 | 0.86281 | 0.85917
| ABERNETHY | LW |  |  | 1.4296 | 1.355 | 1.3175 | 1.2809 | 1.2671 | 1.2512 | 1.2353 | 1.2182 | 1.1993 | 1.1791 | 1.1416 | 1.1071 | 1.103 | 1.0986 | 1.4632 | 1.4064 | 1.3755 | 1.3431 | 1.3212 | 1.2976 | 1.2743 | 1.2496 | 1.2202 | 1.1968 | 1.1479 | 1.1195 | 1.1244 | 1.1195 | 1.2764 | 1.2246 | 1.1922 | 1.1572 | 1.1182 | 1.0792 | 1.0415 | 1.0031 | 0.9593 | 0.93 | 0.86494 | 0.83457 | 0.85157 | 0.84357
| ABERNETHY | ST |  |  | 1.4315 | 1.3581 | 1.3217 | 1.2872 | 1.2768 | 1.2654 | 1.2534 | 1.2417 | 1.2297 | 1.2154 | 1.1926 | 1.132 | 1.11 | 1.1026 | 1.4694 | 1.4074 | 1.3761 | 1.3471 | 1.3387 | 1.3286 | 1.317 | 1.3078 | 1.2969 | 1.2817 | 1.252 | 1.168 | 1.1296 | 1.087 | 1.2913 | 1.2262 | 1.1937 | 1.166 | 1.1595 | 1.1504 | 1.1394 | 1.1326 | 1.1219 | 1.1045 | 1.0688 | 0.97635 | 0.95078 | 0.93722
| ABERNETHY | SP |  |  | 1.4325 | 1.3595 | 1.3233 | 1.2892 | 1.2792 | 1.2685 | 1.2575 | 1.2463 | 1.2345 | 1.2226 | 1.209 | 1.1649 | 1.1255 | 1.1154 | 1.4715 | 1.4094 | 1.3777 | 1.3471 | 1.3316 | 1.3161 | 1.2994 | 1.2816 | 1.2631 | 1.2414 | 1.2095 | 1.1249 | 1.0479 | 0.96729 | 1.2931 | 1.2272 | 1.1942 | 1.1623 | 1.1375 | 1.1135 | 1.0873 | 1.06 | 1.0327 | 0.99681 | 0.95114 | 0.84772 | 0.80922 | 0.80638
TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | 7.4824 | 7.3556 | 7.206 | 7.0334 | 6.8422 | 6.6343 | 6.1675 | 5.5859 | 4.772 | 4.235 | 2.8392 | 2.302 | 2.5272 | 2.027 | 9.3808 | 9.2526 | 9.1043 | 8.9323 | 8.6394 | 8.3085 | 7.9658 | 7.59 | 7.1051 | 6.7285 | 5.8772 | 5.524 | 5.4822 | 4.9859 | 8.5189 | 8.3618 | 8.1708 | 7.945 | 7.4524 | 6.9107 | 6.3614 | 5.7768 | 4.9768 | 4.4554 | 3.2134 | 2.7261 | 2.9388 | 2.4845
| ABOYNE | CT |  |  | 7.4824 | 7.3556 | 7.206 | 7.0334 | 6.8422 | 6.6343 | 6.4225 | 5.7517 | 5.1092 | 4.711 | 3.3962 | 2.584 | 2.5272 | 2.4454 | 9.4064 | 9.297 | 9.1534 | 8.9871 | 8.7002 | 8.4066 | 8.0573 | 7.6799 | 7.3135 | 6.9983 | 6.0961 | 5.5983 | 5.5087 | 5.3662 | 8.6012 | 8.4902 | 8.3273 | 8.1383 | 7.6685 | 7.2014 | 6.603 | 5.9666 | 5.3574 | 4.9352 | 3.6953 | 2.9759 | 2.9388 | 2.8723
| ABOYNE | LW |  |  | 7.503 | 7.3738 | 7.2336 | 7.0754 | 6.8879 | 6.6681 | 6.1675 | 5.5859 | 4.772 | 4.235 | 2.8392 | 2.302 | 2.5587 | 2.4721 | 9.3808 | 9.2526 | 9.1043 | 8.9323 | 8.6394 | 8.3085 | 7.9658 | 7.59 | 7.1051 | 6.7285 | 5.8772 | 5.524 | 5.616 | 5.5801 | 8.5189 | 8.3618 | 8.1708 | 7.945 | 7.4524 | 6.9107 | 6.3614 | 5.7768 | 4.9768 | 4.4554 | 3.2134 | 2.7261 | 2.9544 | 2.8766
| ABOYNE | ST |  |  | 7.5361 | 7.4287 | 7.315 | 7.1986 | 7.0867 | 6.9533 | 6.8041 | 6.6404 | 6.4761 | 6.2794 | 5.7611 | 4.5934 | 3.9143 | 3.6508 | 9.4302 | 9.3308 | 9.2229 | 9.1122 | 9.0115 | 8.8832 | 8.7465 | 8.5926 | 8.4118 | 8.1847 | 7.5564 | 6.4447 | 6.0241 | 5.7993 | 8.6108 | 8.5023 | 8.3865 | 8.2724 | 8.1733 | 8.0425 | 7.9035 | 7.7429 | 7.5248 | 7.2353 | 6.3899 | 4.8601 | 4.2418 | 4.0013
| ABOYNE | SP |  |  | 7.5419 | 7.438 | 7.3292 | 7.2197 | 7.1117 | 6.9863 | 6.8446 | 6.6865 | 6.5372 | 6.3629 | 5.9792 | 4.0481 | 2.6412 | 2.027 | 9.4496 | 9.3586 | 9.2621 | 9.1621 | 9.0395 | 8.8982 | 8.7432 | 8.565 | 8.3861 | 8.1672 | 7.5646 | 6.3279 | 5.4822 | 4.9859 | 8.6503 | 8.5596 | 8.467 | 8.3704 | 8.2165 | 8.045 | 7.8576 | 7.6408 | 7.4222 | 7.1344 | 6.2147 | 4.268 | 3.0268 | 2.4845
GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | 0.47149 | 0.47146 | 0.46065 | 0.4448 | 0.40226 | 0.35781 | 0.31292 | 0.26509 | 0.20729 | 0.16978 | 0.033143 | 0.016731 | 0.012479 | -0.013186 | 0.25848 | 0.2568 | 0.25506 | 0.25209 | 0.24849 | 0.24513 | 0.24173 | 0.2368 | 0.23101 | 0.22327 | 0.1952 | 0.18144 | 0.18151 | 0.18132 | 0.53127 | 0.53065 | 0.52997 | 0.52829 | 0.50539 | 0.47003 | 0.43389 | 0.39465 | 0.34788 | 0.31521 | 0.1929 | 0.18256 | 0.17984 | 0.16141
| ACHILTIBUIE | CT |  |  | 0.49453 | 0.49717 | 0.49175 | 0.47533 | 0.42932 | 0.38931 | 0.34236 | 0.2947 | 0.24867 | 0.22033 | 0.092525 | 0.043305 | 0.042925 | 0.037821 | 0.25848 | 0.2568 | 0.25506 | 0.25209 | 0.24849 | 0.24513 | 0.24173 | 0.2381 | 0.23417 | 0.22845 | 0.20462 | 0.19165 | 0.19131 | 0.19082 | 0.53127 | 0.53065 | 0.52997 | 0.52829 | 0.52208 | 0.49033 | 0.45356 | 0.4164 | 0.38022 | 0.35576 | 0.23932 | 0.20172 | 0.20413 | 0.20152
| ACHILTIBUIE | LW |  |  | 0.47149 | 0.47146 | 0.46065 | 0.4448 | 0.40226 | 0.35781 | 0.31292 | 0.26509 | 0.20729 | 0.16978 | 0.033143 | 0.016731 | 0.037672 | 0.028763 | 0.25879 | 0.25719 | 0.25552 | 0.2531 | 0.2502 | 0.24647 | 0.24215 | 0.2368 | 0.23101 | 0.22327 | 0.1952 | 0.18144 | 0.18151 | 0.18132 | 0.53158 | 0.53117 | 0.53069 | 0.52976 | 0.50539 | 0.47003 | 0.43389 | 0.39465 | 0.34788 | 0.31521 | 0.1929 | 0.18256 | 0.19851 | 0.19118
| ACHILTIBUIE | ST |  |  | 0.48921 | 0.48595 | 0.48296 | 0.47977 | 0.47605 | 0.4712 | 0.46454 | 0.45859 | 0.44857 | 0.43077 | 0.37111 | 0.2051 | 0.16624 | 0.14394 | 0.26001 | 0.25931 | 0.25849 | 0.25736 | 0.25617 | 0.25483 | 0.25316 | 0.25125 | 0.24909 | 0.24555 | 0.23256 | 0.19359 | 0.18575 | 0.18513 | 0.53179 | 0.53163 | 0.53145 | 0.53097 | 0.53066 | 0.53034 | 0.52982 | 0.52922 | 0.52863 | 0.52465 | 0.47368 | 0.32501 | 0.29889 | 0.28354
| ACHILTIBUIE | SP |  |  | 0.48951 | 0.48608 | 0.48384 | 0.48115 | 0.46484 | 0.45011 | 0.43304 | 0.4135 | 0.39216 | 0.36229 | 0.29005 | 0.12382 | 0.012479 | -0.013186 | 0.26004 | 0.2594 | 0.25883 | 0.25802 | 0.2571 | 0.25612 | 0.2549 | 0.25342 | 0.25145 | 0.24894 | 0.24109 | 0.21478 | 0.19041 | 0.18804 | 0.53186 | 0.53175 | 0.53167 | 0.53153 | 0.5313 | 0.53115 | 0.53085 | 0.51624 | 0.49904 | 0.47539 | 0.4174 | 0.27793 | 0.17984 | 0.16141
BROADFORD | ACHINTEE | MINIMUM HEADROOM | NG 93973 41406 | YES | 1.1232 | 1.1223 | 1.1205 | 1.119 | 1.1148 | 1.1099 | 1.1045 | 1.0987 | 1.0914 | 1.0876 | 1.0702 | 1.0621 | 1.0638 | 1.0634 | 1.0546 | 1.054 | 1.0529 | 1.052 | 1.0496 | 1.047 | 1.0444 | 1.0414 | 1.0377 | 1.0356 | 1.0242 | 1.017 | 1.0175 | 1.0174 | 1.0419 | 1.0409 | 1.0391 | 1.0374 | 1.0328 | 1.0279 | 1.023 | 1.0176 | 1.0109 | 1.0074 | 0.99094 | 0.98525 | 0.98637 | 0.98494
| ACHINTEE | CT |  |  | 1.1247 | 1.1244 | 1.1231 | 1.1213 | 1.1178 | 1.1135 | 1.1095 | 1.1038 | 1.0982 | 1.0948 | 1.079 | 1.0707 | 1.068 | 1.0663 | 1.0553 | 1.055 | 1.0541 | 1.0529 | 1.051 | 1.0485 | 1.0463 | 1.0438 | 1.0412 | 1.0391 | 1.0283 | 1.0243 | 1.0234 | 1.0228 | 1.0438 | 1.0435 | 1.0423 | 1.0406 | 1.0365 | 1.0319 | 1.0273 | 1.0223 | 1.0172 | 1.0139 | 0.99887 | 0.99137 | 0.989 | 0.98748
| ACHINTEE | LW |  |  | 1.1232 | 1.1223 | 1.1205 | 1.119 | 1.1148 | 1.1099 | 1.1045 | 1.0987 | 1.0914 | 1.0876 | 1.0702 | 1.0621 | 1.0638 | 1.0636 | 1.0546 | 1.054 | 1.0529 | 1.052 | 1.0496 | 1.047 | 1.0444 | 1.0414 | 1.0377 | 1.0356 | 1.0242 | 1.017 | 1.0175 | 1.0174 | 1.0419 | 1.0409 | 1.0391 | 1.0374 | 1.0328 | 1.0279 | 1.023 | 1.0176 | 1.0109 | 1.0074 | 0.99094 | 0.98525 | 0.98637 | 0.9862
| ACHINTEE | ST |  |  | 1.1248 | 1.1242 | 1.1238 | 1.1236 | 1.1225 | 1.122 | 1.1213 | 1.1199 | 1.1186 | 1.1165 | 1.1087 | 1.0864 | 1.0753 | 1.073 | 1.0555 | 1.0551 | 1.0549 | 1.0547 | 1.054 | 1.0537 | 1.0532 | 1.0523 | 1.0515 | 1.0501 | 1.0451 | 1.0305 | 1.0235 | 1.0226 | 1.0437 | 1.0431 | 1.0427 | 1.0424 | 1.0414 | 1.0408 | 1.0401 | 1.0387 | 1.0374 | 1.0352 | 1.0273 | 1.007 | 0.99679 | 0.99477
| ACHINTEE | SP |  |  | 1.1248 | 1.1244 | 1.1241 | 1.1236 | 1.1226 | 1.1208 | 1.1196 | 1.1181 | 1.116 | 1.114 | 1.1061 | 1.087 | 1.0686 | 1.0634 | 1.0555 | 1.0553 | 1.055 | 1.0547 | 1.0542 | 1.0531 | 1.0524 | 1.0516 | 1.0503 | 1.0492 | 1.045 | 1.0349 | 1.0234 | 1.0215 | 1.0438 | 1.0434 | 1.043 | 1.0425 | 1.0413 | 1.0395 | 1.0381 | 1.0365 | 1.0344 | 1.0321 | 1.0243 | 1.0068 | 0.98945 | 0.98494
BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | 0.46379 | 0.46086 | 0.45435 | 0.44448 | 0.42467 | 0.40442 | 0.37947 | 0.35674 | 0.32472 | 0.28103 | 0.2515 | 0.2401 | 0.24344 | 0.22365 | 0.47197 | 0.47007 | 0.46626 | 0.46092 | 0.45157 | 0.44208 | 0.42798 | 0.41584 | 0.40014 | 0.36501 | 0.3515 | 0.34637 | 0.34038 | 0.3283 | 0.43894 | 0.43616 | 0.43018 | 0.42096 | 0.40306 | 0.38478 | 0.36176 | 0.34095 | 0.3119 | 0.26727 | 0.24132 | 0.23174 | 0.23295 | 0.21663
| AIGAS | CT |  |  | 0.46976 | 0.46817 | 0.46049 | 0.45258 | 0.43323 | 0.41596 | 0.39065 | 0.36273 | 0.3384 | 0.3237 | 0.26758 | 0.24969 | 0.25033 | 0.24819 | 0.47365 | 0.47202 | 0.46626 | 0.4616 | 0.45219 | 0.44424 | 0.43285 | 0.41968 | 0.4087 | 0.3989 | 0.35755 | 0.34941 | 0.34753 | 0.34349 | 0.44406 | 0.4424 | 0.43499 | 0.42766 | 0.41013 | 0.39459 | 0.37186 | 0.34665 | 0.3248 | 0.31095 | 0.25537 | 0.24043 | 0.24052 | 0.23861
| AIGAS | LW |  |  | 0.46379 | 0.46086 | 0.45435 | 0.44448 | 0.42467 | 0.40442 | 0.37947 | 0.35674 | 0.32472 | 0.28103 | 0.2515 | 0.2401 | 0.24932 | 0.24437 | 0.47197 | 0.47007 | 0.46666 | 0.46092 | 0.45157 | 0.44208 | 0.42798 | 0.41584 | 0.40014 | 0.36501 | 0.3515 | 0.34637 | 0.34945 | 0.34775 | 0.43894 | 0.43616 | 0.43018 | 0.42096 | 0.40306 | 0.38478 | 0.36176 | 0.34095 | 0.3119 | 0.26727 | 0.24132 | 0.23174 | 0.23921 | 0.23532
| AIGAS | ST |  |  | 0.47061 | 0.46858 | 0.46728 | 0.46436 | 0.46305 | 0.45847 | 0.45633 | 0.45285 | 0.44785 | 0.43928 | 0.40399 | 0.33064 | 0.31082 | 0.30053 | 0.47518 | 0.4738 | 0.47297 | 0.47085 | 0.46985 | 0.46617 | 0.46457 | 0.46157 | 0.45873 | 0.45369 | 0.42995 | 0.37965 | 0.36983 | 0.36284 | 0.44512 | 0.44319 | 0.44198 | 0.43916 | 0.4379 | 0.4334 | 0.43137 | 0.42797 | 0.42336 | 0.4153 | 0.38072 | 0.31048 | 0.29303 | 0.28405
| AIGAS | SP |  |  | 0.47079 | 0.46942 | 0.46843 | 0.46698 | 0.46231 | 0.45635 | 0.44818 | 0.44151 | 0.43387 | 0.42345 | 0.38814 | 0.27882 | 0.24344 | 0.22365 | 0.47498 | 0.47399 | 0.47313 | 0.47191 | 0.46978 | 0.46649 | 0.46135 | 0.45767 | 0.45327 | 0.44786 | 0.42986 | 0.35881 | 0.34038 | 0.3283 | 0.44521 | 0.44391 | 0.44293 | 0.44149 | 0.43731 | 0.43181 | 0.42416 | 0.41805 | 0.41101 | 0.40152 | 0.36945 | 0.2646 | 0.23295 | 0.21663
ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | YES | 5.1798 | 5.1303 | 5.0563 | 4.9911 | 4.8852 | 4.7561 | 4.6341 | 4.5057 | 4.3765 | 4.3058 | 4.0653 | 3.9571 | 4.0218 | 3.9791 | 5.8912 | 5.8516 | 5.7767 | 5.728 | 5.6431 | 5.562 | 5.4845 | 5.3897 | 5.2906 | 5.219 | 4.9229 | 4.7842 | 4.8054 | 4.7054 | 5.4855 | 5.4553 | 5.3651 | 5.2925 | 5.1382 | 4.9904 | 4.8485 | 4.6834 | 4.5075 | 4.3959 | 3.9791 | 3.8052 | 3.871 | 3.7998
| AIRD | CT |  |  | 5.1886 | 5.1346 | 5.0566 | 4.9911 | 4.8972 | 4.7681 | 4.6786 | 4.5532 | 4.4346 | 4.3734 | 4.1794 | 4.0526 | 4.1373 | 4.1636 | 5.9201 | 5.8801 | 5.8075 | 5.7453 | 5.6484 | 5.5668 | 5.4977 | 5.4135 | 5.33 | 5.2685 | 5.0263 | 4.8466 | 4.8413 | 4.8159 | 5.5422 | 5.4774 | 5.4041 | 5.3476 | 5.1745 | 5.0268 | 4.9024 | 4.7467 | 4.5957 | 4.5009 | 4.1595 | 3.9213 | 3.9578 | 3.9633
| AIRD | LW |  |  | 5.1798 | 5.1303 | 5.0563 | 5.0085 | 4.8852 | 4.7561 | 4.6341 | 4.5057 | 4.3765 | 4.3058 | 4.0653 | 3.9571 | 4.0325 | 3.9936 | 5.8912 | 5.8516 | 5.7767 | 5.728 | 5.6431 | 5.562 | 5.4845 | 5.3897 | 5.2906 | 5.219 | 4.9229 | 4.7842 | 4.8146 | 4.8003 | 5.4855 | 5.4553 | 5.3651 | 5.2925 | 5.1382 | 4.9904 | 4.8485 | 4.6834 | 4.5075 | 4.3959 | 3.9791 | 3.8052 | 3.8801 | 3.8469
| AIRD | ST |  |  | 5.1963 | 5.1452 | 5.0861 | 5.0573 | 5.0354 | 5.0175 | 5.0017 | 4.9849 | 4.9624 | 4.9333 | 4.8374 | 4.5832 | 4.5111 | 4.4974 | 5.9182 | 5.8715 | 5.8106 | 5.7831 | 5.7576 | 5.7355 | 5.7148 | 5.6924 | 5.6636 | 5.6246 | 5.4921 | 5.1121 | 5.002 | 4.9607 | 5.5425 | 5.4919 | 5.4291 | 5.3989 | 5.3734 | 5.3491 | 5.3247 | 5.3004 | 5.2608 | 5.2003 | 5.0041 | 4.5263 | 4.3819 | 4.3386
| AIRD | SP |  |  | 5.1989 | 5.149 | 5.0917 | 5.0696 | 5.0361 | 5.0047 | 4.9623 | 4.9046 | 4.8415 | 4.754 | 4.5751 | 4.2154 | 4.0218 | 3.9791 | 5.9189 | 5.872 | 5.8115 | 5.787 | 5.742 | 5.7028 | 5.6656 | 5.6229 | 5.5752 | 5.5164 | 5.3796 | 5.0789 | 4.8054 | 4.7054 | 5.5435 | 5.4917 | 5.4296 | 5.4032 | 5.3304 | 5.2654 | 5.1996 | 5.1252 | 5.0434 | 4.9335 | 4.6948 | 4.2042 | 3.871 | 3.7998
PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | 0.31518 | 0.31468 | 0.31342 | 0.31142 | 0.30899 | 0.30674 | 0.30349 | 0.30018 | 0.29627 | 0.29457 | 0.28508 | 0.28592 | 0.28858 | 0.28691 | 0.30562 | 0.3053 | 0.30455 | 0.30345 | 0.30205 | 0.30074 | 0.29895 | 0.29713 | 0.29533 | 0.29416 | 0.28678 | 0.2865 | 0.28725 | 0.28655 | 0.30091 | 0.30046 | 0.29922 | 0.29717 | 0.29454 | 0.29212 | 0.28847 | 0.28473 | 0.2812 | 0.27957 | 0.27063 | 0.27103 | 0.27351 | 0.27185
| AIRIGH-NA-BRODAIG | CT |  |  | 0.31518 | 0.31468 | 0.31342 | 0.31142 | 0.30899 | 0.30674 | 0.30349 | 0.30018 | 0.29627 | 0.29457 | 0.28508 | 0.28592 | 0.29075 | 0.29261 | 0.30562 | 0.3053 | 0.30455 | 0.30345 | 0.30205 | 0.30074 | 0.29895 | 0.29713 | 0.29533 | 0.29416 | 0.28688 | 0.2866 | 0.28849 | 0.2892 | 0.30091 | 0.30046 | 0.29922 | 0.29717 | 0.29454 | 0.29212 | 0.28847 | 0.28473 | 0.2812 | 0.27957 | 0.27063 | 0.27103 | 0.27553 | 0.27723
| AIRIGH-NA-BRODAIG | LW |  |  | 0.3155 | 0.31534 | 0.31451 | 0.31385 | 0.3115 | 0.30908 | 0.30614 | 0.30281 | 0.29853 | 0.29627 | 0.28641 | 0.28689 | 0.28858 | 0.28691 | 0.30574 | 0.30556 | 0.30503 | 0.30462 | 0.3033 | 0.30192 | 0.30018 | 0.29817 | 0.29576 | 0.29417 | 0.28678 | 0.2865 | 0.28725 | 0.28655 | 0.30117 | 0.30103 | 0.30021 | 0.29944 | 0.29686 | 0.2942 | 0.29113 | 0.28776 | 0.28307 | 0.28093 | 0.27167 | 0.27173 | 0.27351 | 0.27185
| AIRIGH-NA-BRODAIG | ST |  |  | 0.31554 | 0.3156 | 0.31557 | 0.3152 | 0.31509 | 0.31527 | 0.31537 | 0.31565 | 0.31509 | 0.31399 | 0.31036 | 0.30003 | 0.29958 | 0.29903 | 0.30584 | 0.30585 | 0.30579 | 0.30555 | 0.30537 | 0.30537 | 0.30532 | 0.30538 | 0.30495 | 0.30419 | 0.30158 | 0.29299 | 0.2934 | 0.29376 | 0.30123 | 0.30129 | 0.30127 | 0.30093 | 0.30095 | 0.30119 | 0.30134 | 0.30166 | 0.30114 | 0.30007 | 0.29646 | 0.28587 | 0.28654 | 0.28606
| AIRIGH-NA-BRODAIG | SP |  |  | 0.31587 | 0.31608 | 0.31623 | 0.3162 | 0.31634 | 0.31634 | 0.31596 | 0.31583 | 0.31511 | 0.31438 | 0.3102 | 0.30037 | 0.28965 | 0.28823 | 0.30599 | 0.30608 | 0.3061 | 0.30601 | 0.30604 | 0.30597 | 0.30565 | 0.3055 | 0.305 | 0.30453 | 0.30195 | 0.29565 | 0.28792 | 0.28714 | 0.3016 | 0.30183 | 0.30202 | 0.30206 | 0.30215 | 0.30215 | 0.30182 | 0.30166 | 0.30098 | 0.30016 | 0.29577 | 0.28548 | 0.2746 | 0.27281
COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | YES | 3.445 | 3.3675 | 3.2458 | 3.1299 | 2.8776 | 2.5624 | 2.2423 | 1.8824 | 1.4772 | 1.148 | 0.26806 | -0.80266 | -1.336 | -1.53 | 4.2462 | 4.1996 | 4.1233 | 4.0546 | 3.9261 | 3.7543 | 3.5859 | 3.3942 | 3.183 | 2.9849 | 2.4447 | 1.9135 | 1.6655 | 1.5095 | 3.7543 | 3.6902 | 3.5902 | 3.4914 | 3.2816 | 3.0177 | 2.7458 | 2.4329 | 2.0709 | 1.758 | 0.93509 | 0.024859 | -0.41355 | -0.57105
| ALYTH | CT |  |  | 3.4962 | 3.4295 | 3.319 | 3.2011 | 2.9434 | 2.6436 | 2.3187 | 1.9687 | 1.6469 | 1.3553 | 0.3665 | -0.80266 | -1.336 | -1.53 | 4.2571 | 4.2137 | 4.1429 | 4.0667 | 3.9316 | 3.7659 | 3.5995 | 3.4208 | 3.2584 | 3.1034 | 2.5234 | 1.9135 | 1.6655 | 1.5095 | 3.7941 | 3.7381 | 3.6452 | 3.539 | 3.3212 | 3.0715 | 2.8013 | 2.5083 | 2.2339 | 1.9718 | 1.05 | 0.024859 | -0.41355 | -0.57105
| ALYTH | LW |  |  | 3.445 | 3.3675 | 3.2458 | 3.1299 | 2.8776 | 2.5624 | 2.2423 | 1.8824 | 1.4772 | 1.148 | 0.26806 | -0.60337 | -0.91911 | -1.0386 | 4.2462 | 4.1996 | 4.1233 | 4.0546 | 3.9261 | 3.7543 | 3.5859 | 3.3942 | 3.183 | 2.9849 | 2.4447 | 1.9889 | 1.8767 | 1.8339 | 3.7543 | 3.6902 | 3.5902 | 3.4914 | 3.2816 | 3.0177 | 2.7458 | 2.4329 | 2.0709 | 1.758 | 0.93509 | 0.1697 | -0.085385 | -0.18195
| ALYTH | ST |  |  | 3.5154 | 3.4476 | 3.3546 | 3.2867 | 3.1947 | 3.064 | 2.9483 | 2.8293 | 2.7187 | 2.602 | 2.196 | 1.1476 | 0.61891 | 0.33029 | 4.273 | 4.2364 | 4.1754 | 4.1301 | 4.0712 | 3.9816 | 3.9071 | 3.8297 | 3.7575 | 3.6849 | 3.4161 | 2.6459 | 2.3353 | 2.1418 | 3.8154 | 3.7623 | 3.6887 | 3.6332 | 3.5598 | 3.455 | 3.3623 | 3.2671 | 3.1718 | 3.0655 | 2.6777 | 1.6417 | 1.1776 | 0.94157
| ALYTH | SP |  |  | 3.5189 | 3.4538 | 3.3624 | 3.297 | 3.1811 | 3.0333 | 2.8913 | 2.7416 | 2.6097 | 2.4834 | 2.1135 | 1.2679 | 0.68527 | 0.54184 | 4.2745 | 4.2397 | 4.1794 | 4.137 | 4.0707 | 3.9771 | 3.8934 | 3.8048 | 3.7242 | 3.6507 | 3.4278 | 2.8398 | 2.307 | 2.0293 | 3.8184 | 3.7682 | 3.6958 | 3.6446 | 3.5535 | 3.4375 | 3.3244 | 3.2042 | 3.0907 | 2.9801 | 2.6489 | 1.8356 | 1.2447 | 1.118
FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | 4.6216 | 4.621 | 4.6092 | 4.5841 | 4.5342 | 4.4665 | 4.3255 | 4.1525 | 3.923 | 3.8347 | 3.4728 | 3.328 | 3.4243 | 3.2784 | 5.7564 | 5.7506 | 5.7437 | 5.7321 | 5.7176 | 5.6975 | 5.6842 | 5.6114 | 5.5097 | 5.462 | 5.2876 | 5.2156 | 5.2055 | 5.034 | 5.2738 | 5.2694 | 5.2324 | 5.183 | 5.0312 | 4.8719 | 4.7174 | 4.5417 | 4.3188 | 4.2142 | 3.8312 | 3.6922 | 3.7769 | 3.6547
| ANNAT | CT |  |  | 4.6285 | 4.6254 | 4.6121 | 4.5841 | 4.5342 | 4.4815 | 4.4045 | 4.2351 | 4.0478 | 3.9723 | 3.7014 | 3.4404 | 3.4637 | 3.4554 | 5.7564 | 5.7506 | 5.7437 | 5.7321 | 5.7176 | 5.6975 | 5.6842 | 5.6393 | 5.5587 | 5.5166 | 5.3726 | 5.2493 | 5.2326 | 5.1845 | 5.3347 | 5.3407 | 5.3185 | 5.2648 | 5.1182 | 4.9793 | 4.8041 | 4.6177 | 4.446 | 4.3554 | 4.0393 | 3.7934 | 3.8128 | 3.8058
| ANNAT | LW |  |  | 4.6216 | 4.621 | 4.6092 | 4.5909 | 4.5391 | 4.4665 | 4.3255 | 4.1525 | 3.923 | 3.8347 | 3.4728 | 3.328 | 3.4243 | 3.3758 | 5.7584 | 5.7535 | 5.7479 | 5.7393 | 5.7263 | 5.7062 | 5.6899 | 5.6114 | 5.5097 | 5.462 | 5.2876 | 5.2156 | 5.2525 | 5.2319 | 5.2738 | 5.2694 | 5.2324 | 5.183 | 5.0312 | 4.8719 | 4.7174 | 4.5417 | 4.3188 | 4.2142 | 3.8312 | 3.6922 | 3.7769 | 3.7348
| ANNAT | ST |  |  | 4.6349 | 4.6268 | 4.6241 | 4.6181 | 4.6189 | 4.6183 | 4.6153 | 4.6075 | 4.5998 | 4.5817 | 4.506 | 4.2427 | 4.0271 | 3.9388 | 5.7663 | 5.7597 | 5.7573 | 5.7533 | 5.7498 | 5.7457 | 5.74 | 5.7297 | 5.7228 | 5.7114 | 5.659 | 5.5259 | 5.4187 | 5.3503 | 5.3207 | 5.3079 | 5.2982 | 5.2848 | 5.2771 | 5.266 | 5.249 | 5.2311 | 5.2017 | 5.1458 | 4.9509 | 4.507 | 4.3078 | 4.2297
| ANNAT | SP |  |  | 4.6401 | 4.6352 | 4.636 | 4.636 | 4.6277 | 4.6195 | 4.6099 | 4.5978 | 4.5776 | 4.5526 | 4.3795 | 3.8427 | 3.4415 | 3.2784 | 5.7665 | 5.7609 | 5.7589 | 5.7565 | 5.754 | 5.7508 | 5.7473 | 5.7427 | 5.7322 | 5.7245 | 5.6895 | 5.4206 | 5.2055 | 5.034 | 5.3296 | 5.3218 | 5.3185 | 5.3135 | 5.2714 | 5.2303 | 5.1845 | 5.1338 | 5.0711 | 4.9854 | 4.7329 | 4.174 | 3.8007 | 3.6547
NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | YES | 4.1151 | 4.0722 | 4.0462 | 4.015 | 3.9142 | 3.7779 | 3.6335 | 3.467 | 3.2217 | 3.025 | 2.5124 | 2.0912 | 2.1341 | 2.0477 | 5.2415 | 5.216 | 5.2019 | 5.1849 | 5.1411 | 5.0776 | 5.0035 | 4.9161 | 4.7957 | 4.6622 | 4.3406 | 4.0708 | 4.0638 | 3.9218 | 4.5813 | 4.5486 | 4.5248 | 4.4962 | 4.4065 | 4.2921 | 4.1689 | 4.025 | 3.8163 | 3.6464 | 3.2155 | 2.8623 | 2.9059 | 2.834
| ARDERSIER | CT |  |  | 4.1376 | 4.1062 | 4.0902 | 4.0621 | 3.9587 | 3.8311 | 3.6557 | 3.467 | 3.2688 | 3.1335 | 2.6508 | 2.1669 | 2.1341 | 2.1109 | 5.2477 | 5.2259 | 5.2148 | 5.193 | 5.1443 | 5.0824 | 5.0035 | 4.9161 | 4.8196 | 4.7362 | 4.4129 | 4.1026 | 4.066 | 4.024 | 4.6007 | 4.578 | 4.5629 | 4.536 | 4.4432 | 4.3363 | 4.1867 | 4.025 | 3.8599 | 3.7491 | 3.3466 | 2.9338 | 2.9059 | 2.8861
| ARDERSIER | LW |  |  | 4.1151 | 4.0722 | 4.0462 | 4.015 | 3.9142 | 3.7779 | 3.6335 | 3.4687 | 3.2217 | 3.025 | 2.5124 | 2.0912 | 2.1405 | 2.1181 | 5.2415 | 5.216 | 5.2019 | 5.1849 | 5.1411 | 5.0776 | 5.0061 | 4.9169 | 4.7957 | 4.6622 | 4.3406 | 4.0708 | 4.087 | 4.0782 | 4.5813 | 4.5486 | 4.5248 | 4.4962 | 4.4065 | 4.2921 | 4.1689 | 4.0258 | 3.8163 | 3.6464 | 3.2155 | 2.8623 | 2.9074 | 2.8882
| ARDERSIER | ST |  |  | 4.1345 | 4.1032 | 4.0959 | 4.0858 | 4.0799 | 4.0438 | 4.0074 | 3.9683 | 3.8882 | 3.7868 | 3.4157 | 2.7304 | 2.523 | 2.4582 | 5.2501 | 5.2306 | 5.2255 | 5.2165 | 5.2099 | 5.1842 | 5.1577 | 5.1297 | 5.082 | 5.021 | 4.7862 | 4.3418 | 4.2091 | 4.1519 | 4.5986 | 4.5766 | 4.5698 | 4.5599 | 4.5542 | 4.5282 | 4.5013 | 4.472 | 4.412 | 4.3331 | 4.0273 | 3.4364 | 3.2471 | 3.1908
| ARDERSIER | SP |  |  | 4.1427 | 4.1171 | 4.1148 | 4.1122 | 4.0925 | 4.0463 | 4.0002 | 3.9491 | 3.8717 | 3.7745 | 3.37 | 2.5991 | 2.2015 | 2.0477 | 5.2525 | 5.2356 | 5.2322 | 5.2284 | 5.2172 | 5.1896 | 5.1616 | 5.1306 | 5.0826 | 5.0242 | 4.798 | 4.3311 | 4.0638 | 3.9218 | 4.6058 | 4.5888 | 4.5864 | 4.5837 | 4.5659 | 4.5315 | 4.4964 | 4.457 | 4.399 | 4.3243 | 4.0111 | 3.3357 | 2.9668 | 2.834
FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | 2.2742 | 2.2741 | 2.2705 | 2.2621 | 2.2447 | 2.2131 | 2.173 | 2.1147 | 2.0496 | 2.0096 | 1.8626 | 1.8244 | 1.8364 | 1.7979 | 2.1028 | 2.1021 | 2.0976 | 2.0914 | 2.0724 | 2.0513 | 2.024 | 1.9904 | 1.955 | 1.9269 | 1.8227 | 1.7985 | 1.7956 | 1.763 | 2.1311 | 2.1311 | 2.1243 | 2.1145 | 2.0829 | 2.0497 | 2.0065 | 1.9519 | 1.8947 | 1.8524 | 1.6942 | 1.6619 | 1.6755 | 1.6454
| ARISAIG | CT |  |  | 2.275 | 2.2741 | 2.2705 | 2.2621 | 2.2447 | 2.2201 | 2.1829 | 2.1147 | 2.0496 | 2.019 | 1.914 | 1.8386 | 1.8509 | 1.8512 | 2.1103 | 2.1095 | 2.1057 | 2.0952 | 2.0741 | 2.052 | 2.024 | 1.9904 | 1.9594 | 1.9363 | 1.8567 | 1.804 | 1.8055 | 1.7985 | 2.144 | 2.1437 | 2.1382 | 2.1218 | 2.0874 | 2.0532 | 2.0065 | 1.9519 | 1.9018 | 1.8673 | 1.7471 | 1.6735 | 1.6865 | 1.6884
| ARISAIG | LW |  |  | 2.2742 | 2.2753 | 2.2729 | 2.2677 | 2.2457 | 2.2131 | 2.173 | 2.1305 | 2.0508 | 2.0096 | 1.8626 | 1.8244 | 1.8468 | 1.8334 | 2.1028 | 2.1021 | 2.0976 | 2.0914 | 2.0724 | 2.0513 | 2.0306 | 1.9994 | 1.955 | 1.9269 | 1.8227 | 1.7985 | 1.8085 | 1.8023 | 2.1311 | 2.1311 | 2.1243 | 2.1145 | 2.0829 | 2.0497 | 2.0159 | 1.9668 | 1.8947 | 1.8524 | 1.6942 | 1.6619 | 1.68 | 1.6687
| ARISAIG | ST |  |  | 2.2752 | 2.2746 | 2.2741 | 2.2725 | 2.2734 | 2.2741 | 2.2736 | 2.2647 | 2.2567 | 2.2448 | 2.212 | 2.0385 | 1.9918 | 1.9739 | 2.1079 | 2.1064 | 2.1048 | 2.1017 | 2.0995 | 2.0977 | 2.0933 | 2.0859 | 2.0741 | 2.0576 | 2.0144 | 1.8968 | 1.8671 | 1.8521 | 2.1393 | 2.1373 | 2.1353 | 2.1309 | 2.1285 | 2.1266 | 2.1208 | 2.1125 | 2.0956 | 2.0713 | 2.0068 | 1.8355 | 1.7989 | 1.7867
| ARISAIG | SP |  |  | 2.2777 | 2.278 | 2.2785 | 2.279 | 2.2772 | 2.2744 | 2.2694 | 2.2543 | 2.2421 | 2.2232 | 2.1507 | 1.969 | 1.8364 | 1.7979 | 2.1114 | 2.1106 | 2.1097 | 2.1087 | 2.1028 | 2.0975 | 2.0912 | 2.0782 | 2.0644 | 2.0451 | 1.9982 | 1.8883 | 1.7956 | 1.763 | 2.145 | 2.1443 | 2.1434 | 2.1426 | 2.1332 | 2.1252 | 2.1153 | 2.0969 | 2.0763 | 2.0467 | 1.9734 | 1.8061 | 1.6755 | 1.6454
STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | 6.1055 | 6.106 | 6.1058 | 6.1056 | 6.1047 | 6.1036 | 6.1029 | 6.1013 | 6.0996 | 6.0982 | 6.0928 | 6.0915 | 6.0897 | 6.089 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.9989 | 11.9984 | 11.9979 | 11.9973 | 11.9965 | 11.9958 | 11.9921 | 11.9914 | 11.9908 | 11.9906 | 11.9992 | 11.9994 | 11.9992 | 11.999 | 11.9982 | 11.9973 | 11.9966 | 11.9953 | 11.9938 | 11.9925 | 11.9873 | 11.9861 | 11.9846 | 11.984
| ARNISH | CT |  |  | 6.1065 | 6.1065 | 6.1065 | 6.1062 | 6.1054 | 6.1046 | 6.1029 | 6.1013 | 6.0996 | 6.0986 | 6.0945 | 6.0921 | 6.0914 | 6.0909 | 11.9998 | 11.9997 | 11.9995 | 11.9993 | 11.999 | 11.9986 | 11.9979 | 11.9973 | 11.9965 | 11.9959 | 11.993 | 11.9918 | 11.9915 | 11.9914 | 11.9998 | 11.9997 | 11.9995 | 11.9992 | 11.9988 | 11.9981 | 11.9967 | 11.9953 | 11.9938 | 11.9929 | 11.9888 | 11.9867 | 11.986 | 11.9856
| ARNISH | LW |  |  | 6.1055 | 6.106 | 6.1058 | 6.1056 | 6.1047 | 6.1036 | 6.1029 | 6.1016 | 6.0996 | 6.0982 | 6.0928 | 6.0915 | 6.0919 | 6.0919 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.9989 | 11.9984 | 11.998 | 11.9975 | 11.9967 | 11.9958 | 11.9921 | 11.9914 | 11.9916 | 11.9915 | 11.9992 | 11.9994 | 11.9992 | 11.999 | 11.9982 | 11.9973 | 11.9966 | 11.9956 | 11.9939 | 11.9925 | 11.9873 | 11.9861 | 11.9865 | 11.9864
| ARNISH | ST |  |  | 6.1062 | 6.1061 | 6.1061 | 6.1061 | 6.106 | 6.1057 | 6.1055 | 6.1053 | 6.1049 | 6.1041 | 6.102 | 6.0958 | 6.0938 | 6.0928 | 11.9999 | 11.9998 | 11.9997 | 11.9997 | 11.9996 | 11.9995 | 11.9993 | 11.9991 | 11.9989 | 11.9985 | 11.9972 | 11.9931 | 11.9923 | 11.9919 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9994 | 11.9993 | 11.999 | 11.9988 | 11.9985 | 11.9978 | 11.9958 | 11.9899 | 11.9881 | 11.9872
| ARNISH | SP |  |  | 6.1061 | 6.106 | 6.1059 | 6.1058 | 6.1051 | 6.1043 | 6.1036 | 6.1028 | 6.1019 | 6.1008 | 6.0981 | 6.0933 | 6.0897 | 6.089 | 11.9999 | 11.9998 | 11.9997 | 11.9996 | 11.9994 | 11.9991 | 11.9988 | 11.9985 | 11.9981 | 11.9976 | 11.9963 | 11.9937 | 11.9908 | 11.9906 | 11.9997 | 11.9996 | 11.9995 | 11.9993 | 11.9987 | 11.9981 | 11.9975 | 11.9968 | 11.996 | 11.9949 | 11.9925 | 11.9881 | 11.9846 | 11.984
ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | 1.8224 | 14.6202 | 14.0996 | 13.4037 | 12.4687 | 11.6226 | 10.732 | 9.7328 | 8.3473 | 7.2427 | 3.7086 | 0.14193 | -1.0112 | -1.4105 | 4.9412 | 16.5252 | 15.9729 | 15.2357 | 14.4443 | 13.8359 | 13.2209 | 12.6017 | 11.6358 | 10.8709 | 8.345 | 6.307 | 5.6552 | 5.1752 | 4.3925 | 16.0454 | 15.5709 | 14.9255 | 14.0562 | 13.278 | 12.4609 | 11.5424 | 10.2797 | 9.2779 | 6.0894 | 3.0807 | 2.075 | 1.7297
| ASHGROVE | CT |  |  | 1.8527 | 14.6579 | 14.1396 | 13.4406 | 12.5146 | 11.6774 | 10.7622 | 9.8201 | 8.579 | 7.4231 | 3.7453 | 0.14193 | -1.0112 | -1.4105 | 4.9412 | 16.5252 | 15.9729 | 15.2357 | 14.4443 | 13.8359 | 13.2209 | 12.6017 | 11.6657 | 10.8915 | 8.345 | 6.307 | 5.6552 | 5.1752 | 4.4164 | 16.0756 | 15.6017 | 14.9488 | 14.085 | 13.3164 | 12.4788 | 11.6168 | 10.4927 | 9.4495 | 6.1495 | 3.0807 | 2.075 | 1.7297
| ASHGROVE | LW |  |  | 1.8224 | 14.6202 | 14.0996 | 13.4037 | 12.4687 | 11.6226 | 10.732 | 9.7328 | 8.3473 | 7.2427 | 3.7086 | 0.77789 | -0.084994 | -0.37312 | 4.9495 | 16.5357 | 15.988 | 15.2618 | 14.4781 | 13.8745 | 13.2569 | 12.6063 | 11.6358 | 10.8709 | 8.3531 | 6.6833 | 6.3341 | 6.2131 | 4.3925 | 16.0454 | 15.5709 | 14.9255 | 14.0562 | 13.278 | 12.4609 | 11.5424 | 10.2797 | 9.2779 | 6.0894 | 3.621 | 2.8737 | 2.6258
| ASHGROVE | ST |  |  | 1.8975 | 14.7015 | 14.2103 | 13.5639 | 12.901 | 12.3536 | 11.785 | 11.2137 | 10.3548 | 9.5832 | 7.1747 | 4.2744 | 3.395 | 2.8672 | 4.9603 | 16.5554 | 16.0177 | 15.3053 | 14.5466 | 13.9752 | 13.3922 | 12.8184 | 11.9969 | 11.3385 | 9.3765 | 7.984 | 7.3762 | 6.8391 | 4.4608 | 16.1215 | 15.6752 | 15.0756 | 14.4457 | 13.9318 | 13.371 | 12.8147 | 11.9943 | 11.3227 | 9.2692 | 6.7503 | 5.9582 | 5.4979
| ASHGROVE | SP |  |  | 1.9056 | 14.7195 | 14.2385 | 13.6009 | 12.9051 | 12.3297 | 11.7304 | 11.1303 | 10.2301 | 9.442 | 7.0952 | 4.5926 | 3.6857 | 3.5012 | 4.9597 | 16.5567 | 16.0206 | 15.3133 | 14.558 | 13.9904 | 13.4121 | 12.8443 | 12.0283 | 11.3754 | 9.4184 | 8.1054 | 7.1821 | 6.2589 | 4.4672 | 16.1371 | 15.7002 | 15.1103 | 14.4481 | 13.9161 | 13.3628 | 12.8105 | 12.002 | 11.2989 | 9.2262 | 7.0931 | 6.222 | 6.0549
MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | 1.9069 | 1.2991 | 0.65661 | -0.0088877 | -0.95569 | -1.9485 | -3.1507 | -4.3749 | -5.7689 | -7.0131 | -11.0272 | -14.7731 | -16.2926 | -16.8562 | 4.8558 | 4.3693 | 3.8546 | 3.3221 | 2.6685 | 1.9749 | 1.0963 | 0.21551 | -0.74504 | -1.6781 | -4.7466 | -7.1987 | -8.128 | -8.8396 | 3.298 | 2.7487 | 2.1639 | 1.5549 | 0.69196 | -0.22722 | -1.3508 | -2.4899 | -3.7782 | -4.9417 | -8.6979 | -12.0775 | -13.4114 | -13.8984
| ASHLUDIE | CT |  |  | 1.968 | 1.4061 | 0.78881 | 0.15909 | -0.73284 | -1.6096 | -2.7139 | -3.8351 | -5.0049 | -6.2656 | -10.8894 | -14.7731 | -16.2926 | -16.8562 | 4.8663 | 4.3917 | 3.8724 | 3.3393 | 2.7021 | 2.0695 | 1.2903 | 0.51604 | -0.29686 | -1.2161 | -4.6922 | -7.1987 | -8.128 | -8.8396 | 3.3497 | 2.8405 | 2.2755 | 1.6958 | 0.88183 | 0.07155 | -0.94659 | -1.974 | -3.0451 | -4.2147 | -8.5452 | -12.0775 | -13.4114 | -13.8984
| ASHLUDIE | LW |  |  | 1.9069 | 1.2991 | 0.65661 | -0.0088877 | -0.95569 | -1.9485 | -3.1507 | -4.3749 | -5.7689 | -7.0131 | -11.0272 | -14.1243 | -15.245 | -15.6696 | 4.8558 | 4.3693 | 3.8546 | 3.3221 | 2.6685 | 1.9749 | 1.0963 | 0.21551 | -0.74504 | -1.6781 | -4.7466 | -6.7954 | -7.2961 | -7.4931 | 3.298 | 2.7487 | 2.1639 | 1.5549 | 0.69196 | -0.22722 | -1.3508 | -2.4899 | -3.7782 | -4.9417 | -8.6979 | -11.5329 | -12.5137 | -12.8788
| ASHLUDIE | ST |  |  | 2.0593 | 1.5614 | 1.0453 | 0.52393 | 0.0078037 | -0.49679 | -1.1112 | -1.7311 | -2.3972 | -3.1979 | -6.1164 | -9.7891 | -11.0408 | -11.7932 | 4.9298 | 4.499 | 4.0482 | 3.5948 | 3.1396 | 2.6813 | 2.1225 | 1.5673 | 0.97241 | 0.27749 | -2.3429 | -5.2306 | -6.1475 | -6.9275 | 3.4375 | 2.9898 | 2.5219 | 2.0478 | 1.575 | 1.1008 | 0.52262 | -0.05623 | -0.67713 | -1.4289 | -4.1844 | -7.6732 | -8.7942 | -9.4466
| ASHLUDIE | SP |  |  | 2.103 | 1.6254 | 1.124 | 0.62733 | 0.087086 | -0.44368 | -1.091 | -1.7442 | -2.4418 | -3.2119 | -5.9797 | -9.3428 | -10.8138 | -11.2387 | 4.9542 | 4.534 | 4.0884 | 3.6475 | 3.1838 | 2.7148 | 2.1409 | 1.5683 | 0.95704 | 0.28528 | -2.2016 | -4.9302 | -6.4767 | -7.7531 | 3.4784 | 3.0495 | 2.5947 | 2.1436 | 1.65 | 1.153 | 0.54561 | -0.063329 | -0.71246 | -1.4315 | -4.0216 | -7.2046 | -8.5934 | -8.9676
GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | 5.2224 | 5.2161 | 5.1814 | 5.137 | 5.0044 | 4.8658 | 4.7297 | 4.5901 | 4.3897 | 4.3 | 3.8496 | 3.7337 | 3.8091 | 3.6745 | 5.4396 | 5.4308 | 5.412 | 5.3869 | 5.3241 | 5.2521 | 5.1832 | 5.0916 | 4.9744 | 4.899 | 4.5743 | 4.5059 | 4.5265 | 4.4443 | 5.2243 | 5.2152 | 5.1841 | 5.1444 | 5.027 | 4.9043 | 4.7836 | 4.6595 | 4.4818 | 4.4008 | 3.9422 | 3.8356 | 3.9074 | 3.7823
| AULTBEA | CT |  |  | 5.2765 | 5.2829 | 5.2663 | 5.2308 | 5.1073 | 4.9887 | 4.8188 | 4.6411 | 4.476 | 4.4053 | 4.084 | 3.8229 | 3.8285 | 3.8152 | 5.4583 | 5.4536 | 5.4377 | 5.4024 | 5.3331 | 5.2688 | 5.1866 | 5.1027 | 5.0212 | 4.9602 | 4.6964 | 4.5406 | 4.5346 | 4.5148 | 5.2731 | 5.2765 | 5.2603 | 5.2273 | 5.1166 | 5.0114 | 4.8613 | 4.7043 | 4.5582 | 4.4943 | 4.1508 | 3.9187 | 3.9285 | 3.9178
| AULTBEA | LW |  |  | 5.2224 | 5.2161 | 5.1814 | 5.137 | 5.0044 | 4.8658 | 4.7297 | 4.5901 | 4.3897 | 4.3 | 3.8496 | 3.7337 | 3.8091 | 3.7766 | 5.4396 | 5.4308 | 5.412 | 5.3869 | 5.3241 | 5.2521 | 5.1832 | 5.0916 | 4.9744 | 4.899 | 4.5743 | 4.5059 | 4.536 | 4.5227 | 5.2243 | 5.2152 | 5.1841 | 5.1444 | 5.027 | 4.9043 | 4.7836 | 4.6595 | 4.4818 | 4.4008 | 3.9422 | 3.8356 | 3.9074 | 3.8759
| AULTBEA | ST |  |  | 5.2604 | 5.2524 | 5.2453 | 5.2378 | 5.2343 | 5.2223 | 5.2074 | 5.1917 | 5.1596 | 5.1095 | 4.9441 | 4.4353 | 4.2728 | 4.2016 | 5.4593 | 5.4525 | 5.4466 | 5.4354 | 5.4258 | 5.4154 | 5.4011 | 5.3853 | 5.3631 | 5.3262 | 5.1912 | 4.7924 | 4.7059 | 4.6638 | 5.2613 | 5.2529 | 5.2451 | 5.237 | 5.231 | 5.2224 | 5.2119 | 5.2011 | 5.1744 | 5.1313 | 4.9498 | 4.4135 | 4.2982 | 4.2484
| AULTBEA | SP |  |  | 5.2702 | 5.2663 | 5.2653 | 5.2641 | 5.23 | 5.1964 | 5.1595 | 5.119 | 5.0754 | 5.0066 | 4.7838 | 4.3144 | 3.8133 | 3.6745 | 5.4654 | 5.4611 | 5.4568 | 5.4527 | 5.4357 | 5.4184 | 5.3993 | 5.3769 | 5.3452 | 5.3016 | 5.1699 | 4.839 | 4.5265 | 4.4443 | 5.2694 | 5.2645 | 5.262 | 5.259 | 5.2275 | 5.1977 | 5.165 | 5.1291 | 5.0903 | 5.0292 | 4.8314 | 4.3693 | 3.9124 | 3.7823
BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | YES | 15.11 | 15.0951 | 15.0797 | 15.0449 | 15.0177 | 14.9942 | 14.9697 | 14.9458 | 14.9233 | 14.8995 | 13.9714 | 12.7233 | 12.6964 | 12.6912 | 16.4365 | 16.3907 | 16.3388 | 16.2537 | 16.1629 | 16.0772 | 15.994 | 15.9071 | 15.8201 | 15.7151 | 15.052 | 14.1682 | 14.1489 | 14.1453 | 14.9613 | 14.905 | 14.8428 | 14.752 | 14.671 | 14.5852 | 14.4986 | 14.4071 | 14.3143 | 14.205 | 13.5667 | 12.3634 | 12.3379 | 12.3329
| AVIEMORE | CT |  |  | 15.11 | 15.0951 | 15.0797 | 15.0449 | 15.0177 | 14.9942 | 14.9697 | 14.9458 | 14.9233 | 14.901 | 14.2545 | 13.2274 | 13.1543 | 13.1489 | 16.4365 | 16.3907 | 16.3388 | 16.2537 | 16.1629 | 16.0772 | 15.994 | 15.9071 | 15.8201 | 15.72 | 15.2491 | 14.52 | 14.4651 | 14.4558 | 14.9626 | 14.9051 | 14.8428 | 14.752 | 14.671 | 14.5852 | 14.4986 | 14.4071 | 14.3164 | 14.2199 | 13.8402 | 12.8505 | 12.7803 | 12.7751
| AVIEMORE | LW |  |  | 15.1104 | 15.0957 | 15.0805 | 15.0462 | 15.0194 | 14.9963 | 14.9715 | 14.9469 | 14.9235 | 14.8995 | 13.9714 | 12.7233 | 12.6964 | 12.6912 | 16.4429 | 16.3988 | 16.3503 | 16.2698 | 16.1851 | 16.1045 | 16.0184 | 15.9258 | 15.8303 | 15.7151 | 15.052 | 14.1682 | 14.1489 | 14.1453 | 14.9613 | 14.905 | 14.8446 | 14.7569 | 14.6803 | 14.598 | 14.5084 | 14.4117 | 14.3143 | 14.205 | 13.5667 | 12.3634 | 12.3379 | 12.3329
| AVIEMORE | ST |  |  | 15.1122 | 15.0989 | 15.0855 | 15.0537 | 15.03 | 15.0106 | 14.9893 | 14.9687 | 14.9495 | 14.9306 | 14.8803 | 13.6447 | 12.9607 | 12.9372 | 16.4593 | 16.4284 | 16.3958 | 16.3388 | 16.2834 | 16.2364 | 16.1832 | 16.127 | 16.0699 | 15.9998 | 15.7794 | 14.8162 | 14.329 | 14.3069 | 14.9755 | 14.9285 | 14.8804 | 14.8113 | 14.7596 | 14.7046 | 14.6419 | 14.5752 | 14.5083 | 14.4349 | 14.2262 | 13.2538 | 12.5932 | 12.5705
| AVIEMORE | SP |  |  | 15.1128 | 15.0997 | 15.0865 | 15.0548 | 15.0311 | 15.0119 | 14.9909 | 14.9708 | 14.9524 | 14.9347 | 14.8938 | 14.5148 | 13.5184 | 13.3159 | 16.4622 | 16.433 | 16.402 | 16.347 | 16.2933 | 16.2495 | 16.201 | 16.1507 | 16.1018 | 16.0456 | 15.9104 | 15.4316 | 14.7197 | 14.5624 | 14.9837 | 14.9379 | 14.8909 | 14.8233 | 14.7708 | 14.717 | 14.6566 | 14.5925 | 14.5308 | 14.4667 | 14.3267 | 13.998 | 13.1326 | 12.9368
ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | 1.5185 | 1.5351 | 1.5129 | 1.4724 | 1.3091 | 1.1325 | 0.9434 | 0.6662 | 0.25989 | -0.011 | -0.96576 | -1.4743 | -1.3753 | -1.5822 | 2.5377 | 2.5318 | 2.5059 | 2.4638 | 2.3622 | 2.248 | 2.126 | 1.9605 | 1.7511 | 1.5883 | 0.99329 | 0.64495 | 0.67621 | 0.48283 | 1.8375 | 1.8484 | 1.8173 | 1.7649 | 1.5764 | 1.3721 | 1.1589 | 0.88684 | 0.51143 | 0.26317 | -0.60325 | -1.0749 | -0.97891 | -1.1765
| BALALDIE | CT |  |  | 1.5907 | 1.6154 | 1.6081 | 1.5834 | 1.4203 | 1.2624 | 1.0103 | 0.72147 | 0.41025 | 0.1931 | -0.58809 | -1.1943 | -1.2657 | -1.3183 | 2.5668 | 2.5636 | 2.5412 | 2.4997 | 2.3892 | 2.2798 | 2.1303 | 1.9694 | 1.8111 | 1.6779 | 1.1848 | 0.7961 | 0.73175 | 0.66686 | 1.9171 | 1.9378 | 1.9237 | 1.8899 | 1.7023 | 1.5174 | 1.2367 | 0.93765 | 0.64964 | 0.4507 | -0.25553 | -0.81279 | -0.87436 | -0.92123
| BALALDIE | LW |  |  | 1.5185 | 1.5351 | 1.5129 | 1.4724 | 1.3091 | 1.1325 | 0.9434 | 0.6662 | 0.25989 | -0.011 | -0.96576 | -1.4743 | -1.3753 | -1.4163 | 2.5377 | 2.5318 | 2.5059 | 2.4638 | 2.3622 | 2.248 | 2.126 | 1.9605 | 1.7511 | 1.5883 | 0.99329 | 0.64495 | 0.67621 | 0.65861 | 1.8375 | 1.8484 | 1.8173 | 1.7649 | 1.5764 | 1.3721 | 1.1589 | 0.88684 | 0.51143 | 0.26317 | -0.60325 | -1.0749 | -0.97891 | -1.0173
| BALALDIE | ST |  |  | 1.5587 | 1.5417 | 1.521 | 1.5056 | 1.4907 | 1.4721 | 1.4355 | 1.3993 | 1.3442 | 1.2479 | 0.89776 | -0.23104 | -0.66891 | -0.81713 | 2.5648 | 2.5508 | 2.5335 | 2.5138 | 2.4945 | 2.4729 | 2.438 | 2.4014 | 2.3565 | 2.2818 | 2.0004 | 1.2228 | 0.94032 | 0.83242 | 1.8886 | 1.8686 | 1.8454 | 1.8293 | 1.8118 | 1.7891 | 1.7498 | 1.7096 | 1.6456 | 1.535 | 1.1292 | 0.094169 | -0.31139 | -0.44766
| BALALDIE | SP |  |  | 1.5688 | 1.5571 | 1.5424 | 1.5219 | 1.4586 | 1.3982 | 1.3202 | 1.2389 | 1.1499 | 1.0222 | 0.64285 | -0.45786 | -1.3255 | -1.5822 | 2.5698 | 2.5595 | 2.5455 | 2.5268 | 2.4888 | 2.4512 | 2.402 | 2.3503 | 2.2905 | 2.2093 | 1.9573 | 1.3036 | 0.71493 | 0.48283 | 1.8992 | 1.8849 | 1.8686 | 1.8469 | 1.7769 | 1.7097 | 1.6261 | 1.5378 | 1.4416 | 1.3008 | 0.87615 | -0.14457 | -0.93703 | -1.1765
ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | 1.8296 | 3.3514 | 3.2399 | 3.08 | 2.8398 | 2.584 | 2.3857 | 2.1852 | 1.8448 | 1.5578 | 0.7268 | 0.11217 | -0.10848 | -0.20285 | 2.5542 | 4.5597 | 4.4809 | 4.3851 | 4.2313 | 4.0705 | 3.9238 | 3.7736 | 3.5619 | 3.3857 | 2.858 | 2.4265 | 2.2801 | 2.1735 | 1.7911 | 3.7791 | 3.6743 | 3.5438 | 3.3197 | 3.0818 | 2.8554 | 2.6193 | 2.2657 | 1.9844 | 1.1948 | 0.66498 | 0.47976 | 0.40063
| BALBEGGIE | CT |  |  | 1.8296 | 3.3554 | 3.2459 | 3.0936 | 2.8499 | 2.5987 | 2.3931 | 2.1852 | 1.9596 | 1.7206 | 0.85185 | 0.11217 | -0.10848 | -0.20285 | 2.5593 | 4.5671 | 4.4888 | 4.3896 | 4.2328 | 4.0828 | 3.9326 | 3.7818 | 3.6288 | 3.4801 | 2.9141 | 2.4265 | 2.2801 | 2.1735 | 1.8077 | 3.803 | 3.703 | 3.5692 | 3.3427 | 3.1269 | 2.8937 | 2.6557 | 2.4071 | 2.1742 | 1.3187 | 0.66498 | 0.47976 | 0.40063
| BALBEGGIE | LW |  |  | 1.83 | 3.3514 | 3.2399 | 3.08 | 2.8398 | 2.584 | 2.3857 | 2.1855 | 1.8448 | 1.5578 | 0.7268 | 0.1494 | 0.048744 | -0.030878 | 2.5542 | 4.5597 | 4.4809 | 4.3851 | 4.2313 | 4.0705 | 3.9238 | 3.7736 | 3.5619 | 3.3857 | 2.858 | 2.4614 | 2.3971 | 2.3545 | 1.7911 | 3.7791 | 3.6743 | 3.5438 | 3.3197 | 3.0818 | 2.8554 | 2.6193 | 2.2657 | 1.9844 | 1.1948 | 0.68753 | 0.603 | 0.53706
| BALBEGGIE | ST |  |  | 1.9066 | 3.4773 | 3.4228 | 3.3674 | 3.3016 | 3.2421 | 3.1713 | 3.1008 | 3.0143 | 2.8887 | 2.346 | 1.0449 | 0.36884 | 0.2798 | 2.5928 | 4.6186 | 4.569 | 4.5223 | 4.4706 | 4.4262 | 4.3739 | 4.3276 | 4.2697 | 4.188 | 3.8234 | 2.9601 | 2.6136 | 2.4786 | 1.8496 | 3.8675 | 3.8078 | 3.7482 | 3.6825 | 3.6254 | 3.5565 | 3.4956 | 3.4156 | 3.2984 | 2.8134 | 1.654 | 1.2203 | 1.0836
| BALBEGGIE | SP |  |  | 1.9129 | 3.4914 | 3.4402 | 3.3914 | 3.3332 | 3.2873 | 3.2274 | 3.1703 | 3.1063 | 3.0199 | 2.5847 | 1.4633 | 0.729 | 0.46272 | 2.6004 | 4.6318 | 4.5869 | 4.5466 | 4.4922 | 4.4451 | 4.3921 | 4.3436 | 4.2878 | 4.2209 | 3.9256 | 3.1683 | 2.6513 | 2.3925 | 1.8618 | 3.8881 | 3.836 | 3.7862 | 3.7129 | 3.6478 | 3.5739 | 3.5042 | 3.4232 | 3.3257 | 2.9301 | 1.8926 | 1.1913 | 0.9583
MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | 14.8052 | 14.7164 | 14.644 | 14.5762 | 14.2733 | 13.7767 | 13.1972 | 12.4533 | 11.676 | 10.9101 | 8.527 | 5.5237 | 3.8607 | 3.1096 | 14.6976 | 14.6284 | 14.564 | 14.5016 | 14.4342 | 14.3557 | 14.2605 | 14.0168 | 13.5386 | 13.046 | 11.4475 | 9.8043 | 8.878 | 8.1257 | 14.7402 | 14.665 | 14.5986 | 14.54 | 14.1983 | 13.75 | 13.2227 | 12.5462 | 11.8368 | 11.124 | 8.899 | 6.2435 | 4.8307 | 4.2303
| BALDOVIE | CT |  |  | 14.8052 | 14.7164 | 14.644 | 14.5762 | 14.3574 | 13.9032 | 13.4402 | 12.8619 | 12.1678 | 11.3171 | 8.6032 | 5.5237 | 3.8607 | 3.1096 | 14.6976 | 14.6284 | 14.564 | 14.5016 | 14.4342 | 14.3557 | 14.2605 | 14.0291 | 13.6938 | 13.1629 | 11.4748 | 9.8043 | 8.878 | 8.1257 | 14.7576 | 14.6884 | 14.6313 | 14.603 | 14.2649 | 13.8539 | 13.434 | 12.9112 | 12.2826 | 11.5014 | 8.9948 | 6.2435 | 4.8307 | 4.2303
| BALDOVIE | LW |  |  | 14.812 | 14.7257 | 14.6584 | 14.5992 | 14.2733 | 13.7767 | 13.1972 | 12.4533 | 11.676 | 10.9101 | 8.527 | 6.3209 | 5.0286 | 4.4203 | 14.7034 | 14.6371 | 14.5778 | 14.5245 | 14.462 | 14.3847 | 14.2811 | 14.0168 | 13.5386 | 13.046 | 11.4475 | 10.2763 | 9.7452 | 9.4631 | 14.7402 | 14.665 | 14.5986 | 14.54 | 14.1983 | 13.75 | 13.2227 | 12.5462 | 11.8368 | 11.124 | 8.899 | 6.9249 | 5.8407 | 5.3605
| BALDOVIE | ST |  |  | 14.8301 | 14.758 | 14.7068 | 14.6762 | 14.6514 | 14.6206 | 14.5581 | 14.3864 | 14.1337 | 13.8054 | 12.814 | 10.8338 | 9.6441 | 8.7041 | 14.7176 | 14.6622 | 14.6156 | 14.584 | 14.5605 | 14.5328 | 14.4739 | 14.2792 | 13.9973 | 13.6622 | 12.7415 | 11.9414 | 11.113 | 10.2712 | 14.812 | 14.7431 | 14.6902 | 14.6715 | 14.658 | 14.6356 | 14.5794 | 14.4302 | 14.215 | 13.8627 | 12.8098 | 10.9508 | 9.9281 | 9.1528
| BALDOVIE | SP |  |  | 14.8313 | 14.7622 | 14.7138 | 14.6888 | 14.6677 | 14.6422 | 14.5865 | 14.4215 | 14.1679 | 13.8029 | 12.7867 | 11.4088 | 10.3205 | 9.928 | 14.718 | 14.6647 | 14.6198 | 14.5927 | 14.5718 | 14.5479 | 14.4936 | 14.3035 | 14.0241 | 13.7014 | 12.8379 | 12.1662 | 10.9557 | 9.6891 | 14.8295 | 14.7736 | 14.7315 | 14.7071 | 14.6618 | 14.6131 | 14.5317 | 14.356 | 14.1068 | 13.7648 | 12.8131 | 11.5286 | 10.5324 | 10.2302
TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | 9.067 | 9.0135 | 8.9619 | 8.9015 | 8.5568 | 8.1931 | 7.825 | 7.4271 | 6.9526 | 6.6997 | 5.6938 | 5.3488 | 5.4745 | 5.2555 | 10.2752 | 10.2406 | 10.2064 | 10.157 | 10.0021 | 9.8346 | 9.6538 | 9.4246 | 9.1686 | 8.9655 | 8.2966 | 8.076 | 8.1013 | 7.8531 | 9.5284 | 9.5039 | 9.483 | 9.4582 | 9.2249 | 8.9771 | 8.689 | 8.3193 | 7.8436 | 7.5481 | 6.5248 | 6.2096 | 6.3222 | 6.1436
| BALLATER | CT |  |  | 9.1302 | 9.1237 | 9.1021 | 9.0602 | 8.7466 | 8.3977 | 7.9855 | 7.5728 | 7.1888 | 6.9927 | 6.2017 | 5.5362 | 5.4745 | 5.4125 | 10.2932 | 10.2739 | 10.2506 | 10.199 | 10.0172 | 9.8494 | 9.6565 | 9.4628 | 9.2766 | 9.1335 | 8.5478 | 8.152 | 8.1013 | 8.0377 | 9.5568 | 9.558 | 9.5572 | 9.5646 | 9.3142 | 9.0796 | 8.797 | 8.4471 | 8.0794 | 7.8643 | 6.993 | 6.3757 | 6.3222 | 6.2676
| BALLATER | LW |  |  | 9.067 | 9.0135 | 8.9619 | 8.9015 | 8.5568 | 8.1931 | 7.825 | 7.4271 | 6.9526 | 6.6997 | 5.6938 | 5.3488 | 5.5308 | 5.4802 | 10.2752 | 10.2406 | 10.2064 | 10.157 | 10.0021 | 9.8346 | 9.6538 | 9.4246 | 9.1686 | 8.9655 | 8.2966 | 8.076 | 8.1419 | 8.1208 | 9.5284 | 9.5039 | 9.483 | 9.4582 | 9.2249 | 8.9771 | 8.689 | 8.3193 | 7.8436 | 7.5481 | 6.5248 | 6.2096 | 6.3654 | 6.321
| BALLATER | ST |  |  | 9.1098 | 9.0839 | 9.0613 | 9.0512 | 9.0348 | 9.0158 | 8.9822 | 8.943 | 8.8712 | 8.7436 | 8.3117 | 7.0259 | 6.5525 | 6.3665 | 10.3002 | 10.2845 | 10.2685 | 10.2442 | 10.2191 | 10.1916 | 10.1491 | 10.1102 | 10.0515 | 9.9611 | 9.6242 | 8.7518 | 8.485 | 8.3722 | 9.5425 | 9.5244 | 9.5097 | 9.5068 | 9.5015 | 9.4939 | 9.4719 | 9.4478 | 9.4004 | 9.3066 | 8.9825 | 7.6884 | 7.2612 | 7.0977
| BALLATER | SP |  |  | 9.1413 | 9.137 | 9.1351 | 9.1261 | 9.0661 | 9.0065 | 8.9395 | 8.8654 | 8.7934 | 8.6597 | 8.0945 | 6.8111 | 5.6596 | 5.2555 | 10.3119 | 10.3033 | 10.2957 | 10.2814 | 10.2445 | 10.2096 | 10.1696 | 10.1196 | 10.0575 | 9.9699 | 9.6443 | 8.8226 | 8.1062 | 7.8531 | 9.5687 | 9.565 | 9.5662 | 9.562 | 9.5258 | 9.49 | 9.4461 | 9.3974 | 9.3519 | 9.2573 | 8.8607 | 7.5723 | 6.4803 | 6.1436
CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | 0.69224 | 0.69135 | 0.69082 | 0.68612 | 0.67469 | 0.66248 | 0.63826 | 0.61298 | 0.58663 | 0.56608 | 0.46453 | 0.45183 | 0.45388 | 0.4369 | 0.59582 | 0.59579 | 0.59528 | 0.59366 | 0.59217 | 0.5904 | 0.5818 | 0.56902 | 0.55578 | 0.54644 | 0.50497 | 0.49871 | 0.4975 | 0.4863 | 0.56583 | 0.56525 | 0.56438 | 0.56245 | 0.5608 | 0.55871 | 0.55671 | 0.55455 | 0.55152 | 0.54701 | 0.51019 | 0.50208 | 0.50148 | 0.48157
| BALLIEKINE | CT |  |  | 0.69327 | 0.69463 | 0.69326 | 0.68612 | 0.67469 | 0.66248 | 0.63826 | 0.61298 | 0.58934 | 0.57412 | 0.49366 | 0.46469 | 0.47973 | 0.48433 | 0.59582 | 0.59579 | 0.59528 | 0.59366 | 0.59217 | 0.5904 | 0.5818 | 0.56902 | 0.55718 | 0.55025 | 0.51698 | 0.50445 | 0.51165 | 0.51255 | 0.56583 | 0.56525 | 0.56438 | 0.56245 | 0.5608 | 0.55871 | 0.55671 | 0.55455 | 0.55223 | 0.5489 | 0.53015 | 0.5143 | 0.52225 | 0.52211
| BALLIEKINE | LW |  |  | 0.69307 | 0.69487 | 0.69448 | 0.69251 | 0.67931 | 0.6645 | 0.64998 | 0.62497 | 0.58663 | 0.56608 | 0.46453 | 0.45183 | 0.46424 | 0.45755 | 0.59693 | 0.59743 | 0.59764 | 0.59751 | 0.59574 | 0.59302 | 0.5856 | 0.57412 | 0.55578 | 0.54644 | 0.50497 | 0.49871 | 0.50518 | 0.50169 | 0.56629 | 0.56568 | 0.56509 | 0.56421 | 0.56302 | 0.56153 | 0.55994 | 0.55582 | 0.55152 | 0.54701 | 0.51019 | 0.50208 | 0.51763 | 0.50948
| BALLIEKINE | ST |  |  | 0.69224 | 0.69135 | 0.69082 | 0.68909 | 0.68954 | 0.68966 | 0.68963 | 0.68904 | 0.68525 | 0.67672 | 0.64512 | 0.54587 | 0.54224 | 0.54123 | 0.59609 | 0.59596 | 0.59591 | 0.5955 | 0.59582 | 0.59605 | 0.59622 | 0.59625 | 0.59571 | 0.59423 | 0.58619 | 0.54564 | 0.54285 | 0.54088 | 0.56657 | 0.56626 | 0.56599 | 0.56527 | 0.5646 | 0.56387 | 0.56309 | 0.56213 | 0.56089 | 0.55886 | 0.55095 | 0.52472 | 0.5218 | 0.52163
| BALLIEKINE | SP |  |  | 0.69437 | 0.69515 | 0.69598 | 0.6968 | 0.69562 | 0.69442 | 0.69273 | 0.68996 | 0.68301 | 0.67402 | 0.63605 | 0.55112 | 0.45388 | 0.4369 | 0.59658 | 0.59684 | 0.59707 | 0.59728 | 0.59747 | 0.59765 | 0.59776 | 0.59764 | 0.59667 | 0.5953 | 0.58016 | 0.53974 | 0.4975 | 0.4863 | 0.56652 | 0.56638 | 0.5661 | 0.56582 | 0.56546 | 0.56506 | 0.56462 | 0.56401 | 0.56245 | 0.56095 | 0.55547 | 0.54178 | 0.50148 | 0.48157
BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | YES | 7.7977 | 7.7898 | 7.7688 | 7.7385 | 7.6269 | 7.5035 | 7.3761 | 7.2168 | 6.9844 | 6.8185 | 6.3669 | 6.1985 | 6.1937 | 6.0167 | 8.5062 | 8.4975 | 8.4836 | 8.461 | 8.4088 | 8.3474 | 8.2814 | 8.1929 | 8.0783 | 7.9706 | 7.6776 | 7.5824 | 7.5627 | 7.4605 | 7.8368 | 7.8264 | 7.8066 | 7.7734 | 7.687 | 7.586 | 7.4776 | 7.3359 | 7.1441 | 6.981 | 6.5339 | 6.4009 | 6.4105 | 6.2835
| BALLINDALLOCH | CT |  |  | 7.8439 | 7.8497 | 7.8465 | 7.8344 | 7.7207 | 7.613 | 7.441 | 7.2537 | 7.0667 | 6.9585 | 6.5706 | 6.3012 | 6.228 | 6.1787 | 8.5198 | 8.514 | 8.5048 | 8.4816 | 8.4198 | 8.3641 | 8.2871 | 8.203 | 8.1131 | 8.0464 | 7.7764 | 7.6247 | 7.586 | 7.5506 | 7.8677 | 7.8639 | 7.8553 | 7.8279 | 7.7285 | 7.6388 | 7.5073 | 7.3625 | 7.2126 | 7.1126 | 6.7062 | 6.4808 | 6.4284 | 6.3935
| BALLINDALLOCH | LW |  |  | 7.7977 | 7.7898 | 7.7688 | 7.7385 | 7.6269 | 7.5035 | 7.3761 | 7.2168 | 6.9844 | 6.8185 | 6.3669 | 6.1985 | 6.2578 | 6.2425 | 8.5062 | 8.4975 | 8.4836 | 8.461 | 8.4088 | 8.3474 | 8.2814 | 8.1929 | 8.0783 | 7.9706 | 7.6776 | 7.5824 | 7.6019 | 7.5951 | 7.8368 | 7.8264 | 7.8066 | 7.7734 | 7.687 | 7.586 | 7.4776 | 7.3359 | 7.1441 | 6.981 | 6.5339 | 6.4009 | 6.4406 | 6.4294
| BALLINDALLOCH | ST |  |  | 7.8283 | 7.8175 | 7.8071 | 7.802 | 7.7889 | 7.7737 | 7.7457 | 7.7229 | 7.6792 | 7.6168 | 7.3744 | 6.8242 | 6.5667 | 6.4476 | 8.5197 | 8.5131 | 8.5065 | 8.4983 | 8.487 | 8.4747 | 8.4515 | 8.4329 | 8.4064 | 8.3693 | 8.2112 | 7.8244 | 7.6909 | 7.6243 | 7.8608 | 7.851 | 7.8414 | 7.8314 | 7.8166 | 7.8003 | 7.7691 | 7.7438 | 7.7052 | 7.6497 | 7.4185 | 6.8616 | 6.6676 | 6.5807
| BALLINDALLOCH | SP |  |  | 7.8364 | 7.8291 | 7.823 | 7.8156 | 7.7765 | 7.7411 | 7.699 | 7.651 | 7.6021 | 7.5234 | 7.2681 | 6.6239 | 6.1937 | 6.0167 | 8.5241 | 8.5195 | 8.5148 | 8.509 | 8.4894 | 8.4723 | 8.4507 | 8.4242 | 8.3955 | 8.3507 | 8.2193 | 7.8274 | 7.5627 | 7.4605 | 7.8681 | 7.8614 | 7.8551 | 7.8473 | 7.8156 | 7.7879 | 7.7544 | 7.7125 | 7.668 | 7.5978 | 7.3886 | 6.7897 | 6.4105 | 6.2835
CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | 1.6811 | 1.6785 | 1.6697 | 1.6508 | 1.6222 | 1.5924 | 1.5303 | 1.4555 | 1.3884 | 1.3584 | 1.2418 | 1.2065 | 1.2416 | 1.2021 | 1.6886 | 1.6875 | 1.6857 | 1.6824 | 1.6781 | 1.672 | 1.6592 | 1.6459 | 1.6342 | 1.6304 | 1.6164 | 1.608 | 1.6077 | 1.6076 | 1.6808 | 1.6799 | 1.6784 | 1.6756 | 1.6616 | 1.6392 | 1.5952 | 1.5311 | 1.4725 | 1.4435 | 1.3423 | 1.2916 | 1.32 | 1.2972
| BALLURE | CT |  |  | 1.6811 | 1.6785 | 1.6697 | 1.6508 | 1.6222 | 1.596 | 1.5303 | 1.4555 | 1.3884 | 1.3584 | 1.2627 | 1.2133 | 1.2624 | 1.2769 | 1.6886 | 1.6875 | 1.6857 | 1.6824 | 1.6781 | 1.672 | 1.6592 | 1.6459 | 1.6342 | 1.6304 | 1.6186 | 1.6112 | 1.6105 | 1.61 | 1.6808 | 1.6799 | 1.6784 | 1.6756 | 1.6616 | 1.6449 | 1.5952 | 1.5311 | 1.4725 | 1.4462 | 1.3704 | 1.3162 | 1.3476 | 1.3555
| BALLURE | LW |  |  | 1.6811 | 1.6818 | 1.6757 | 1.665 | 1.6372 | 1.5924 | 1.5419 | 1.4896 | 1.3992 | 1.3636 | 1.2418 | 1.2065 | 1.2416 | 1.2169 | 1.6892 | 1.6883 | 1.6872 | 1.6849 | 1.6829 | 1.6742 | 1.6655 | 1.6569 | 1.6408 | 1.6366 | 1.6164 | 1.608 | 1.6077 | 1.6076 | 1.6822 | 1.682 | 1.6816 | 1.6803 | 1.6694 | 1.6392 | 1.5952 | 1.5511 | 1.4757 | 1.4435 | 1.3423 | 1.2916 | 1.32 | 1.3016
| BALLURE | ST |  |  | 1.6839 | 1.683 | 1.6822 | 1.6793 | 1.6819 | 1.6834 | 1.6831 | 1.6842 | 1.6796 | 1.6691 | 1.6309 | 1.5113 | 1.4788 | 1.4717 | 1.6898 | 1.6892 | 1.6885 | 1.6872 | 1.6859 | 1.6844 | 1.6821 | 1.6805 | 1.6781 | 1.6748 | 1.6612 | 1.6153 | 1.6099 | 1.6094 | 1.6818 | 1.6816 | 1.6814 | 1.6806 | 1.6804 | 1.68 | 1.6791 | 1.6788 | 1.6779 | 1.6763 | 1.6562 | 1.5596 | 1.5131 | 1.5019
| BALLURE | SP |  |  | 1.6874 | 1.6885 | 1.6902 | 1.6918 | 1.6893 | 1.6871 | 1.6835 | 1.6781 | 1.6718 | 1.6584 | 1.5753 | 1.3807 | 1.2525 | 1.2021 | 1.6897 | 1.6893 | 1.6888 | 1.688 | 1.6872 | 1.6865 | 1.6849 | 1.6831 | 1.6811 | 1.6782 | 1.6694 | 1.6393 | 1.6115 | 1.609 | 1.6821 | 1.6821 | 1.6821 | 1.682 | 1.6821 | 1.6822 | 1.6819 | 1.6814 | 1.6806 | 1.6792 | 1.6232 | 1.4559 | 1.3437 | 1.2972
DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | -0.357 | -0.62248 | -0.92623 | -1.2768 | -1.6481 | -2.2116 | -2.8915 | -3.5838 | -4.4398 | -5.3365 | -6.995 | -8.3366 | -8.8814 | -9.0793 | 0.84818 | 0.63731 | 0.39122 | 0.12284 | -0.14164 | -0.58007 | -1.1141 | -1.6605 | -2.3203 | -3.0601 | -4.3554 | -5.2243 | -5.4949 | -5.6893 | 0.3445 | 0.11691 | -0.14683 | -0.44871 | -0.79325 | -1.3188 | -1.9556 | -2.6025 | -3.3998 | -4.244 | -5.7845 | -6.9958 | -7.4728 | -7.6461
| BALMEDIE | CT |  |  | -0.3385 | -0.5975 | -0.90074 | -1.2381 | -1.5775 | -2.084 | -2.6984 | -3.3677 | -4.122 | -5.02 | -6.995 | -8.3366 | -8.8814 | -9.0793 | 0.84818 | 0.63731 | 0.39122 | 0.12284 | -0.13276 | -0.53627 | -1.0053 | -1.518 | -2.1089 | -2.8985 | -4.3554 | -5.2243 | -5.4949 | -5.6893 | 0.35873 | 0.13632 | -0.12847 | -0.41907 | -0.73373 | -1.2048 | -1.7724 | -2.3915 | -3.0902 | -3.9323 | -5.7845 | -6.9958 | -7.4728 | -7.6461
| BALMEDIE | LW |  |  | -0.357 | -0.62248 | -0.92623 | -1.2768 | -1.6481 | -2.2116 | -2.8915 | -3.5838 | -4.4398 | -5.3365 | -6.9771 | -8.044 | -8.4223 | -8.5568 | 0.85009 | 0.64022 | 0.40108 | 0.13094 | -0.14164 | -0.58007 | -1.1141 | -1.6605 | -2.3203 | -3.0601 | -4.3392 | -5.0811 | -5.2358 | -5.2949 | 0.3445 | 0.11691 | -0.14683 | -0.44871 | -0.79325 | -1.3188 | -1.9556 | -2.6025 | -3.3998 | -4.244 | -5.7747 | -6.7444 | -7.0748 | -7.1925
| BALMEDIE | ST |  |  | -0.29847 | -0.53944 | -0.80334 | -1.0926 | -1.2863 | -1.6392 | -2.0442 | -2.4919 | -3.0353 | -3.7041 | -5.0256 | -6.3898 | -6.81 | -7.1082 | 0.88316 | 0.6925 | 0.47989 | 0.24966 | 0.073439 | -0.28635 | -0.72805 | -1.2231 | -1.8184 | -2.5299 | -3.8032 | -4.6381 | -4.8261 | -4.9883 | 0.39918 | 0.19617 | -0.029064 | -0.2722 | -0.45248 | -0.78252 | -1.1602 | -1.5794 | -2.0889 | -2.7185 | -3.9688 | -5.2671 | -5.6423 | -5.9071
| BALMEDIE | SP |  |  | -0.29481 | -0.53047 | -0.78992 | -1.0753 | -1.2914 | -1.6601 | -2.0907 | -2.568 | -3.1248 | -3.7804 | -5.0115 | -6.3663 | -6.7832 | -6.9216 | 0.88351 | 0.69608 | 0.48543 | 0.25913 | 0.073186 | -0.27649 | -0.71653 | -1.2097 | -1.8014 | -2.5084 | -3.7594 | -4.5584 | -4.7879 | -5.0436 | 0.40218 | 0.2042 | -0.016947 | -0.25589 | -0.4562 | -0.80005 | -1.201 | -1.6471 | -2.1685 | -2.7835 | -3.9377 | -5.2277 | -5.6208 | -5.7457
CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | NO | 7.8853 | 7.8113 | 7.7319 | 7.6785 | 7.3907 | 7.0472 | 6.6901 | 6.2457 | 6.0365 | 5.8475 | 5.1718 | 3.9319 | 3.041 | 2.3246 | 7.5261 | 7.5077 | 7.4679 | 7.433 | 7.3773 | 7.309 | 7.2626 | 7.2061 | 7.1406 | 7.0805 | 6.75 | 6.2762 | 5.7489 | 5.0829 | 7.8746 | 7.8252 | 7.7683 | 7.7346 | 7.546 | 7.3214 | 7.0844 | 6.7631 | 6.5979 | 6.4374 | 5.8653 | 4.9256 | 4.2731 | 3.7452
| BALNAGASK | CT |  |  | 7.8968 | 7.8495 | 7.776 | 7.724 | 7.4332 | 7.0687 | 6.8852 | 6.6808 | 6.4485 | 6.1913 | 5.3583 | 3.9319 | 3.041 | 2.3246 | 7.5261 | 7.5077 | 7.4679 | 7.433 | 7.3773 | 7.309 | 7.2626 | 7.2061 | 7.1406 | 7.0852 | 6.8108 | 6.2872 | 5.7489 | 5.0829 | 7.8824 | 7.8511 | 7.7981 | 7.7623 | 7.5689 | 7.3274 | 7.204 | 7.0494 | 6.8743 | 6.6747 | 6.0265 | 4.9258 | 4.2731 | 3.7452
| BALNAGASK | LW |  |  | 7.8853 | 7.8113 | 7.7319 | 7.6785 | 7.3907 | 7.0472 | 6.6901 | 6.2457 | 6.0365 | 5.8475 | 5.1718 | 4.0203 | 3.1904 | 2.4852 | 7.5306 | 7.5151 | 7.4796 | 7.4493 | 7.3973 | 7.3322 | 7.2888 | 7.2317 | 7.1699 | 7.0805 | 6.75 | 6.2762 | 5.9562 | 5.6528 | 7.8746 | 7.8252 | 7.7683 | 7.7346 | 7.546 | 7.3214 | 7.0844 | 6.7631 | 6.5979 | 6.4374 | 5.8653 | 4.9256 | 4.3252 | 3.818
| BALNAGASK | ST |  |  | 7.9771 | 7.952 | 7.8826 | 7.8495 | 7.8188 | 7.7853 | 7.7616 | 7.7427 | 7.7227 | 7.6686 | 7.4271 | 6.52 | 5.4965 | 4.5644 | 7.5391 | 7.5291 | 7.4998 | 7.4874 | 7.4747 | 7.4594 | 7.4428 | 7.4227 | 7.4008 | 7.3707 | 7.2399 | 6.8446 | 6.415 | 5.9461 | 7.9319 | 7.9123 | 7.8583 | 7.8306 | 7.8056 | 7.7778 | 7.756 | 7.736 | 7.7142 | 7.6653 | 7.4602 | 6.7536 | 6.0168 | 5.3759
| BALNAGASK | SP |  |  | 7.9953 | 7.9809 | 7.9207 | 7.9043 | 7.871 | 7.8324 | 7.8012 | 7.768 | 7.7321 | 7.6813 | 7.476 | 6.7712 | 5.9244 | 5.238 | 7.5404 | 7.5319 | 7.5042 | 7.4948 | 7.4844 | 7.4724 | 7.4597 | 7.4448 | 7.4281 | 7.4062 | 7.3124 | 6.9847 | 6.5047 | 5.1738 | 7.9437 | 7.9313 | 7.8834 | 7.8685 | 7.8427 | 7.8126 | 7.7867 | 7.7583 | 7.725 | 7.6797 | 7.502 | 6.9293 | 6.2605 | 5.7564
KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | YES | 2.9681 | 2.4374 | 1.9626 | 1.4711 | 0.71159 | -0.17376 | -1.1027 | -1.9969 | -3.124 | -4.0869 | -6.2501 | -8.3138 | -9.3785 | -9.776 | 5.9823 | 5.557 | 5.1893 | 4.8043 | 4.337 | 3.7883 | 3.2283 | 2.6919 | 2.0449 | 1.4513 | 0.13644 | -1.0713 | -1.692 | -2.2035 | 3.876 | 3.3988 | 2.9764 | 2.5259 | 1.8326 | 1.0238 | 0.18034 | -0.6348 | -1.6678 | -2.5425 | -4.5253 | -6.4555 | -7.3917 | -7.741
| BANCHORY | CT |  |  | 3.0448 | 2.5638 | 2.1183 | 1.6415 | 0.92686 | 0.17141 | -0.68011 | -1.554 | -2.4352 | -3.3659 | -6.0285 | -8.3138 | -9.3785 | -9.776 | 5.9935 | 5.5812 | 5.2164 | 4.8297 | 4.3758 | 3.8912 | 3.3905 | 2.8874 | 2.3784 | 1.7918 | 0.19731 | -1.0713 | -1.692 | -2.2035 | 3.9383 | 3.5043 | 3.1132 | 2.6881 | 2.0318 | 1.3419 | 0.55987 | -0.23392 | -1.0312 | -1.9001 | -4.3317 | -6.4555 | -7.3917 | -7.741
| BANCHORY | LW |  |  | 2.9681 | 2.4374 | 1.9626 | 1.4711 | 0.71159 | -0.17376 | -1.1027 | -1.9969 | -3.124 | -4.0869 | -6.2501 | -7.8692 | -8.4486 | -8.7207 | 5.9823 | 5.557 | 5.1893 | 4.8043 | 4.337 | 3.7883 | 3.2283 | 2.6919 | 2.0449 | 1.4513 | 0.13644 | -0.73965 | -0.97815 | -1.0893 | 3.876 | 3.3988 | 2.9764 | 2.5259 | 1.8326 | 1.0238 | 0.18034 | -0.6348 | -1.6678 | -2.5425 | -4.5253 | -6.0339 | -6.5794 | -6.8278
| BANCHORY | ST |  |  | 3.1397 | 2.7172 | 2.3493 | 2.0092 | 1.7592 | 1.461 | 1.1919 | 0.91163 | 0.61242 | 0.20445 | -1.0641 | -3.9191 | -5.0093 | -5.6148 | 6.0674 | 5.6991 | 5.3911 | 5.0852 | 4.8618 | 4.6072 | 4.3795 | 4.1423 | 3.8942 | 3.5923 | 2.7473 | 0.83436 | 0.068951 | -0.54756 | 4.0343 | 3.659 | 3.3385 | 3.0326 | 2.8052 | 2.5375 | 2.2936 | 2.0362 | 1.7612 | 1.3865 | 0.23714 | -2.3928 | -3.3856 | -3.9253
| BANCHORY | SP |  |  | 3.1561 | 2.7575 | 2.4108 | 2.092 | 1.7852 | 1.4444 | 1.1167 | 0.77606 | 0.42863 | 0.03978 | -1.0499 | -3.8345 | -5.3835 | -5.8671 | 6.0697 | 5.7132 | 5.4142 | 5.1211 | 4.8767 | 4.6085 | 4.3589 | 4.0989 | 3.8326 | 3.5458 | 2.8256 | 1.0531 | -0.30264 | -1.3142 | 4.0471 | 3.6937 | 3.3925 | 3.1072 | 2.8302 | 2.5266 | 2.2311 | 1.9203 | 1.6021 | 1.2449 | 0.23758 | -2.2795 | -3.7068 | -4.1478
TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | 3.4912 | 3.4717 | 3.4252 | 3.3672 | 3.2515 | 3.1257 | 3.0002 | 2.8701 | 2.6871 | 2.5742 | 2.2227 | 2.1656 | 2.2154 | 2.14 | 4.4171 | 4.4033 | 4.3771 | 4.3433 | 4.2843 | 4.2169 | 4.1485 | 4.0717 | 3.966 | 3.8886 | 3.6445 | 3.6033 | 3.6208 | 3.5548 | 4.125 | 4.1071 | 4.0658 | 4.0132 | 3.909 | 3.794 | 3.6784 | 3.5578 | 3.3881 | 3.2797 | 2.9411 | 2.8874 | 2.931 | 2.867
| BARCALDINE | CT |  |  | 3.5267 | 3.5124 | 3.4704 | 3.4025 | 3.2829 | 3.1779 | 3.0557 | 2.9248 | 2.7964 | 2.7126 | 2.3401 | 2.2242 | 2.2467 | 2.244 | 4.4314 | 4.4192 | 4.3927 | 4.3505 | 4.2872 | 4.2292 | 4.1681 | 4.1006 | 4.0318 | 3.9752 | 3.7085 | 3.6301 | 3.626 | 3.6079 | 4.1563 | 4.1424 | 4.1044 | 4.0417 | 3.9331 | 3.8369 | 3.7268 | 3.6083 | 3.4912 | 3.4112 | 3.0497 | 2.9419 | 2.9613 | 2.9588
| BARCALDINE | LW |  |  | 3.4912 | 3.4717 | 3.4252 | 3.3672 | 3.2515 | 3.1257 | 3.0002 | 2.8701 | 2.6871 | 2.5742 | 2.2227 | 2.1656 | 2.2154 | 2.1863 | 4.4171 | 4.4033 | 4.3771 | 4.3433 | 4.2843 | 4.2169 | 4.1485 | 4.0717 | 3.966 | 3.8886 | 3.6445 | 3.6033 | 3.6222 | 3.61 | 4.125 | 4.1071 | 4.0658 | 4.0132 | 3.909 | 3.794 | 3.6784 | 3.5578 | 3.3881 | 3.2797 | 2.9411 | 2.8874 | 2.931 | 2.9053
| BARCALDINE | ST |  |  | 3.5233 | 3.509 | 3.4867 | 3.4606 | 3.446 | 3.4309 | 3.4117 | 3.3873 | 3.3597 | 3.3065 | 3.121 | 2.6591 | 2.5642 | 2.5103 | 4.4332 | 4.424 | 4.4103 | 4.393 | 4.3819 | 4.3702 | 4.3556 | 4.3366 | 4.3182 | 4.2834 | 4.1569 | 3.8209 | 3.7575 | 3.7135 | 4.1542 | 4.1413 | 4.1221 | 4.0986 | 4.0849 | 4.0703 | 4.0516 | 4.0279 | 4.0019 | 3.9516 | 3.7744 | 3.3267 | 3.2406 | 3.1922
| BARCALDINE | SP |  |  | 3.5336 | 3.524 | 3.5061 | 3.4887 | 3.4531 | 3.4247 | 3.3891 | 3.3514 | 3.3014 | 3.2409 | 3.0497 | 2.5209 | 2.2284 | 2.14 | 4.4392 | 4.4328 | 4.4209 | 4.4088 | 4.3892 | 4.3737 | 4.3533 | 4.3321 | 4.3016 | 4.2685 | 4.1594 | 3.8205 | 3.6208 | 3.5548 | 4.1639 | 4.1555 | 4.1401 | 4.1248 | 4.0928 | 4.067 | 4.0342 | 3.9998 | 3.9533 | 3.898 | 3.7218 | 3.2225 | 2.9459 | 2.867
STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | YES | 0.3284 | 0.31059 | 0.21091 | 0.092934 | -0.22647 | -0.5276 | -0.81611 | -1.1383 | -1.5042 | -1.6836 | -2.3584 | -2.5277 | -2.6621 | -2.7766 | 1.5635 | 1.4854 | 1.4421 | 1.4001 | 1.3708 | 1.3398 | 1.2512 | 1.0928 | 0.91859 | 0.81499 | 0.35343 | 0.21105 | 0.16354 | 0.075263 | 1.0993 | 1.0671 | 0.98961 | 0.89572 | 0.66084 | 0.43539 | 0.21413 | -0.063083 | -0.38379 | -0.56863 | -1.3185 | -1.5146 | -1.6011 | -1.7012
| BARVAS | CT |  |  | 0.53721 | 0.53269 | 0.47215 | 0.33439 | 0.0064952 | -0.28367 | -0.58325 | -0.91365 | -1.2231 | -1.3719 | -1.8816 | -2.3411 | -2.3015 | -2.3176 | 1.5635 | 1.4854 | 1.4421 | 1.4001 | 1.3708 | 1.3398 | 1.3072 | 1.1635 | 1.0272 | 0.94259 | 0.61564 | 0.26812 | 0.25888 | 0.22976 | 1.1644 | 1.0915 | 1.045 | 0.99471 | 0.79107 | 0.56489 | 0.33434 | 0.080944 | -0.15859 | -0.30289 | -0.85155 | -1.3627 | -1.3475 | -1.3652
| BARVAS | LW |  |  | 0.3284 | 0.31059 | 0.21091 | 0.092934 | -0.22647 | -0.5276 | -0.81611 | -1.1383 | -1.5042 | -1.6836 | -2.3584 | -2.5277 | -2.358 | -2.4292 | 1.5653 | 1.4881 | 1.4451 | 1.4092 | 1.3841 | 1.3553 | 1.2512 | 1.0928 | 0.91859 | 0.81499 | 0.35343 | 0.21105 | 0.26541 | 0.24319 | 1.0993 | 1.0671 | 0.98961 | 0.89572 | 0.66084 | 0.43539 | 0.21413 | -0.063083 | -0.38379 | -0.56863 | -1.3185 | -1.5146 | -1.3848 | -1.4371
| BARVAS | ST |  |  | 0.4707 | 0.38019 | 0.3285 | 0.28869 | 0.26197 | 0.2269 | 0.18795 | 0.15627 | 0.093911 | -0.0056483 | -0.32441 | -1.1367 | -1.4381 | -1.5815 | 1.57 | 1.4949 | 1.4558 | 1.4229 | 1.4046 | 1.39 | 1.3745 | 1.3518 | 1.333 | 1.3138 | 1.2575 | 0.71203 | 0.53157 | 0.46097 | 1.1659 | 1.087 | 1.0443 | 1.0097 | 0.98684 | 0.96623 | 0.93743 | 0.9002 | 0.83872 | 0.74643 | 0.43118 | -0.47468 | -0.74649 | -0.84899
| BARVAS | SP |  |  | 0.46833 | 0.37245 | 0.32332 | 0.28017 | 0.12658 | -0.01206 | -0.16674 | -0.33062 | -0.50834 | -0.75525 | -1.2294 | -2.1421 | -2.6621 | -2.7766 | 1.57 | 1.4955 | 1.4571 | 1.4261 | 1.409 | 1.3956 | 1.3815 | 1.3613 | 1.3421 | 1.2664 | 1.0459 | 0.58385 | 0.16354 | 0.075263 | 1.1651 | 1.0862 | 1.0442 | 1.0091 | 0.92799 | 0.82568 | 0.71176 | 0.58968 | 0.44584 | 0.25735 | -0.13867 | -0.99324 | -1.6011 | -1.7012
STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | YES | 5.5464 | 5.3487 | 4.8141 | 4.1617 | 2.8813 | 1.5864 | 0.32183 | -1.0548 | -2.3949 | -3.5307 | -7.9391 | -10.8323 | -11.0782 | -11.2917 | 7.1979 | 7.0651 | 6.688 | 6.2138 | 5.4276 | 4.5888 | 3.7437 | 2.7982 | 1.8646 | 0.93839 | -2.7558 | -5.0316 | -5.2024 | -5.4707 | 4.6847 | 4.5271 | 4.1784 | 3.6655 | 2.4483 | 1.1894 | -0.061047 | -1.4305 | -2.7577 | -3.928 | -8.4117 | -11.209 | -11.3927 | -11.5792
| BATTERY POINT | CT |  |  | 5.8824 | 5.7402 | 5.2852 | 4.6016 | 3.2665 | 1.9637 | 0.91452 | -0.30887 | -1.5471 | -2.6347 | -6.8049 | -10.5575 | -11.0782 | -11.2917 | 7.3064 | 7.1897 | 6.8339 | 6.3252 | 5.5093 | 4.6568 | 3.9032 | 3.0529 | 2.191 | 1.312 | -2.1753 | -4.8669 | -5.2024 | -5.4707 | 4.6847 | 4.5271 | 4.1784 | 3.7212 | 2.7681 | 1.4998 | 0.44062 | -0.77987 | -2.004 | -3.1211 | -7.3548 | -10.9291 | -11.3927 | -11.5792
| BATTERY POINT | LW |  |  | 5.5464 | 5.3487 | 4.8141 | 4.1617 | 2.8813 | 1.5864 | 0.32183 | -1.0548 | -2.3949 | -3.5307 | -7.9391 | -10.8323 | -10.9219 | -11.2349 | 7.1979 | 7.0651 | 6.688 | 6.2138 | 5.4276 | 4.5888 | 3.7437 | 2.7982 | 1.8646 | 0.93839 | -2.7558 | -5.0316 | -5.0774 | -5.2046 | 4.7112 | 4.5625 | 4.2197 | 3.6655 | 2.4483 | 1.1894 | -0.061047 | -1.4305 | -2.7577 | -3.928 | -8.4117 | -11.209 | -11.2865 | -11.5602
| BATTERY POINT | ST |  |  | 5.9233 | 5.788 | 5.5091 | 5.1597 | 4.7922 | 4.3622 | 3.9251 | 3.4582 | 2.9199 | 2.162 | -1.005 | -5.9991 | -7.9698 | -8.2939 | 7.3603 | 7.2692 | 7.0047 | 6.6743 | 6.2824 | 5.8253 | 5.3465 | 4.8318 | 4.2847 | 3.5828 | 0.63242 | -3.2788 | -4.6377 | -4.7545 | 4.7875 | 4.6952 | 4.41 | 4.0709 | 3.672 | 3.2198 | 2.7448 | 2.2295 | 1.6741 | 0.98744 | -2.0703 | -6.7928 | -8.688 | -9.0823
| BATTERY POINT | SP |  |  | 5.9474 | 5.8273 | 5.5757 | 5.278 | 4.7142 | 4.1183 | 3.507 | 2.8496 | 2.1078 | 1.1445 | -2.1256 | -6.2769 | -8.4978 | -9.0586 | 7.3667 | 7.2845 | 7.0337 | 6.7319 | 6.2744 | 5.7609 | 5.2265 | 4.6502 | 4.0271 | 3.2662 | 0.36362 | -2.5968 | -4.2674 | -5.0012 | 4.791 | 4.7072 | 4.4353 | 4.1057 | 3.7275 | 3.2893 | 2.8045 | 2.0969 | 1.3213 | 0.33565 | -3.0209 | -6.9618 | -9.0906 | -9.6067
DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | NO | 2.1715 | 2.1624 | 2.1484 | 2.1295 | 2.0839 | 2.0324 | 1.9821 | 1.9196 | 1.836 | 1.7835 | 1.5858 | 1.5288 | 1.5528 | 1.5013 | 2.136 | 2.1302 | 2.123 | 2.112 | 2.0895 | 2.0667 | 2.0418 | 2.0068 | 1.9651 | 1.9329 | 1.8013 | 1.7668 | 1.7733 | 1.7442 | 2.1041 | 2.0952 | 2.0815 | 2.0618 | 2.0149 | 1.9618 | 1.9098 | 1.8447 | 1.7593 | 1.7078 | 1.5147 | 1.4581 | 1.4818 | 1.4306
| BETTYHILL | CT |  |  | 2.1835 | 2.1806 | 2.1706 | 2.1476 | 2.1027 | 2.0593 | 1.9995 | 1.933 | 1.8715 | 1.8329 | 1.656 | 1.5633 | 1.5607 | 1.5545 | 2.1384 | 2.135 | 2.1281 | 2.112 | 2.0895 | 2.0674 | 2.0418 | 2.0116 | 1.9833 | 1.958 | 1.8353 | 1.779 | 1.7752 | 1.7684 | 2.1127 | 2.109 | 2.0989 | 2.0757 | 2.0345 | 1.9894 | 1.9282 | 1.8598 | 1.7964 | 1.7565 | 1.5841 | 1.4927 | 1.4896 | 1.4833
| BETTYHILL | LW |  |  | 2.1715 | 2.1624 | 2.1484 | 2.1295 | 2.0839 | 2.0324 | 1.9821 | 1.9196 | 1.836 | 1.7835 | 1.5858 | 1.5288 | 1.5528 | 1.5421 | 2.136 | 2.1302 | 2.123 | 2.1125 | 2.0918 | 2.0667 | 2.0424 | 2.0068 | 1.9651 | 1.9329 | 1.8013 | 1.7668 | 1.7749 | 1.7711 | 2.1041 | 2.0952 | 2.0815 | 2.0618 | 2.0149 | 1.9618 | 1.9098 | 1.8447 | 1.7593 | 1.7078 | 1.5147 | 1.4581 | 1.4818 | 1.4713
| BETTYHILL | ST |  |  | 2.1837 | 2.1803 | 2.1754 | 2.1695 | 2.1638 | 2.1574 | 2.1494 | 2.1397 | 2.1274 | 2.1023 | 2.0216 | 1.7747 | 1.709 | 1.6812 | 2.1415 | 2.1394 | 2.1358 | 2.1315 | 2.1267 | 2.1216 | 2.1151 | 2.1072 | 2.1001 | 2.0837 | 2.0289 | 1.8541 | 1.8231 | 1.8092 | 2.1147 | 2.1115 | 2.1065 | 2.1005 | 2.0943 | 2.0875 | 2.079 | 2.0686 | 2.0569 | 2.0302 | 1.9436 | 1.701 | 1.6355 | 1.6077
| BETTYHILL | SP |  |  | 2.1883 | 2.187 | 2.1853 | 2.1824 | 2.172 | 2.1628 | 2.151 | 2.1363 | 2.1184 | 2.0925 | 2.003 | 1.7727 | 1.5596 | 1.5013 | 2.1439 | 2.1429 | 2.141 | 2.138 | 2.1328 | 2.1281 | 2.1216 | 2.1129 | 2.1019 | 2.0866 | 2.0406 | 1.9095 | 1.7733 | 1.7442 | 2.119 | 2.1176 | 2.1155 | 2.1122 | 2.1029 | 2.0946 | 2.0828 | 2.0671 | 2.0481 | 2.0208 | 1.9276 | 1.6972 | 1.4885 | 1.4306
ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | 8.3152 | 8.2967 | 19.5473 | 19.5098 | 19.427 | 19.3252 | 19.1997 | 19.0342 | 18.8052 | 18.5966 | 18.0915 | 17.4288 | 17.0878 | 16.9666 | 9.5712 | 9.5571 | 19.6179 | 19.5932 | 19.5466 | 19.4942 | 19.4376 | 19.3723 | 19.2887 | 19.2021 | 18.955 | 18.7104 | 18.6611 | 18.5845 | 8.2771 | 8.2658 | 18.3315 | 18.3115 | 18.2671 | 18.2008 | 18.1295 | 18.0467 | 17.9392 | 17.8301 | 17.5221 | 17.1714 | 17.0108 | 16.9471
| BILBOHALL | CT |  |  | 8.3344 | 8.3216 | 19.5782 | 19.5443 | 19.4637 | 19.3781 | 19.2199 | 19.0342 | 18.8471 | 18.6798 | 18.1245 | 17.4288 | 17.0878 | 16.9666 | 9.5767 | 9.5647 | 19.6273 | 19.6034 | 19.557 | 19.5075 | 19.4472 | 19.3812 | 19.3118 | 19.2394 | 19.0285 | 18.7727 | 18.6929 | 18.5845 | 8.2771 | 8.2658 | 18.3315 | 18.3115 | 18.2792 | 18.2198 | 18.1424 | 18.0574 | 17.9684 | 17.8776 | 17.608 | 17.1911 | 17.0108 | 16.9471
| BILBOHALL | LW |  |  | 8.3152 | 8.2967 | 19.5473 | 19.5098 | 19.427 | 19.3252 | 19.1997 | 19.0388 | 18.8052 | 18.5966 | 18.0915 | 17.6091 | 17.3813 | 17.2956 | 9.5712 | 9.5571 | 19.6179 | 19.5932 | 19.5466 | 19.4942 | 19.4376 | 19.3723 | 19.2887 | 19.2021 | 18.955 | 18.7104 | 18.6611 | 18.6426 | 8.2789 | 8.2681 | 18.3354 | 18.3183 | 18.2671 | 18.2008 | 18.1295 | 18.0467 | 17.9392 | 17.8301 | 17.5221 | 17.1714 | 17.0579 | 17.0173
| BILBOHALL | ST |  |  | 8.3468 | 8.3372 | 19.6075 | 19.596 | 19.5765 | 19.554 | 19.5287 | 19.5015 | 19.465 | 19.4109 | 19.2282 | 18.6386 | 18.3358 | 18.1779 | 9.588 | 9.5814 | 19.6545 | 19.6456 | 19.63 | 19.6124 | 19.5927 | 19.5712 | 19.5444 | 19.5059 | 19.3769 | 19.0662 | 18.9216 | 18.8788 | 8.2873 | 8.2823 | 18.3574 | 18.3495 | 18.3337 | 18.3163 | 18.2975 | 18.2768 | 18.2529 | 18.2204 | 18.0683 | 17.6867 | 17.5075 | 17.4535
| BILBOHALL | SP |  |  | 8.3489 | 8.3411 | 19.6132 | 19.6039 | 19.5763 | 19.5484 | 19.5178 | 19.4849 | 19.4395 | 19.3744 | 19.1668 | 18.6979 | 18.351 | 18.2623 | 9.5894 | 9.5841 | 19.6585 | 19.6517 | 19.6344 | 19.6164 | 19.597 | 19.5761 | 19.5515 | 19.5197 | 19.4271 | 19.1888 | 18.9907 | 18.8456 | 8.2888 | 8.2852 | 18.361 | 18.3558 | 18.3419 | 18.3273 | 18.3114 | 18.2948 | 18.2732 | 18.2369 | 18.1219 | 17.8249 | 17.5819 | 17.5287
RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | 0.018525 | 0.018069 | 0.017479 | 0.016757 | 0.014412 | 0.012353 | 0.0079883 | 0.0035319 | -0.0010612 | -0.0039976 | -0.017136 | -0.027836 | -0.02769 | -0.028061 | 0.03152 | 0.031207 | 0.030854 | 0.030126 | 0.028473 | 0.027286 | 0.02517 | 0.023149 | 0.020933 | 0.018036 | 0.007151 | -0.0023299 | -0.0023599 | -0.0025808 | 0.024559 | 0.024126 | 0.023578 | 0.022905 | 0.020583 | 0.018677 | 0.014728 | 0.010733 | 0.0066392 | 0.0038417 | -0.0088144 | -0.021174 | -0.021063 | -0.021405
| BLACKMOUNT | CT |  |  | 0.019005 | 0.018725 | 0.018085 | 0.017054 | 0.014412 | 0.012353 | 0.0079883 | 0.0035319 | -0.0010612 | -0.0039976 | -0.015808 | -0.022325 | -0.024278 | -0.025521 | 0.031641 | 0.031387 | 0.030899 | 0.030126 | 0.028473 | 0.027286 | 0.02517 | 0.023149 | 0.020933 | 0.018532 | 0.01081 | 0.0028386 | 0.002263 | 0.0018457 | 0.02497 | 0.02469 | 0.02407 | 0.02307 | 0.020583 | 0.018677 | 0.014728 | 0.010733 | 0.0066392 | 0.0038417 | -0.0074606 | -0.015155 | -0.016334 | -0.017128
| BLACKMOUNT | LW |  |  | 0.018525 | 0.018069 | 0.017479 | 0.016757 | 0.015123 | 0.013178 | 0.011213 | 0.008011 | 0.0020858 | -0.0023001 | -0.017136 | -0.027836 | -0.02769 | -0.028061 | 0.03152 | 0.031207 | 0.030854 | 0.030414 | 0.029536 | 0.028454 | 0.026751 | 0.024548 | 0.021404 | 0.018036 | 0.007151 | -0.0023299 | -0.0023599 | -0.0025808 | 0.024559 | 0.024126 | 0.023578 | 0.022905 | 0.021414 | 0.019653 | 0.017853 | 0.014746 | 0.009399 | 0.0052646 | -0.0088144 | -0.021174 | -0.021063 | -0.021405
| BLACKMOUNT | ST |  |  | 0.019156 | 0.018976 | 0.018827 | 0.018416 | 0.018075 | 0.01751 | 0.016971 | 0.015914 | 0.014853 | 0.012675 | 0.0068367 | -0.01194 | -0.021848 | -0.024468 | 0.031817 | 0.031697 | 0.031596 | 0.031263 | 0.031021 | 0.030603 | 0.030208 | 0.029385 | 0.028878 | 0.027538 | 0.023328 | 0.0076474 | 0.0011539 | -0.00026249 | 0.025128 | 0.02496 | 0.024822 | 0.024417 | 0.024093 | 0.023547 | 0.023028 | 0.021992 | 0.02104 | 0.018997 | 0.013568 | -0.0063971 | -0.015666 | -0.018061
| BLACKMOUNT | SP |  |  | 0.019192 | 0.019044 | 0.018877 | 0.018727 | 0.018171 | 0.017546 | 0.016959 | 0.016366 | 0.015242 | 0.014107 | 0.007384 | -0.0060052 | -0.02053 | -0.024954 | 0.031841 | 0.031749 | 0.031635 | 0.031531 | 0.031232 | 0.03087 | 0.030547 | 0.030246 | 0.029536 | 0.028888 | 0.025086 | 0.0161 | 0.0051619 | 0.0027649 | 0.025162 | 0.025026 | 0.02487 | 0.024732 | 0.024223 | 0.023644 | 0.023106 | 0.022571 | 0.021513 | 0.020465 | 0.014244 | 0.0018827 | -0.012019 | -0.01594
BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | 3.9303 | 3.901 | 3.8468 | 3.7693 | 3.5499 | 3.312 | 3.0583 | 2.8039 | 2.5128 | 2.3175 | 1.7729 | 1.6373 | 1.7666 | 1.5717 | 4.6463 | 4.6275 | 4.5987 | 4.556 | 4.4587 | 4.3512 | 4.2302 | 4.1092 | 3.971 | 3.8412 | 3.478 | 3.3808 | 3.3775 | 3.1868 | 3.992 | 3.9641 | 3.9143 | 3.8449 | 3.6482 | 3.4343 | 3.2044 | 2.9741 | 2.7127 | 2.5288 | 2.0161 | 1.8877 | 2.0018 | 1.8386
| BLACKSTAND | CT |  |  | 4.0046 | 4.0036 | 3.9753 | 3.9223 | 3.7162 | 3.5163 | 3.282 | 3.0497 | 2.8134 | 2.6806 | 2.1597 | 1.8301 | 1.7895 | 1.7484 | 4.6708 | 4.6616 | 4.6393 | 4.6 | 4.5059 | 4.4142 | 4.3098 | 4.2076 | 4.0999 | 4.0194 | 3.6479 | 3.4383 | 3.3837 | 3.316 | 4.0565 | 4.0535 | 4.0257 | 3.9766 | 3.7913 | 3.6114 | 3.4015 | 3.1938 | 2.9837 | 2.8601 | 2.3657 | 2.0611 | 2.0246 | 1.9894
| BLACKSTAND | LW |  |  | 3.9303 | 3.901 | 3.8468 | 3.7693 | 3.5499 | 3.312 | 3.0583 | 2.8039 | 2.5128 | 2.3175 | 1.7729 | 1.6373 | 1.7666 | 1.7287 | 4.6463 | 4.6275 | 4.5987 | 4.556 | 4.4587 | 4.3512 | 4.2302 | 4.1092 | 3.971 | 3.8412 | 3.478 | 3.3808 | 3.4234 | 3.4098 | 3.992 | 3.9641 | 3.9143 | 3.8449 | 3.6482 | 3.4343 | 3.2044 | 2.9741 | 2.7127 | 2.5288 | 2.0161 | 1.8877 | 2.0018 | 1.9693
| BLACKSTAND | ST |  |  | 3.9884 | 3.9722 | 3.9557 | 3.9329 | 3.9203 | 3.9013 | 3.8804 | 3.856 | 3.8069 | 3.7273 | 3.4508 | 2.7633 | 2.5409 | 2.4282 | 4.6728 | 4.6635 | 4.6534 | 4.6365 | 4.6259 | 4.6112 | 4.5953 | 4.5774 | 4.5479 | 4.5013 | 4.3181 | 3.7997 | 3.6694 | 3.5771 | 4.0445 | 4.0296 | 4.0143 | 3.9947 | 3.9823 | 3.9639 | 3.9436 | 3.9203 | 3.8766 | 3.8029 | 3.5443 | 2.8878 | 2.6892 | 2.5913
| BLACKSTAND | SP |  |  | 4.0058 | 3.9975 | 3.992 | 3.9741 | 3.9235 | 3.8713 | 3.8145 | 3.7498 | 3.6736 | 3.568 | 3.2153 | 2.3944 | 1.7887 | 1.5717 | 4.68 | 4.6739 | 4.6685 | 4.655 | 4.6317 | 4.6058 | 4.5775 | 4.5443 | 4.503 | 4.4502 | 4.2753 | 3.8046 | 3.3775 | 3.1868 | 4.06 | 4.0521 | 4.0467 | 4.0319 | 3.9865 | 3.9393 | 3.8879 | 3.829 | 3.7612 | 3.6658 | 3.3477 | 2.5937 | 2.0298 | 1.8386
COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | YES | 14.1199 | 13.9456 | 13.7583 | 13.5539 | 13.039 | 12.5002 | 11.9469 | 11.269 | 10.4353 | 9.4876 | 6.5765 | 3.5541 | 2.3186 | 1.904 | 15.3016 | 15.2087 | 15.0867 | 14.9419 | 14.6594 | 14.3516 | 14.0194 | 13.6353 | 13.166 | 12.5227 | 10.4993 | 8.8037 | 8.1556 | 7.7531 | 14.0496 | 13.9053 | 13.7538 | 13.5883 | 13.1378 | 12.6708 | 12.1915 | 11.6055 | 10.8771 | 10.0295 | 7.3533 | 4.6829 | 3.6058 | 3.2324
| BLAIRGOWRIE | CT |  |  | 14.1581 | 14.0176 | 13.8584 | 13.6697 | 13.172 | 12.6423 | 12.0443 | 11.3873 | 10.693 | 9.7746 | 6.6455 | 3.5541 | 2.3186 | 1.904 | 15.3075 | 15.2233 | 15.1035 | 14.9485 | 14.6617 | 14.3516 | 14.0194 | 13.6524 | 13.2611 | 12.6607 | 10.5588 | 8.8037 | 8.1556 | 7.7531 | 14.0836 | 13.9698 | 13.8444 | 13.6953 | 13.2639 | 12.8067 | 12.2843 | 11.7113 | 11.1056 | 10.2899 | 7.4389 | 4.6829 | 3.6058 | 3.2324
| BLAIRGOWRIE | LW |  |  | 14.1199 | 13.9456 | 13.7583 | 13.5539 | 13.039 | 12.5002 | 11.9469 | 11.269 | 10.4353 | 9.4876 | 6.5765 | 4.2924 | 3.3466 | 3.0158 | 15.3016 | 15.2087 | 15.0867 | 14.9419 | 14.6594 | 14.3524 | 14.0353 | 13.6353 | 13.166 | 12.5227 | 10.4993 | 9.1513 | 8.7576 | 8.6192 | 14.0496 | 13.9053 | 13.7538 | 13.5883 | 13.1378 | 12.6708 | 12.1915 | 11.6055 | 10.8771 | 10.0295 | 7.3533 | 5.3117 | 4.4919 | 4.2023
| BLAIRGOWRIE | ST |  |  | 14.2269 | 14.1422 | 14.0055 | 13.8438 | 13.6703 | 13.4685 | 13.2569 | 13.0174 | 12.787 | 12.3006 | 10.6098 | 7.9402 | 6.9959 | 6.4605 | 15.3505 | 15.2981 | 15.2011 | 15.0824 | 14.9515 | 14.8 | 14.6382 | 14.4584 | 14.2752 | 13.8768 | 12.474 | 10.6543 | 10.0137 | 9.5385 | 14.1459 | 14.083 | 13.9763 | 13.8489 | 13.7124 | 13.5548 | 13.3853 | 13.1933 | 13.0116 | 12.5883 | 11.0642 | 8.628 | 7.7746 | 7.3022
| BLAIRGOWRIE | SP |  |  | 14.2598 | 14.1988 | 14.082 | 13.95 | 13.7575 | 13.5366 | 13.3044 | 13.058 | 12.7679 | 12.2599 | 10.6412 | 8.4692 | 7.1898 | 6.9399 | 15.3631 | 15.3216 | 15.2329 | 15.131 | 14.9968 | 14.8428 | 14.677 | 14.5009 | 14.292 | 13.8895 | 12.5462 | 10.9693 | 9.891 | 9.1676 | 14.1767 | 14.1357 | 14.0476 | 13.9463 | 13.7915 | 13.6154 | 13.4264 | 13.2272 | 12.993 | 12.5491 | 11.0927 | 9.15 | 7.9581 | 7.7265
STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | 2.5335 | 2.5315 | 2.5274 | 2.5222 | 2.5077 | 2.4926 | 2.4756 | 2.4572 | 2.4306 | 2.4094 | 2.3543 | 2.3162 | 2.3194 | 2.3092 | 2.4829 | 2.4812 | 2.4794 | 2.4761 | 2.4681 | 2.4616 | 2.4539 | 2.4464 | 2.4346 | 2.4207 | 2.3881 | 2.3709 | 2.3702 | 2.3631 | 2.3611 | 2.3602 | 2.3589 | 2.3568 | 2.3514 | 2.3438 | 2.333 | 2.317 | 2.2942 | 2.276 | 2.2269 | 2.1751 | 2.1767 | 2.1763
| BLAIRLINNANS | CT |  |  | 2.54 | 2.5391 | 2.5354 | 2.5294 | 2.5127 | 2.4978 | 2.4783 | 2.4581 | 2.4373 | 2.4229 | 2.3741 | 2.3424 | 2.3332 | 2.3275 | 2.4843 | 2.4828 | 2.4802 | 2.4761 | 2.4681 | 2.4616 | 2.4539 | 2.4464 | 2.4373 | 2.4289 | 2.3958 | 2.3806 | 2.377 | 2.3745 | 2.3611 | 2.3602 | 2.3589 | 2.3568 | 2.3514 | 2.3438 | 2.3351 | 2.3172 | 2.2992 | 2.2863 | 2.245 | 2.2135 | 2.2064 | 2.2015
| BLAIRLINNANS | LW |  |  | 2.5335 | 2.5315 | 2.5274 | 2.5222 | 2.5077 | 2.4926 | 2.4756 | 2.4572 | 2.4306 | 2.4094 | 2.3543 | 2.3162 | 2.3194 | 2.3186 | 2.4829 | 2.4812 | 2.4794 | 2.477 | 2.4715 | 2.4653 | 2.4572 | 2.4476 | 2.4346 | 2.4207 | 2.3881 | 2.3709 | 2.3728 | 2.3722 | 2.3612 | 2.3603 | 2.3596 | 2.3587 | 2.3572 | 2.3479 | 2.333 | 2.317 | 2.2942 | 2.276 | 2.2269 | 2.1751 | 2.1767 | 2.1763
| BLAIRLINNANS | ST |  |  | 2.5402 | 2.5382 | 2.5359 | 2.5339 | 2.531 | 2.5277 | 2.5231 | 2.5186 | 2.5121 | 2.5023 | 2.4668 | 2.3842 | 2.337 | 2.3298 | 2.4851 | 2.4841 | 2.4827 | 2.4813 | 2.4795 | 2.4778 | 2.4746 | 2.4717 | 2.4682 | 2.463 | 2.4417 | 2.3946 | 2.3797 | 2.375 | 2.3617 | 2.3613 | 2.3607 | 2.3599 | 2.3591 | 2.3584 | 2.3569 | 2.3554 | 2.354 | 2.3462 | 2.3124 | 2.2246 | 2.1824 | 2.1787
| BLAIRLINNANS | SP |  |  | 2.5421 | 2.5404 | 2.5385 | 2.5361 | 2.5302 | 2.5241 | 2.5176 | 2.5103 | 2.5026 | 2.4899 | 2.4571 | 2.3686 | 2.3246 | 2.3092 | 2.4873 | 2.4865 | 2.4856 | 2.484 | 2.4821 | 2.4797 | 2.4772 | 2.4742 | 2.4707 | 2.4642 | 2.4489 | 2.395 | 2.3702 | 2.3631 | 2.363 | 2.3628 | 2.3624 | 2.3616 | 2.3613 | 2.3606 | 2.36 | 2.3591 | 2.3568 | 2.3459 | 2.317 | 2.2407 | 2.1989 | 2.1851
BOAT OF GARTEN | BOAT OF GARTEN 11 kV | MINIMUM HEADROOM | NH 95609 19427 | YES | 7.1375 | 7.1355 | 7.1323 | 7.1283 | 7.0603 | 6.897 | 6.733 | 6.5651 | 6.3433 | 6.2338 | 5.7568 | 5.6338 | 5.7132 | 5.5904 | 8.506 | 8.4917 | 8.4743 | 8.4559 | 8.4187 | 8.3773 | 8.3329 | 8.2836 | 8.2113 | 8.1361 | 7.7928 | 7.6868 | 7.6719 | 7.5429 | 8.1181 | 8.1116 | 8.0786 | 8.0376 | 7.8789 | 7.7104 | 7.5407 | 7.3632 | 7.1356 | 7.0292 | 6.5943 | 6.4541 | 6.5393 | 6.4056
| BOAT OF GARTEN 11 kV | CT |  |  | 7.1381 | 7.1356 | 7.1323 | 7.1283 | 7.1191 | 7.0309 | 6.8522 | 6.6683 | 6.4852 | 6.4074 | 5.9612 | 5.7233 | 5.7765 | 5.7828 | 8.5142 | 8.5032 | 8.4885 | 8.4713 | 8.4335 | 8.396 | 8.3531 | 8.3077 | 8.2594 | 8.2142 | 7.9083 | 7.7213 | 7.7136 | 7.6786 | 8.169 | 8.1713 | 8.151 | 8.1154 | 7.9627 | 7.8184 | 7.637 | 7.452 | 7.2764 | 7.1913 | 6.8176 | 6.5559 | 6.59 | 6.5874
| BOAT OF GARTEN 11 kV | LW |  |  | 7.1375 | 7.1355 | 7.1325 | 7.1299 | 7.0603 | 6.897 | 6.733 | 6.5651 | 6.3433 | 6.2338 | 5.7568 | 5.6338 | 5.7359 | 5.6991 | 8.506 | 8.4917 | 8.4743 | 8.4559 | 8.4187 | 8.3773 | 8.3329 | 8.2836 | 8.2113 | 8.1361 | 7.7928 | 7.6868 | 7.7293 | 7.7147 | 8.1181 | 8.1116 | 8.0786 | 8.0376 | 7.8789 | 7.7104 | 7.5407 | 7.3632 | 7.1356 | 7.0292 | 6.5943 | 6.4541 | 6.5558 | 6.5216
| BOAT OF GARTEN 11 kV | ST |  |  | 7.1384 | 7.1358 | 7.1337 | 7.1329 | 7.1333 | 7.1333 | 7.1327 | 7.1321 | 7.1286 | 7.1225 | 6.9888 | 6.4359 | 6.3249 | 6.2837 | 8.5198 | 8.5105 | 8.5022 | 8.4958 | 8.4891 | 8.4803 | 8.4699 | 8.4586 | 8.4392 | 8.4106 | 8.321 | 8.0475 | 7.9467 | 7.89 | 8.1531 | 8.1402 | 8.1293 | 8.1244 | 8.1282 | 8.1274 | 8.123 | 8.1195 | 8.0921 | 8.0395 | 7.8731 | 7.2824 | 7.1419 | 7.0873
| BOAT OF GARTEN 11 kV | SP |  |  | 7.1389 | 7.1369 | 7.1356 | 7.1355 | 7.134 | 7.1323 | 7.1303 | 7.1273 | 7.1223 | 7.0441 | 6.7992 | 6.1851 | 5.7132 | 5.5904 | 8.5201 | 8.5121 | 8.5049 | 8.5 | 8.4887 | 8.4764 | 8.4633 | 8.4477 | 8.4276 | 8.3998 | 8.3248 | 8.0317 | 7.6719 | 7.5429 | 8.1632 | 8.1562 | 8.1533 | 8.1529 | 8.1172 | 8.0828 | 8.0446 | 7.9984 | 7.9469 | 7.8618 | 7.6158 | 7.0329 | 6.5393 | 6.4056
PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | NO | 0.94354 | 0.61997 | 0.2559 | -0.11853 | -0.51919 | -1.6609 | -3.0074 | -4.5622 | -6.3239 | -8.3129 | -11.8052 | -13.4448 | -13.4753 | -13.4999 | 0.90474 | 0.51627 | 0.079318 | -0.36437 | -0.82513 | -2.1538 | -3.7136 | -5.5143 | -7.557 | -9.8633 | -13.7599 | -15.4613 | -15.4961 | -15.5271 | 1.0801 | 0.7326 | 0.34347 | -0.054092 | -0.46844 | -1.6569 | -3.0449 | -4.6475 | -6.4666 | -8.523 | -12.0137 | -13.6316 | -13.7643 | -13.818
| BODDAM | CT |  |  | 0.9445 | 0.62075 | 0.2559 | -0.11853 | -0.51919 | -1.6609 | -3.0074 | -4.5622 | -6.3239 | -8.3129 | -11.7509 | -13.3747 | -13.4213 | -13.4495 | 0.90474 | 0.51627 | 0.079318 | -0.36437 | -0.82513 | -2.1538 | -3.7136 | -5.5143 | -7.557 | -9.8633 | -13.7491 | -15.4594 | -15.4961 | -15.5271 | 1.0801 | 0.7326 | 0.34347 | -0.054092 | -0.46844 | -1.6569 | -3.0449 | -4.6475 | -6.4666 | -8.523 | -11.993 | -13.6316 | -13.7643 | -13.818
| BODDAM | LW |  |  | 0.94354 | 0.61997 | 0.25627 | -0.11524 | -0.51605 | -1.6609 | -2.9968 | -4.5426 | -6.317 | -8.3055 | -11.8052 | -13.4448 | -13.4753 | -13.4999 | 0.90806 | 0.52057 | 0.085707 | -0.35509 | -0.81443 | -2.1435 | -3.7014 | -5.5031 | -7.5522 | -9.861 | -13.7599 | -15.4613 | -15.4828 | -15.4979 | 1.086 | 0.74022 | 0.3543 | -0.039217 | -0.45159 | -1.6402 | -3.0281 | -4.6345 | -6.4609 | -8.5215 | -12.0137 | -13.5669 | -13.6681 | -13.7126
| BODDAM | ST |  |  | 0.95646 | 0.63822 | 0.28393 | -0.069855 | -0.42898 | -1.5228 | -2.8201 | -4.3204 | -6.0261 | -7.9757 | -11.3757 | -13.0803 | -13.3046 | -13.4148 | 0.91541 | 0.5328 | 0.10421 | -0.32419 | -0.75974 | -2.058 | -3.5955 | -5.372 | -7.3884 | -9.6771 | -13.5232 | -15.2997 | -15.4095 | -15.4817 | 1.0944 | 0.75509 | 0.37693 | -0.00092623 | -0.38478 | -1.536 | -2.9002 | -4.4774 | -6.2682 | -8.3063 | -11.74 | -13.3773 | -13.4976 | -13.5645
| BODDAM | SP |  |  | 0.95661 | 0.63988 | 0.28722 | -0.063298 | -0.42312 | -1.5177 | -2.8144 | -4.3151 | -6.0193 | -7.9642 | -11.2961 | -12.8561 | -13.0803 | -13.1841 | 0.91506 | 0.53352 | 0.10598 | -0.31994 | -0.75382 | -2.0508 | -3.5855 | -5.3596 | -7.3729 | -9.6559 | -13.4742 | -15.1923 | -15.3319 | -15.4176 | 1.094 | 0.75615 | 0.37938 | 0.0048141 | -0.37606 | -1.5249 | -2.8846 | -4.4574 | -6.2433 | -8.2728 | -11.666 | -13.2229 | -13.3727 | -13.4304
TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | 3.1894 | 3.1624 | 3.1273 | 3.0723 | 3.0021 | 2.8754 | 2.7356 | 2.5719 | 2.4012 | 2.2567 | 1.7903 | 1.3687 | 1.2242 | 1.1695 | 3.0928 | 3.0755 | 3.0499 | 3.0082 | 2.9375 | 2.8686 | 2.787 | 2.7008 | 2.6077 | 2.5122 | 2.1891 | 1.7727 | 1.5518 | 1.5117 | 2.6897 | 2.6645 | 2.6319 | 2.5802 | 2.5218 | 2.4108 | 2.2696 | 2.1179 | 1.9516 | 1.8072 | 1.3166 | 0.93299 | 0.80328 | 0.74446
| BONSKEID | CT |  |  | 3.1894 | 3.1624 | 3.1273 | 3.0723 | 3.0088 | 2.8929 | 2.7356 | 2.5719 | 2.4086 | 2.2703 | 1.8605 | 1.3687 | 1.2242 | 1.1695 | 3.0945 | 3.0772 | 3.0512 | 3.0082 | 2.9375 | 2.8686 | 2.787 | 2.7008 | 2.6122 | 2.5247 | 2.2458 | 1.9437 | 1.8882 | 1.8463 | 2.6897 | 2.6645 | 2.6319 | 2.5802 | 2.5218 | 2.4145 | 2.2696 | 2.1179 | 1.9653 | 1.8312 | 1.3954 | 0.93299 | 0.80328 | 0.75473
| BONSKEID | LW |  |  | 3.2006 | 3.1756 | 3.144 | 3.0948 | 3.0021 | 2.8754 | 2.7463 | 2.6013 | 2.4012 | 2.2567 | 1.7903 | 1.3985 | 1.3224 | 1.2693 | 3.0928 | 3.0755 | 3.0499 | 3.0126 | 2.95 | 2.8814 | 2.81 | 2.7191 | 2.6077 | 2.5122 | 2.1891 | 1.7727 | 1.7611 | 1.7533 | 2.7031 | 2.6813 | 2.6534 | 2.6092 | 2.5289 | 2.4108 | 2.2888 | 2.1445 | 1.9516 | 1.8072 | 1.3166 | 0.95327 | 0.88764 | 0.84223
| BONSKEID | ST |  |  | 3.2179 | 3.2073 | 3.1869 | 3.1647 | 3.1369 | 3.1111 | 3.0641 | 3.0235 | 2.9686 | 2.9011 | 2.6611 | 1.7904 | 1.295 | 1.2391 | 3.1094 | 3.101 | 3.0877 | 3.0708 | 3.0522 | 3.0346 | 3.0053 | 2.9779 | 2.9402 | 2.888 | 2.715 | 1.937 | 1.5518 | 1.5117 | 2.7175 | 2.7083 | 2.6905 | 2.6714 | 2.6482 | 2.6263 | 2.5843 | 2.5486 | 2.4993 | 2.4375 | 2.1054 | 1.2654 | 0.86117 | 0.79068
| BONSKEID | SP |  |  | 3.2189 | 3.2105 | 3.1911 | 3.1725 | 3.1481 | 3.1272 | 3.0845 | 3.0507 | 3.0114 | 2.9459 | 2.7335 | 2.2246 | 1.5136 | 1.2319 | 3.1118 | 3.1058 | 3.0938 | 3.0811 | 3.0603 | 3.0428 | 3.0119 | 2.9843 | 2.9494 | 2.8979 | 2.7564 | 2.3332 | 1.7386 | 1.5557 | 2.7192 | 2.7126 | 2.696 | 2.681 | 2.6609 | 2.6438 | 2.6058 | 2.5765 | 2.542 | 2.4817 | 2.275 | 1.7029 | 1.0113 | 0.74446
PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | 0.68695 | 0.66608 | 0.61096 | 0.55467 | 0.067723 | -0.40143 | -0.92196 | -1.3016 | -1.6914 | -1.9232 | -2.6689 | -2.8964 | -2.791 | -2.8399 | 1.6096 | 1.5943 | 1.5657 | 1.5381 | 1.1281 | 0.73039 | 0.26673 | -0.024419 | -0.28684 | -0.4788 | -1.0926 | -1.2898 | -1.2645 | -1.341 | 1.4448 | 1.43 | 1.3869 | 1.3406 | 0.86094 | 0.3836 | -0.15058 | -0.52575 | -0.89551 | -1.123 | -1.8744 | -2.1243 | -2.0341 | -2.0771
| BOWMORE | CT |  |  | 0.72218 | 0.70046 | 0.66313 | 0.59258 | 0.097358 | -0.36683 | -0.91034 | -1.3001 | -1.6324 | -1.8449 | -2.5222 | -2.851 | -2.7746 | -2.7614 | 1.6221 | 1.6051 | 1.5797 | 1.5426 | 1.1281 | 0.73039 | 0.26673 | -0.024419 | -0.26729 | -0.44964 | -1.0277 | -1.2794 | -1.2645 | -1.2842 | 1.4725 | 1.4473 | 1.4245 | 1.3756 | 0.88256 | 0.41017 | -0.14432 | -0.52575 | -0.84897 | -1.0603 | -1.7291 | -2.0786 | -2.0177 | -2.0062
| BOWMORE | LW |  |  | 0.68695 | 0.66608 | 0.61096 | 0.55467 | 0.067723 | -0.40143 | -0.92196 | -1.3016 | -1.6914 | -1.9232 | -2.6689 | -2.8964 | -2.791 | -2.8399 | 1.6096 | 1.5943 | 1.5657 | 1.5381 | 1.1296 | 0.73245 | 0.27686 | -0.016475 | -0.28684 | -0.4788 | -1.0926 | -1.2898 | -1.2502 | -1.2713 | 1.4448 | 1.43 | 1.3869 | 1.3406 | 0.86094 | 0.3836 | -0.15058 | -0.52238 | -0.89551 | -1.123 | -1.8744 | -2.1243 | -2.0341 | -2.0771
| BOWMORE | ST |  |  | 0.71951 | 0.70092 | 0.68001 | 0.6636 | 0.34293 | 0.041546 | -0.31619 | -0.51321 | -0.68923 | -0.86898 | -1.4247 | -2.0066 | -2.1829 | -2.2378 | 1.6247 | 1.611 | 1.598 | 1.5878 | 1.2469 | 0.91754 | 0.52767 | 0.3158 | 0.13808 | -0.026565 | -0.53113 | -0.91727 | -1.0196 | -1.0683 | 1.4747 | 1.4593 | 1.4454 | 1.4344 | 1.0921 | 0.74851 | 0.34686 | 0.12727 | -0.050264 | -0.20936 | -0.76175 | -1.3177 | -1.473 | -1.5213
| BOWMORE | SP |  |  | 0.73327 | 0.72161 | 0.70842 | 0.70226 | 0.35156 | 0.022711 | -0.36261 | -0.59125 | -0.79166 | -0.99707 | -1.609 | -2.2781 | -2.6693 | -2.8134 | 1.6295 | 1.6191 | 1.6097 | 1.6051 | 1.2544 | 0.91623 | 0.51801 | 0.29602 | 0.10863 | -0.063162 | -0.5762 | -0.97436 | -1.2182 | -1.341 | 1.4851 | 1.473 | 1.461 | 1.4546 | 1.1002 | 0.75292 | 0.33767 | 0.098953 | -0.10547 | -0.30899 | -0.92092 | -1.5214 | -1.9124 | -2.0418
WOODHILL | BRAE | MINIMUM HEADROOM | HU 3604068816 | NO | 3.6415 | 3.4199 | 3.1308 | 2.7961 | 2.4024 | 1.9676 | 1.5257 | 0.93247 | 0.27492 | -0.4109 | -2.6666 | -3.6423 | -3.6163 | -3.6268 | 4.2843 | 4.0127 | 3.6887 | 3.3583 | 2.9922 | 2.5935 | 2.1707 | 1.5906 | 0.94532 | 0.20528 | -2.3567 | -3.3309 | -3.3092 | -3.3396 | 3.4459 | 3.2278 | 2.9464 | 2.6246 | 2.2503 | 1.8606 | 1.4833 | 0.91407 | 0.28319 | -0.38263 | -2.6693 | -3.5602 | -3.4957 | -3.5316
| BRAE | CT |  |  | 3.6624 | 3.436 | 3.1396 | 2.7961 | 2.4024 | 1.9676 | 1.5426 | 0.93779 | 0.29568 | -0.36937 | -2.5688 | -3.5227 | -3.5253 | -3.5319 | 4.2942 | 4.0233 | 3.6993 | 3.3613 | 2.9933 | 2.596 | 2.1816 | 1.5999 | 0.96474 | 0.23572 | -2.3485 | -3.3159 | -3.267 | -3.2575 | 3.4641 | 3.2418 | 2.954 | 2.6246 | 2.2503 | 1.8606 | 1.4877 | 0.91918 | 0.30241 | -0.34544 | -2.5789 | -3.4635 | -3.3951 | -3.383
| BRAE | LW |  |  | 3.6415 | 3.4199 | 3.1308 | 2.818 | 2.4185 | 1.9816 | 1.5257 | 0.93247 | 0.27492 | -0.4109 | -2.6666 | -3.6423 | -3.6163 | -3.6268 | 4.2843 | 4.0127 | 3.6887 | 3.3583 | 2.9922 | 2.5935 | 2.1707 | 1.5906 | 0.94532 | 0.20528 | -2.3567 | -3.3309 | -3.3092 | -3.3263 | 3.4459 | 3.2278 | 2.9464 | 2.6505 | 2.2821 | 1.8912 | 1.4833 | 0.91407 | 0.28319 | -0.38263 | -2.6693 | -3.5602 | -3.4957 | -3.5316
| BRAE | ST |  |  | 3.669 | 3.4504 | 3.198 | 2.9266 | 2.6423 | 2.3352 | 2.0051 | 1.4703 | 0.87067 | 0.1609 | -2.1744 | -3.3123 | -3.4395 | -3.4678 | 4.2998 | 4.032 | 3.7222 | 3.4084 | 3.0885 | 2.7448 | 2.3781 | 1.8388 | 1.2347 | 0.47863 | -2.1024 | -3.1705 | -3.168 | -3.1656 | 3.4703 | 3.255 | 3.0061 | 2.7449 | 2.4948 | 2.2246 | 1.9361 | 1.4813 | 0.92934 | 0.25243 | -1.9934 | -3.0864 | -3.204 | -3.2284
| BRAE | SP |  |  | 3.6802 | 3.4664 | 3.221 | 2.9545 | 2.6456 | 2.3193 | 1.9698 | 1.4437 | 0.8409 | 0.13006 | -2.183 | -3.3345 | -3.556 | -3.612 | 4.3024 | 4.0363 | 3.7287 | 3.4203 | 3.0917 | 2.7419 | 2.3685 | 1.8209 | 1.2132 | 0.47523 | -2.1044 | -3.2089 | -3.3034 | -3.3396 | 3.4801 | 3.2691 | 3.0264 | 2.7833 | 2.51 | 2.2212 | 1.9117 | 1.426 | 0.86352 | 0.17625 | -2.0525 | -3.211 | -3.4402 | -3.519
BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | YES | 4.7318 | 4.6228 | 4.4896 | 4.3192 | 3.8637 | 3.2922 | 2.6948 | 1.937 | 1.0742 | 0.3619 | -1.9703 | -5.2093 | -6.4456 | -6.8531 | 6.3604 | 6.2889 | 6.2035 | 6.081 | 5.8504 | 5.5465 | 5.2358 | 4.8473 | 4.2857 | 3.799 | 2.1859 | 0.35219 | -0.32244 | -0.74839 | 4.8789 | 4.7907 | 4.6801 | 4.5316 | 4.1337 | 3.6314 | 3.1059 | 2.4141 | 1.6159 | 0.94964 | -1.2337 | -4.1568 | -5.2489 | -5.6062
| BRECHIN | CT |  |  | 4.7318 | 4.6228 | 4.4896 | 4.3192 | 3.8637 | 3.2922 | 2.7435 | 2.1502 | 1.4007 | 0.63295 | -1.9278 | -5.2093 | -6.4456 | -6.8531 | 6.3604 | 6.2889 | 6.2035 | 6.081 | 5.8504 | 5.5465 | 5.2358 | 4.8906 | 4.4037 | 3.9223 | 2.274 | 0.35219 | -0.32244 | -0.74839 | 4.8789 | 4.7907 | 4.6801 | 4.5316 | 4.1337 | 3.6314 | 3.138 | 2.5978 | 1.9092 | 1.2026 | -1.163 | -4.1568 | -5.2489 | -5.6062
| BRECHIN | LW |  |  | 4.7475 | 4.6431 | 4.5181 | 4.3635 | 3.8876 | 3.3155 | 2.6948 | 1.937 | 1.0742 | 0.3619 | -1.9703 | -4.6135 | -5.6439 | -6.0506 | 6.3744 | 6.3094 | 6.2335 | 6.1331 | 5.9073 | 5.6129 | 5.2757 | 4.8473 | 4.2857 | 3.799 | 2.1859 | 0.55489 | 0.12667 | -0.045049 | 4.8943 | 4.8108 | 4.7085 | 4.5779 | 4.1644 | 3.6631 | 3.1059 | 2.4141 | 1.6159 | 0.94964 | -1.2337 | -3.6728 | -4.5784 | -4.9352
| BRECHIN | ST |  |  | 4.8252 | 4.7553 | 4.6832 | 4.587 | 4.5087 | 4.3705 | 4.2059 | 4.0521 | 3.7616 | 3.4484 | 2.2749 | 0.098374 | -0.98674 | -1.5373 | 6.4097 | 6.3615 | 6.3106 | 6.2375 | 6.1673 | 6.0449 | 5.8901 | 5.7449 | 5.4596 | 5.1893 | 4.1778 | 2.4629 | 1.6644 | 1.1844 | 4.9642 | 4.9123 | 4.858 | 4.7802 | 4.7181 | 4.6008 | 4.4478 | 4.3025 | 4.0245 | 3.7279 | 2.6125 | 0.53728 | -0.46694 | -0.95008
| BRECHIN | SP |  |  | 4.8571 | 4.8076 | 4.7528 | 4.6829 | 4.586 | 4.4262 | 4.251 | 4.0831 | 3.7626 | 3.4625 | 2.393 | 0.62087 | -0.45008 | -0.69058 | 6.4212 | 6.3827 | 6.3389 | 6.2812 | 6.2087 | 6.0813 | 5.9288 | 5.7819 | 5.4833 | 5.2262 | 4.3032 | 2.8138 | 1.6559 | 0.8161 | 4.9921 | 4.9587 | 4.92 | 4.8668 | 4.7899 | 4.655 | 4.4945 | 4.3383 | 4.0339 | 3.7527 | 2.7482 | 1.0632 | 0.02486 | -0.22236
PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | 7.3824 | 6.2303 | 4.5984 | 2.819 | 16.0948 | 13.6041 | 11.0455 | 8.6433 | 6.327 | 4.583 | -1.4772 | -6.1792 | -6.5408 | -6.694 | 8.996 | 7.7709 | 5.9754 | 4.0386 | 16.312 | 13.8099 | 11.3565 | 9.1069 | 6.7732 | 4.9027 | -0.66038 | -4.416 | -4.519 | -4.5778 | 8.4151 | 7.2504 | 5.5646 | 3.7235 | 16.1206 | 13.7432 | 11.3725 | 9.0032 | 6.7092 | 4.9897 | -0.58511 | -5.0717 | -5.3902 | -5.5237
| BRIDGE OF DON | CT |  |  | 7.3824 | 6.2303 | 4.5984 | 2.819 | 16.0948 | 13.8023 | 11.533 | 9.2667 | 6.9238 | 5.0577 | -0.38931 | -4.6556 | -5.7851 | -6.3217 | 8.996 | 7.7709 | 5.9754 | 4.0386 | 16.312 | 13.8099 | 11.3565 | 9.1069 | 6.8279 | 5.1288 | 0.18252 | -3.0348 | -3.2801 | -3.3924 | 8.4151 | 7.2504 | 5.5646 | 3.7235 | 16.1206 | 13.7432 | 11.4268 | 9.2638 | 7.0552 | 5.3397 | 0.45649 | -3.5829 | -4.7914 | -5.2523
| BRIDGE OF DON | LW |  |  | 7.4231 | 6.2404 | 4.6475 | 2.9049 | 16.1406 | 13.6041 | 11.0455 | 8.6433 | 6.327 | 4.583 | -1.4772 | -6.1792 | -6.5408 | -6.694 | 9.0218 | 7.7991 | 6.0212 | 4.1072 | 16.4106 | 13.9352 | 11.4427 | 9.1331 | 6.7732 | 4.9027 | -0.66038 | -4.416 | -4.519 | -4.5778 | 8.4444 | 7.299 | 5.6367 | 3.8257 | 16.2674 | 13.897 | 11.3725 | 9.0032 | 6.7092 | 4.9897 | -0.58511 | -5.0717 | -5.3902 | -5.5237
| BRIDGE OF DON | ST |  |  | 7.5624 | 6.5089 | 5.0135 | 3.4223 | 16.9393 | 14.9249 | 12.8965 | 10.9975 | 9.0895 | 7.7093 | 3.074 | -2.7678 | -5.0135 | -5.1777 | 9.1074 | 7.9471 | 6.243 | 4.4321 | 16.8628 | 14.5571 | 12.2453 | 10.1528 | 8.0693 | 6.6171 | 2.3417 | -2.156 | -3.896 | -4.0408 | 8.5532 | 7.4992 | 5.9926 | 4.3923 | 17.0943 | 15.0668 | 13.0162 | 11.065 | 9.1151 | 7.6342 | 3.0949 | -2.0463 | -3.9644 | -4.0984
| BRIDGE OF DON | SP |  |  | 7.571 | 6.5322 | 5.0504 | 3.4812 | 17.0209 | 15.0378 | 13.0379 | 11.1675 | 9.317 | 8.0533 | 4.3557 | -0.00085171 | -3.3618 | -4.074 | 9.1114 | 7.9598 | 6.2632 | 4.4656 | 16.9101 | 14.6237 | 12.3396 | 10.2719 | 8.2291 | 6.8593 | 2.9071 | -0.012178 | -2.6232 | -3.2484 | 8.5589 | 7.5163 | 6.0198 | 4.4372 | 17.1574 | 15.1551 | 13.1562 | 11.3131 | 9.452 | 8.1426 | 4.2459 | 0.41176 | -2.467 | -3.0811
BRIDGE OF DUN | BRIDGE OF DUN 11kV | MINIMUM HEADROOM | NO 66018 58883 | YES | 2.2626 | 2.2539 | 2.2434 | 2.2307 | 2.2114 | 2.1893 | 2.1645 | 2.1375 | 2.0954 | 2.0589 | 1.9521 | 1.857 | 1.8588 | 1.8558 | 2.023 | 2.0196 | 2.0145 | 2.0066 | 1.9945 | 1.9841 | 1.9678 | 1.9507 | 1.9179 | 1.8909 | 1.8462 | 1.8277 | 1.8219 | 1.8033 | 1.9439 | 1.9383 | 1.9302 | 1.9208 | 1.9018 | 1.8787 | 1.8522 | 1.8227 | 1.7705 | 1.731 | 1.6589 | 1.6258 | 1.6207 | 1.6117
| BRIDGE OF DUN 11kV | CT |  |  | 2.2652 | 2.2586 | 2.2498 | 2.2387 | 2.2196 | 2.1998 | 2.1702 | 2.1379 | 2.106 | 2.077 | 1.9997 | 1.9159 | 1.9023 | 1.8952 | 2.023 | 2.0199 | 2.0145 | 2.0066 | 1.9945 | 1.9844 | 1.9679 | 1.9507 | 1.9332 | 1.9069 | 1.8546 | 1.8323 | 1.8219 | 1.8119 | 1.9466 | 1.9427 | 1.9357 | 1.925 | 1.9046 | 1.8869 | 1.8558 | 1.8227 | 1.7903 | 1.7534 | 1.6763 | 1.6363 | 1.6207 | 1.6117
| BRIDGE OF DUN 11kV | LW |  |  | 2.2626 | 2.2539 | 2.2434 | 2.2307 | 2.2114 | 2.1893 | 2.1645 | 2.1375 | 2.0954 | 2.0589 | 1.9521 | 1.857 | 1.8588 | 1.8558 | 2.023 | 2.0196 | 2.0145 | 2.0085 | 1.9978 | 1.9841 | 1.9678 | 1.9512 | 1.9179 | 1.8909 | 1.8462 | 1.8277 | 1.8283 | 1.8262 | 1.9439 | 1.9383 | 1.9302 | 1.9208 | 1.9018 | 1.8787 | 1.8522 | 1.8253 | 1.7705 | 1.731 | 1.6589 | 1.6258 | 1.628 | 1.6237
| BRIDGE OF DUN 11kV | ST |  |  | 2.2705 | 2.2671 | 2.2634 | 2.2587 | 2.2536 | 2.2476 | 2.2406 | 2.2325 | 2.2205 | 2.2031 | 2.1409 | 1.9918 | 1.9241 | 1.9097 | 2.0263 | 2.0244 | 2.0228 | 2.0197 | 2.0169 | 2.0133 | 2.0094 | 2.0045 | 1.9989 | 1.9898 | 1.9531 | 1.874 | 1.851 | 1.8368 | 1.9501 | 1.9476 | 1.9454 | 1.9414 | 1.9375 | 1.9326 | 1.9274 | 1.9209 | 1.9119 | 1.8978 | 1.8441 | 1.7322 | 1.692 | 1.6732
| BRIDGE OF DUN 11kV | SP |  |  | 2.2708 | 2.2682 | 2.2653 | 2.2619 | 2.2564 | 2.2508 | 2.2443 | 2.2372 | 2.2288 | 2.217 | 2.1699 | 2.0369 | 1.9298 | 1.9001 | 2.0249 | 2.0238 | 2.0219 | 2.0202 | 2.017 | 2.0139 | 2.0097 | 2.005 | 1.9984 | 1.9906 | 1.9635 | 1.864 | 1.8258 | 1.8033 | 1.9487 | 1.9473 | 1.945 | 1.943 | 1.9378 | 1.9329 | 1.9265 | 1.9193 | 1.9096 | 1.8978 | 1.8518 | 1.7051 | 1.6432 | 1.6142
ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | YES | 10.2076 | 9.9011 | 9.6097 | 9.3245 | 8.8821 | 8.4222 | 7.9352 | 7.3957 | 6.7329 | 6.1426 | 4.234 | 2.7883 | 2.304 | 2.1385 | 11.0055 | 10.7781 | 10.5424 | 10.3069 | 10.0027 | 9.6779 | 9.3293 | 8.9422 | 8.4818 | 8.0409 | 6.5714 | 5.5031 | 5.1989 | 5.0221 | 10.6576 | 10.3777 | 10.1148 | 9.8568 | 9.4536 | 9.0356 | 8.5945 | 8.1074 | 7.5086 | 6.9758 | 5.2325 | 3.9259 | 3.4858 | 3.3307
| BRIDGE OF EARN | CT |  |  | 10.2533 | 9.9919 | 9.7271 | 9.4707 | 9.0477 | 8.6206 | 8.1328 | 7.61 | 7.0605 | 6.492 | 4.4556 | 2.7883 | 2.304 | 2.1385 | 11.0215 | 10.8104 | 10.5818 | 10.3528 | 10.054 | 9.7466 | 9.4059 | 9.0387 | 8.6523 | 8.2306 | 6.6857 | 5.5031 | 5.1989 | 5.0221 | 10.7001 | 10.4624 | 10.2249 | 9.9951 | 9.6111 | 9.223 | 8.7786 | 8.3035 | 7.8034 | 7.288 | 5.4302 | 3.9259 | 3.4858 | 3.3307
| BRIDGE OF EARN | LW |  |  | 10.2076 | 9.9011 | 9.6097 | 9.3245 | 8.8821 | 8.4222 | 7.9352 | 7.3957 | 6.7329 | 6.1426 | 4.234 | 2.8998 | 2.5885 | 2.4666 | 11.0055 | 10.7781 | 10.5424 | 10.3069 | 10.0027 | 9.6779 | 9.3293 | 8.9422 | 8.4818 | 8.0409 | 6.5714 | 5.5801 | 5.3973 | 5.3264 | 10.6576 | 10.3777 | 10.1148 | 9.8568 | 9.4536 | 9.0356 | 8.5945 | 8.1074 | 7.5086 | 6.9758 | 5.2325 | 4.0346 | 3.7555 | 3.64
| BRIDGE OF EARN | ST |  |  | 10.2735 | 10.0402 | 9.7782 | 9.5156 | 9.239 | 8.9409 | 8.624 | 8.2954 | 7.9456 | 7.5267 | 6.0695 | 4.2931 | 3.8503 | 3.6231 | 11.0345 | 10.8381 | 10.6173 | 10.3946 | 10.1638 | 9.9145 | 9.6492 | 9.3711 | 9.0738 | 8.7274 | 7.4009 | 6.1373 | 5.8352 | 5.6297 | 10.7181 | 10.5061 | 10.2692 | 10.0307 | 9.7825 | 9.5147 | 9.2304 | 8.9363 | 8.6234 | 8.2464 | 6.9145 | 5.3446 | 4.9472 | 4.7341
| BRIDGE OF EARN | SP |  |  | 10.3014 | 10.0837 | 9.8317 | 9.5851 | 9.2989 | 8.9916 | 8.6586 | 8.3076 | 7.9309 | 7.5054 | 6.0511 | 4.3081 | 3.5712 | 3.3859 | 11.048 | 10.859 | 10.6417 | 10.427 | 10.1935 | 9.9426 | 9.6702 | 9.3825 | 9.0732 | 8.728 | 7.4162 | 6.1534 | 5.6478 | 5.3473 | 10.7441 | 10.5467 | 10.3194 | 10.0955 | 9.8379 | 9.5607 | 9.2614 | 8.9462 | 8.6085 | 8.2238 | 6.8874 | 5.3362 | 4.6835 | 4.5111
RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | 0.25054 | 0.24918 | 0.24621 | 0.2423 | 0.22736 | 0.21419 | 0.19596 | 0.17527 | 0.15599 | 0.14273 | 0.088622 | 0.078555 | 0.084836 | 0.074312 | 0.3518 | 0.35051 | 0.34861 | 0.34512 | 0.33629 | 0.32898 | 0.32042 | 0.31075 | 0.30007 | 0.29239 | 0.25262 | 0.2471 | 0.24762 | 0.24383 | 0.29459 | 0.2932 | 0.29039 | 0.28648 | 0.27263 | 0.26079 | 0.24396 | 0.22532 | 0.20773 | 0.19525 | 0.14155 | 0.13272 | 0.1376 | 0.12995
| BRIDGE OF GAUR | CT |  |  | 0.25201 | 0.25062 | 0.248 | 0.2423 | 0.22748 | 0.21471 | 0.19596 | 0.17527 | 0.15599 | 0.14273 | 0.092797 | 0.079529 | 0.084836 | 0.085057 | 0.35207 | 0.35062 | 0.34881 | 0.34512 | 0.33629 | 0.32898 | 0.32042 | 0.31075 | 0.30148 | 0.29265 | 0.25536 | 0.2473 | 0.24762 | 0.24571 | 0.29582 | 0.29437 | 0.29187 | 0.28648 | 0.27263 | 0.26079 | 0.24396 | 0.22532 | 0.2079 | 0.19525 | 0.14616 | 0.13397 | 0.1376 | 0.1374
| BRIDGE OF GAUR | LW |  |  | 0.25054 | 0.24918 | 0.24621 | 0.24236 | 0.22736 | 0.21419 | 0.20102 | 0.1854 | 0.15641 | 0.14367 | 0.088622 | 0.078555 | 0.085086 | 0.07976 | 0.3518 | 0.35051 | 0.34861 | 0.34627 | 0.33779 | 0.33097 | 0.324 | 0.31509 | 0.30007 | 0.29239 | 0.25262 | 0.2471 | 0.24899 | 0.2468 | 0.29459 | 0.2932 | 0.29039 | 0.2868 | 0.27289 | 0.26087 | 0.24879 | 0.23428 | 0.20773 | 0.19579 | 0.14155 | 0.13272 | 0.13784 | 0.13348
| BRIDGE OF GAUR | ST |  |  | 0.25201 | 0.25164 | 0.2511 | 0.24938 | 0.24896 | 0.24853 | 0.24809 | 0.24407 | 0.24076 | 0.23377 | 0.20964 | 0.15147 | 0.13689 | 0.12758 | 0.35255 | 0.3523 | 0.35185 | 0.35047 | 0.34969 | 0.34894 | 0.34822 | 0.34457 | 0.34264 | 0.33822 | 0.32246 | 0.27643 | 0.26746 | 0.26044 | 0.29594 | 0.2956 | 0.29507 | 0.29337 | 0.29285 | 0.29233 | 0.29182 | 0.28772 | 0.28466 | 0.27806 | 0.25507 | 0.19391 | 0.1806 | 0.17191
| BRIDGE OF GAUR | SP |  |  | 0.25328 | 0.25333 | 0.2536 | 0.25344 | 0.25117 | 0.24988 | 0.24744 | 0.24495 | 0.24141 | 0.23306 | 0.20865 | 0.14582 | 0.092392 | 0.074312 | 0.35307 | 0.35295 | 0.35287 | 0.35245 | 0.35106 | 0.35035 | 0.34884 | 0.34737 | 0.34524 | 0.33997 | 0.32738 | 0.2907 | 0.25417 | 0.24383 | 0.29707 | 0.29709 | 0.29729 | 0.29706 | 0.29494 | 0.29375 | 0.29147 | 0.28915 | 0.28585 | 0.27795 | 0.25568 | 0.1973 | 0.1454 | 0.12995
BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | 3.3193 | 3.326 | 3.3145 | 3.296 | 3.2115 | 3.1323 | 3.0506 | 2.9661 | 2.8907 | 2.845 | 2.6879 | 2.6555 | 2.5975 | 2.6004 | 3.8704 | 3.8714 | 3.8647 | 3.8545 | 3.8105 | 3.7688 | 3.7268 | 3.6842 | 3.6464 | 3.6189 | 3.52 | 3.4938 | 3.4456 | 3.4167 | 3.5263 | 3.5356 | 3.5231 | 3.5035 | 3.419 | 3.3401 | 3.2608 | 3.1811 | 3.1078 | 3.0636 | 2.9106 | 2.8787 | 2.8222 | 2.8249
| BROADFORD | CT |  |  | 3.3706 | 3.3759 | 3.3717 | 3.3505 | 3.2601 | 3.18 | 3.1082 | 3.0354 | 2.9722 | 2.9314 | 2.7712 | 2.69 | 2.6983 | 2.6947 | 3.8949 | 3.8948 | 3.8914 | 3.8794 | 3.8322 | 3.7898 | 3.7514 | 3.713 | 3.6811 | 3.6592 | 3.5586 | 3.5051 | 3.4995 | 3.4822 | 3.5772 | 3.5822 | 3.5775 | 3.5572 | 3.4726 | 3.3925 | 3.3208 | 3.2497 | 3.1883 | 3.1489 | 2.9935 | 2.9137 | 2.9215 | 2.9178
| BROADFORD | LW |  |  | 3.3193 | 3.326 | 3.3145 | 3.296 | 3.2115 | 3.1323 | 3.0506 | 2.9661 | 2.8907 | 2.845 | 2.6879 | 2.6555 | 2.6954 | 2.6814 | 3.8704 | 3.8714 | 3.8647 | 3.8545 | 3.8105 | 3.7688 | 3.7268 | 3.6842 | 3.6464 | 3.6189 | 3.52 | 3.4938 | 3.5116 | 3.5051 | 3.5263 | 3.5356 | 3.5231 | 3.5035 | 3.419 | 3.3401 | 3.2608 | 3.1811 | 3.1078 | 3.0636 | 2.9106 | 2.8787 | 2.9185 | 2.9049
| BROADFORD | ST |  |  | 3.3548 | 3.3388 | 3.336 | 3.3359 | 3.3268 | 3.3118 | 3.2949 | 3.2846 | 3.2738 | 3.2497 | 3.1693 | 2.9563 | 2.9025 | 2.8762 | 3.8882 | 3.8783 | 3.8762 | 3.8753 | 3.8686 | 3.8589 | 3.8481 | 3.8404 | 3.8331 | 3.8187 | 3.7695 | 3.6281 | 3.5884 | 3.5611 | 3.5635 | 3.5495 | 3.5465 | 3.5455 | 3.5372 | 3.5233 | 3.5074 | 3.4977 | 3.4865 | 3.4621 | 3.3842 | 3.1762 | 3.1225 | 3.0961
| BROADFORD | SP |  |  | 3.3518 | 3.3334 | 3.3298 | 3.3252 | 3.2746 | 3.2288 | 3.1789 | 3.1265 | 3.0796 | 3.0118 | 2.9068 | 2.6811 | 2.5975 | 2.6004 | 3.8867 | 3.8757 | 3.8732 | 3.8701 | 3.8433 | 3.8187 | 3.7921 | 3.7641 | 3.7408 | 3.7074 | 3.6533 | 3.5229 | 3.4456 | 3.4167 | 3.5605 | 3.5444 | 3.5402 | 3.5348 | 3.4849 | 3.4399 | 3.3906 | 3.3388 | 3.2935 | 3.2273 | 3.125 | 2.9038 | 2.8222 | 2.8249
CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | YES | 3.0616 | 3.0516 | 3.0348 | 3.0251 | 2.9969 | 2.7464 | 2.4605 | 2.0978 | 1.6465 | 1.4242 | 0.74768 | 0.40068 | 0.54562 | 0.415 | 4.4018 | 4.3707 | 4.3129 | 4.2759 | 4.1643 | 4.0753 | 3.9772 | 3.8647 | 3.72 | 3.5653 | 3.0478 | 2.7694 | 2.8016 | 2.6795 | 3.7275 | 3.6805 | 3.6019 | 3.5527 | 3.3477 | 3.1136 | 2.8564 | 2.4999 | 2.084 | 1.8487 | 1.0861 | 0.73128 | 0.90216 | 0.73106
| BRODICK | CT |  |  | 3.071 | 3.0649 | 3.0544 | 3.0439 | 3.0127 | 2.8411 | 2.4959 | 2.0978 | 1.7338 | 1.5588 | 1.0156 | 0.45215 | 0.55396 | 0.57607 | 4.4135 | 4.3707 | 4.338 | 4.2901 | 4.1852 | 4.0958 | 3.9847 | 3.8694 | 3.7496 | 3.6322 | 3.2247 | 2.7866 | 2.8016 | 2.7744 | 3.759 | 3.7231 | 3.6721 | 3.5883 | 3.3644 | 3.151 | 2.8564 | 2.4999 | 2.17 | 1.9891 | 1.3883 | 0.79971 | 0.90606 | 0.92261
| BRODICK | LW |  |  | 3.0616 | 3.0516 | 3.0348 | 3.0251 | 2.9969 | 2.7464 | 2.4605 | 2.1249 | 1.6465 | 1.4242 | 0.74768 | 0.40068 | 0.54562 | 0.46423 | 4.4018 | 4.3744 | 4.3129 | 4.2759 | 4.1643 | 4.0753 | 3.9772 | 3.8647 | 3.72 | 3.5653 | 3.0478 | 2.7694 | 2.8377 | 2.7966 | 3.7275 | 3.6805 | 3.6019 | 3.5527 | 3.3477 | 3.1136 | 2.858 | 2.53 | 2.084 | 1.8487 | 1.0861 | 0.73128 | 0.90216 | 0.81181
| BRODICK | ST |  |  | 3.0706 | 3.0663 | 3.0573 | 3.0519 | 3.0458 | 3.0381 | 3.0306 | 3.0211 | 3.0101 | 2.9943 | 2.729 | 1.7611 | 1.4124 | 1.3256 | 4.4247 | 4.4133 | 4.3928 | 4.3788 | 4.3637 | 4.3244 | 4.2939 | 4.2485 | 4.1984 | 4.1353 | 3.9218 | 3.4741 | 3.2303 | 3.1347 | 3.7592 | 3.7396 | 3.7054 | 3.6699 | 3.6509 | 3.6218 | 3.5919 | 3.5479 | 3.4824 | 3.3889 | 3.0263 | 2.0834 | 1.7443 | 1.6647
| BRODICK | SP |  |  | 3.0724 | 3.0692 | 3.0614 | 3.0589 | 3.0509 | 3.0419 | 3.0326 | 3.0232 | 3.0095 | 2.9926 | 2.6497 | 1.6511 | 0.72809 | 0.415 | 4.4295 | 4.4214 | 4.4045 | 4.3966 | 4.3797 | 4.3398 | 4.2888 | 4.2672 | 4.2194 | 4.1624 | 3.9718 | 3.554 | 2.9208 | 2.6795 | 3.7856 | 3.78 | 3.7619 | 3.7589 | 3.7245 | 3.6717 | 3.5985 | 3.5608 | 3.4905 | 3.4023 | 2.9744 | 1.9854 | 1.0607 | 0.73106
BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | YES | 3.9263 | 3.9284 | 3.9074 | 3.8802 | 3.7619 | 2.3369 | 2.205 | 2.0412 | 1.8266 | 1.7137 | 1.3283 | 1.1836 | 1.2562 | 1.1182 | 5.0611 | 5.0603 | 5.0483 | 5.0329 | 4.9713 | 3.6066 | 3.537 | 3.4472 | 3.3335 | 3.2669 | 3.0392 | 2.9449 | 2.9366 | 2.7992 | 4.9876 | 4.988 | 4.9874 | 4.9861 | 4.8688 | 3.4538 | 3.3385 | 3.2176 | 3.0434 | 2.9559 | 2.6914 | 2.5428 | 2.6157 | 2.4675
| BRORA | CT |  |  | 3.9511 | 3.9516 | 3.951 | 3.9411 | 3.8244 | 2.4061 | 2.2431 | 2.0737 | 1.9172 | 1.832 | 1.5183 | 1.2672 | 1.267 | 1.2561 | 5.0845 | 5.0871 | 5.0808 | 5.0564 | 4.9952 | 3.6317 | 3.5469 | 3.4584 | 3.3764 | 3.3251 | 3.1376 | 2.9788 | 2.9591 | 2.926 | 4.9892 | 4.9896 | 4.989 | 4.9861 | 4.9714 | 3.5711 | 3.428 | 3.279 | 3.1395 | 3.0694 | 2.8734 | 2.6296 | 2.6295 | 2.618
| BRORA | LW |  |  | 3.9263 | 3.9284 | 3.9074 | 3.8802 | 3.7619 | 2.3369 | 2.205 | 2.0412 | 1.8266 | 1.7137 | 1.3283 | 1.1836 | 1.2634 | 1.2372 | 5.0611 | 5.0603 | 5.0483 | 5.0329 | 4.9713 | 3.6066 | 3.537 | 3.4472 | 3.3335 | 3.2669 | 3.0392 | 2.9449 | 2.9827 | 2.9703 | 4.9876 | 4.9881 | 4.9874 | 4.9863 | 4.8688 | 3.4538 | 3.3385 | 3.2176 | 3.0434 | 2.9559 | 2.6914 | 2.5428 | 2.6245 | 2.6015
| BRORA | ST |  |  | 3.9501 | 3.948 | 3.9409 | 3.9326 | 3.9261 | 2.6112 | 2.5913 | 2.5708 | 2.5416 | 2.4882 | 2.305 | 1.8809 | 1.6873 | 1.6275 | 5.0766 | 5.0718 | 5.0674 | 5.0614 | 5.0558 | 3.7449 | 3.7295 | 3.7148 | 3.6968 | 3.6651 | 3.553 | 3.2813 | 3.1352 | 3.0802 | 4.9884 | 4.988 | 4.9877 | 4.9871 | 4.987 | 3.6853 | 3.683 | 3.6808 | 3.679 | 3.6428 | 3.4994 | 3.1734 | 2.9915 | 2.9419
| BRORA | SP |  |  | 3.9511 | 3.9511 | 3.9512 | 3.9513 | 3.925 | 2.5897 | 2.5471 | 2.5023 | 2.4474 | 2.3732 | 2.1366 | 1.6255 | 1.2562 | 1.1182 | 5.0818 | 5.0792 | 5.077 | 5.0751 | 5.057 | 3.7373 | 3.712 | 3.6868 | 3.6554 | 3.6145 | 3.4807 | 3.1839 | 2.9366 | 2.7992 | 4.9892 | 4.9892 | 4.9893 | 4.9894 | 4.9879 | 3.6853 | 3.6579 | 3.6179 | 3.5777 | 3.5153 | 3.3129 | 2.9162 | 2.6157 | 2.4675
MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | 5.8501 | 5.7817 | 5.7026 | 5.6193 | 5.378 | 5.1172 | 4.8319 | 4.5118 | 4.2056 | 3.9291 | 2.9078 | 1.2198 | -0.1389 | -1.1567 | 8.0514 | 8.0258 | 7.9966 | 7.9611 | 7.9223 | 7.833 | 7.7065 | 7.5463 | 7.375 | 7.2048 | 6.5633 | 5.4964 | 4.5839 | 3.6151 | 6.6398 | 6.5876 | 6.5257 | 6.4571 | 6.2369 | 6.001 | 5.7452 | 5.4592 | 5.1911 | 4.9553 | 4.11 | 2.6607 | 1.611 | 0.89075
| BROUGHTY FERRY | CT |  |  | 5.8616 | 5.7992 | 5.7193 | 5.6336 | 5.4094 | 5.1608 | 4.9316 | 4.6867 | 4.4287 | 4.1232 | 3.0097 | 1.2198 | -0.1389 | -1.1567 | 8.0514 | 8.0258 | 7.9966 | 7.9611 | 7.9223 | 7.833 | 7.7065 | 7.5683 | 7.4232 | 7.2438 | 6.564 | 5.4964 | 4.5839 | 3.6151 | 6.6494 | 6.6026 | 6.5402 | 6.4713 | 6.2703 | 6.0462 | 5.841 | 5.6225 | 5.3921 | 5.1208 | 4.1694 | 2.6607 | 1.611 | 0.89075
| BROUGHTY FERRY | LW |  |  | 5.8501 | 5.7817 | 5.7026 | 5.6193 | 5.378 | 5.1172 | 4.8319 | 4.5118 | 4.2056 | 3.9291 | 2.9078 | 1.4866 | 0.26812 | -0.70826 | 8.058 | 8.0359 | 8.0126 | 7.9893 | 7.9512 | 7.8643 | 7.7164 | 7.5463 | 7.375 | 7.2048 | 6.5633 | 5.7802 | 5.1876 | 4.6742 | 6.6398 | 6.5876 | 6.5257 | 6.4571 | 6.2369 | 6.001 | 5.7452 | 5.4592 | 5.1911 | 4.9553 | 4.11 | 2.9025 | 1.9876 | 1.2983
| BROUGHTY FERRY | ST |  |  | 5.9107 | 5.8735 | 5.8364 | 5.8046 | 5.7697 | 5.7309 | 5.6889 | 5.6363 | 5.5837 | 5.4908 | 5.0893 | 3.6887 | 2.4378 | 1.3422 | 8.0656 | 8.0486 | 8.031 | 8.016 | 7.9972 | 7.9765 | 7.9503 | 7.9242 | 7.8953 | 7.8535 | 7.5945 | 6.5299 | 5.5903 | 4.5906 | 6.6944 | 6.6693 | 6.6441 | 6.6211 | 6.5989 | 6.5737 | 6.5444 | 6.508 | 6.4723 | 6.4 | 6.0981 | 4.8837 | 3.9199 | 3.1252
| BROUGHTY FERRY | SP |  |  | 5.9358 | 5.9051 | 5.8731 | 5.852 | 5.8083 | 5.7617 | 5.7113 | 5.6512 | 5.5822 | 5.5009 | 5.1662 | 4.1113 | 2.7601 | 1.8418 | 8.0689 | 8.0529 | 8.0358 | 8.0228 | 8.0056 | 7.9867 | 7.9664 | 7.939 | 7.9119 | 7.8796 | 7.6219 | 6.7024 | 5.2959 | 3.738 | 6.7158 | 6.697 | 6.6769 | 6.663 | 6.6312 | 6.597 | 6.5599 | 6.5144 | 6.4636 | 6.3993 | 6.1453 | 5.3037 | 4.2108 | 3.5648
DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | YES | 9.904 | 9.2197 | 8.9396 | 8.7535 | 8.045 | 7.6256 | 7.3515 | 7.1133 | 6.9878 | 6.9137 | 6.6381 | 6.6174 | 6.7281 | 6.3824 | 11.0495 | 10.7979 | 10.6949 | 10.6236 | 10.3669 | 10.2108 | 10.1011 | 9.9588 | 9.8509 | 9.7483 | 9.3761 | 9.0658 | 9.1446 | 8.8813 | 10.6388 | 10.2 | 9.958 | 9.7978 | 9.1849 | 8.8227 | 8.5855 | 8.3999 | 8.3047 | 8.2282 | 7.8733 | 7.606 | 7.8234 | 7.4972
| BRUCHAG | CT |  |  | 9.9135 | 9.6262 | 9.5297 | 9.5723 | 8.961 | 8.5375 | 8.2616 | 8.0815 | 7.9182 | 7.7958 | 7.4393 | 6.9704 | 7.1181 | 7.1132 | 11.0925 | 10.9426 | 10.9037 | 10.9054 | 10.6752 | 10.5087 | 10.3968 | 10.2879 | 10.1834 | 10.0783 | 9.7428 | 9.2831 | 9.2781 | 9.2387 | 10.6695 | 10.4866 | 10.4467 | 10.4704 | 9.9835 | 9.6199 | 9.3833 | 9.2424 | 9.1167 | 9.0046 | 8.6187 | 8.0001 | 8.0602 | 8.0585
| BRUCHAG | LW |  |  | 9.904 | 9.2197 | 8.9396 | 8.7535 | 8.045 | 7.6256 | 7.3515 | 7.1133 | 6.9878 | 6.9137 | 6.6381 | 6.6174 | 6.9301 | 6.8745 | 11.0495 | 10.7979 | 10.6949 | 10.6236 | 10.3669 | 10.2108 | 10.1011 | 9.9588 | 9.8509 | 9.7483 | 9.3761 | 9.0658 | 9.1826 | 9.1573 | 10.6388 | 10.2 | 9.958 | 9.7978 | 9.1849 | 8.8227 | 8.5855 | 8.3999 | 8.3047 | 8.2282 | 7.8733 | 7.606 | 7.8729 | 7.8267
| BRUCHAG | ST |  |  | 9.9652 | 9.9327 | 9.8979 | 9.7633 | 9.5605 | 9.3894 | 9.2433 | 9.1065 | 9.1136 | 9.0463 | 8.8006 | 8.2021 | 8.0454 | 7.9443 | 11.1473 | 11.0976 | 11.0431 | 10.9588 | 10.8733 | 10.797 | 10.7267 | 10.6599 | 10.6368 | 10.5808 | 10.3722 | 9.8277 | 9.6532 | 9.5756 | 10.7506 | 10.6978 | 10.6417 | 10.5573 | 10.4795 | 10.3707 | 10.2508 | 10.1388 | 10.1512 | 10.1027 | 9.8656 | 9.0801 | 8.8775 | 8.7913
| BRUCHAG | SP |  |  | 10.0069 | 10.0009 | 9.9898 | 9.9816 | 9.9625 | 9.9329 | 9.8262 | 9.7234 | 9.6099 | 9.4135 | 8.8288 | 7.5641 | 6.7281 | 6.3824 | 11.1959 | 11.179 | 11.1527 | 11.1242 | 11.0697 | 10.9999 | 10.9441 | 10.894 | 10.8315 | 10.7335 | 10.4383 | 9.7358 | 9.1446 | 8.8813 | 10.8184 | 10.8093 | 10.7911 | 10.7754 | 10.7332 | 10.6733 | 10.6341 | 10.5999 | 10.5586 | 10.4127 | 9.9123 | 8.7014 | 7.8234 | 7.4972
KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | YES | 9.1858 | 9.0991 | 8.9647 | 8.8049 | 8.4118 | 7.9803 | 7.43 | 6.7494 | 6.0453 | 5.3561 | 3.0643 | -0.19176 | -1.8317 | -2.402 | 10.2861 | 10.2156 | 10.1268 | 9.9676 | 9.7187 | 9.4692 | 9.1681 | 8.8333 | 8.487 | 8.1013 | 6.6672 | 5.0597 | 4.3303 | 3.8553 | 8.5913 | 8.5149 | 8.4031 | 8.2671 | 7.9231 | 7.5431 | 7.0324 | 6.4285 | 5.8042 | 5.1885 | 3.1203 | 0.20209 | -1.2367 | -1.7361
| BUCKIE | CT |  |  | 9.2629 | 9.1874 | 9.0698 | 8.8739 | 8.4611 | 8.0407 | 7.43 | 6.7494 | 6.0453 | 5.3561 | 3.0643 | -0.19176 | -1.8317 | -2.402 | 10.3026 | 10.2292 | 10.1379 | 9.9676 | 9.7187 | 9.4692 | 9.1681 | 8.8333 | 8.487 | 8.1125 | 6.7729 | 5.0597 | 4.3303 | 3.8553 | 8.6575 | 8.5899 | 8.4919 | 8.3164 | 7.9491 | 7.5745 | 7.0324 | 6.4285 | 5.8042 | 5.1885 | 3.1203 | 0.20209 | -1.2367 | -1.7361
| BUCKIE | LW |  |  | 9.1858 | 9.0991 | 8.9647 | 8.8049 | 8.4118 | 7.9803 | 7.5659 | 6.99 | 6.1031 | 5.4242 | 3.2339 | 0.97122 | -0.22417 | -0.62088 | 10.2861 | 10.2156 | 10.1268 | 10.0197 | 9.8184 | 9.5965 | 9.3801 | 9.0023 | 8.5248 | 8.1013 | 6.6672 | 5.5413 | 5.1422 | 5.003 | 8.5913 | 8.5149 | 8.4031 | 8.2671 | 7.9231 | 7.5431 | 7.1758 | 6.6511 | 5.8545 | 5.2385 | 3.2349 | 1.2149 | 0.1696 | -0.17758
| BUCKIE | ST |  |  | 9.2872 | 9.2073 | 9.1207 | 9.0254 | 8.9363 | 8.8424 | 8.743 | 8.6391 | 8.505 | 8.2978 | 7.5402 | 5.4291 | 4.0125 | 3.2072 | 10.3325 | 10.2738 | 10.2134 | 10.133 | 10.0596 | 9.9815 | 9.895 | 9.8034 | 9.6951 | 9.5352 | 8.9232 | 7.2068 | 6.2622 | 5.6727 | 8.6828 | 8.6142 | 8.5469 | 8.4692 | 8.3978 | 8.321 | 8.2354 | 8.1466 | 8.031 | 7.8474 | 7.1602 | 5.1503 | 3.8426 | 3.177
| BUCKIE | SP |  |  | 9.3033 | 9.2323 | 9.1561 | 9.0844 | 8.9609 | 8.8436 | 8.7251 | 8.5866 | 8.4006 | 8.1749 | 7.463 | 5.9487 | 4.7142 | 4.3424 | 10.3406 | 10.2877 | 10.2331 | 10.181 | 10.1073 | 10.0354 | 9.9645 | 9.8769 | 9.7355 | 9.576 | 9.0464 | 7.7853 | 6.3676 | 5.3925 | 8.6976 | 8.6372 | 8.5796 | 8.5259 | 8.4263 | 8.3314 | 8.233 | 8.1167 | 7.9538 | 7.7566 | 7.1268 | 5.7282 | 4.526 | 4.1692
FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | 2.1859 | 2.1844 | 2.1805 | 2.1707 | 2.1363 | 2.1014 | 2.0655 | 2.0355 | 1.9999 | 1.9785 | 1.8983 | 1.8681 | 1.8697 | 1.8469 | 2.0724 | 2.0711 | 2.0688 | 2.0633 | 2.0455 | 2.0275 | 2.0084 | 1.9919 | 1.9734 | 1.9608 | 1.9094 | 1.89 | 1.8847 | 1.8665 | 2.0152 | 2.0137 | 2.0102 | 2.0023 | 1.9745 | 1.9463 | 1.9168 | 1.8911 | 1.8611 | 1.8422 | 1.7685 | 1.7416 | 1.7433 | 1.7251
| BUNOICH | CT |  |  | 2.1932 | 2.1936 | 2.1928 | 2.183 | 2.1506 | 2.1167 | 2.0765 | 2.0474 | 2.0204 | 2.0029 | 1.9423 | 1.8838 | 1.8716 | 1.8641 | 2.0751 | 2.0742 | 2.0732 | 2.066 | 2.0485 | 2.0306 | 2.0096 | 1.9952 | 1.9819 | 1.9713 | 1.9324 | 1.8947 | 1.8866 | 1.8789 | 2.0214 | 2.0215 | 2.0207 | 2.0116 | 1.9842 | 1.9567 | 1.9238 | 1.9 | 1.878 | 1.8624 | 1.807 | 1.7542 | 1.7448 | 1.739
| BUNOICH | LW |  |  | 2.1859 | 2.1844 | 2.1805 | 2.1707 | 2.1363 | 2.1014 | 2.0655 | 2.0355 | 1.9999 | 1.9785 | 1.8983 | 1.8681 | 1.8778 | 1.8757 | 2.0724 | 2.0711 | 2.0688 | 2.0633 | 2.0455 | 2.0275 | 2.0084 | 1.9919 | 1.9734 | 1.9608 | 1.9094 | 1.89 | 1.8937 | 1.8928 | 2.0152 | 2.0137 | 2.0102 | 2.0023 | 1.9745 | 1.9463 | 1.9168 | 1.8911 | 1.8611 | 1.8422 | 1.7685 | 1.7416 | 1.7494 | 1.7478
| BUNOICH | ST |  |  | 2.1919 | 2.1905 | 2.1887 | 2.183 | 2.168 | 2.1523 | 2.1356 | 2.13 | 2.1221 | 2.1102 | 2.0718 | 1.9752 | 1.9354 | 1.9194 | 2.0755 | 2.0745 | 2.0733 | 2.0694 | 2.0603 | 2.0506 | 2.0402 | 2.0367 | 2.0323 | 2.0251 | 2.001 | 1.9354 | 1.9119 | 1.9008 | 2.0205 | 2.0192 | 2.0176 | 2.0127 | 2.0003 | 1.9873 | 1.9735 | 1.9687 | 1.9622 | 1.9517 | 1.9175 | 1.8278 | 1.7948 | 1.7825
| BUNOICH | SP |  |  | 2.1912 | 2.1899 | 2.1887 | 2.1829 | 2.1634 | 2.1431 | 2.1233 | 2.1125 | 2.0998 | 2.0861 | 2.0403 | 1.9489 | 1.8697 | 1.8469 | 2.0747 | 2.0738 | 2.0729 | 2.0693 | 2.0583 | 2.0472 | 2.0366 | 2.0309 | 2.0236 | 2.0165 | 1.9913 | 1.9386 | 1.8847 | 1.8665 | 2.0198 | 2.0185 | 2.0174 | 2.0126 | 1.9963 | 1.9801 | 1.9644 | 1.9556 | 1.9447 | 1.9334 | 1.8945 | 1.8155 | 1.7433 | 1.7251
THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | 2.1217 | 2.1321 | 2.0974 | 2.0451 | 1.9034 | 1.7623 | 1.6217 | 1.4693 | 1.2951 | 1.1721 | 0.83979 | 0.78645 | 0.7297 | 0.66813 | 2.9462 | 2.9451 | 2.9273 | 2.8995 | 2.838 | 2.7735 | 2.7066 | 2.6284 | 2.5426 | 2.4625 | 2.2334 | 2.2058 | 2.1584 | 2.1062 | 0.74869 | 0.74499 | 0.74046 | 0.7302 | 0.72081 | 0.71356 | 0.66034 | 0.56468 | 0.41913 | 0.33069 | 0.085037 | 0.0039639 | -0.0052085 | -0.060443
| BURGARHILL | CT |  |  | 2.2051 | 2.2243 | 2.2051 | 2.146 | 1.9984 | 1.8711 | 1.729 | 1.5758 | 1.4266 | 1.3489 | 0.99744 | 0.87851 | 0.88392 | 0.86979 | 2.9738 | 2.9755 | 2.9618 | 2.9261 | 2.8587 | 2.8012 | 2.7381 | 2.669 | 2.5989 | 2.5522 | 2.2949 | 2.2378 | 2.2275 | 2.2036 | 0.74869 | 0.74499 | 0.74046 | 0.7302 | 0.72081 | 0.71356 | 0.70607 | 0.63979 | 0.52685 | 0.46639 | 0.22215 | 0.11326 | 0.12265 | 0.10672
| BURGARHILL | LW |  |  | 2.1217 | 2.1321 | 2.0974 | 2.0451 | 1.9034 | 1.7623 | 1.6217 | 1.4693 | 1.2951 | 1.1721 | 0.83979 | 0.78645 | 0.85405 | 0.82321 | 2.9462 | 2.9451 | 2.9273 | 2.8995 | 2.838 | 2.7735 | 2.7066 | 2.6284 | 2.5426 | 2.4625 | 2.2334 | 2.2058 | 2.2282 | 2.2174 | 0.75076 | 0.74723 | 0.74353 | 0.73724 | 0.73055 | 0.72136 | 0.66034 | 0.56468 | 0.41913 | 0.33069 | 0.085037 | 0.0039639 | 0.038497 | 0.025029
| BURGARHILL | ST |  |  | 2.186 | 2.1753 | 2.1658 | 2.1552 | 2.146 | 2.1284 | 2.1047 | 2.0928 | 2.0639 | 2.0135 | 1.8268 | 1.3932 | 1.2694 | 1.1955 | 2.9725 | 2.9661 | 2.9601 | 2.9507 | 2.9436 | 2.9314 | 2.9147 | 2.9049 | 2.8873 | 2.8582 | 2.737 | 2.4208 | 2.3605 | 2.3146 | 0.75283 | 0.75133 | 0.74986 | 0.74597 | 0.74356 | 0.73965 | 0.73397 | 0.73041 | 0.72579 | 0.71841 | 0.68424 | 0.42182 | 0.27285 | 0.21926
| BURGARHILL | SP |  |  | 2.1824 | 2.1698 | 2.1625 | 2.1528 | 2.0905 | 2.0308 | 1.9683 | 1.8944 | 1.8191 | 1.7107 | 1.4918 | 0.92844 | 0.7297 | 0.66813 | 2.97 | 2.9633 | 2.9587 | 2.9523 | 2.9258 | 2.8992 | 2.8729 | 2.8382 | 2.8021 | 2.7524 | 2.6457 | 2.3005 | 2.1584 | 2.1062 | 0.75198 | 0.75075 | 0.74977 | 0.74813 | 0.74571 | 0.74254 | 0.74056 | 0.73529 | 0.72936 | 0.72247 | 0.58573 | 0.15248 | -0.0052085 | -0.060443
ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | YES | 7.6359 | 7.5222 | 7.3823 | 7.2107 | 6.8066 | 6.3503 | 5.8656 | 5.3805 | 4.833 | 4.4957 | 3.3158 | 2.8812 | 3.081 | 2.9145 | 8.1669 | 8.1046 | 8.0295 | 7.9323 | 7.7476 | 7.5333 | 7.2885 | 7.0368 | 6.7657 | 6.5473 | 5.7196 | 5.4085 | 5.4383 | 4.998 | 7.7531 | 7.651 | 7.5286 | 7.3762 | 7.0182 | 6.6122 | 6.1736 | 5.7327 | 5.2366 | 4.9207 | 3.7985 | 3.3727 | 3.5333 | 3.4373
| BURGHEAD | CT |  |  | 7.7041 | 7.6394 | 7.5335 | 7.3863 | 6.9852 | 6.5865 | 6.1286 | 5.6717 | 5.2407 | 4.9758 | 3.9598 | 3.2279 | 3.1965 | 3.1382 | 8.1819 | 8.1335 | 8.0638 | 7.9619 | 7.768 | 7.5739 | 7.3632 | 7.1541 | 6.9508 | 6.7786 | 6.0408 | 5.5272 | 5.4383 | 5.3027 | 7.8111 | 7.7516 | 7.6579 | 7.5243 | 7.1672 | 6.8122 | 6.4026 | 5.9936 | 5.6058 | 5.3583 | 4.3913 | 3.6784 | 3.642 | 3.5914
| BURGHEAD | LW |  |  | 7.6359 | 7.5222 | 7.3823 | 7.2107 | 6.8066 | 6.3503 | 5.8656 | 5.3805 | 4.833 | 4.4957 | 3.3158 | 2.8812 | 3.081 | 3.0093 | 8.1669 | 8.1046 | 8.0295 | 7.9323 | 7.7476 | 7.5333 | 7.2885 | 7.0368 | 6.7657 | 6.5473 | 5.7196 | 5.4085 | 5.47 | 5.4426 | 7.7531 | 7.651 | 7.5286 | 7.3762 | 7.0182 | 6.6122 | 6.1736 | 5.7327 | 5.2366 | 4.9207 | 3.7985 | 3.3727 | 3.5333 | 3.4765
| BURGHEAD | ST |  |  | 7.7181 | 7.6772 | 7.6231 | 7.5584 | 7.4982 | 7.436 | 7.3801 | 7.3092 | 7.2042 | 7.0356 | 6.444 | 4.9666 | 4.4412 | 4.2308 | 8.2075 | 8.1821 | 8.1486 | 8.105 | 8.0612 | 8.0158 | 7.9722 | 7.9193 | 7.8527 | 7.7454 | 7.3483 | 6.2234 | 5.8821 | 5.6862 | 7.8278 | 7.7922 | 7.7477 | 7.6927 | 7.6413 | 7.5883 | 7.5372 | 7.4716 | 7.3749 | 7.2185 | 6.6537 | 5.1445 | 4.6717 | 4.4934
| BURGHEAD | SP |  |  | 7.7539 | 7.7337 | 7.6995 | 7.6639 | 7.5759 | 7.49 | 7.4092 | 7.3171 | 7.2091 | 7.0534 | 6.3762 | 4.7846 | 3.4021 | 2.9145 | 8.2212 | 8.2049 | 8.1782 | 8.1502 | 8.0999 | 8.0504 | 8.0017 | 7.9457 | 7.8758 | 7.7838 | 7.4173 | 6.4594 | 5.4619 | 4.998 | 7.8596 | 7.8426 | 7.8156 | 7.7874 | 7.7123 | 7.6394 | 7.5672 | 7.484 | 7.3844 | 7.242 | 6.6268 | 5.1604 | 3.8495 | 3.4373
BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | YES | 2.0584 | 1.679 | 1.2376 | 0.58845 | -0.64829 | -2.0176 | -3.0973 | -4.3206 | -5.5944 | -6.7899 | -10.6649 | -15.2581 | -16.8832 | -17.3947 | 4.5296 | 4.2211 | 3.8741 | 3.3772 | 2.5339 | 1.2694 | 0.44762 | -0.39236 | -1.2945 | -2.3601 | -5.5034 | -8.0759 | -8.151 | -8.1865 | 3.0995 | 2.7446 | 2.3299 | 1.7142 | 0.57028 | -0.86322 | -1.8769 | -2.9171 | -4.0417 | -5.379 | -9.2589 | -12.6823 | -14.0858 | -14.5297
| BURGHMUIR | CT |  |  | 2.0584 | 1.679 | 1.2376 | 0.58845 | -0.64829 | -2.0176 | -3.0252 | -4.0818 | -5.197 | -6.4267 | -10.5075 | -15.2581 | -16.8832 | -17.3947 | 4.5296 | 4.2211 | 3.8741 | 3.3772 | 2.5339 | 1.2694 | 0.44762 | -0.39236 | -1.2945 | -2.321 | -5.1702 | -7.9164 | -8.0376 | -8.1442 | 3.0995 | 2.7446 | 2.3299 | 1.7142 | 0.57028 | -0.86322 | -1.8769 | -2.9171 | -4.0417 | -5.3277 | -8.8595 | -12.6823 | -14.0858 | -14.5297
| BURGHMUIR | LW |  |  | 2.0777 | 1.6879 | 1.2447 | 0.60127 | -0.60925 | -1.9933 | -3.0973 | -4.3206 | -5.5944 | -6.7899 | -10.6649 | -14.3711 | -15.6371 | -16.0283 | 4.5761 | 4.2692 | 3.9328 | 3.4492 | 2.6377 | 1.4604 | 0.59835 | -0.29644 | -1.2573 | -2.3601 | -5.5034 | -8.0759 | -8.151 | -8.1865 | 3.1248 | 2.7612 | 2.3468 | 1.7383 | 0.62148 | -0.65701 | -1.6979 | -2.8077 | -4.0052 | -5.379 | -9.2589 | -12.4284 | -13.0078 | -13.349
| BURGHMUIR | ST |  |  | 2.4654 | 2.2626 | 2.0569 | 1.8557 | 1.4874 | 1.0631 | 0.68385 | 0.26851 | -0.19679 | -0.84066 | -3.085 | -7.8358 | -10.6218 | -11.2684 | 4.8267 | 4.6591 | 4.4852 | 4.3146 | 4.012 | 3.665 | 3.3657 | 3.0375 | 2.6785 | 2.1973 | -0.32397 | -4.6867 | -7.124 | -7.3576 | 3.4902 | 3.3077 | 3.12 | 2.9348 | 2.6037 | 2.2199 | 1.8784 | 1.5029 | 1.0817 | 0.49022 | -2.5853 | -7.944 | -10.999 | -11.2716
| BURGHMUIR | SP |  |  | 2.516 | 2.3507 | 2.1772 | 2.0232 | 1.6708 | 1.2889 | 0.96227 | 0.61462 | 0.23547 | -0.2251 | -1.7969 | -5.3927 | -8.3792 | -9.1718 | 4.8621 | 4.7225 | 4.5715 | 4.4374 | 4.1639 | 3.8631 | 3.6193 | 3.3602 | 3.0771 | 2.7365 | 1.5374 | -1.454 | -4.8273 | -5.9339 | 3.5387 | 3.3925 | 3.2357 | 3.0968 | 2.7855 | 2.4466 | 2.1603 | 1.855 | 1.52 | 1.1091 | -0.29664 | -3.898 | -8.088 | -9.4108
CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | 0.10182 | 0.10429 | 0.10225 | 0.098266 | 0.085984 | 0.072334 | 0.059837 | 0.047148 | 0.029394 | 0.021566 | -0.016493 | -0.025232 | -0.036119 | -0.038953 | 0.10013 | 0.09981 | 0.099024 | 0.096402 | 0.091012 | 0.084665 | 0.078714 | 0.07204 | 0.062909 | 0.058166 | 0.030964 | 0.018601 | 0.018693 | 0.013477 | 0.095071 | 0.096862 | 0.095285 | 0.091554 | 0.080427 | 0.068067 | 0.056871 | 0.045229 | 0.029014 | 0.021624 | -0.015408 | -0.023499 | -0.032755 | -0.03533
| BUTTERBRIDGE | CT |  |  | 0.10849 | 0.10727 | 0.10523 | 0.10234 | 0.093256 | 0.08032 | 0.065703 | 0.051189 | 0.037388 | 0.029257 | -0.0062752 | -0.02183 | -0.021129 | -0.022499 | 0.10211 | 0.10129 | 0.099504 | 0.097278 | 0.092216 | 0.086363 | 0.079877 | 0.073524 | 0.067399 | 0.061782 | 0.035417 | 0.025905 | 0.024666 | 0.021799 | 0.10116 | 0.10002 | 0.097961 | 0.095179 | 0.086327 | 0.074857 | 0.061746 | 0.048948 | 0.036607 | 0.028825 | -0.0060922 | -0.020417 | -0.0198 | -0.020981
| BUTTERBRIDGE | LW |  |  | 0.10182 | 0.10506 | 0.10225 | 0.098266 | 0.085984 | 0.072334 | 0.059837 | 0.047148 | 0.029394 | 0.021566 | -0.016493 | -0.025232 | -0.021334 | -0.023114 | 0.10013 | 0.10094 | 0.099024 | 0.096402 | 0.091012 | 0.084665 | 0.078714 | 0.07204 | 0.062909 | 0.058166 | 0.030964 | 0.018601 | 0.019834 | 0.018972 | 0.095071 | 0.097928 | 0.095285 | 0.091554 | 0.080427 | 0.068067 | 0.056871 | 0.045229 | 0.029014 | 0.021624 | -0.015408 | -0.023499 | -0.020114 | -0.021705
| BUTTERBRIDGE | ST |  |  | 0.1086 | 0.10787 | 0.10743 | 0.10721 | 0.10621 | 0.10469 | 0.10304 | 0.10135 | 0.098529 | 0.093762 | 0.076514 | 0.028726 | 0.0076745 | 0.00066074 | 0.10278 | 0.10225 | 0.10192 | 0.10159 | 0.10098 | 0.099842 | 0.098619 | 0.097194 | 0.095233 | 0.092027 | 0.080568 | 0.047008 | 0.033562 | 0.030012 | 0.10105 | 0.10033 | 0.099945 | 0.099882 | 0.099103 | 0.09765 | 0.096074 | 0.094416 | 0.091754 | 0.087037 | 0.07085 | 0.025566 | 0.0059509 | -0.00039133
| BUTTERBRIDGE | SP |  |  | 0.10537 | 0.10429 | 0.10364 | 0.10279 | 0.09564 | 0.088729 | 0.08158 | 0.073693 | 0.065351 | 0.05322 | 0.033839 | -0.0092348 | -0.036119 | -0.038953 | 0.1005 | 0.09981 | 0.099403 | 0.098824 | 0.095858 | 0.09285 | 0.090067 | 0.086775 | 0.082818 | 0.07777 | 0.068562 | 0.043852 | 0.018693 | 0.013477 | 0.098034 | 0.096862 | 0.096267 | 0.09547 | 0.08919 | 0.083012 | 0.076796 | 0.069819 | 0.062318 | 0.05154 | 0.034135 | -0.0053702 | -0.032755 | -0.03533
BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | 2.9027 | 2.7401 | 2.6353 | 2.519 | 2.324 | 2.1315 | 1.9499 | 1.7036 | 1.4118 | 1.2091 | 0.54249 | -0.10512 | -0.52973 | -0.69536 | 3.5046 | 3.3389 | 3.2452 | 3.1558 | 2.9896 | 2.8339 | 2.7001 | 2.5457 | 2.3655 | 2.2365 | 1.8028 | 1.4027 | 1.3287 | 1.2678 | 2.851 | 2.653 | 2.5802 | 2.5094 | 2.2528 | 2.0149 | 1.7919 | 1.554 | 1.2537 | 1.0644 | 0.47338 | -0.26983 | -0.67789 | -0.84325
| CALLANDER | CT |  |  | 2.9027 | 2.7439 | 2.6353 | 2.519 | 2.324 | 2.1315 | 1.9801 | 1.8091 | 1.5585 | 1.3365 | 0.70358 | -0.10512 | -0.52973 | -0.69536 | 3.5161 | 3.3627 | 3.2715 | 3.1865 | 3.0201 | 2.8654 | 2.7307 | 2.5799 | 2.427 | 2.2901 | 1.9066 | 1.4555 | 1.3287 | 1.2678 | 2.8968 | 2.7445 | 2.6395 | 2.527 | 2.3408 | 2.146 | 1.9643 | 1.7253 | 1.4733 | 1.2616 | 0.59429 | -0.26983 | -0.67789 | -0.84325
| CALLANDER | LW |  |  | 2.9034 | 2.7401 | 2.6355 | 2.5222 | 2.3325 | 2.1411 | 1.9499 | 1.7036 | 1.4118 | 1.2091 | 0.54249 | -0.096623 | -0.25737 | -0.34592 | 3.5046 | 3.3389 | 3.2452 | 3.1558 | 2.9896 | 2.8339 | 2.7001 | 2.5457 | 2.3655 | 2.2365 | 1.8028 | 1.4027 | 1.334 | 1.2899 | 2.851 | 2.653 | 2.5802 | 2.5094 | 2.2528 | 2.0149 | 1.7919 | 1.554 | 1.2537 | 1.0644 | 0.47338 | -0.10861 | -0.34569 | -0.47124
| CALLANDER | ST |  |  | 2.9642 | 2.8359 | 2.747 | 2.693 | 2.6362 | 2.588 | 2.5233 | 2.4688 | 2.4075 | 2.3216 | 2.0137 | 1.22 | 0.76952 | 0.47847 | 3.563 | 3.431 | 3.3433 | 3.2925 | 3.2384 | 3.1951 | 3.1388 | 3.0967 | 3.0476 | 2.9788 | 2.7379 | 2.1142 | 1.7766 | 1.6047 | 2.9512 | 2.8185 | 2.7324 | 2.6762 | 2.6136 | 2.5615 | 2.5118 | 2.4811 | 2.422 | 2.3363 | 2.0267 | 1.2225 | 0.77433 | 0.53554
| CALLANDER | SP |  |  | 2.9711 | 2.8488 | 2.7669 | 2.7219 | 2.6697 | 2.6288 | 2.5718 | 2.5258 | 2.4758 | 2.4113 | 2.1833 | 1.4585 | 0.87069 | 0.63427 | 3.5708 | 3.445 | 3.3639 | 3.3207 | 3.2661 | 3.2236 | 3.1679 | 3.1222 | 3.0743 | 3.0128 | 2.8398 | 2.3751 | 1.9624 | 1.8021 | 2.9626 | 2.8454 | 2.7668 | 2.7236 | 2.6636 | 2.5875 | 2.5075 | 2.431 | 2.356 | 2.2511 | 1.9748 | 1.3155 | 0.87721 | 0.70134
STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | 2.6201 | 2.6299 | 2.5968 | 2.5507 | 2.4165 | 2.2735 | 2.1083 | 1.9199 | 1.6942 | 1.5747 | 1.0868 | 0.95886 | 0.87913 | 0.80428 | 2.8771 | 2.8757 | 2.855 | 2.8273 | 2.7563 | 2.6814 | 2.6093 | 2.5101 | 2.4013 | 2.3276 | 2.011 | 1.9345 | 1.886 | 1.8265 | 2.549 | 2.5537 | 2.5221 | 2.4786 | 2.3563 | 2.2161 | 2.0761 | 1.9015 | 1.7001 | 1.5784 | 1.0784 | 0.95725 | 0.89068 | 0.82453
| CALLANISH | CT |  |  | 2.7082 | 2.7277 | 2.7114 | 2.6568 | 2.505 | 2.3719 | 2.2238 | 2.0479 | 1.8606 | 1.7634 | 1.3932 | 1.0615 | 1.0356 | 1.0065 | 2.9202 | 2.9235 | 2.9106 | 2.8762 | 2.793 | 2.7181 | 2.6378 | 2.5484 | 2.467 | 2.4074 | 2.1664 | 1.9691 | 1.9488 | 1.9201 | 2.6256 | 2.639 | 2.6218 | 2.5688 | 2.4309 | 2.3097 | 2.1699 | 1.9991 | 1.8413 | 1.7434 | 1.3624 | 1.0486 | 1.0257 | 1.0003
| CALLANISH | LW |  |  | 2.6201 | 2.6299 | 2.5968 | 2.5507 | 2.4165 | 2.2735 | 2.1083 | 1.9199 | 1.6942 | 1.5747 | 1.0868 | 0.95886 | 1.0379 | 1.0096 | 2.8771 | 2.8757 | 2.855 | 2.8273 | 2.7563 | 2.6814 | 2.6093 | 2.5101 | 2.4013 | 2.3276 | 2.011 | 1.9345 | 1.9659 | 1.9543 | 2.549 | 2.5537 | 2.5221 | 2.4786 | 2.3563 | 2.2161 | 2.0761 | 1.9015 | 1.7001 | 1.5784 | 1.0784 | 0.95725 | 1.0266 | 1.0019
| CALLANISH | ST |  |  | 2.6853 | 2.6682 | 2.6551 | 2.6441 | 2.6292 | 2.6097 | 2.5886 | 2.5537 | 2.5193 | 2.4599 | 2.2514 | 1.6246 | 1.4641 | 1.3657 | 2.9109 | 2.8965 | 2.8862 | 2.8765 | 2.8658 | 2.8528 | 2.8388 | 2.8097 | 2.7871 | 2.75 | 2.6191 | 2.2179 | 2.1166 | 2.0604 | 2.6069 | 2.5885 | 2.575 | 2.5626 | 2.5479 | 2.529 | 2.5087 | 2.4725 | 2.4394 | 2.3829 | 2.1843 | 1.5726 | 1.4005 | 1.3144
| CALLANISH | SP |  |  | 2.6837 | 2.6634 | 2.6519 | 2.6394 | 2.5765 | 2.5173 | 2.4508 | 2.3695 | 2.2713 | 2.1232 | 1.8282 | 1.2814 | 0.87913 | 0.80428 | 2.9101 | 2.8941 | 2.8849 | 2.8749 | 2.8414 | 2.8094 | 2.7736 | 2.7234 | 2.6768 | 2.6103 | 2.466 | 2.182 | 1.886 | 1.8265 | 2.6056 | 2.5844 | 2.5725 | 2.5595 | 2.5035 | 2.4504 | 2.3863 | 2.3011 | 2.2138 | 2.0867 | 1.8236 | 1.3233 | 0.89068 | 0.82453
TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | 1.9266 | 1.9237 | 1.9187 | 1.9092 | 1.883 | 1.8553 | 1.8195 | 1.7738 | 1.7333 | 1.6908 | 1.5877 | 1.551 | 1.553 | 1.5297 | 1.8117 | 1.8085 | 1.8044 | 1.799 | 1.7921 | 1.7845 | 1.7775 | 1.77 | 1.7612 | 1.7469 | 1.7082 | 1.6767 | 1.6761 | 1.6749 | 1.5474 | 1.5427 | 1.5368 | 1.529 | 1.519 | 1.5081 | 1.4977 | 1.4814 | 1.4622 | 1.4372 | 1.3662 | 1.306 | 1.3062 | 1.3042
| CALVINE | CT |  |  | 1.9334 | 1.9319 | 1.9256 | 1.915 | 1.8879 | 1.8623 | 1.8195 | 1.7738 | 1.7333 | 1.7094 | 1.6178 | 1.5542 | 1.553 | 1.5485 | 1.8117 | 1.8085 | 1.8044 | 1.799 | 1.7921 | 1.7845 | 1.7775 | 1.77 | 1.7622 | 1.7527 | 1.7219 | 1.692 | 1.6904 | 1.689 | 1.5474 | 1.5427 | 1.5368 | 1.529 | 1.519 | 1.5081 | 1.4977 | 1.4814 | 1.4646 | 1.4472 | 1.3932 | 1.3377 | 1.3334 | 1.3307
| CALVINE | LW |  |  | 1.9266 | 1.9237 | 1.9187 | 1.9092 | 1.883 | 1.8553 | 1.8275 | 1.7945 | 1.7369 | 1.6908 | 1.5877 | 1.551 | 1.5642 | 1.5565 | 1.8129 | 1.8099 | 1.807 | 1.8024 | 1.7959 | 1.7881 | 1.7805 | 1.7713 | 1.7612 | 1.7469 | 1.7082 | 1.6767 | 1.6761 | 1.6749 | 1.5491 | 1.5447 | 1.5403 | 1.5335 | 1.524 | 1.5126 | 1.5006 | 1.4834 | 1.4622 | 1.4372 | 1.3662 | 1.306 | 1.3062 | 1.3042
| CALVINE | ST |  |  | 1.9341 | 1.9314 | 1.9297 | 1.9272 | 1.9258 | 1.9218 | 1.9198 | 1.9169 | 1.9069 | 1.8918 | 1.8369 | 1.7023 | 1.6557 | 1.635 | 1.815 | 1.8136 | 1.8122 | 1.8104 | 1.8084 | 1.8058 | 1.8034 | 1.8002 | 1.7965 | 1.7907 | 1.7687 | 1.7067 | 1.685 | 1.679 | 1.5523 | 1.5502 | 1.5481 | 1.5455 | 1.5427 | 1.5389 | 1.5353 | 1.5306 | 1.5251 | 1.5165 | 1.4823 | 1.373 | 1.3304 | 1.3192
| CALVINE | SP |  |  | 1.9363 | 1.935 | 1.9337 | 1.9313 | 1.9253 | 1.9196 | 1.9111 | 1.9039 | 1.8917 | 1.8769 | 1.8194 | 1.6776 | 1.5677 | 1.5297 | 1.8153 | 1.8144 | 1.8131 | 1.8117 | 1.8104 | 1.809 | 1.8067 | 1.8048 | 1.8018 | 1.7981 | 1.7865 | 1.7433 | 1.7036 | 1.6952 | 1.5527 | 1.5513 | 1.5494 | 1.5474 | 1.5454 | 1.5433 | 1.54 | 1.5372 | 1.5328 | 1.5274 | 1.5088 | 1.4275 | 1.3551 | 1.3385
CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | YES | 8.0205 | 7.9415 | 7.8764 | 7.7926 | 7.6697 | 7.5438 | 7.4507 | 7.2662 | 6.8944 | 6.6116 | 5.6907 | 4.8575 | 4.6149 | 4.4959 | 9.2973 | 9.257 | 9.225 | 9.1826 | 9.1086 | 9.0466 | 8.9265 | 8.7494 | 8.5346 | 8.3433 | 7.721 | 7.1505 | 6.9196 | 6.7185 | 8.8326 | 8.7579 | 8.6856 | 8.5994 | 8.3343 | 8.0463 | 7.7624 | 7.4211 | 7.0097 | 6.7204 | 5.7908 | 4.8672 | 4.5564 | 4.4476
| CAMPBELTOWN | CT |  |  | 8.0205 | 7.9415 | 7.8764 | 7.7926 | 7.6697 | 7.5438 | 7.4507 | 7.2662 | 6.9693 | 6.7164 | 5.8113 | 4.8575 | 4.6149 | 4.4959 | 9.3011 | 9.262 | 9.2296 | 9.1826 | 9.1086 | 9.0466 | 8.9265 | 8.7494 | 8.5638 | 8.3954 | 7.7943 | 7.1505 | 6.9196 | 6.7185 | 8.8671 | 8.7987 | 8.7357 | 8.6233 | 8.3367 | 8.057 | 7.7624 | 7.438 | 7.1061 | 6.8355 | 5.9061 | 4.8672 | 4.5564 | 4.4476
| CAMPBELTOWN | LW |  |  | 8.0303 | 7.9543 | 7.8958 | 7.8211 | 7.7075 | 7.5834 | 7.4886 | 7.2759 | 6.8944 | 6.6116 | 5.6907 | 4.9983 | 4.7878 | 4.6449 | 9.2973 | 9.257 | 9.225 | 9.1905 | 9.1364 | 9.078 | 8.9708 | 8.7688 | 8.5346 | 8.3433 | 7.721 | 7.2632 | 7.1635 | 7.0933 | 8.8326 | 8.7579 | 8.6856 | 8.5994 | 8.3343 | 8.0463 | 7.7696 | 7.4211 | 7.0097 | 6.7204 | 5.7908 | 5.046 | 4.8212 | 4.6649
| CAMPBELTOWN | ST |  |  | 8.0548 | 8.003 | 7.9637 | 7.9265 | 7.8803 | 7.8469 | 7.8076 | 7.764 | 7.7161 | 7.6478 | 7.3805 | 6.7121 | 6.3612 | 6.1583 | 9.3094 | 9.2756 | 9.2508 | 9.2244 | 9.1946 | 9.1712 | 9.1455 | 9.1177 | 9.0902 | 9.0465 | 8.8788 | 8.1872 | 7.7924 | 7.5151 | 8.8942 | 8.8432 | 8.8041 | 8.7591 | 8.7215 | 8.6906 | 8.6512 | 8.6074 | 8.5593 | 8.4607 | 8.0956 | 7.0879 | 6.6056 | 6.358
| CAMPBELTOWN | SP |  |  | 8.0578 | 8.0095 | 7.9746 | 7.9442 | 7.9054 | 7.8799 | 7.8519 | 7.8276 | 7.7842 | 7.7362 | 7.5851 | 6.892 | 6.1857 | 6.0134 | 9.3109 | 9.2785 | 9.2549 | 9.2346 | 9.2098 | 9.1881 | 9.1689 | 9.1467 | 9.1129 | 9.0697 | 8.9418 | 8.3136 | 7.6105 | 7.1072 | 8.9144 | 8.8747 | 8.8482 | 8.8249 | 8.7675 | 8.715 | 8.6627 | 8.6034 | 8.5227 | 8.4019 | 8.0382 | 7.1235 | 6.4102 | 6.2049
COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | YES | 9.2725 | 9.1773 | 9.0784 | 8.954 | 8.6162 | 8.2456 | 7.87 | 7.4461 | 6.955 | 6.6619 | 5.5144 | 4.8916 | 4.7358 | 4.6222 | 10.8948 | 10.8397 | 10.7871 | 10.7185 | 10.5614 | 10.3891 | 10.2131 | 9.9821 | 9.7103 | 9.469 | 8.6664 | 8.2678 | 8.1535 | 8.036 | 9.6675 | 9.5727 | 9.472 | 9.3407 | 9.0261 | 8.6721 | 8.3064 | 7.8689 | 7.3734 | 7.0297 | 5.9194 | 5.338 | 5.2027 | 5.0976
| CAPUTH | CT |  |  | 9.3329 | 9.2754 | 9.2042 | 9.103 | 8.7625 | 8.4246 | 8.0247 | 7.5896 | 7.1999 | 6.9469 | 5.8573 | 4.9652 | 4.7358 | 4.6222 | 10.9105 | 10.8668 | 10.8194 | 10.7502 | 10.5875 | 10.4289 | 10.2482 | 10.033 | 9.8495 | 9.6739 | 8.8267 | 8.2903 | 8.1535 | 8.036 | 9.7133 | 9.6499 | 9.5682 | 9.4463 | 9.118 | 8.797 | 8.425 | 8.0186 | 7.6516 | 7.3687 | 6.2347 | 5.4124 | 5.2027 | 5.0976
| CAPUTH | LW |  |  | 9.2725 | 9.1773 | 9.0784 | 8.954 | 8.6162 | 8.2456 | 7.87 | 7.4461 | 6.955 | 6.6619 | 5.5144 | 4.8916 | 4.8997 | 4.8145 | 10.8948 | 10.8397 | 10.7871 | 10.7185 | 10.5614 | 10.3891 | 10.2131 | 9.9821 | 9.7103 | 9.469 | 8.6664 | 8.2678 | 8.2671 | 8.2327 | 9.6675 | 9.5727 | 9.472 | 9.3407 | 9.0261 | 8.6721 | 8.3064 | 7.8689 | 7.3734 | 7.0297 | 5.9194 | 5.338 | 5.3446 | 5.2695
| CAPUTH | ST |  |  | 9.3496 | 9.3139 | 9.2848 | 9.2506 | 9.2149 | 9.18 | 9.1376 | 9.0678 | 8.9731 | 8.8396 | 8.2482 | 6.8222 | 6.2686 | 6.0126 | 10.9308 | 10.9038 | 10.8829 | 10.858 | 10.8306 | 10.8037 | 10.7717 | 10.7108 | 10.6489 | 10.5677 | 10.1219 | 9.0697 | 8.7431 | 8.562 | 9.7438 | 9.7063 | 9.6741 | 9.6319 | 9.5876 | 9.5396 | 9.4892 | 9.4101 | 9.3039 | 9.158 | 8.5026 | 7.065 | 6.5606 | 6.3333
| CAPUTH | SP |  |  | 9.3744 | 9.3553 | 9.3402 | 9.3252 | 9.2671 | 9.2127 | 9.1477 | 9.056 | 8.9682 | 8.8434 | 8.1798 | 6.7842 | 5.716 | 5.3276 | 10.9399 | 10.9208 | 10.905 | 10.8899 | 10.8577 | 10.8279 | 10.7893 | 10.7227 | 10.6655 | 10.5927 | 10.1622 | 9.2413 | 8.5275 | 8.2094 | 9.7634 | 9.7416 | 9.7207 | 9.6989 | 9.6407 | 9.5828 | 9.5111 | 9.4176 | 9.3162 | 9.1854 | 8.5429 | 7.0835 | 6.0827 | 5.7344
ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | YES | 4.3884 | 3.6277 | 3.0819 | 2.5984 | 1.9493 | 1.3011 | 0.60717 | -0.20285 | -1.1275 | -1.887 | -4.1384 | -7.1001 | -8.5888 | -9.0902 | 6.4451 | 5.7305 | 5.237 | 4.7995 | 4.3447 | 3.9075 | 3.4133 | 2.8631 | 2.3012 | 1.8258 | 0.46877 | -1.0719 | -1.9076 | -2.5192 | 4.458 | 3.7499 | 3.2445 | 2.7968 | 2.2053 | 1.6139 | 0.97734 | 0.22789 | -0.62557 | -1.3373 | -3.4173 | -6.0911 | -7.3971 | -7.8311
| CARNOUSTIE | CT |  |  | 4.4188 | 3.6754 | 3.1351 | 2.6553 | 2.0409 | 1.4421 | 0.69413 | -0.12098 | -0.8455 | -1.5992 | -4.1384 | -7.1001 | -8.5888 | -9.0902 | 6.4485 | 5.7368 | 5.2377 | 4.7995 | 4.3447 | 3.9133 | 3.4133 | 2.8714 | 2.4199 | 1.9694 | 0.46877 | -1.0719 | -1.9076 | -2.5192 | 4.4829 | 3.79 | 3.2879 | 2.8386 | 2.2756 | 1.7287 | 1.0493 | 0.30658 | -0.35492 | -1.0486 | -3.4086 | -6.0911 | -7.3971 | -7.8311
| CARNOUSTIE | LW |  |  | 4.3884 | 3.6277 | 3.0819 | 2.5984 | 1.9493 | 1.3011 | 0.60717 | -0.20285 | -1.1275 | -1.887 | -4.1041 | -6.2046 | -7.3162 | -7.6791 | 6.4451 | 5.7305 | 5.237 | 4.8143 | 4.3554 | 3.9075 | 3.4244 | 2.8631 | 2.3012 | 1.8258 | 0.47672 | -0.56646 | -1.0028 | -1.1482 | 4.458 | 3.7499 | 3.2445 | 2.7968 | 2.2053 | 1.6139 | 0.97734 | 0.22789 | -0.62557 | -1.3373 | -3.4173 | -5.3281 | -6.2974 | -6.6101
| CARNOUSTIE | ST |  |  | 4.4671 | 3.7476 | 3.2558 | 2.838 | 2.4844 | 2.1495 | 1.7974 | 1.4232 | 1.1446 | 0.85178 | -0.052913 | -2.1213 | -3.2068 | -3.8333 | 6.4786 | 5.7836 | 5.3146 | 4.9199 | 4.5843 | 4.2702 | 3.9395 | 3.59 | 3.3295 | 3.0883 | 2.3693 | 0.95254 | 0.18364 | -0.47892 | 4.5292 | 3.86 | 3.4045 | 3.0169 | 2.6896 | 2.3801 | 2.054 | 1.7063 | 1.4432 | 1.1652 | 0.29914 | -1.686 | -2.6711 | -3.2147
| CARNOUSTIE | SP |  |  | 4.4856 | 3.7784 | 3.2978 | 2.8985 | 2.5247 | 2.1714 | 1.7932 | 1.3943 | 1.0765 | 0.78975 | -0.019057 | -1.512 | -2.6983 | -2.9228 | 6.4856 | 5.7962 | 5.3317 | 4.9481 | 4.6063 | 4.2864 | 3.9457 | 3.5867 | 3.3062 | 3.067 | 2.4003 | 1.2434 | -0.050386 | -1.2245 | 4.5456 | 3.8876 | 3.4422 | 3.0728 | 2.7291 | 2.4048 | 2.0566 | 1.6881 | 1.3896 | 1.1212 | 0.36095 | -1.066 | -2.2145 | -2.4166
KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | 0.86266 | 2.6323 | 2.6296 | 2.6263 | 2.6168 | 2.6065 | 2.5906 | 2.5734 | 2.5555 | 2.5449 | 2.4997 | 2.4819 | 2.474 | 2.4687 | 0.89019 | 2.5247 | 2.523 | 2.5211 | 2.514 | 2.5074 | 2.5 | 2.4919 | 2.4828 | 2.4764 | 2.4461 | 2.4381 | 2.4344 | 2.4315 | 0.75898 | 2.3936 | 2.391 | 2.388 | 2.3792 | 2.369 | 2.3547 | 2.3392 | 2.3229 | 2.3129 | 2.2698 | 2.2539 | 2.2469 | 2.2422
| CASHLIE | CT |  |  | 0.86672 | 2.6363 | 2.6345 | 2.6302 | 2.6178 | 2.6065 | 2.5906 | 2.5734 | 2.5555 | 2.5449 | 2.5027 | 2.4819 | 2.474 | 2.4687 | 0.89157 | 2.5258 | 2.5244 | 2.5212 | 2.514 | 2.5074 | 2.5 | 2.4919 | 2.4828 | 2.4764 | 2.4481 | 2.4381 | 2.4344 | 2.4315 | 0.76251 | 2.397 | 2.3952 | 2.3911 | 2.3796 | 2.369 | 2.3547 | 2.3392 | 2.3229 | 2.3129 | 2.2727 | 2.2539 | 2.2469 | 2.2422
| CASHLIE | LW |  |  | 0.86266 | 2.6323 | 2.6296 | 2.6263 | 2.6168 | 2.6075 | 2.597 | 2.5858 | 2.5621 | 2.5489 | 2.4997 | 2.4838 | 2.486 | 2.4841 | 0.89019 | 2.5247 | 2.523 | 2.5211 | 2.5158 | 2.5108 | 2.5046 | 2.4978 | 2.4855 | 2.4779 | 2.4461 | 2.4386 | 2.439 | 2.4379 | 0.75898 | 2.3936 | 2.391 | 2.388 | 2.3792 | 2.3707 | 2.3609 | 2.3504 | 2.3287 | 2.3165 | 2.2698 | 2.2554 | 2.2573 | 2.2555
| CASHLIE | ST |  |  | 0.86671 | 2.6358 | 2.6352 | 2.6344 | 2.6327 | 2.6311 | 2.6286 | 2.6262 | 2.6215 | 2.6145 | 2.5908 | 2.5348 | 2.5091 | 2.4944 | 0.89209 | 2.5265 | 2.5261 | 2.5253 | 2.524 | 2.5229 | 2.521 | 2.5192 | 2.5166 | 2.5126 | 2.4981 | 2.4605 | 2.4485 | 2.4407 | 0.76263 | 2.3968 | 2.3962 | 2.3953 | 2.3937 | 2.3922 | 2.3897 | 2.3874 | 2.3831 | 2.3766 | 2.3543 | 2.3012 | 2.278 | 2.2647
| CASHLIE | SP |  |  | 0.86643 | 2.6357 | 2.6348 | 2.6338 | 2.6307 | 2.6277 | 2.6238 | 2.6204 | 2.6156 | 2.6078 | 2.5852 | 2.529 | 2.4894 | 2.4731 | 0.89199 | 2.5266 | 2.526 | 2.5254 | 2.5241 | 2.5228 | 2.5208 | 2.5192 | 2.5166 | 2.5122 | 2.5005 | 2.4676 | 2.4437 | 2.4352 | 0.76238 | 2.3967 | 2.3959 | 2.395 | 2.3922 | 2.3895 | 2.386 | 2.3829 | 2.3784 | 2.3713 | 2.3505 | 2.2982 | 2.2612 | 2.2465
KILLIN | CHAORACH | MINIMUM HEADROOM | NN 4540027553 | YES | 4.4439 | 4.4434 | 4.4423 | 4.4399 | 4.4374 | 4.4348 | 4.4306 | 4.4261 | 4.422 | 4.4204 | 4.4124 | 4.4111 | 4.4149 | 4.4127 | 4.1684 | 4.1682 | 4.1677 | 4.1665 | 4.1651 | 4.1636 | 4.1618 | 4.1598 | 4.1579 | 4.1567 | 4.1494 | 4.1481 | 4.1487 | 4.1479 | 4.1197 | 4.1194 | 4.1184 | 4.1163 | 4.114 | 4.1115 | 4.1079 | 4.1039 | 4.1003 | 4.0987 | 4.0901 | 4.0882 | 4.0912 | 4.0894
| CHAORACH | CT |  |  | 4.4439 | 4.4434 | 4.4423 | 4.4399 | 4.4374 | 4.4348 | 4.4306 | 4.4261 | 4.422 | 4.4204 | 4.4124 | 4.4111 | 4.4168 | 4.4189 | 4.1684 | 4.1682 | 4.1677 | 4.1665 | 4.1651 | 4.1636 | 4.1618 | 4.1598 | 4.1579 | 4.1567 | 4.1502 | 4.1481 | 4.1501 | 4.1508 | 4.1197 | 4.1194 | 4.1184 | 4.1163 | 4.114 | 4.1115 | 4.1079 | 4.1039 | 4.1003 | 4.0987 | 4.0901 | 4.0882 | 4.093 | 4.0948
| CHAORACH | LW |  |  | 4.4446 | 4.4446 | 4.4441 | 4.4431 | 4.441 | 4.439 | 4.4364 | 4.4333 | 4.4274 | 4.4252 | 4.4147 | 4.4131 | 4.4149 | 4.4127 | 4.1687 | 4.1686 | 4.1684 | 4.1677 | 4.1668 | 4.1659 | 4.1645 | 4.1625 | 4.1596 | 4.158 | 4.1494 | 4.1481 | 4.1487 | 4.1479 | 4.1203 | 4.1203 | 4.1199 | 4.1189 | 4.1171 | 4.1153 | 4.113 | 4.1099 | 4.1046 | 4.1025 | 4.0912 | 4.0897 | 4.0912 | 4.0894
| CHAORACH | ST |  |  | 4.4445 | 4.4445 | 4.4445 | 4.4441 | 4.4444 | 4.4448 | 4.4447 | 4.445 | 4.4438 | 4.4429 | 4.439 | 4.4284 | 4.4294 | 4.4305 | 4.1688 | 4.1687 | 4.1686 | 4.1684 | 4.1683 | 4.1683 | 4.168 | 4.1679 | 4.1669 | 4.1663 | 4.1634 | 4.1544 | 4.1543 | 4.1547 | 4.1203 | 4.1203 | 4.1203 | 4.1198 | 4.1201 | 4.1203 | 4.12 | 4.1202 | 4.1189 | 4.118 | 4.1141 | 4.1032 | 4.1039 | 4.1049
| CHAORACH | SP |  |  | 4.4449 | 4.4451 | 4.4453 | 4.4456 | 4.4459 | 4.4462 | 4.4463 | 4.4463 | 4.4459 | 4.4447 | 4.4402 | 4.4279 | 4.4176 | 4.4153 | 4.1689 | 4.1689 | 4.1689 | 4.169 | 4.169 | 4.1691 | 4.169 | 4.1689 | 4.1685 | 4.1676 | 4.165 | 4.1573 | 4.1503 | 4.1494 | 4.1206 | 4.1208 | 4.1209 | 4.1212 | 4.1213 | 4.1216 | 4.1216 | 4.1215 | 4.121 | 4.1199 | 4.1155 | 4.1037 | 4.0937 | 4.0916
ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | YES | 2.8239 | 2.4849 | 2.2596 | 2.0169 | 1.4011 | 0.78296 | 0.090939 | -0.65449 | -1.4227 | -2.1773 | -4.4821 | -7.8736 | -9.541 | -10.1878 | 5.4565 | 5.1308 | 4.9385 | 4.733 | 4.3729 | 4.0562 | 3.6684 | 3.2802 | 2.8425 | 2.3471 | 0.84604 | -0.95723 | -1.9055 | -2.6463 | 2.9755 | 2.5989 | 2.3587 | 2.1113 | 1.5538 | 1.0004 | 0.37277 | -0.33631 | -1.0654 | -1.8012 | -4.0532 | -7.0346 | -8.4359 | -8.9604
| CHARLES AVENUE | CT |  |  | 2.8489 | 2.5404 | 2.3329 | 2.0823 | 1.4614 | 0.87626 | 0.21881 | -0.41609 | -1.0742 | -1.8968 | -4.4455 | -7.8736 | -9.541 | -10.1878 | 5.4572 | 5.1379 | 4.9447 | 4.733 | 4.3729 | 4.0562 | 3.6684 | 3.3139 | 2.943 | 2.4453 | 0.89972 | -0.95723 | -1.9055 | -2.6463 | 2.9954 | 2.6442 | 2.417 | 2.1511 | 1.5789 | 1.0469 | 0.44883 | -0.14102 | -0.75171 | -1.5198 | -3.9206 | -7.0346 | -8.4359 | -8.9604
| CHARLES AVENUE | LW |  |  | 2.8239 | 2.4849 | 2.2596 | 2.0169 | 1.4011 | 0.78296 | 0.090939 | -0.65449 | -1.4227 | -2.1773 | -4.4821 | -7.0218 | -8.3308 | -8.8767 | 5.4565 | 5.1308 | 4.9385 | 4.7463 | 4.4034 | 4.0864 | 3.6908 | 3.2802 | 2.8425 | 2.3471 | 0.84604 | -0.53982 | -1.0537 | -1.2912 | 2.9755 | 2.5989 | 2.3587 | 2.1113 | 1.5538 | 1.0004 | 0.37277 | -0.33631 | -1.0654 | -1.8012 | -4.0532 | -6.41 | -7.4904 | -7.9271
| CHARLES AVENUE | ST |  |  | 2.9399 | 2.6989 | 2.5568 | 2.394 | 2.2199 | 2.0902 | 1.8678 | 1.7034 | 1.5667 | 1.2618 | 0.31111 | -1.8044 | -3.1469 | -3.9721 | 5.5029 | 5.2163 | 5.0577 | 4.8982 | 4.7268 | 4.6035 | 4.3937 | 4.2458 | 4.1092 | 3.8523 | 3.0489 | 1.3794 | 0.34735 | -0.43634 | 3.0761 | 2.7845 | 2.6169 | 2.4372 | 2.2538 | 2.1163 | 1.891 | 1.7195 | 1.5684 | 1.2626 | 0.30408 | -1.8558 | -3.0788 | -3.7575
| CHARLES AVENUE | SP |  |  | 2.9767 | 2.7574 | 2.635 | 2.5103 | 2.3282 | 2.1867 | 1.9597 | 1.8022 | 1.6192 | 1.3121 | 0.44143 | -1.1084 | -2.387 | -2.7714 | 5.5175 | 5.2403 | 5.0897 | 4.9488 | 4.7771 | 4.6515 | 4.4432 | 4.3018 | 4.1425 | 3.8844 | 3.1434 | 1.8136 | 0.16543 | -1.2831 | 3.1075 | 2.835 | 2.6845 | 2.5416 | 2.3563 | 2.2132 | 1.9899 | 1.8292 | 1.6372 | 1.3372 | 0.49211 | -1.075 | -2.3957 | -2.7365
CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | 9.3273 | 9.2504 | 9.1507 | 9.037 | 8.8644 | 8.4658 | 8.1313 | 7.6644 | 7.3328 | 7.0316 | 5.9786 | 4.3058 | 3.7453 | 3.4068 | 3.3902 | 3.3284 | 3.2552 | 3.1656 | 3.0342 | 2.8799 | 2.7539 | 2.6206 | 2.4625 | 2.2738 | 1.5832 | 0.63113 | 0.18974 | -0.20424 | 4.1711 | 4.0919 | 3.9938 | 3.8758 | 3.737 | 3.5772 | 3.3994 | 3.0226 | 2.7127 | 2.4252 | 1.1331 | -0.47628 | -0.77362 | -0.92653
| CHARLESTON | CT |  |  | 9.3273 | 9.2504 | 9.1507 | 9.037 | 8.8644 | 8.4658 | 8.1857 | 7.8968 | 7.5856 | 7.2425 | 6.1353 | 4.4314 | 3.7453 | 3.4068 | 3.3902 | 3.3284 | 3.2552 | 3.1656 | 3.0342 | 2.8799 | 2.7539 | 2.6215 | 2.4783 | 2.3118 | 1.6427 | 0.63113 | 0.18974 | -0.20424 | 4.1711 | 4.0919 | 3.9938 | 3.8758 | 3.737 | 3.5772 | 3.3994 | 3.2033 | 2.9227 | 2.5825 | 1.465 | -0.091112 | -0.53223 | -0.79
| CHARLESTON | LW |  |  | 9.344 | 9.2695 | 9.1773 | 9.0748 | 8.9194 | 8.541 | 8.1313 | 7.6644 | 7.3328 | 7.0316 | 5.9786 | 4.3058 | 3.925 | 3.6004 | 3.4055 | 3.3476 | 3.2826 | 3.2057 | 3.0875 | 2.9444 | 2.7937 | 2.6206 | 2.4625 | 2.2738 | 1.5832 | 0.68653 | 0.43343 | 0.27587 | 4.1881 | 4.1111 | 4.0206 | 3.9138 | 3.7899 | 3.6411 | 3.4164 | 3.0226 | 2.7127 | 2.4252 | 1.1331 | -0.47628 | -0.77362 | -0.92653
| CHARLESTON | ST |  |  | 9.3854 | 9.3465 | 9.294 | 9.2517 | 9.2139 | 9.1689 | 9.1159 | 9.0521 | 8.9721 | 8.8589 | 8.3202 | 6.2785 | 5.246 | 5.0352 | 3.439 | 3.4059 | 3.3705 | 3.337 | 3.312 | 3.2818 | 3.2459 | 3.2023 | 3.1471 | 3.0656 | 2.6696 | 1.6946 | 1.1261 | 0.75239 | 4.2324 | 4.1929 | 4.1444 | 4.1012 | 4.0623 | 4.016 | 3.9614 | 3.8959 | 3.8134 | 3.697 | 3.1009 | 1.2141 | 0.22929 | 0.038693
| CHARLESTON | SP |  |  | 9.3881 | 9.354 | 9.3067 | 9.2726 | 9.2439 | 9.2115 | 9.1743 | 9.1308 | 9.074 | 9.0026 | 8.6791 | 7.4534 | 6.0805 | 5.6894 | 3.4434 | 3.4146 | 3.3835 | 3.3574 | 3.3352 | 3.31 | 3.2817 | 3.2485 | 3.2047 | 3.1472 | 2.8616 | 2.1272 | 1.3486 | 0.55837 | 4.2352 | 4.2007 | 4.1574 | 4.1226 | 4.0931 | 4.0598 | 4.0216 | 3.9771 | 3.9189 | 3.8457 | 3.5156 | 2.3506 | 1.036 | 0.67057
ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | 6.5562 | 6.3936 | 6.1776 | 6.0552 | 5.8881 | 5.6923 | 5.5089 | 5.3066 | 5.0591 | 4.9192 | 4.4508 | 4.3505 | 4.3298 | 4.2281 | 6.6839 | 6.5085 | 6.3058 | 6.2014 | 6.0542 | 5.9299 | 5.8197 | 5.7037 | 5.5704 | 5.4857 | 5.2761 | 5.2092 | 5.1966 | 5.1273 | 6.2152 | 6.0151 | 5.7658 | 5.6252 | 5.4284 | 5.2528 | 5.0903 | 4.9032 | 4.6818 | 4.5462 | 4.0696 | 3.9794 | 3.976 | 3.8973
| CLACHAN | CT |  |  | 6.5993 | 6.3936 | 6.1776 | 6.0552 | 5.9356 | 5.758 | 5.5714 | 5.3565 | 5.1505 | 5.0336 | 4.641 | 4.4248 | 4.4596 | 4.4566 | 6.6839 | 6.5401 | 6.3426 | 6.2212 | 6.0757 | 5.9476 | 5.8413 | 5.7188 | 5.5991 | 5.527 | 5.346 | 5.2412 | 5.2523 | 5.2423 | 6.274 | 6.0753 | 5.834 | 5.6698 | 5.4591 | 5.283 | 5.1195 | 4.9356 | 4.757 | 4.6423 | 4.241 | 4.0364 | 4.0574 | 4.0536
| CLACHAN | LW |  |  | 6.5562 | 6.4064 | 6.1955 | 6.0915 | 5.8881 | 5.6923 | 5.5089 | 5.3066 | 5.0591 | 4.9192 | 4.4508 | 4.3505 | 4.4299 | 4.3871 | 6.6843 | 6.5085 | 6.3058 | 6.2014 | 6.0542 | 5.9299 | 5.8197 | 5.7037 | 5.5704 | 5.4857 | 5.2761 | 5.2092 | 5.2392 | 5.2205 | 6.2152 | 6.0151 | 5.7658 | 5.6252 | 5.4284 | 5.2528 | 5.0903 | 4.9032 | 4.6818 | 4.5462 | 4.0696 | 3.9794 | 4.0357 | 4.0048
| CLACHAN | ST |  |  | 6.6033 | 6.424 | 6.2199 | 6.1246 | 6.0453 | 5.9911 | 5.9345 | 5.89 | 5.8358 | 5.7798 | 5.5911 | 5.0543 | 4.8977 | 4.8172 | 6.685 | 6.5391 | 6.348 | 6.2586 | 6.1688 | 6.1011 | 6.0394 | 5.9864 | 5.9236 | 5.8625 | 5.7274 | 5.4951 | 5.4032 | 5.3578 | 6.2622 | 6.0498 | 5.8222 | 5.7119 | 5.6259 | 5.5554 | 5.4952 | 5.4314 | 5.3577 | 5.2742 | 5.0475 | 4.5148 | 4.3736 | 4.311
| CLACHAN | SP |  |  | 6.6064 | 6.4281 | 6.2258 | 6.1363 | 6.0591 | 6.0079 | 5.9097 | 5.8164 | 5.6988 | 5.5601 | 5.2651 | 4.7095 | 4.3298 | 4.2281 | 6.6857 | 6.5401 | 6.3502 | 6.264 | 6.1552 | 6.0736 | 5.9956 | 5.9269 | 5.8455 | 5.7695 | 5.6158 | 5.3756 | 5.1966 | 5.1273 | 6.2648 | 6.0529 | 5.8269 | 5.7238 | 5.6032 | 5.5077 | 5.4139 | 5.3273 | 5.215 | 5.0941 | 4.8395 | 4.3517 | 3.976 | 3.8973
CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | 0.20377 | 0.2029 | 0.19971 | 0.1935 | 0.18436 | 0.17664 | 0.16546 | 0.15175 | 0.13608 | 0.1269 | 0.092274 | 0.087363 | 0.093464 | 0.083414 | 0.22376 | 0.22309 | 0.2211 | 0.21714 | 0.21188 | 0.20748 | 0.20135 | 0.19426 | 0.18564 | 0.18002 | 0.15485 | 0.1521 | 0.15108 | 0.1443 | 0.21035 | 0.20949 | 0.20629 | 0.20131 | 0.19159 | 0.18201 | 0.17054 | 0.1566 | 0.14201 | 0.13338 | 0.099687 | 0.095375 | 0.10021 | 0.09147
| CLAONAIG | CT |  |  | 0.20453 | 0.20368 | 0.20017 | 0.1935 | 0.18436 | 0.17664 | 0.16546 | 0.15175 | 0.13675 | 0.12937 | 0.095093 | 0.088959 | 0.095782 | 0.097164 | 0.22408 | 0.22344 | 0.2212 | 0.21714 | 0.21188 | 0.20748 | 0.20135 | 0.19426 | 0.18707 | 0.18245 | 0.15651 | 0.15292 | 0.1539 | 0.15243 | 0.21164 | 0.2109 | 0.2076 | 0.20131 | 0.19159 | 0.18311 | 0.17054 | 0.1566 | 0.14303 | 0.13607 | 0.10282 | 0.097394 | 0.10245 | 0.10349
| CLAONAIG | LW |  |  | 0.20377 | 0.2029 | 0.19971 | 0.19455 | 0.18708 | 0.17666 | 0.16756 | 0.15412 | 0.13608 | 0.1269 | 0.092274 | 0.087363 | 0.093464 | 0.08918 | 0.22376 | 0.22309 | 0.2211 | 0.21787 | 0.21377 | 0.20777 | 0.20257 | 0.19446 | 0.18564 | 0.18002 | 0.15485 | 0.1521 | 0.15412 | 0.15266 | 0.21035 | 0.20949 | 0.20629 | 0.20134 | 0.19293 | 0.18201 | 0.17219 | 0.15888 | 0.14201 | 0.13338 | 0.099687 | 0.095375 | 0.10029 | 0.096943
| CLAONAIG | ST |  |  | 0.20582 | 0.20494 | 0.20419 | 0.20257 | 0.20252 | 0.20214 | 0.19965 | 0.19905 | 0.19576 | 0.19152 | 0.17364 | 0.13397 | 0.13043 | 0.12873 | 0.22505 | 0.2244 | 0.22382 | 0.22272 | 0.22245 | 0.22197 | 0.22013 | 0.21947 | 0.21724 | 0.21449 | 0.2021 | 0.17196 | 0.16808 | 0.1651 | 0.21258 | 0.21177 | 0.21108 | 0.20964 | 0.20968 | 0.20939 | 0.20735 | 0.20687 | 0.20372 | 0.19943 | 0.18193 | 0.1421 | 0.13672 | 0.13418
| CLAONAIG | SP |  |  | 0.20614 | 0.20601 | 0.20557 | 0.20528 | 0.20435 | 0.20149 | 0.19998 | 0.19813 | 0.19327 | 0.18838 | 0.17343 | 0.11604 | 0.093903 | 0.083414 | 0.22514 | 0.22492 | 0.22448 | 0.2241 | 0.22348 | 0.22158 | 0.22056 | 0.21935 | 0.21619 | 0.21316 | 0.20419 | 0.16555 | 0.15108 | 0.1443 | 0.21303 | 0.21292 | 0.21261 | 0.21242 | 0.21124 | 0.20852 | 0.20686 | 0.20481 | 0.20026 | 0.19525 | 0.17903 | 0.12243 | 0.10021 | 0.09147
CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | 8.9107 | 8.3052 | 7.7123 | 6.993 | 4.8866 | 2.5379 | -0.098905 | -2.4018 | -3.4236 | -4.5296 | -8.2392 | -13.3286 | -14.7523 | -16.0283 | 13.0083 | 12.8558 | 12.4687 | 11.9261 | 10.8243 | 9.5459 | 8.4924 | 7.459 | 6.8526 | 6.1053 | 3.5134 | -0.59151 | -2.7591 | -5.2858 | 9.9443 | 9.4006 | 8.8362 | 8.1451 | 6.2315 | 4.0903 | 1.6761 | -0.39371 | -1.3477 | -2.393 | -5.9889 | -10.9146 | -12.0522 | -12.8974
| CLAYHILLS | CT |  |  | 8.9389 | 8.4513 | 7.92 | 7.2954 | 5.2099 | 2.7718 | 1.1917 | 0.16952 | -0.9678 | -2.3703 | -6.4415 | -12.5547 | -14.7523 | -16.0283 | 13.0083 | 12.8558 | 12.4687 | 11.9261 | 10.8243 | 9.5459 | 8.4924 | 7.856 | 7.1629 | 6.3001 | 3.6648 | -0.59151 | -2.7591 | -5.2858 | 9.9741 | 9.5109 | 8.991 | 8.3717 | 6.4671 | 4.2421 | 2.6999 | 1.7472 | 0.69675 | -0.61165 | -4.4512 | -10.1273 | -11.9267 | -12.8974
| CLAYHILLS | LW |  |  | 8.9107 | 8.3052 | 7.7123 | 6.993 | 4.8866 | 2.5379 | -0.098905 | -2.4018 | -3.4236 | -4.5296 | -8.2392 | -13.3286 | -14.7334 | -15.7942 | 13.0725 | 12.9336 | 12.5863 | 12.0883 | 11.0534 | 9.872 | 8.5101 | 7.459 | 6.8526 | 6.1053 | 3.5134 | 0.06854 | -0.59157 | -1.0882 | 9.9443 | 9.4006 | 8.8362 | 8.1451 | 6.2315 | 4.0903 | 1.6761 | -0.39371 | -1.3477 | -2.393 | -5.9889 | -10.9146 | -12.0522 | -12.8632
| CLAYHILLS | ST |  |  | 9.741 | 9.5293 | 9.3704 | 9.2285 | 9.0695 | 8.8941 | 8.7127 | 8.5408 | 8.3981 | 8.0317 | 6.6459 | 1.9749 | -1.3549 | -3.3581 | 13.1608 | 13.1072 | 13.0475 | 12.9753 | 12.8916 | 12.8081 | 12.6983 | 12.5812 | 12.4116 | 12.0841 | 10.8364 | 6.9459 | 3.8876 | 1.0451 | 10.6859 | 10.4993 | 10.3607 | 10.2407 | 10.1 | 9.9316 | 9.754 | 9.5861 | 9.4399 | 9.0862 | 7.7267 | 3.1978 | 0.23835 | -1.3927
| CLAYHILLS | SP |  |  | 9.9001 | 9.7982 | 9.6539 | 9.4915 | 9.204 | 8.862 | 8.5748 | 8.311 | 8.0534 | 7.6639 | 6.3908 | 2.916 | -0.06146 | -1.0671 | 13.1608 | 13.1126 | 13.0557 | 12.9888 | 12.9137 | 12.8327 | 12.6948 | 12.4697 | 12.2267 | 11.8769 | 10.6472 | 7.1006 | 2.4874 | -2.8089 | 10.8335 | 10.7479 | 10.6231 | 10.4825 | 10.2224 | 9.9096 | 9.6419 | 9.3955 | 9.152 | 8.7879 | 7.6039 | 4.2504 | 1.4005 | 0.57693
DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | NO | 2.1318 | 2.1163 | 2.1014 | 2.0799 | 2.0361 | 1.9862 | 1.9341 | 1.8793 | 1.7927 | 1.7458 | 1.6202 | 1.531 | 1.4591 | 1.3745 | 2.1488 | 2.1398 | 2.1317 | 2.1225 | 2.1027 | 2.0834 | 2.0603 | 2.0328 | 1.9965 | 1.9723 | 1.8722 | 1.8364 | 1.7924 | 1.7419 | 2.0796 | 2.0689 | 2.0619 | 2.0511 | 2.0392 | 2.0263 | 1.9823 | 1.9361 | 1.8628 | 1.8089 | 1.6696 | 1.5484 | 1.4539 | 1.378
| COLDBACKIE | CT |  |  | 2.1439 | 2.1388 | 2.1295 | 2.1097 | 2.0635 | 2.0262 | 1.9627 | 1.8923 | 1.8181 | 1.7861 | 1.6829 | 1.5873 | 1.588 | 1.5823 | 2.1524 | 2.1456 | 2.1381 | 2.1265 | 2.1043 | 2.0855 | 2.0603 | 2.0357 | 2.0095 | 1.9905 | 1.9053 | 1.8448 | 1.8425 | 1.8385 | 2.0796 | 2.0689 | 2.0619 | 2.0511 | 2.0392 | 2.0339 | 2.0002 | 1.9475 | 1.8828 | 1.8486 | 1.7309 | 1.6153 | 1.6092 | 1.6033
| COLDBACKIE | LW |  |  | 2.1318 | 2.1163 | 2.1014 | 2.0799 | 2.0361 | 1.9862 | 1.9341 | 1.8793 | 1.7927 | 1.7458 | 1.6202 | 1.531 | 1.5525 | 1.5433 | 2.1488 | 2.1398 | 2.1317 | 2.1225 | 2.1027 | 2.0834 | 2.0621 | 2.0328 | 1.9965 | 1.9723 | 1.8722 | 1.8364 | 1.844 | 1.8401 | 2.0856 | 2.0697 | 2.0633 | 2.0536 | 2.0476 | 2.0263 | 1.9823 | 1.9361 | 1.8628 | 1.8089 | 1.6696 | 1.5484 | 1.5615 | 1.5564
| COLDBACKIE | ST |  |  | 2.1447 | 2.1356 | 2.1299 | 2.1253 | 2.1164 | 2.1131 | 2.1037 | 2.0942 | 2.0757 | 2.042 | 1.9477 | 1.6763 | 1.5429 | 1.5216 | 2.1542 | 2.148 | 2.1432 | 2.1385 | 2.1334 | 2.1293 | 2.1247 | 2.1167 | 2.1091 | 2.0951 | 2.0524 | 1.9045 | 1.8155 | 1.8076 | 2.0869 | 2.0773 | 2.0718 | 2.0681 | 2.0591 | 2.0564 | 2.0485 | 2.0393 | 2.0306 | 2.0156 | 1.9073 | 1.6497 | 1.5246 | 1.506
| COLDBACKIE | SP |  |  | 2.1476 | 2.1398 | 2.1361 | 2.1339 | 2.116 | 2.1053 | 2.088 | 2.0694 | 2.0472 | 2.0084 | 1.9069 | 1.6734 | 1.4591 | 1.3745 | 2.1549 | 2.149 | 2.1452 | 2.1426 | 2.1358 | 2.1302 | 2.1232 | 2.116 | 2.1047 | 2.0918 | 2.049 | 1.952 | 1.7924 | 1.7419 | 2.0869 | 2.0774 | 2.0721 | 2.069 | 2.0605 | 2.0581 | 2.0505 | 2.0427 | 2.0338 | 2.0085 | 1.9145 | 1.672 | 1.4539 | 1.378
DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | 0.46546 | 0.46706 | 0.46721 | 0.46042 | 0.45093 | 0.44179 | 0.42822 | 0.41271 | 0.39652 | 0.38953 | 0.35431 | 0.34719 | 0.34481 | 0.34015 | 0.45777 | 0.4586 | 0.4584 | 0.45439 | 0.44898 | 0.4436 | 0.43619 | 0.42838 | 0.4209 | 0.41649 | 0.38603 | 0.38269 | 0.37939 | 0.37551 | 0.44213 | 0.44419 | 0.44402 | 0.43886 | 0.42895 | 0.41969 | 0.40478 | 0.38912 | 0.37453 | 0.36792 | 0.33181 | 0.32567 | 0.32334 | 0.31931
| COLINTRAIVE | CT |  |  | 0.46814 | 0.46877 | 0.46735 | 0.46042 | 0.45093 | 0.44179 | 0.42822 | 0.41271 | 0.39652 | 0.38953 | 0.35714 | 0.34719 | 0.35883 | 0.36248 | 0.45913 | 0.45959 | 0.4584 | 0.45439 | 0.44898 | 0.4436 | 0.43619 | 0.42838 | 0.4209 | 0.41649 | 0.3909 | 0.38269 | 0.38615 | 0.38613 | 0.44539 | 0.44533 | 0.44402 | 0.43886 | 0.42895 | 0.41969 | 0.40478 | 0.38912 | 0.37453 | 0.36792 | 0.33549 | 0.32567 | 0.33593 | 0.33919
| COLINTRAIVE | LW |  |  | 0.46546 | 0.46804 | 0.46722 | 0.46523 | 0.45741 | 0.45113 | 0.44267 | 0.43069 | 0.40832 | 0.39857 | 0.35431 | 0.35093 | 0.35683 | 0.3508 | 0.45777 | 0.45893 | 0.4584 | 0.45722 | 0.45297 | 0.4496 | 0.44471 | 0.43743 | 0.42587 | 0.41895 | 0.38603 | 0.38378 | 0.38589 | 0.38361 | 0.44213 | 0.44521 | 0.44432 | 0.44227 | 0.4336 | 0.42643 | 0.41766 | 0.40623 | 0.38496 | 0.37566 | 0.33181 | 0.32864 | 0.33388 | 0.32865
| COLINTRAIVE | ST |  |  | 0.46762 | 0.46706 | 0.46721 | 0.46607 | 0.46605 | 0.46569 | 0.46464 | 0.46458 | 0.46055 | 0.45678 | 0.43927 | 0.39469 | 0.39498 | 0.39519 | 0.45904 | 0.4586 | 0.45859 | 0.45778 | 0.45744 | 0.45692 | 0.45596 | 0.45555 | 0.45275 | 0.45011 | 0.43745 | 0.40312 | 0.40107 | 0.39936 | 0.44468 | 0.44419 | 0.44432 | 0.44345 | 0.44378 | 0.4437 | 0.443 | 0.44277 | 0.4388 | 0.4352 | 0.41786 | 0.3734 | 0.37206 | 0.37129
| COLINTRAIVE | SP |  |  | 0.46804 | 0.46813 | 0.46803 | 0.46827 | 0.46607 | 0.46417 | 0.46107 | 0.4583 | 0.45291 | 0.4448 | 0.42496 | 0.36932 | 0.34481 | 0.34015 | 0.45922 | 0.45917 | 0.45895 | 0.45892 | 0.45767 | 0.45657 | 0.45473 | 0.45313 | 0.44985 | 0.4451 | 0.43351 | 0.39711 | 0.37939 | 0.37551 | 0.44512 | 0.44514 | 0.44517 | 0.44542 | 0.44271 | 0.44034 | 0.43689 | 0.43357 | 0.42812 | 0.41966 | 0.40011 | 0.3468 | 0.32334 | 0.31931
STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | 0.67472 | 0.67523 | 0.65044 | 0.61542 | 0.42346 | 0.13997 | -0.13714 | -0.41398 | -0.68403 | -0.8075 | -1.3711 | -1.5004 | -1.4914 | -1.6195 | 1.308 | 1.3013 | 1.2687 | 1.2234 | 1.1187 | 0.991 | 0.85623 | 0.70883 | 0.54834 | 0.4513 | 0.0298 | -0.062423 | -0.083624 | -0.18104 | 0.53842 | 0.54141 | 0.48124 | 0.3991 | 0.17872 | -0.053649 | -0.32485 | -0.60533 | -0.89192 | -1.0344 | -1.5975 | -1.7105 | -1.6993 | -1.8149
| COLL | CT |  |  | 0.70436 | 0.70515 | 0.68194 | 0.63246 | 0.54453 | 0.39181 | 0.15142 | -0.11046 | -0.35717 | -0.46014 | -0.93482 | -1.2858 | -1.2617 | -1.2808 | 1.3433 | 1.3401 | 1.3113 | 1.2537 | 1.1454 | 1.0448 | 0.9486 | 0.82908 | 0.7118 | 0.62716 | 0.22807 | 0.012801 | 0.0034637 | -0.030272 | 0.60098 | 0.59943 | 0.58262 | 0.53376 | 0.30843 | 0.10237 | -0.086974 | -0.32087 | -0.5599 | -0.6854 | -1.2065 | -1.5149 | -1.4869 | -1.5017
| COLL | LW |  |  | 0.67472 | 0.67523 | 0.65044 | 0.61542 | 0.42346 | 0.13997 | -0.13714 | -0.41398 | -0.68403 | -0.8075 | -1.3711 | -1.5004 | -1.3466 | -1.4052 | 1.308 | 1.3013 | 1.2687 | 1.2234 | 1.1187 | 0.991 | 0.85623 | 0.70883 | 0.54834 | 0.4513 | 0.0298 | -0.062423 | -0.0061992 | -0.028064 | 0.53842 | 0.54141 | 0.48124 | 0.3991 | 0.17872 | -0.053649 | -0.32485 | -0.60533 | -0.89192 | -1.0344 | -1.5975 | -1.7105 | -1.5681 | -1.6227
| COLL | ST |  |  | 0.70368 | 0.69868 | 0.69427 | 0.68532 | 0.6827 | 0.67714 | 0.67064 | 0.6634 | 0.65186 | 0.62553 | 0.53386 | -0.21288 | -0.44944 | -0.57491 | 1.3464 | 1.3362 | 1.3264 | 1.3119 | 1.2981 | 1.2808 | 1.2611 | 1.2356 | 1.2081 | 1.1559 | 0.9639 | 0.35927 | 0.25356 | 0.20133 | 0.60239 | 0.59217 | 0.5817 | 0.57006 | 0.55484 | 0.53584 | 0.5103 | 0.47987 | 0.4401 | 0.36166 | 0.088966 | -0.68647 | -0.86337 | -0.9477
| COLL | SP |  |  | 0.70553 | 0.70187 | 0.70031 | 0.69759 | 0.67229 | 0.64786 | 0.61201 | 0.4914 | 0.36569 | 0.17704 | -0.20144 | -0.96452 | -1.4914 | -1.6195 | 1.3422 | 1.3336 | 1.3257 | 1.3155 | 1.2795 | 1.2419 | 1.1979 | 1.1461 | 1.0817 | 0.99406 | 0.79241 | 0.3211 | -0.083624 | -0.18104 | 0.59723 | 0.58764 | 0.57851 | 0.56738 | 0.50178 | 0.42156 | 0.32984 | 0.23419 | 0.12706 | -0.029339 | -0.41083 | -1.1999 | -1.6993 | -1.8149
CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | 10.6643 | 10.2101 | 10.0205 | 9.9028 | 9.3531 | 8.9305 | 8.6139 | 8.2969 | 8.056 | 7.5039 | 5.3518 | 2.9861 | 2.578 | 1.9079 | 12.6386 | 12.4994 | 12.4114 | 12.3084 | 12.0767 | 11.8248 | 11.6289 | 11.4225 | 11.1441 | 10.6584 | 8.9891 | 7.1557 | 6.7766 | 6.2673 | 10.9198 | 10.3939 | 10.2195 | 10.1024 | 9.6015 | 9.2054 | 8.9066 | 8.6059 | 8.3668 | 8.1 | 6.1286 | 3.8559 | 3.471 | 2.841
| COMMERCE STREET | CT |  |  | 10.6643 | 10.4492 | 10.3957 | 10.2673 | 9.8899 | 9.429 | 9.1368 | 8.7145 | 8.1766 | 7.5735 | 5.9153 | 3.9097 | 3.5594 | 3.3114 | 12.6386 | 12.5056 | 12.4352 | 12.3346 | 12.1104 | 11.8583 | 11.6778 | 11.4613 | 11.1441 | 10.6859 | 9.4087 | 7.8715 | 7.612 | 7.4247 | 10.9563 | 10.5952 | 10.5566 | 10.5178 | 10.0579 | 9.6275 | 9.3512 | 9.1175 | 8.841 | 8.2606 | 6.6659 | 4.7444 | 4.423 | 4.2007
| COMMERCE STREET | LW |  |  | 10.6882 | 10.2101 | 10.0205 | 9.9028 | 9.3531 | 8.9305 | 8.6139 | 8.2969 | 8.056 | 7.5039 | 5.3518 | 2.9861 | 2.741 | 2.5139 | 12.6527 | 12.4994 | 12.4114 | 12.3084 | 12.0767 | 11.8248 | 11.6289 | 11.4225 | 11.1711 | 10.6584 | 8.9891 | 7.1557 | 6.9742 | 6.8113 | 10.9198 | 10.3939 | 10.2195 | 10.1024 | 9.6015 | 9.2054 | 8.9066 | 8.6059 | 8.3668 | 8.1 | 6.1286 | 3.8559 | 3.6338 | 3.4308
| COMMERCE STREET | ST |  |  | 10.7983 | 10.7428 | 10.6809 | 10.6061 | 10.5299 | 10.354 | 10.174 | 10.0092 | 9.9597 | 9.8124 | 8.5862 | 4.7158 | 2.578 | 1.9079 | 12.7372 | 12.6946 | 12.647 | 12.5887 | 12.5288 | 12.4537 | 12.3712 | 12.281 | 12.2032 | 12.0708 | 11.4331 | 8.4306 | 6.7766 | 6.2673 | 11.166 | 11.0718 | 10.9693 | 10.8253 | 10.6709 | 10.5111 | 10.3466 | 10.1934 | 10.1387 | 9.9924 | 9.2369 | 5.5167 | 3.471 | 2.841
| COMMERCE STREET | SP |  |  | 10.8302 | 10.7977 | 10.7647 | 10.7213 | 10.6749 | 10.6013 | 10.5416 | 10.4635 | 10.3791 | 10.2599 | 9.667 | 6.9566 | 4.0966 | 3.0401 | 12.7592 | 12.7334 | 12.7061 | 12.6701 | 12.6304 | 12.5706 | 12.5205 | 12.4566 | 12.3868 | 12.2921 | 11.9197 | 10.1867 | 7.9714 | 7.1456 | 11.2495 | 11.2144 | 11.1649 | 11.1072 | 11.0136 | 10.88 | 10.7823 | 10.678 | 10.5705 | 10.409 | 9.8544 | 7.6816 | 4.9438 | 3.943
ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487
| COMRIE | CT |  |  | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487
| COMRIE | LW |  |  | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487
| COMRIE | ST |  |  | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487
| COMRIE | SP |  |  | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.040926 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.041924 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487 | 0.039487
TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | 2.2565 | 2.2336 | 2.1908 | 2.1328 | 1.9958 | 1.8357 | 1.6793 | 1.5288 | 1.364 | 1.2596 | 0.93714 | 0.8801 | 0.95804 | 0.88813 | 2.9435 | 2.9274 | 2.9024 | 2.8674 | 2.797 | 2.718 | 2.6406 | 2.5615 | 2.4761 | 2.4025 | 2.1698 | 2.1208 | 2.1412 | 2.0817 | 2.791 | 2.7891 | 2.7734 | 2.7186 | 2.5804 | 2.4316 | 2.2908 | 2.1546 | 2.0052 | 1.9064 | 1.5995 | 1.5444 | 1.6132 | 1.5582
| CONNEL | CT |  |  | 2.2906 | 2.2763 | 2.243 | 2.1852 | 2.0458 | 1.917 | 1.7828 | 1.6422 | 1.5067 | 1.4271 | 1.1009 | 0.96487 | 0.98152 | 0.9729 | 2.9492 | 2.9399 | 2.9175 | 2.8784 | 2.8054 | 2.7353 | 2.6662 | 2.601 | 2.5355 | 2.4824 | 2.235 | 2.15 | 2.1412 | 2.1187 | 2.7917 | 2.7898 | 2.7791 | 2.7545 | 2.6393 | 2.5115 | 2.3799 | 2.2546 | 2.133 | 2.0585 | 1.7459 | 1.6209 | 1.6358 | 1.6288
| CONNEL | LW |  |  | 2.2565 | 2.2336 | 2.1908 | 2.1328 | 1.9958 | 1.8357 | 1.6793 | 1.5288 | 1.364 | 1.2596 | 0.93714 | 0.8801 | 0.95804 | 0.93111 | 2.9435 | 2.9274 | 2.9024 | 2.8674 | 2.797 | 2.718 | 2.6406 | 2.5615 | 2.4761 | 2.4025 | 2.1698 | 2.1208 | 2.1457 | 2.1357 | 2.791 | 2.7891 | 2.7734 | 2.7186 | 2.5804 | 2.4316 | 2.2908 | 2.1546 | 2.0052 | 1.9064 | 1.5995 | 1.5444 | 1.6132 | 1.5902
| CONNEL | ST |  |  | 2.298 | 2.2831 | 2.2685 | 2.2526 | 2.237 | 2.2191 | 2.1951 | 2.1725 | 2.1434 | 2.0951 | 1.9151 | 1.4793 | 1.3711 | 1.3244 | 2.9595 | 2.9553 | 2.9466 | 2.9352 | 2.9237 | 2.9111 | 2.8939 | 2.8777 | 2.8581 | 2.8267 | 2.7045 | 2.3911 | 2.3186 | 2.2799 | 2.7928 | 2.7912 | 2.7897 | 2.788 | 2.7866 | 2.7835 | 2.7766 | 2.7695 | 2.7445 | 2.6995 | 2.5334 | 2.1343 | 2.0258 | 1.9798
| CONNEL | SP |  |  | 2.2966 | 2.2847 | 2.2744 | 2.2628 | 2.2229 | 2.1837 | 2.1414 | 2.0923 | 2.0403 | 1.9722 | 1.7753 | 1.2542 | 0.98455 | 0.88813 | 2.9591 | 2.9542 | 2.947 | 2.9386 | 2.9179 | 2.8971 | 2.8746 | 2.8471 | 2.8171 | 2.7806 | 2.673 | 2.3454 | 2.1571 | 2.0817 | 2.7927 | 2.7915 | 2.7903 | 2.7891 | 2.7865 | 2.772 | 2.7312 | 2.6844 | 2.6349 | 2.567 | 2.3802 | 1.8953 | 1.6436 | 1.5582
BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | YES | 1.7812 | 1.6846 | 1.5594 | 1.3101 | 1.0568 | 0.77609 | 0.47194 | 0.11683 | -0.4282 | -0.8839 | -1.8829 | -2.7539 | -3.2329 | -3.416 | 3.0939 | 3.0238 | 2.9439 | 2.7851 | 2.6499 | 2.5026 | 2.3267 | 2.1099 | 1.814 | 1.4965 | 0.86834 | 0.45144 | 0.20652 | 0.016283 | 1.3951 | 1.3214 | 1.2208 | 1.0295 | 0.80377 | 0.54991 | 0.27284 | -0.05092 | -0.53384 | -0.95991 | -1.8846 | -2.6488 | -3.0676 | -3.2276
| CONON BRIDGE | CT |  |  | 1.8486 | 1.7653 | 1.6575 | 1.4077 | 1.1685 | 0.9463 | 0.60391 | 0.21955 | -0.19691 | -0.54063 | -1.7626 | -2.7539 | -3.2329 | -3.416 | 3.1066 | 3.0375 | 2.9574 | 2.7851 | 2.6499 | 2.5257 | 2.3576 | 2.1667 | 1.9579 | 1.7481 | 0.93061 | 0.45144 | 0.20652 | 0.016283 | 1.4523 | 1.39 | 1.3037 | 1.1089 | 0.89447 | 0.69438 | 0.38861 | 0.047212 | -0.31344 | -0.62653 | -1.7672 | -2.6488 | -3.0676 | -3.2276
| CONON BRIDGE | LW |  |  | 1.7812 | 1.6846 | 1.5594 | 1.3101 | 1.0568 | 0.77609 | 0.47194 | 0.11683 | -0.4282 | -0.8839 | -1.8829 | -2.5572 | -2.8345 | -2.9707 | 3.0939 | 3.0238 | 2.9439 | 2.7884 | 2.6566 | 2.5026 | 2.3267 | 2.1099 | 1.814 | 1.4965 | 0.86834 | 0.56352 | 0.46438 | 0.41544 | 1.3951 | 1.3214 | 1.2208 | 1.0295 | 0.80377 | 0.54991 | 0.27284 | -0.05092 | -0.53384 | -0.95991 | -1.8846 | -2.4831 | -2.7244 | -2.8432
| CONON BRIDGE | ST |  |  | 1.8516 | 1.7582 | 1.6679 | 1.4846 | 1.4435 | 1.3896 | 1.3377 | 1.2742 | 1.1409 | 1.0043 | 0.51617 | -0.69879 | -1.179 | -1.4762 | 3.1279 | 3.07 | 3.0114 | 2.8954 | 2.8609 | 2.8146 | 2.7708 | 2.7184 | 2.6288 | 2.5349 | 2.1692 | 1.2244 | 0.93664 | 0.6989 | 1.4591 | 1.3909 | 1.3232 | 1.1936 | 1.1595 | 1.1112 | 1.0653 | 1.011 | 0.90327 | 0.78104 | 0.32475 | -0.83258 | -1.2615 | -1.5233
| CONON BRIDGE | SP |  |  | 1.8587 | 1.7711 | 1.6923 | 1.5094 | 1.4244 | 1.342 | 1.2471 | 1.1323 | 0.95803 | 0.79942 | 0.33252 | -0.93331 | -1.6 | -1.8071 | 3.1291 | 3.0745 | 3.0229 | 2.9095 | 2.8622 | 2.8125 | 2.7551 | 2.6849 | 2.5728 | 2.4785 | 2.1887 | 1.2585 | 0.6718 | 0.30908 | 1.4652 | 1.4024 | 1.3455 | 1.2169 | 1.1449 | 1.073 | 0.98964 | 0.89054 | 0.7453 | 0.60579 | 0.18453 | -1.0059 | -1.6327 | -1.8169
GRUDIE BRIDGE | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | 0.22437 | 0.22328 | 0.22202 | 0.21907 | 0.20447 | 0.18945 | 0.17255 | 0.15237 | 0.12541 | 0.10919 | 0.047437 | 0.033421 | 0.038363 | 0.019888 | 0.27014 | 0.26879 | 0.2665 | 0.26375 | 0.25631 | 0.24973 | 0.24045 | 0.231 | 0.21814 | 0.20748 | 0.16415 | 0.1579 | 0.15827 | 0.15 | 0.2092 | 0.20726 | 0.20309 | 0.19807 | 0.18522 | 0.17202 | 0.15655 | 0.13792 | 0.11349 | 0.097668 | 0.038671 | 0.026049 | 0.030526 | 0.014297
| CONON FALLS | CT |  |  | 0.22437 | 0.22328 | 0.22202 | 0.22017 | 0.21136 | 0.19767 | 0.1757 | 0.15237 | 0.13064 | 0.11768 | 0.065491 | 0.042109 | 0.039447 | 0.03638 | 0.2717 | 0.27058 | 0.26853 | 0.26448 | 0.25631 | 0.24973 | 0.24045 | 0.231 | 0.22172 | 0.21287 | 0.1742 | 0.16212 | 0.16043 | 0.15822 | 0.21393 | 0.21305 | 0.21019 | 0.2042 | 0.18983 | 0.17744 | 0.15814 | 0.13792 | 0.11887 | 0.10609 | 0.055368 | 0.034095 | 0.031763 | 0.029079
| CONON FALLS | LW |  |  | 0.22485 | 0.22397 | 0.22296 | 0.21907 | 0.20447 | 0.18945 | 0.17255 | 0.15448 | 0.12541 | 0.10919 | 0.047437 | 0.033421 | 0.04037 | 0.036983 | 0.27014 | 0.26879 | 0.2665 | 0.26375 | 0.25741 | 0.25089 | 0.24218 | 0.23202 | 0.21814 | 0.20748 | 0.16415 | 0.1579 | 0.16026 | 0.15913 | 0.2092 | 0.20726 | 0.20309 | 0.19807 | 0.18522 | 0.17202 | 0.15655 | 0.13964 | 0.11349 | 0.097668 | 0.038671 | 0.026049 | 0.032143 | 0.029179
| CONON FALLS | ST |  |  | 0.22552 | 0.22508 | 0.22453 | 0.22377 | 0.22307 | 0.22229 | 0.22124 | 0.21974 | 0.21636 | 0.20874 | 0.1795 | 0.11026 | 0.088064 | 0.07713 | 0.2724 | 0.2717 | 0.27067 | 0.26912 | 0.26796 | 0.26663 | 0.26454 | 0.26123 | 0.25812 | 0.25388 | 0.23505 | 0.18533 | 0.17623 | 0.17133 | 0.21384 | 0.21274 | 0.21132 | 0.20932 | 0.20779 | 0.20596 | 0.20322 | 0.19929 | 0.19428 | 0.18727 | 0.15984 | 0.093848 | 0.074211 | 0.064631
| CONON FALLS | SP |  |  | 0.22552 | 0.22526 | 0.2248 | 0.22435 | 0.22388 | 0.22325 | 0.22159 | 0.21681 | 0.21005 | 0.19994 | 0.16927 | 0.096877 | 0.038363 | 0.019888 | 0.27248 | 0.27211 | 0.27122 | 0.27064 | 0.26885 | 0.26691 | 0.26449 | 0.26241 | 0.25837 | 0.25229 | 0.23729 | 0.1959 | 0.15827 | 0.15 | 0.21421 | 0.21358 | 0.21254 | 0.21181 | 0.20816 | 0.20447 | 0.20013 | 0.19593 | 0.18951 | 0.17987 | 0.15221 | 0.085266 | 0.030526 | 0.014297
DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | 7.2391 | 6.5336 | 6.1237 | 5.8315 | 4.3313 | 2.8159 | 1.2601 | -0.42702 | -1.0798 | -1.7185 | -3.9898 | -7.4292 | -9.2934 | -10.5985 | 9.7413 | 9.4175 | 9.1773 | 8.9954 | 8.3781 | 7.7405 | 7.0801 | 6.3608 | 6.0087 | 5.6438 | 4.4022 | 1.828 | 0.040511 | -2.1418 | 7.4266 | 6.8137 | 6.4645 | 6.2258 | 4.9269 | 3.6188 | 2.285 | 0.84363 | 0.2561 | -0.3325 | -2.3608 | -5.3373 | -6.8497 | -7.8243
| CONSTABLE STREET | CT |  |  | 7.2812 | 6.8167 | 6.5915 | 6.4652 | 5.1116 | 3.5655 | 2.742 | 2.0655 | 1.2906 | 0.33765 | -2.6337 | -7.2797 | -9.2934 | -10.5985 | 9.7413 | 9.4651 | 9.2615 | 9.118 | 8.5027 | 7.8165 | 7.392 | 7.017 | 6.5935 | 6.0932 | 4.5381 | 1.828 | 0.040511 | -2.1418 | 7.4797 | 7.0591 | 6.8704 | 6.8197 | 5.6282 | 4.3055 | 3.6173 | 3.0274 | 2.3294 | 1.4783 | -1.1298 | -5.22 | -6.8497 | -7.8243
| CONSTABLE STREET | LW |  |  | 7.2391 | 6.5336 | 6.1237 | 5.8315 | 4.3313 | 2.8159 | 1.2601 | -0.42702 | -1.0798 | -1.7185 | -3.9898 | -7.4292 | -8.8819 | -10.0435 | 9.7509 | 9.4175 | 9.1773 | 8.9954 | 8.3781 | 7.7405 | 7.0801 | 6.3608 | 6.0087 | 5.6438 | 4.4022 | 2.6107 | 1.9224 | 1.3396 | 7.4266 | 6.8137 | 6.4645 | 6.2258 | 4.9269 | 3.6188 | 2.285 | 0.84363 | 0.2561 | -0.3325 | -2.3608 | -5.3373 | -6.4643 | -7.312
| CONSTABLE STREET | ST |  |  | 7.4265 | 7.304 | 7.1463 | 7.0511 | 7.009 | 6.8808 | 6.7635 | 6.5756 | 6.5044 | 6.2804 | 5.4445 | 2.4961 | 0.1357 | -1.7038 | 9.9381 | 9.8008 | 9.6345 | 9.4964 | 9.3913 | 9.2815 | 9.1698 | 9.0354 | 8.9404 | 8.7735 | 8.1479 | 6.006 | 3.9239 | 1.5734 | 7.8543 | 7.704 | 7.5272 | 7.3743 | 7.2528 | 7.1379 | 7.0424 | 6.9154 | 6.9103 | 6.7674 | 6.2685 | 3.9385 | 1.9244 | 0.44759
| CONSTABLE STREET | SP |  |  | 7.4752 | 7.3797 | 7.2261 | 7.1394 | 7.1016 | 7.0548 | 7.0014 | 6.9269 | 6.7613 | 6.5041 | 5.6212 | 3.085 | 0.84339 | -0.27554 | 9.9867 | 9.8806 | 9.7364 | 9.631 | 9.5223 | 9.3894 | 9.264 | 9.1296 | 8.9815 | 8.7705 | 8.0084 | 5.7756 | 2.5974 | -1.7751 | 7.981 | 7.9078 | 7.7955 | 7.7236 | 7.5993 | 7.4422 | 7.3314 | 7.2252 | 7.1277 | 6.9457 | 6.33 | 4.4406 | 2.5675 | 1.6978
ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426
| CONTULLICH | CT |  |  | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426
| CONTULLICH | LW |  |  | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426
| CONTULLICH | ST |  |  | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426
| CONTULLICH | SP |  |  | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.0928 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426 | 0.088426
FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | 1.8232 | 1.8143 | 1.79 | 1.7501 | 1.6607 | 1.5633 | 1.4711 | 1.3743 | 1.2607 | 1.182 | 0.94927 | 0.89225 | 0.92625 | 0.90487 | 1.7164 | 1.7088 | 1.6954 | 1.6724 | 1.63 | 1.5817 | 1.5357 | 1.4853 | 1.4284 | 1.3763 | 1.2217 | 1.1855 | 1.186 | 1.1735 | 1.5897 | 1.5807 | 1.5604 | 1.5271 | 1.4578 | 1.3811 | 1.3072 | 1.2281 | 1.1369 | 1.0656 | 0.8549 | 0.80476 | 0.8334 | 0.81658
| CORRAN | CT |  |  | 1.8413 | 1.8337 | 1.8149 | 1.7764 | 1.6907 | 1.5994 | 1.5086 | 1.4125 | 1.3203 | 1.2627 | 1.0212 | 0.92317 | 0.92867 | 0.92082 | 1.722 | 1.7141 | 1.7009 | 1.6751 | 1.63 | 1.5833 | 1.5425 | 1.4981 | 1.4545 | 1.4178 | 1.2483 | 1.191 | 1.186 | 1.1735 | 1.6049 | 1.597 | 1.579 | 1.5424 | 1.4704 | 1.398 | 1.3287 | 1.2544 | 1.183 | 1.1326 | 0.90623 | 0.83012 | 0.83762 | 0.83349
| CORRAN | LW |  |  | 1.8232 | 1.8143 | 1.79 | 1.7501 | 1.6607 | 1.5633 | 1.4711 | 1.3743 | 1.2607 | 1.182 | 0.94927 | 0.89225 | 0.92625 | 0.90487 | 1.7164 | 1.7088 | 1.6954 | 1.6724 | 1.63 | 1.5817 | 1.5357 | 1.4853 | 1.4284 | 1.3763 | 1.2217 | 1.1855 | 1.1952 | 1.1863 | 1.5897 | 1.5807 | 1.5604 | 1.5271 | 1.4578 | 1.3811 | 1.3072 | 1.2281 | 1.1369 | 1.0656 | 0.8549 | 0.80476 | 0.8334 | 0.81658
| CORRAN | ST |  |  | 1.848 | 1.8422 | 1.836 | 1.8282 | 1.8212 | 1.8127 | 1.8009 | 1.7899 | 1.772 | 1.7352 | 1.6073 | 1.282 | 1.1676 | 1.116 | 1.7304 | 1.7263 | 1.7218 | 1.7159 | 1.7099 | 1.703 | 1.6937 | 1.6847 | 1.6724 | 1.6496 | 1.5669 | 1.3376 | 1.2695 | 1.2359 | 1.6123 | 1.6068 | 1.6009 | 1.5933 | 1.5864 | 1.5781 | 1.5666 | 1.5558 | 1.5393 | 1.5074 | 1.3951 | 1.0967 | 1.0107 | 0.97371
| CORRAN | SP |  |  | 1.8478 | 1.8442 | 1.8413 | 1.8378 | 1.8193 | 1.7992 | 1.7738 | 1.7462 | 1.7147 | 1.6692 | 1.5409 | 1.2152 | 0.98635 | 0.90676 | 1.7292 | 1.7265 | 1.7239 | 1.7208 | 1.7109 | 1.7008 | 1.6888 | 1.6755 | 1.6592 | 1.6374 | 1.5733 | 1.3833 | 1.2318 | 1.1803 | 1.6118 | 1.6084 | 1.6055 | 1.6021 | 1.5853 | 1.5687 | 1.5491 | 1.5277 | 1.5023 | 1.4667 | 1.3651 | 1.088 | 0.88719 | 0.82183
KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | 1.6206 | 1.6203 | 1.6187 | 1.6157 | 1.5685 | 1.4781 | 1.3893 | 1.2816 | 1.1039 | 1.0071 | 0.67194 | 0.5962 | 0.63036 | 0.52275 | 1.5784 | 1.5764 | 1.5658 | 1.5521 | 1.5109 | 1.4676 | 1.421 | 1.3634 | 1.2995 | 1.2601 | 1.1252 | 1.0838 | 1.0929 | 1.0382 | 1.4213 | 1.4155 | 1.3906 | 1.3612 | 1.2783 | 1.1907 | 1.0913 | 0.97799 | 0.81304 | 0.71775 | 0.35774 | 0.29574 | 0.32281 | 0.24533
| COSHIEVILLE | CT |  |  | 1.6217 | 1.621 | 1.6192 | 1.6157 | 1.6082 | 1.5261 | 1.4061 | 1.2816 | 1.1404 | 1.0531 | 0.75505 | 0.62194 | 0.63789 | 0.63112 | 1.5911 | 1.5893 | 1.5799 | 1.5622 | 1.5179 | 1.4773 | 1.421 | 1.3634 | 1.3075 | 1.2719 | 1.1535 | 1.0912 | 1.0929 | 1.0819 | 1.4465 | 1.4416 | 1.4212 | 1.3828 | 1.2878 | 1.205 | 1.0913 | 0.97799 | 0.86541 | 0.77511 | 0.44428 | 0.3218 | 0.3283 | 0.32174
| COSHIEVILLE | LW |  |  | 1.6206 | 1.6203 | 1.6187 | 1.6166 | 1.5685 | 1.4781 | 1.3893 | 1.2941 | 1.1039 | 1.0071 | 0.67194 | 0.5962 | 0.6513 | 0.62033 | 1.5784 | 1.5764 | 1.5658 | 1.5521 | 1.5109 | 1.4676 | 1.4227 | 1.3744 | 1.2995 | 1.2601 | 1.1252 | 1.0838 | 1.1036 | 1.0911 | 1.4213 | 1.4155 | 1.3906 | 1.3612 | 1.2783 | 1.1907 | 1.0919 | 0.98042 | 0.81304 | 0.71775 | 0.35774 | 0.29574 | 0.33278 | 0.31186
| COSHIEVILLE | ST |  |  | 1.6218 | 1.6214 | 1.621 | 1.6201 | 1.6188 | 1.6173 | 1.6157 | 1.6135 | 1.6107 | 1.6064 | 1.4486 | 1.0032 | 0.9199 | 0.87701 | 1.5899 | 1.5869 | 1.5839 | 1.5797 | 1.5755 | 1.5704 | 1.5643 | 1.5563 | 1.5423 | 1.521 | 1.4526 | 1.2858 | 1.2302 | 1.1966 | 1.4425 | 1.4372 | 1.4314 | 1.4206 | 1.4108 | 1.3977 | 1.3823 | 1.3599 | 1.3285 | 1.2802 | 1.1162 | 0.67507 | 0.58644 | 0.54089
| COSHIEVILLE | SP |  |  | 1.6226 | 1.6226 | 1.6224 | 1.6222 | 1.6201 | 1.6177 | 1.6152 | 1.6125 | 1.5895 | 1.5396 | 1.3747 | 0.93971 | 0.63036 | 0.52275 | 1.5932 | 1.5917 | 1.5899 | 1.5879 | 1.5758 | 1.5634 | 1.5494 | 1.5348 | 1.5163 | 1.4912 | 1.4136 | 1.2291 | 1.0952 | 1.0382 | 1.4516 | 1.4495 | 1.4457 | 1.4411 | 1.4175 | 1.3902 | 1.3597 | 1.3288 | 1.2852 | 1.2311 | 1.0587 | 0.63245 | 0.32281 | 0.24533
COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | YES | 1.5768 | 1.5719 | 1.5354 | 1.491 | 1.3173 | 1.1173 | 0.85793 | 0.55067 | 0.13944 | -0.20318 | -1.5712 | -2.9894 | -3.5429 | -3.7449 | 2.387 | 2.3743 | 2.3426 | 2.2907 | 2.196 | 2.1025 | 1.9527 | 1.8056 | 1.5899 | 1.368 | 0.45089 | -0.301 | -0.5637 | -0.74098 | 1.3605 | 1.3503 | 1.315 | 1.2743 | 1.131 | 0.94954 | 0.71024 | 0.42591 | 0.042692 | -0.28858 | -1.5884 | -2.8425 | -3.3108 | -3.48
| COUPAR ANGUS | CT |  |  | 1.6122 | 1.6111 | 1.5802 | 1.5383 | 1.3664 | 1.184 | 0.86902 | 0.55067 | 0.22302 | -0.089384 | -1.5295 | -2.9894 | -3.5429 | -3.7449 | 2.3898 | 2.3758 | 2.3426 | 2.2907 | 2.196 | 2.1025 | 1.9527 | 1.8056 | 1.6545 | 1.4792 | 0.52714 | -0.301 | -0.5637 | -0.74098 | 1.3875 | 1.3805 | 1.3484 | 1.2996 | 1.1571 | 0.98966 | 0.71024 | 0.42591 | 0.13316 | -0.15709 | -1.521 | -2.8425 | -3.3108 | -3.48
| COUPAR ANGUS | LW |  |  | 1.5768 | 1.5719 | 1.5354 | 1.491 | 1.3173 | 1.1173 | 0.85793 | 0.56928 | 0.13944 | -0.20318 | -1.5712 | -2.7335 | -3.0822 | -3.2174 | 2.387 | 2.3743 | 2.3438 | 2.3087 | 2.2281 | 2.1323 | 1.9908 | 1.8166 | 1.5899 | 1.368 | 0.45089 | -0.23672 | -0.34344 | -0.387 | 1.3605 | 1.3503 | 1.315 | 1.2743 | 1.131 | 0.94954 | 0.71372 | 0.44036 | 0.042692 | -0.28858 | -1.5884 | -2.6501 | -2.9418 | -3.0545
| COUPAR ANGUS | ST |  |  | 1.6178 | 1.6048 | 1.5786 | 1.5615 | 1.5343 | 1.503 | 1.4158 | 1.3551 | 1.2744 | 1.1527 | 0.32914 | -1.0226 | -1.5524 | -1.8047 | 2.4049 | 2.3946 | 2.3735 | 2.351 | 2.3237 | 2.294 | 2.2223 | 2.1695 | 2.1105 | 2.0229 | 1.3944 | 0.39108 | 0.069731 | -0.12194 | 1.393 | 1.3816 | 1.359 | 1.3379 | 1.3093 | 1.2774 | 1.2023 | 1.146 | 1.0763 | 0.9706 | 0.18505 | -1.0979 | -1.5893 | -1.8257
| COUPAR ANGUS | SP |  |  | 1.632 | 1.6245 | 1.6028 | 1.5873 | 1.5372 | 1.4873 | 1.3784 | 1.2938 | 1.2 | 1.0788 | 0.28207 | -0.91809 | -1.5384 | -1.7232 | 2.4099 | 2.4058 | 2.3854 | 2.3727 | 2.3447 | 2.3152 | 2.2431 | 2.1889 | 2.1212 | 2.0412 | 1.4761 | 0.56005 | 0.034426 | -0.28447 | 1.4045 | 1.3967 | 1.3765 | 1.3614 | 1.3205 | 1.2791 | 1.1927 | 1.1223 | 1.0377 | 0.92532 | 0.18683 | -0.99209 | -1.5745 | -1.7446
CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | 16.7978 | 16.5167 | 16.3009 | 16.1272 | 15.7147 | 15.2819 | 14.8608 | 14.4751 | 14.0574 | 13.5987 | 12.2086 | 10.1063 | 8.7367 | 8.0058 | 17.9292 | 17.7935 | 17.6717 | 17.5514 | 17.3335 | 17.0841 | 16.8295 | 16.6058 | 16.3766 | 16.0789 | 15.1588 | 14.0147 | 13.2533 | 12.5822 | 16.6841 | 16.4365 | 16.2447 | 16.0858 | 15.7151 | 15.3294 | 14.9353 | 14.5773 | 14.1932 | 13.7625 | 12.4486 | 10.63 | 9.5029 | 8.945
| CRAIGIEBUCKLER | CT |  |  | 16.8272 | 16.6184 | 16.4797 | 16.3751 | 16.0034 | 15.6018 | 15.221 | 14.8866 | 14.5162 | 14.0322 | 12.362 | 10.1063 | 8.7367 | 8.0058 | 17.9292 | 17.8103 | 17.7072 | 17.6016 | 17.3942 | 17.1636 | 16.9486 | 16.7698 | 16.5727 | 16.2942 | 15.248 | 14.0147 | 13.2533 | 12.5822 | 16.7064 | 16.522 | 16.3964 | 16.2965 | 15.9617 | 15.6069 | 15.2565 | 14.9526 | 14.6161 | 14.1701 | 12.6275 | 10.63 | 9.5029 | 8.945
| CRAIGIEBUCKLER | LW |  |  | 16.7978 | 16.5167 | 16.3009 | 16.1272 | 15.7147 | 15.2819 | 14.8608 | 14.4751 | 14.0574 | 13.5987 | 12.2086 | 10.5952 | 9.5292 | 8.9208 | 17.9349 | 17.7935 | 17.6717 | 17.5514 | 17.3335 | 17.0841 | 16.8295 | 16.6058 | 16.3766 | 16.0789 | 15.1588 | 14.292 | 13.841 | 13.5449 | 16.6841 | 16.4365 | 16.2447 | 16.0858 | 15.7151 | 15.3294 | 14.9353 | 14.5773 | 14.1932 | 13.7625 | 12.4486 | 11.025 | 10.1852 | 9.7346
| CRAIGIEBUCKLER | ST |  |  | 16.9624 | 16.8817 | 16.7966 | 16.6968 | 16.5884 | 16.4463 | 16.3566 | 16.2429 | 16.1846 | 16.0474 | 15.5168 | 13.6658 | 12.608 | 11.7977 | 18.0169 | 17.9671 | 17.9137 | 17.8504 | 17.7837 | 17.6957 | 17.635 | 17.5625 | 17.5063 | 17.4021 | 16.9912 | 15.5911 | 14.8387 | 14.1335 | 16.8351 | 16.769 | 16.6984 | 16.6136 | 16.5214 | 16.4067 | 16.3242 | 16.2203 | 16.1643 | 16.0348 | 15.5367 | 13.7937 | 12.9166 | 12.288
| CRAIGIEBUCKLER | SP |  |  | 16.9857 | 16.9295 | 16.8624 | 16.791 | 16.6891 | 16.5365 | 16.4461 | 16.3456 | 16.246 | 16.1103 | 15.6377 | 14.2514 | 12.8467 | 12.2701 | 18.021 | 17.9816 | 17.9343 | 17.8825 | 17.8197 | 17.7266 | 17.666 | 17.5954 | 17.5225 | 17.4267 | 17.081 | 15.9973 | 14.6395 | 13.5759 | 16.8544 | 16.8103 | 16.7557 | 16.6964 | 16.6103 | 16.4863 | 16.4036 | 16.3108 | 16.2185 | 16.0944 | 15.6671 | 14.4025 | 13.1283 | 12.6965
CLAYHILLS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | 17.2087 | 17.1392 | 17.0556 | 16.9295 | 16.5688 | 15.8317 | 15.0653 | 14.2376 | 13.7921 | 13.38 | 12.0028 | 10.0495 | 9.017 | 8.4424 | 18.3819 | 18.3224 | 18.2509 | 18.1436 | 17.9651 | 17.5933 | 17.2447 | 16.8489 | 16.5078 | 16.1277 | 14.8815 | 13.4362 | 13.1663 | 12.967 | 16.3649 | 16.2571 | 16.1272 | 15.936 | 15.6736 | 15.363 | 15.1161 | 14.6068 | 14.1643 | 13.6811 | 12.0081 | 9.9986 | 9.5582 | 9.2992
| CRAIGINCHES | CT |  |  | 17.2087 | 17.1392 | 17.0556 | 16.9295 | 16.7407 | 15.972 | 15.5445 | 15.1129 | 14.6314 | 14.1071 | 12.5134 | 10.0554 | 9.017 | 8.4424 | 18.3819 | 18.3224 | 18.2509 | 18.1436 | 17.9685 | 17.5933 | 17.3221 | 17.0335 | 16.7092 | 16.3515 | 15.3211 | 13.9508 | 13.5903 | 13.3517 | 16.3649 | 16.2571 | 16.1272 | 15.936 | 15.6736 | 15.363 | 15.1161 | 14.8376 | 14.422 | 13.9599 | 12.6163 | 10.5313 | 9.9369 | 9.6138
| CRAIGINCHES | LW |  |  | 17.2246 | 17.1583 | 17.0829 | 16.9669 | 16.5688 | 15.8317 | 15.0653 | 14.2376 | 13.7921 | 13.38 | 12.0028 | 10.0495 | 9.1947 | 8.708 | 18.3967 | 18.3416 | 18.279 | 18.1818 | 17.9651 | 17.6008 | 17.2447 | 16.8489 | 16.5078 | 16.1277 | 14.8815 | 13.4362 | 13.1663 | 12.967 | 16.3892 | 16.2845 | 16.1656 | 15.9851 | 15.7367 | 15.4337 | 15.1285 | 14.6068 | 14.1643 | 13.6811 | 12.0081 | 9.9986 | 9.5582 | 9.2992
| CRAIGINCHES | ST |  |  | 17.2704 | 17.2416 | 17.2083 | 17.1667 | 17.1244 | 17.0741 | 17.0152 | 16.9439 | 16.8596 | 16.7341 | 16.2212 | 14.3218 | 13.0326 | 12.5235 | 18.4344 | 18.4096 | 18.3809 | 18.3448 | 18.3078 | 18.2638 | 18.2122 | 18.15 | 18.0766 | 17.9701 | 17.304 | 15.4668 | 14.4704 | 14.0459 | 16.4648 | 16.4226 | 16.3736 | 16.3123 | 16.2491 | 16.1733 | 16.084 | 15.9765 | 15.8494 | 15.6604 | 14.9132 | 12.9175 | 11.7428 | 11.2165
| CRAIGINCHES | SP |  |  | 17.2757 | 17.2533 | 17.227 | 17.1968 | 17.1662 | 17.1316 | 17.0924 | 17.0464 | 16.9911 | 16.9142 | 16.6277 | 15.5499 | 14.1302 | 13.5253 | 18.4384 | 18.4186 | 18.395 | 18.3676 | 18.3395 | 18.3075 | 18.271 | 18.2284 | 18.1775 | 18.1073 | 17.8496 | 16.606 | 15.2787 | 14.196 | 16.4726 | 16.4404 | 16.4019 | 16.3572 | 16.312 | 16.2606 | 16.202 | 16.1338 | 16.0536 | 15.9402 | 15.5326 | 14.1896 | 12.7725 | 12.239
CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | 8.3266 | 7.6584 | 6.9764 | 6.2997 | 5.0281 | 4.0821 | 3.0769 | 2.1917 | 1.2466 | 0.36028 | -2.0869 | -4.1065 | -4.923 | -5.2242 | 9.6624 | 9.2025 | 8.6834 | 8.1563 | 7.2152 | 6.6267 | 5.9416 | 5.342 | 4.72 | 4.1164 | 2.4128 | 1.1533 | 0.65317 | 0.24779 | 8.6607 | 8.0954 | 7.5107 | 6.9238 | 5.8459 | 5.0296 | 4.1511 | 3.3979 | 2.586 | 1.8255 | -0.27263 | -2.0365 | -2.7436 | -3.0009
| CRAIGTON | CT |  |  | 8.3418 | 7.7186 | 7.073 | 6.4565 | 5.2475 | 4.385 | 3.4937 | 2.6444 | 1.8087 | 0.84141 | -2.0066 | -4.1065 | -4.923 | -5.2242 | 9.6624 | 9.2025 | 8.6834 | 8.1563 | 7.2152 | 6.6338 | 6.0755 | 5.5235 | 4.9938 | 4.3453 | 2.4128 | 1.1533 | 0.65317 | 0.24779 | 8.6705 | 8.1446 | 7.59 | 7.0555 | 6.0365 | 5.3022 | 4.5405 | 3.826 | 3.121 | 2.2859 | -0.19216 | -2.0365 | -2.7436 | -3.0009
| CRAIGTON | LW |  |  | 8.3266 | 7.6584 | 6.9764 | 6.2997 | 5.0281 | 4.0821 | 3.0769 | 2.1917 | 1.2466 | 0.36028 | -2.0869 | -3.8011 | -4.3459 | -4.5336 | 9.6757 | 9.2181 | 8.6955 | 8.1637 | 7.2403 | 6.6267 | 5.9416 | 5.342 | 4.72 | 4.1164 | 2.4232 | 1.3775 | 1.1518 | 1.0714 | 8.6607 | 8.0954 | 7.5107 | 6.9238 | 5.8459 | 5.0296 | 4.1511 | 3.3979 | 2.586 | 1.8255 | -0.27263 | -1.7833 | -2.2498 | -2.4076
| CRAIGTON | ST |  |  | 8.4641 | 7.933 | 7.3672 | 6.8066 | 5.8626 | 5.2663 | 4.6801 | 4.0671 | 3.5093 | 2.8766 | 0.88605 | -1.1283 | -1.8378 | -2.2384 | 9.7057 | 9.2654 | 8.7781 | 8.2919 | 7.402 | 6.9115 | 6.4298 | 5.9355 | 5.4843 | 4.9965 | 3.439 | 2.1057 | 1.7112 | 1.4991 | 8.7894 | 8.3507 | 7.876 | 7.4027 | 6.4255 | 5.8828 | 5.3491 | 4.8029 | 4.3139 | 3.7928 | 2.1668 | 0.64331 | 0.0099581 | -0.33605
| CRAIGTON | SP |  |  | 8.483 | 7.9703 | 7.417 | 6.8714 | 5.9169 | 5.3042 | 4.7022 | 4.0764 | 3.5075 | 2.904 | 1.0546 | -0.92517 | -1.7355 | -1.9809 | 9.706 | 9.2682 | 8.7824 | 8.2994 | 7.4116 | 6.9238 | 6.4456 | 5.961 | 5.5327 | 5.0908 | 3.6767 | 2.5842 | 1.8293 | 1.1455 | 8.8056 | 8.3837 | 7.9201 | 7.4334 | 6.439 | 5.8998 | 5.3704 | 4.8275 | 4.3499 | 3.8607 | 2.3674 | 0.85629 | 0.10022 | -0.11636
BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | 7.6377 | 7.4621 | 7.2677 | 7.0447 | 6.4731 | 5.8918 | 5.3067 | 4.6245 | 3.8099 | 3.0736 | 0.8145 | -1.6263 | -2.6951 | -3.0629 | 8.2597 | 8.1559 | 8.0387 | 7.8905 | 7.6145 | 7.3148 | 6.9955 | 6.5912 | 6.1238 | 5.6188 | 4.0586 | 2.7054 | 2.1403 | 1.7451 | 7.8586 | 7.7114 | 7.5468 | 7.3473 | 6.8849 | 6.3782 | 5.8578 | 5.2312 | 4.4863 | 3.7698 | 1.6014 | -0.4905 | -1.3759 | -1.6778
| CRIEFF | CT |  |  | 7.7038 | 7.5703 | 7.4091 | 7.2531 | 6.7174 | 6.1751 | 5.5749 | 4.9374 | 4.2881 | 3.624 | 1.1276 | -1.6263 | -2.6951 | -3.0629 | 8.2729 | 8.1796 | 8.0627 | 7.9136 | 7.63 | 7.338 | 7.0311 | 6.6866 | 6.3323 | 5.93 | 4.2682 | 2.7054 | 2.1403 | 1.7451 | 7.9022 | 7.785 | 7.6398 | 7.4721 | 7.0308 | 6.5806 | 6.0607 | 5.4978 | 4.9218 | 4.3113 | 1.9481 | -0.4905 | -1.3759 | -1.6778
| CRIEFF | LW |  |  | 7.6377 | 7.4621 | 7.2677 | 7.0447 | 6.4731 | 5.8918 | 5.3067 | 4.6245 | 3.8099 | 3.0736 | 0.8145 | -1.1911 | -1.8632 | -2.1426 | 8.2597 | 8.1559 | 8.0387 | 7.8905 | 7.6145 | 7.3148 | 6.9955 | 6.5912 | 6.1238 | 5.6188 | 4.0586 | 2.8757 | 2.6266 | 2.5264 | 7.8586 | 7.7114 | 7.5468 | 7.3473 | 6.8849 | 6.3782 | 5.8578 | 5.2312 | 4.4863 | 3.7698 | 1.6014 | -0.1975 | -0.74174 | -0.96783
| CRIEFF | ST |  |  | 7.7594 | 7.6639 | 7.5587 | 7.4492 | 7.3324 | 7.1923 | 7.0438 | 6.8649 | 6.6895 | 6.4148 | 5.2663 | 2.7786 | 1.76 | 1.2254 | 8.3167 | 8.2483 | 8.1722 | 8.0831 | 7.9886 | 7.8757 | 7.7553 | 7.6166 | 7.4742 | 7.2664 | 6.3585 | 4.406 | 3.6993 | 3.2372 | 7.958 | 7.8755 | 7.7852 | 7.6823 | 7.5749 | 7.445 | 7.3064 | 7.1431 | 6.9788 | 6.7194 | 5.632 | 3.1593 | 2.278 | 1.8357
| CRIEFF | SP |  |  | 7.8018 | 7.7315 | 7.6494 | 7.5623 | 7.4088 | 7.238 | 7.0519 | 6.8423 | 6.619 | 6.333 | 5.2337 | 2.9864 | 1.5819 | 1.2178 | 8.3333 | 8.276 | 8.2086 | 8.1362 | 8.0362 | 7.923 | 7.7962 | 7.6499 | 7.4847 | 7.2869 | 6.4891 | 4.7857 | 3.4345 | 2.6197 | 7.9905 | 7.9279 | 7.8548 | 7.7763 | 7.6478 | 7.5032 | 7.3434 | 7.1593 | 6.9551 | 6.7028 | 5.736 | 3.5794 | 2.157 | 1.8275
PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | 0.42267 | 0.41801 | 0.41404 | 0.39829 | 0.35472 | 0.28951 | 0.21921 | 0.14825 | 0.064515 | 0.0084165 | -0.11212 | -0.12794 | -0.11172 | -0.15368 | 0.32468 | 0.32306 | 0.32109 | 0.31677 | 0.3124 | 0.30057 | 0.27499 | 0.24915 | 0.21817 | 0.19959 | 0.15086 | 0.12607 | 0.13912 | 0.12111 | 0.28627 | 0.28407 | 0.28205 | 0.27761 | 0.27315 | 0.22183 | 0.16897 | 0.11676 | 0.052301 | 0.017435 | -0.095355 | -0.11355 | -0.08889 | -0.13464
| CRINAN | CT |  |  | 0.42425 | 0.41908 | 0.41446 | 0.40556 | 0.3877 | 0.3407 | 0.26648 | 0.19306 | 0.12207 | 0.090777 | -0.045804 | -0.089159 | -0.081789 | -0.085287 | 0.32488 | 0.32353 | 0.32121 | 0.31677 | 0.3124 | 0.30898 | 0.2924 | 0.26463 | 0.23798 | 0.22489 | 0.18321 | 0.1521 | 0.15735 | 0.1567 | 0.28688 | 0.28453 | 0.28216 | 0.27761 | 0.27315 | 0.26491 | 0.20611 | 0.14645 | 0.090757 | 0.070175 | -0.02942 | -0.075717 | -0.05499 | -0.05305
| CRINAN | LW |  |  | 0.42267 | 0.41801 | 0.41404 | 0.39829 | 0.35472 | 0.28951 | 0.21921 | 0.14825 | 0.064515 | 0.0084165 | -0.11212 | -0.12794 | -0.099806 | -0.11248 | 0.32468 | 0.32306 | 0.32109 | 0.31746 | 0.31334 | 0.30057 | 0.27499 | 0.24915 | 0.21817 | 0.19959 | 0.15086 | 0.12607 | 0.13912 | 0.1326 | 0.28627 | 0.28407 | 0.28205 | 0.27833 | 0.27411 | 0.22183 | 0.16897 | 0.11676 | 0.052301 | 0.017435 | -0.095355 | -0.11355 | -0.079597 | -0.097224
| CRINAN | ST |  |  | 0.42466 | 0.42335 | 0.4218 | 0.41802 | 0.41569 | 0.41276 | 0.40801 | 0.40406 | 0.39883 | 0.38949 | 0.32763 | 0.1255 | 0.081204 | 0.05596 | 0.32496 | 0.32479 | 0.32458 | 0.32298 | 0.3218 | 0.32032 | 0.31793 | 0.31594 | 0.3133 | 0.30961 | 0.29268 | 0.24284 | 0.22116 | 0.21004 | 0.28709 | 0.28656 | 0.28593 | 0.28405 | 0.28288 | 0.2814 | 0.279 | 0.277 | 0.27435 | 0.2702 | 0.2494 | 0.18191 | 0.12547 | 0.10258
| CRINAN | SP |  |  | 0.42907 | 0.42838 | 0.42724 | 0.42511 | 0.42208 | 0.41951 | 0.40552 | 0.38976 | 0.37352 | 0.34893 | 0.26236 | 0.017858 | -0.11172 | -0.15368 | 0.32564 | 0.32555 | 0.32541 | 0.32514 | 0.32472 | 0.32364 | 0.32202 | 0.31911 | 0.31674 | 0.31341 | 0.28839 | 0.20213 | 0.14234 | 0.12111 | 0.28907 | 0.28874 | 0.28822 | 0.28729 | 0.28606 | 0.28485 | 0.28324 | 0.28031 | 0.27794 | 0.27458 | 0.20147 | 0.034039 | -0.08889 | -0.13464
PORT ANN | CROMALT | MINIMUM HEADROOM | NN 0839507755 | YES | 1.5565 | 1.2845 | 0.95944 | 0.64235 | 0.43274 | 0.2629 | 0.11423 | -0.024565 | -0.16832 | -0.26442 | -0.53346 | -0.60615 | -0.62867 | -0.67967 | 1.5525 | 1.2375 | 0.88141 | 0.52075 | 0.33557 | 0.1808 | 0.047734 | -0.060967 | -0.17134 | -0.25411 | -0.44285 | -0.52534 | -0.54797 | -0.58743 | 1.3646 | 1.0803 | 0.75235 | 0.42684 | 0.24162 | 0.09011 | -0.043393 | -0.15416 | -0.28918 | -0.37872 | -0.61516 | -0.66809 | -0.67781 | -0.69426
| CROMALT | CT |  |  | 1.5989 | 1.3249 | 0.99688 | 0.66588 | 0.47865 | 0.30382 | 0.1572 | 0.021991 | -0.11159 | -0.20504 | -0.4513 | -0.56915 | -0.56887 | -0.54839 | 1.5525 | 1.2375 | 0.88141 | 0.52302 | 0.34115 | 0.1808 | 0.04871 | -0.058577 | -0.16593 | -0.24814 | -0.42648 | -0.50293 | -0.50511 | -0.48531 | 1.3795 | 1.095 | 0.77161 | 0.44784 | 0.26118 | 0.10052 | -0.03313 | -0.14303 | -0.2521 | -0.33281 | -0.54802 | -0.6411 | -0.61675 | -0.60622
| CROMALT | LW |  |  | 1.5565 | 1.2845 | 0.95944 | 0.64235 | 0.43274 | 0.2629 | 0.11423 | -0.024565 | -0.16832 | -0.26442 | -0.53346 | -0.60615 | -0.57948 | -0.58439 | 1.554 | 1.2396 | 0.88325 | 0.52075 | 0.33557 | 0.18134 | 0.047734 | -0.060967 | -0.17134 | -0.25411 | -0.44285 | -0.52534 | -0.51772 | -0.52173 | 1.3646 | 1.0803 | 0.75235 | 0.42684 | 0.24162 | 0.09011 | -0.043393 | -0.15416 | -0.28918 | -0.37872 | -0.61516 | -0.66809 | -0.62777 | -0.64294
| CROMALT | ST |  |  | 1.5924 | 1.3257 | 1.0199 | 0.71743 | 0.54552 | 0.41904 | 0.29996 | 0.21443 | 0.10149 | 0.0030941 | -0.20723 | -0.4547 | -0.58166 | -0.60044 | 1.5568 | 1.2524 | 0.89883 | 0.54533 | 0.37518 | 0.23601 | 0.11712 | 0.026274 | -0.072119 | -0.14893 | -0.31201 | -0.43618 | -0.52893 | -0.53923 | 1.3796 | 1.1039 | 0.78494 | 0.46741 | 0.3163 | 0.19393 | 0.08758 | 0.0071643 | -0.081876 | -0.15501 | -0.31402 | -0.43013 | -0.46123 | -0.46361
| CROMALT | SP |  |  | 1.5959 | 1.3299 | 1.0256 | 0.7209 | 0.54179 | 0.40703 | 0.27914 | 0.18234 | 0.063657 | -0.043718 | -0.25377 | -0.48305 | -0.62867 | -0.67967 | 1.5573 | 1.2531 | 0.90001 | 0.54764 | 0.37377 | 0.23048 | 0.10791 | 0.012625 | -0.090553 | -0.16998 | -0.33472 | -0.41981 | -0.54797 | -0.58743 | 1.3824 | 1.1077 | 0.79019 | 0.47372 | 0.31018 | 0.17707 | 0.060305 | -0.031764 | -0.13314 | -0.21831 | -0.38735 | -0.57958 | -0.67781 | -0.69426
ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | YES | 6.8828 | 6.5549 | 5.989 | 5.4624 | 4.7193 | 4.2328 | 3.6382 | 3.0247 | 2.4318 | 1.8403 | 0.023636 | -2.0011 | -2.7493 | -2.9737 | 7.9267 | 7.5005 | 6.7909 | 6.1947 | 5.4494 | 5.0196 | 4.6471 | 4.2979 | 3.9802 | 3.6389 | 2.6724 | 1.8384 | 1.6623 | 1.4764 | 7.2776 | 6.964 | 6.4203 | 5.914 | 5.2095 | 4.7524 | 4.2094 | 3.6532 | 3.1197 | 2.5843 | 0.94175 | -0.86979 | -1.5313 | -1.7278
| CROSSHILLS | CT |  |  | 6.8828 | 6.5549 | 5.989 | 5.4624 | 4.7193 | 4.2328 | 3.6382 | 3.0247 | 2.4318 | 1.8403 | 0.023636 | -2.0011 | -2.7493 | -2.9737 | 7.9267 | 7.5005 | 6.7909 | 6.1947 | 5.4494 | 5.0196 | 4.6471 | 4.2979 | 3.986 | 3.675 | 2.8314 | 2.0053 | 1.6623 | 1.4764 | 7.2776 | 6.964 | 6.4203 | 5.914 | 5.2095 | 4.7524 | 4.2094 | 3.6532 | 3.1197 | 2.5843 | 0.94175 | -0.86979 | -1.5313 | -1.7278
| CROSSHILLS | LW |  |  | 6.8938 | 6.579 | 6.0318 | 5.5527 | 4.8171 | 4.3125 | 3.8146 | 3.2775 | 2.5423 | 1.953 | 0.18198 | -1.4874 | -2.121 | -2.3698 | 7.9397 | 7.5158 | 6.813 | 6.2298 | 5.4956 | 5.0722 | 4.6935 | 4.3225 | 3.9802 | 3.6389 | 2.6724 | 1.8384 | 1.795 | 1.7806 | 7.2889 | 6.9871 | 6.461 | 6 | 5.3048 | 4.8331 | 4.3736 | 3.8777 | 3.2103 | 2.6706 | 1.053 | -0.44479 | -1.0006 | -1.2184
| CROSSHILLS | ST |  |  | 6.9261 | 6.6183 | 6.1033 | 5.6683 | 5.1249 | 4.834 | 4.5322 | 4.2398 | 3.9734 | 3.6955 | 2.837 | 1.2873 | 0.56787 | 0.26454 | 7.9654 | 7.5631 | 6.8842 | 6.3336 | 5.6444 | 5.2747 | 4.9499 | 4.6496 | 4.3872 | 4.1288 | 3.3795 | 2.4388 | 2.0656 | 1.9902 | 7.3202 | 7.027 | 6.5319 | 6.1125 | 5.5911 | 5.313 | 5.0126 | 4.7232 | 4.463 | 4.193 | 3.3719 | 1.7542 | 1.0322 | 0.95898
| CROSSHILLS | SP |  |  | 6.9425 | 6.6475 | 6.1445 | 5.7295 | 5.1701 | 4.867 | 4.5808 | 4.3041 | 4.0354 | 3.7486 | 2.9134 | 1.6692 | 0.80315 | 0.60939 | 7.9668 | 7.5684 | 6.8925 | 6.3483 | 5.666 | 5.3045 | 4.9902 | 4.7029 | 4.4521 | 4.2187 | 3.5928 | 2.8996 | 2.3057 | 2.0799 | 7.3345 | 7.0533 | 6.569 | 6.1686 | 5.6344 | 5.3471 | 5.0652 | 4.7927 | 4.5482 | 4.3122 | 3.5907 | 2.4494 | 1.5635 | 1.3707
KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | 4.8592 | 4.8561 | 4.8251 | 4.7845 | 4.652 | 4.5079 | 4.3449 | 4.1183 | 3.8432 | 3.6075 | 2.8023 | 1.9234 | 1.4783 | 1.3146 | 5.6253 | 5.618 | 5.5964 | 5.5674 | 5.4961 | 5.4238 | 5.3221 | 5.2161 | 5.0904 | 4.9644 | 4.4936 | 4.066 | 3.8624 | 3.7285 | 5.3036 | 5.2979 | 5.2711 | 5.2373 | 5.1211 | 4.9945 | 4.84 | 4.6361 | 4.3862 | 4.1673 | 3.4098 | 2.6223 | 2.2324 | 2.09
| CULLEN | CT |  |  | 4.891 | 4.8935 | 4.8693 | 4.819 | 4.6909 | 4.5595 | 4.3449 | 4.1183 | 3.8906 | 3.673 | 2.878 | 1.9234 | 1.4783 | 1.3146 | 5.6347 | 5.6279 | 5.6078 | 5.5674 | 5.4961 | 5.4238 | 5.3221 | 5.2161 | 5.1077 | 4.9963 | 4.5676 | 4.066 | 3.8624 | 3.7285 | 5.3296 | 5.3282 | 5.3087 | 5.2626 | 5.1483 | 5.0314 | 4.84 | 4.6361 | 4.4307 | 4.2311 | 3.4912 | 2.6223 | 2.2324 | 2.09
| CULLEN | LW |  |  | 4.8592 | 4.8561 | 4.8251 | 4.7845 | 4.652 | 4.5079 | 4.3602 | 4.1629 | 3.8432 | 3.6075 | 2.8023 | 2.1646 | 1.8829 | 1.7784 | 5.6253 | 5.618 | 5.5964 | 5.5697 | 5.5024 | 5.4293 | 5.3541 | 5.2466 | 5.0904 | 4.9644 | 4.4936 | 4.167 | 4.0679 | 4.0294 | 5.3036 | 5.2979 | 5.2711 | 5.2373 | 5.1211 | 4.9945 | 4.8615 | 4.6777 | 4.3862 | 4.1673 | 3.4098 | 2.8305 | 2.5852 | 2.4947
| CULLEN | ST |  |  | 4.8818 | 4.8686 | 4.8403 | 4.813 | 4.7828 | 4.7464 | 4.7139 | 4.6901 | 4.6466 | 4.5758 | 4.3065 | 3.4766 | 3.0551 | 2.8254 | 5.6363 | 5.6275 | 5.609 | 5.5868 | 5.5656 | 5.5404 | 5.5171 | 5.4987 | 5.4704 | 5.4269 | 5.2577 | 4.671 | 4.4096 | 4.2529 | 5.325 | 5.313 | 5.2902 | 5.2652 | 5.2411 | 5.2111 | 5.182 | 5.1592 | 5.1184 | 5.0517 | 4.795 | 3.9866 | 3.6035 | 3.414
| CULLEN | SP |  |  | 4.8923 | 4.8837 | 4.8605 | 4.8368 | 4.7923 | 4.746 | 4.7044 | 4.6622 | 4.6022 | 4.5263 | 4.2607 | 3.6204 | 3.0358 | 2.8896 | 5.6414 | 5.6348 | 5.6184 | 5.6015 | 5.576 | 5.5497 | 5.5266 | 5.5028 | 5.466 | 5.4214 | 5.2668 | 4.8701 | 4.3718 | 4.1287 | 5.3346 | 5.3268 | 5.3084 | 5.2895 | 5.2523 | 5.2146 | 5.1792 | 5.1409 | 5.0848 | 5.0144 | 4.7685 | 4.1669 | 3.6079 | 3.4769
INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | 7.9884 | 7.024 | 6.2859 | 9.4556 | 8.5814 | 7.8321 | 7.0983 | 6.3375 | 5.4871 | 4.7231 | 2.437 | -0.49553 | -1.7661 | -2.1785 | 11.6409 | 10.9074 | 10.241 | 12.2585 | 11.7217 | 11.2438 | 10.7662 | 10.2613 | 9.728 | 9.2038 | 7.6651 | 6.0925 | 5.3704 | 4.8361 | 8.4163 | 7.534 | 6.8483 | 8.856 | 8.06 | 7.3716 | 6.6908 | 5.9787 | 5.1893 | 4.4642 | 2.2593 | -0.35808 | -1.478 | -1.8365
| CULLODEN | CT |  |  | 8.0376 | 7.207 | 6.5333 | 9.7438 | 8.9497 | 8.2644 | 7.545 | 6.8559 | 6.1309 | 5.3102 | 2.6304 | -0.49553 | -1.7661 | -2.1785 | 11.642 | 10.9534 | 10.2981 | 12.3082 | 11.7889 | 11.3358 | 10.8896 | 10.4589 | 10.0132 | 9.5002 | 7.8144 | 6.0925 | 5.3704 | 4.8361 | 8.4555 | 7.6901 | 7.0584 | 9.0968 | 8.369 | 7.7384 | 7.0789 | 6.4445 | 5.7784 | 5.0146 | 2.5033 | -0.35808 | -1.478 | -1.8365
| CULLODEN | LW |  |  | 7.9884 | 7.024 | 6.2859 | 9.4556 | 8.5814 | 7.8321 | 7.0983 | 6.3375 | 5.4871 | 4.7231 | 2.437 | 0.22574 | -0.75346 | -1.1656 | 11.6409 | 10.9074 | 10.241 | 12.2585 | 11.7217 | 11.2438 | 10.7662 | 10.2613 | 9.728 | 9.2038 | 7.6651 | 6.414 | 6.0423 | 5.8876 | 8.4163 | 7.534 | 6.8483 | 8.856 | 8.06 | 7.3716 | 6.6908 | 5.9787 | 5.1893 | 4.4642 | 2.2593 | 0.15104 | -0.64934 | -0.97914
| CULLODEN | ST |  |  | 8.2192 | 7.5493 | 6.8483 | 10.0092 | 9.6418 | 9.3326 | 9.0653 | 8.8451 | 8.6766 | 8.4201 | 7.5751 | 5.3064 | 4.4165 | 3.8769 | 11.7432 | 11.1345 | 10.4971 | 12.5327 | 12.2185 | 11.9487 | 11.7095 | 11.503 | 11.3086 | 11.0788 | 10.3448 | 8.5538 | 7.8065 | 7.2265 | 8.6239 | 8.0049 | 7.3567 | 9.3634 | 9.0225 | 8.7336 | 8.4813 | 8.2718 | 8.106 | 7.8572 | 7.0295 | 4.616 | 3.7402 | 3.2966
| CULLODEN | SP |  |  | 8.3086 | 7.6982 | 7.0492 | 10.2968 | 9.9248 | 9.5749 | 9.2769 | 8.9972 | 8.6917 | 8.3529 | 7.4639 | 5.3856 | 3.9158 | 3.6959 | 11.7752 | 11.1906 | 10.5734 | 12.6486 | 12.3347 | 12.0531 | 11.8097 | 11.582 | 11.3286 | 11.0809 | 10.4105 | 8.8252 | 7.2704 | 6.2136 | 8.7022 | 8.136 | 7.5339 | 9.619 | 9.2748 | 8.9514 | 8.6746 | 8.4135 | 8.1258 | 7.8107 | 6.9762 | 4.9628 | 3.3652 | 3.1374
CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | 16.9544 | 16.7822 | 16.5574 | 16.3284 | 15.8929 | 15.3535 | 14.7114 | 14.1573 | 13.6006 | 13.112 | 11.6883 | 9.8621 | 9.0547 | 8.7533 | 17.9917 | 17.8705 | 17.7092 | 17.5398 | 17.2967 | 16.9933 | 16.5875 | 16.264 | 15.9453 | 15.6393 | 14.7663 | 13.7011 | 13.2131 | 12.8102 | 16.8028 | 16.6529 | 16.4521 | 16.245 | 15.8578 | 15.3716 | 14.7821 | 14.2907 | 13.8009 | 13.357 | 12.0787 | 10.5507 | 9.9096 | 9.6735
| CULTER | CT |  |  | 16.9544 | 16.7912 | 16.571 | 16.3558 | 15.9563 | 15.5052 | 15.0323 | 14.5995 | 14.1473 | 13.4936 | 11.7947 | 9.8621 | 9.0547 | 8.7533 | 17.9917 | 17.8705 | 17.7092 | 17.5398 | 17.2967 | 17.0254 | 16.7446 | 16.5059 | 16.2566 | 15.8353 | 14.7931 | 13.7011 | 13.2131 | 12.8102 | 16.8028 | 16.6529 | 16.4521 | 16.245 | 15.8909 | 15.4926 | 15.0746 | 14.7048 | 14.3187 | 13.7189 | 12.2005 | 10.5507 | 9.9096 | 9.6735
| CULTER | LW |  |  | 16.9614 | 16.7822 | 16.5574 | 16.3284 | 15.8929 | 15.3535 | 14.7114 | 14.1573 | 13.6006 | 13.112 | 11.6883 | 10.1762 | 9.6131 | 9.4082 | 18.0187 | 17.8983 | 17.7485 | 17.5831 | 17.3236 | 16.9933 | 16.5875 | 16.264 | 15.9453 | 15.6393 | 14.7663 | 13.9189 | 13.699 | 13.6175 | 16.8206 | 16.6594 | 16.4602 | 16.2451 | 15.8578 | 15.3716 | 14.7821 | 14.2907 | 13.8009 | 13.357 | 12.0787 | 10.7538 | 10.3068 | 10.1445
| CULTER | ST |  |  | 17.1073 | 17.0191 | 16.8992 | 16.8154 | 16.7353 | 16.6488 | 16.5489 | 16.4452 | 16.328 | 16.1268 | 15.3344 | 13.4842 | 12.6577 | 12.2554 | 18.1003 | 18.0433 | 17.9667 | 17.9064 | 17.8448 | 17.7789 | 17.7018 | 17.6225 | 17.5337 | 17.3874 | 16.796 | 15.4085 | 14.7997 | 14.365 | 16.9534 | 16.8805 | 16.7821 | 16.7082 | 16.6356 | 16.5578 | 16.4666 | 16.3732 | 16.2675 | 16.081 | 15.335 | 13.5682 | 12.8476 | 12.52
| CULTER | SP |  |  | 17.1065 | 17.0283 | 16.9209 | 16.8377 | 16.7363 | 16.6215 | 16.4944 | 16.3578 | 16.2242 | 16.0635 | 15.4834 | 13.8494 | 12.8893 | 12.6356 | 18.0962 | 18.0444 | 17.9743 | 17.9128 | 17.8443 | 17.7646 | 17.6751 | 17.5786 | 17.4825 | 17.3689 | 16.9555 | 15.6727 | 14.6775 | 13.9155 | 16.9499 | 16.8859 | 16.799 | 16.726 | 16.6371 | 16.5352 | 16.4211 | 16.299 | 16.1797 | 16.0377 | 15.5245 | 13.971 | 13.0569 | 12.8388
ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | YES | 9.8655 | 9.7865 | 9.6813 | 9.5436 | 9.3525 | 9.1386 | 8.8153 | 8.4186 | 7.9871 | 7.5738 | 6.1585 | 3.997 | 3.3637 | 2.9406 | 10.8402 | 10.7656 | 10.6653 | 10.5359 | 10.3638 | 10.1699 | 9.9917 | 9.7974 | 9.5411 | 9.0877 | 7.6417 | 6.0017 | 5.8745 | 5.7385 | 9.3434 | 9.2674 | 9.1661 | 9.0333 | 8.8517 | 8.6482 | 8.4621 | 8.2159 | 7.8096 | 7.2867 | 5.4719 | 3.3035 | 2.9118 | 2.7388
| CUMMING STREET | CT |  |  | 9.8655 | 9.7865 | 9.6813 | 9.5436 | 9.3525 | 9.1386 | 8.943 | 8.5822 | 8.1979 | 7.7567 | 6.4118 | 4.3549 | 3.3637 | 2.9406 | 10.8402 | 10.7656 | 10.6653 | 10.5359 | 10.3638 | 10.1699 | 9.9917 | 9.7974 | 9.554 | 9.1734 | 8.1169 | 6.7592 | 6.5485 | 6.437 | 9.3434 | 9.2674 | 9.1661 | 9.0333 | 8.8517 | 8.6482 | 8.4621 | 8.2535 | 7.8791 | 7.3965 | 6.0528 | 3.9881 | 3.3866 | 3.1558
| CUMMING STREET | LW |  |  | 9.897 | 9.8189 | 9.7322 | 9.6128 | 9.4308 | 9.1733 | 8.8153 | 8.4186 | 7.9871 | 7.5738 | 6.1585 | 3.997 | 3.5519 | 3.3536 | 10.8703 | 10.7961 | 10.7134 | 10.6 | 10.4356 | 10.2549 | 10.0665 | 9.8425 | 9.5411 | 9.0877 | 7.6417 | 6.0017 | 5.8745 | 5.7782 | 9.3739 | 9.2989 | 9.2155 | 9.1004 | 8.9279 | 8.7376 | 8.5411 | 8.2159 | 7.8096 | 7.2867 | 5.4719 | 3.3035 | 2.9118 | 2.7388
| CUMMING STREET | ST |  |  | 9.9538 | 9.9174 | 9.8818 | 9.8366 | 9.7656 | 9.6805 | 9.5817 | 9.4878 | 9.3766 | 9.195 | 8.5326 | 5.6019 | 4.0565 | 3.7861 | 10.925 | 10.8906 | 10.8573 | 10.8151 | 10.7564 | 10.6839 | 10.5973 | 10.5128 | 10.4082 | 10.2357 | 9.5469 | 7.1281 | 5.9408 | 5.7385 | 9.4287 | 9.3938 | 9.3598 | 9.3163 | 9.2508 | 9.1717 | 9.0792 | 8.9901 | 8.8834 | 8.7088 | 7.9295 | 4.9268 | 3.4499 | 3.2024
| CUMMING STREET | SP |  |  | 9.9575 | 9.9281 | 9.8995 | 9.8659 | 9.8075 | 9.7388 | 9.6608 | 9.5937 | 9.511 | 9.3981 | 9.007 | 7.3532 | 5.1059 | 4.4982 | 10.9285 | 10.9008 | 10.8741 | 10.8424 | 10.7955 | 10.7383 | 10.6712 | 10.612 | 10.5352 | 10.4285 | 10.0606 | 8.4997 | 6.7523 | 6.2701 | 9.4322 | 9.4042 | 9.3768 | 9.3446 | 9.2913 | 9.2281 | 9.1558 | 9.0926 | 9.0134 | 8.905 | 8.5302 | 6.6194 | 4.4646 | 3.8913
ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | 5.1239 | 5.1154 | 5.0903 | 5.0532 | 4.9653 | 4.8571 | 4.7372 | 4.5907 | 4.4036 | 4.2384 | 3.6504 | 3.0787 | 2.8069 | 2.7096 | 5.3154 | 5.3054 | 5.2866 | 5.2499 | 5.1939 | 5.1374 | 5.0728 | 5.0028 | 4.9054 | 4.8054 | 4.4272 | 4.1741 | 4.0578 | 3.9837 | 4.8798 | 4.8732 | 4.8528 | 4.8189 | 4.7357 | 4.6403 | 4.5267 | 4.3937 | 4.2204 | 4.0652 | 3.5067 | 2.996 | 2.7574 | 2.6721
| DALCHONZIE | CT |  |  | 5.1307 | 5.1154 | 5.0903 | 5.0532 | 4.9698 | 4.872 | 4.7372 | 4.5907 | 4.4423 | 4.2862 | 3.701 | 3.0787 | 2.8069 | 2.7096 | 5.3167 | 5.3054 | 5.2866 | 5.2499 | 5.1939 | 5.1374 | 5.0728 | 5.0028 | 4.9316 | 4.8446 | 4.4891 | 4.1741 | 4.0578 | 3.9837 | 4.8907 | 4.8819 | 4.8609 | 4.8189 | 4.7357 | 4.6485 | 4.5267 | 4.3937 | 4.2589 | 4.1143 | 3.5641 | 2.996 | 2.7574 | 2.6721
| DALCHONZIE | LW |  |  | 5.1239 | 5.1183 | 5.0943 | 5.06 | 4.9653 | 4.8571 | 4.7498 | 4.6087 | 4.4036 | 4.2384 | 3.6504 | 3.2562 | 3.0664 | 2.9936 | 5.3154 | 5.3063 | 5.2893 | 5.2646 | 5.2145 | 5.1561 | 5.0968 | 5.0112 | 4.9054 | 4.8054 | 4.4272 | 4.2426 | 4.1776 | 4.1515 | 4.8798 | 4.8732 | 4.8528 | 4.8221 | 4.7377 | 4.6403 | 4.5415 | 4.4089 | 4.2204 | 4.0652 | 3.5067 | 3.1492 | 2.9831 | 2.9192
| DALCHONZIE | ST |  |  | 5.1426 | 5.1343 | 5.1154 | 5.0947 | 5.0751 | 5.0533 | 5.0365 | 5.0147 | 4.9881 | 4.9397 | 4.7427 | 4.1076 | 3.8697 | 3.7266 | 5.3251 | 5.3185 | 5.3059 | 5.2891 | 5.273 | 5.2557 | 5.2408 | 5.221 | 5.2002 | 5.1653 | 5.0196 | 4.5455 | 4.4071 | 4.3099 | 4.8972 | 4.8892 | 4.874 | 4.8552 | 4.8377 | 4.8184 | 4.8023 | 4.7806 | 4.7549 | 4.7084 | 4.5176 | 3.9007 | 3.6901 | 3.5631
| DALCHONZIE | SP |  |  | 5.1472 | 5.1431 | 5.1268 | 5.1096 | 5.0788 | 5.0497 | 5.0225 | 4.9935 | 4.9549 | 4.9009 | 4.7328 | 4.2841 | 3.865 | 3.7865 | 5.3269 | 5.3229 | 5.3113 | 5.2988 | 5.2809 | 5.2637 | 5.247 | 5.2287 | 5.2018 | 5.167 | 5.0593 | 4.7457 | 4.3951 | 4.266 | 4.9013 | 4.8972 | 4.8839 | 4.8695 | 4.8439 | 4.8199 | 4.796 | 4.7691 | 4.7326 | 4.682 | 4.5246 | 4.0972 | 3.6908 | 3.6192
NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | YES | 9.4052 | 8.9915 | 8.656 | 8.316 | 8.0244 | 7.6905 | 7.3719 | 7.0355 | 6.6569 | 6.2836 | 5.5687 | 5.2531 | 4.7542 | 4.5323 | 9.4121 | 9.0349 | 8.7222 | 8.4191 | 8.2455 | 8.0545 | 7.8916 | 7.7223 | 7.5451 | 7.3508 | 6.9607 | 6.6128 | 6.0003 | 5.8499 | 9.2834 | 8.9214 | 8.6194 | 8.3183 | 8.0792 | 7.8105 | 7.5629 | 7.3043 | 7.0065 | 6.7424 | 6.2059 | 5.9214 | 5.5342 | 5.3182
| DALCROSS | CT |  |  | 9.4216 | 9.0185 | 8.6879 | 8.3536 | 8.0657 | 7.7524 | 7.4337 | 7.0851 | 6.7379 | 6.4369 | 5.6724 | 5.3157 | 5.2547 | 5.22 | 9.4121 | 9.0349 | 8.7222 | 8.4191 | 8.2455 | 8.0545 | 7.8916 | 7.7223 | 7.5451 | 7.3636 | 6.9791 | 6.7532 | 6.6961 | 6.6679 | 9.2966 | 8.9442 | 8.6481 | 8.3525 | 8.1174 | 7.8639 | 7.6065 | 7.333 | 7.0599 | 6.8355 | 6.3033 | 5.9933 | 5.9392 | 5.9082
| DALCROSS | LW |  |  | 9.4052 | 8.9915 | 8.656 | 8.316 | 8.0244 | 7.6905 | 7.3719 | 7.0355 | 6.6569 | 6.2836 | 5.5687 | 5.2531 | 5.2616 | 5.2243 | 9.4203 | 9.0455 | 8.7364 | 8.4358 | 8.2637 | 8.0712 | 7.9049 | 7.7305 | 7.5492 | 7.3508 | 6.9607 | 6.6128 | 6.5746 | 6.549 | 9.2834 | 8.9214 | 8.6194 | 8.3183 | 8.0792 | 7.8105 | 7.5629 | 7.3043 | 7.0065 | 6.7424 | 6.2059 | 5.9214 | 5.9319 | 5.8962
| DALCROSS | ST |  |  | 9.4379 | 9.0466 | 8.7445 | 8.4532 | 8.2799 | 8.0817 | 7.8957 | 7.6876 | 7.4608 | 7.2087 | 6.5615 | 5.5944 | 4.7542 | 4.5323 | 9.4339 | 9.0665 | 8.7712 | 8.4968 | 8.3697 | 8.2291 | 8.101 | 7.9681 | 7.8279 | 7.6685 | 7.2923 | 6.6608 | 6.0003 | 5.8499 | 9.3129 | 8.9704 | 8.6984 | 8.4416 | 8.3112 | 8.1648 | 8.0297 | 7.8842 | 7.7211 | 7.5332 | 7.0599 | 6.2928 | 5.5342 | 5.3182
| DALCROSS | SP |  |  | 9.4471 | 9.0612 | 8.7637 | 8.4816 | 8.3032 | 8.1062 | 7.913 | 7.7031 | 7.4818 | 7.2463 | 6.6362 | 5.8709 | 5.0596 | 4.6036 | 9.4356 | 9.0699 | 8.776 | 8.5044 | 8.38 | 8.2473 | 8.1224 | 7.9984 | 7.864 | 7.7222 | 7.4247 | 7.0238 | 6.234 | 5.8827 | 9.3211 | 8.9835 | 8.7164 | 8.4676 | 8.3328 | 8.188 | 8.0483 | 7.9036 | 7.7472 | 7.5766 | 7.1344 | 6.4866 | 5.8218 | 5.3579
TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | 0.96498 | 0.95632 | 0.94434 | 0.93095 | 0.90832 | 0.89417 | 0.87732 | 0.85862 | 0.83651 | 0.82565 | 0.78127 | 0.77527 | 0.7733 | 0.7664 | 0.946 | 0.94049 | 0.93339 | 0.92546 | 0.91267 | 0.90483 | 0.8962 | 0.88665 | 0.87604 | 0.86945 | 0.83849 | 0.83473 | 0.8258 | 0.81342 | 0.90493 | 0.8996 | 0.89029 | 0.87954 | 0.85833 | 0.84317 | 0.82726 | 0.81045 | 0.79077 | 0.78089 | 0.7389 | 0.73396 | 0.73241 | 0.7265
| DALMALLY | CT |  |  | 0.9703 | 0.96184 | 0.95025 | 0.93565 | 0.91259 | 0.89955 | 0.88407 | 0.86609 | 0.84809 | 0.83807 | 0.79558 | 0.78114 | 0.7874 | 0.78844 | 0.94852 | 0.94312 | 0.93607 | 0.92744 | 0.91427 | 0.90695 | 0.89838 | 0.88977 | 0.8815 | 0.87531 | 0.84515 | 0.83566 | 0.83481 | 0.83059 | 0.91172 | 0.906 | 0.89622 | 0.88372 | 0.86367 | 0.85097 | 0.8341 | 0.81726 | 0.80143 | 0.79234 | 0.752 | 0.73935 | 0.7441 | 0.7447
| DALMALLY | LW |  |  | 0.96498 | 0.95632 | 0.94434 | 0.93095 | 0.90832 | 0.89417 | 0.87732 | 0.85862 | 0.83651 | 0.82565 | 0.78127 | 0.77527 | 0.7835 | 0.77832 | 0.946 | 0.94049 | 0.93339 | 0.92546 | 0.91267 | 0.90483 | 0.8962 | 0.88665 | 0.87604 | 0.86945 | 0.83849 | 0.83473 | 0.83727 | 0.83547 | 0.90493 | 0.8996 | 0.89029 | 0.87954 | 0.85833 | 0.84317 | 0.82726 | 0.81045 | 0.79077 | 0.78089 | 0.7389 | 0.73396 | 0.74075 | 0.73668
| DALMALLY | ST |  |  | 0.97001 | 0.96 | 0.95047 | 0.94027 | 0.9309 | 0.92857 | 0.92663 | 0.92389 | 0.92034 | 0.91359 | 0.89327 | 0.83922 | 0.83319 | 0.82958 | 0.94874 | 0.9427 | 0.93693 | 0.93069 | 0.92488 | 0.92323 | 0.92181 | 0.91975 | 0.91738 | 0.91305 | 0.8997 | 0.85992 | 0.85312 | 0.84648 | 0.91073 | 0.90356 | 0.89683 | 0.88841 | 0.88071 | 0.87862 | 0.87685 | 0.87424 | 0.87104 | 0.86477 | 0.84559 | 0.79326 | 0.78785 | 0.78312
| DALMALLY | SP |  |  | 0.97006 | 0.96029 | 0.95094 | 0.94149 | 0.92789 | 0.92194 | 0.9157 | 0.90896 | 0.90206 | 0.89143 | 0.8654 | 0.8124 | 0.7733 | 0.7664 | 0.94869 | 0.9428 | 0.93711 | 0.93133 | 0.92344 | 0.92 | 0.9164 | 0.91249 | 0.90848 | 0.90232 | 0.88871 | 0.85868 | 0.8258 | 0.81342 | 0.91084 | 0.90384 | 0.8973 | 0.88959 | 0.87818 | 0.87292 | 0.8666 | 0.85958 | 0.85246 | 0.84127 | 0.81792 | 0.76997 | 0.73241 | 0.7265
INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | NO | 1.8553 | 1.2553 | 0.81499 | 0.44604 | -0.39381 | -1.1707 | -1.9753 | -2.9211 | -3.8972 | -4.7676 | -7.3601 | -11.476 | -13.4491 | -14.1847 | 5.5509 | 5.2028 | 4.94 | 4.6841 | 4.2476 | 3.8405 | 3.4471 | 2.9745 | 2.4262 | 1.8864 | 0.23319 | -1.9275 | -3.0104 | -3.8388 | 2.687 | 2.2159 | 1.869 | 1.5718 | 0.88865 | 0.24446 | -0.43125 | -1.2649 | -2.1273 | -2.9176 | -5.3539 | -8.8829 | -10.5032 | -11.0872
| DALNEIGH | CT |  |  | 1.8713 | 1.3165 | 0.91992 | 0.56532 | -0.25836 | -1.0392 | -1.7963 | -2.5943 | -3.4444 | -4.4298 | -7.3469 | -11.476 | -13.4491 | -14.1847 | 5.5509 | 5.205 | 4.9469 | 4.6841 | 4.2476 | 3.8405 | 3.4471 | 3.0112 | 2.5486 | 1.9991 | 0.3316 | -1.9275 | -3.0104 | -3.8388 | 2.6977 | 2.2645 | 1.9517 | 1.6512 | 0.96843 | 0.3131 | -0.32192 | -1.0069 | -1.7358 | -2.5949 | -5.2132 | -8.8829 | -10.5032 | -11.0872
| DALNEIGH | LW |  |  | 1.8553 | 1.2553 | 0.81499 | 0.44604 | -0.39381 | -1.1707 | -1.9753 | -2.9211 | -3.8972 | -4.7676 | -7.3601 | -10.3522 | -11.9331 | -12.5967 | 5.559 | 5.2028 | 4.94 | 4.7061 | 4.2852 | 3.8952 | 3.4886 | 2.9745 | 2.4262 | 1.8864 | 0.23319 | -1.407 | -1.9934 | -2.2594 | 2.687 | 2.2159 | 1.869 | 1.5718 | 0.88865 | 0.24446 | -0.43125 | -1.2649 | -2.1273 | -2.9176 | -5.3539 | -8.0595 | -9.3251 | -9.8437
| DALNEIGH | ST |  |  | 2.0041 | 1.5451 | 1.1976 | 0.87454 | 0.55429 | 0.29647 | 0.04085 | -0.22384 | -0.46412 | -0.81966 | -1.7989 | -4.1255 | -5.6006 | -6.5306 | 5.6203 | 5.3202 | 5.0972 | 4.888 | 4.6742 | 4.4961 | 4.3149 | 4.1229 | 3.9293 | 3.6684 | 2.882 | 0.96708 | -0.19471 | -1.1209 | 2.8175 | 2.4685 | 2.2049 | 1.9527 | 1.7047 | 1.4992 | 1.2919 | 1.0728 | 0.87101 | 0.56281 | -0.36016 | -2.7108 | -4.042 | -4.813
| DALNEIGH | SP |  |  | 2.0532 | 1.6285 | 1.3109 | 1.038 | 0.70217 | 0.42169 | 0.15073 | -0.12919 | -0.44754 | -0.83259 | -1.7558 | -3.431 | -4.8629 | -5.2751 | 5.6331 | 5.347 | 5.1347 | 4.9529 | 4.7415 | 4.5627 | 4.3841 | 4.1935 | 3.9642 | 3.6986 | 2.9789 | 1.4545 | -0.41555 | -2.0465 | 2.8547 | 2.5348 | 2.2961 | 2.091 | 1.8361 | 1.6179 | 1.4045 | 1.1789 | 0.91105 | 0.5897 | -0.23063 | -1.8828 | -3.3623 | -3.7161
COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | YES | 1.5456 | 1.5309 | 1.5111 | 1.4806 | 1.413 | 1.3486 | 1.2441 | 1.1211 | 0.99479 | 0.8539 | 0.53949 | 0.44458 | 0.44672 | 0.34661 | 2.2073 | 2.197 | 2.1849 | 2.1536 | 2.1137 | 2.0783 | 2.0273 | 1.9647 | 1.9047 | 1.7964 | 1.5998 | 1.5648 | 1.5456 | 1.4842 | 1.8191 | 1.8057 | 1.7877 | 1.7608 | 1.7043 | 1.643 | 1.5585 | 1.4472 | 1.3469 | 1.2142 | 0.92236 | 0.85053 | 0.85707 | 0.77532
| DALRULZION | CT |  |  | 1.5546 | 1.5434 | 1.528 | 1.4826 | 1.413 | 1.3492 | 1.2441 | 1.1211 | 0.99479 | 0.90472 | 0.59303 | 0.46558 | 0.44672 | 0.42669 | 2.2082 | 2.1986 | 2.1875 | 2.1536 | 2.1137 | 2.0783 | 2.0273 | 1.9647 | 1.9136 | 1.8532 | 1.626 | 1.5713 | 1.5573 | 1.5362 | 1.8306 | 1.8222 | 1.8098 | 1.7728 | 1.7109 | 1.654 | 1.5585 | 1.4472 | 1.3524 | 1.2758 | 0.97194 | 0.87182 | 0.85707 | 0.8421
| DALRULZION | LW |  |  | 1.5456 | 1.5309 | 1.5111 | 1.4806 | 1.4174 | 1.3486 | 1.274 | 1.1682 | 1.0044 | 0.8539 | 0.53949 | 0.44458 | 0.48251 | 0.46403 | 2.2073 | 2.197 | 2.1849 | 2.1648 | 2.1311 | 2.0939 | 2.052 | 1.9851 | 1.9047 | 1.7964 | 1.5998 | 1.5648 | 1.5749 | 1.5692 | 1.8191 | 1.8057 | 1.7877 | 1.7608 | 1.7043 | 1.643 | 1.5768 | 1.4848 | 1.3469 | 1.2142 | 0.92236 | 0.85053 | 0.87756 | 0.86421
| DALRULZION | ST |  |  | 1.5622 | 1.5556 | 1.5487 | 1.5374 | 1.5283 | 1.5112 | 1.4976 | 1.4852 | 1.4503 | 1.4071 | 1.2296 | 0.82079 | 0.72161 | 0.67393 | 2.2162 | 2.2113 | 2.2059 | 2.1968 | 2.1887 | 2.1744 | 2.163 | 2.1525 | 2.1303 | 2.1036 | 1.9846 | 1.6921 | 1.64 | 1.6049 | 1.8352 | 1.8297 | 1.8237 | 1.8144 | 1.8063 | 1.7914 | 1.7795 | 1.7688 | 1.7378 | 1.6999 | 1.5471 | 1.1767 | 1.075 | 1.0264
| DALRULZION | SP |  |  | 1.5666 | 1.5634 | 1.5582 | 1.5542 | 1.5404 | 1.5241 | 1.5096 | 1.4841 | 1.4484 | 1.412 | 1.2533 | 0.77474 | 0.47258 | 0.34661 | 2.2183 | 2.2155 | 2.2107 | 2.2067 | 2.1985 | 2.1879 | 2.1791 | 2.162 | 2.1372 | 2.1146 | 2.0255 | 1.7161 | 1.5456 | 1.4842 | 1.8388 | 1.8357 | 1.8312 | 1.8276 | 1.8144 | 1.7992 | 1.7856 | 1.7626 | 1.7312 | 1.6989 | 1.5564 | 1.1345 | 0.86729 | 0.77532
BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | 0.41661 | 0.41461 | 0.4077 | 0.39914 | 0.3794 | 0.35887 | 0.33257 | 0.29355 | 0.25681 | 0.23557 | 0.13261 | 0.084158 | 0.093111 | 0.075455 | 0.50411 | 0.50319 | 0.50014 | 0.49625 | 0.4832 | 0.4715 | 0.45345 | 0.43419 | 0.41618 | 0.4018 | 0.31758 | 0.29904 | 0.29573 | 0.27869 | 0.48715 | 0.48639 | 0.48191 | 0.47607 | 0.45577 | 0.4367 | 0.40627 | 0.37386 | 0.34384 | 0.32142 | 0.2077 | 0.18287 | 0.18105 | 0.16196
| DALWHINNIE | CT |  |  | 0.42453 | 0.42351 | 0.41842 | 0.4098 | 0.3886 | 0.36849 | 0.33257 | 0.29355 | 0.25681 | 0.23557 | 0.14961 | 0.10206 | 0.098173 | 0.093715 | 0.50709 | 0.50588 | 0.50312 | 0.49672 | 0.4832 | 0.4715 | 0.45345 | 0.43419 | 0.41618 | 0.4018 | 0.33052 | 0.30033 | 0.29643 | 0.291 | 0.49292 | 0.49178 | 0.488 | 0.47805 | 0.45577 | 0.4367 | 0.40627 | 0.37386 | 0.34384 | 0.32142 | 0.22214 | 0.18287 | 0.18105 | 0.17791
| DALWHINNIE | LW |  |  | 0.41661 | 0.41461 | 0.4077 | 0.39914 | 0.3794 | 0.35887 | 0.33778 | 0.31504 | 0.26714 | 0.23875 | 0.13261 | 0.084158 | 0.093111 | 0.088167 | 0.50411 | 0.50319 | 0.50014 | 0.49625 | 0.48703 | 0.47558 | 0.46445 | 0.4486 | 0.4208 | 0.40378 | 0.31758 | 0.29904 | 0.30263 | 0.30042 | 0.48715 | 0.48639 | 0.48191 | 0.47607 | 0.46093 | 0.4422 | 0.42431 | 0.39872 | 0.35203 | 0.32545 | 0.2077 | 0.18359 | 0.19104 | 0.1862
| DALWHINNIE | ST |  |  | 0.42532 | 0.42334 | 0.42122 | 0.41927 | 0.41705 | 0.41421 | 0.4105 | 0.40678 | 0.39642 | 0.38182 | 0.33448 | 0.21026 | 0.16428 | 0.14609 | 0.50751 | 0.50653 | 0.50557 | 0.50354 | 0.50178 | 0.49993 | 0.49696 | 0.49348 | 0.48753 | 0.47904 | 0.4501 | 0.34634 | 0.32665 | 0.31652 | 0.49268 | 0.49146 | 0.49033 | 0.4875 | 0.48523 | 0.48282 | 0.47866 | 0.47384 | 0.4647 | 0.45165 | 0.40711 | 0.27517 | 0.24664 | 0.23404
| DALWHINNIE | SP |  |  | 0.42534 | 0.42334 | 0.42166 | 0.41961 | 0.41221 | 0.40516 | 0.39729 | 0.3886 | 0.37919 | 0.36474 | 0.3176 | 0.19797 | 0.10164 | 0.075455 | 0.50756 | 0.50686 | 0.50595 | 0.50494 | 0.5014 | 0.49807 | 0.49402 | 0.4902 | 0.48397 | 0.47399 | 0.44682 | 0.3678 | 0.29573 | 0.27869 | 0.49283 | 0.49205 | 0.49098 | 0.48985 | 0.48418 | 0.47896 | 0.47254 | 0.46663 | 0.45659 | 0.44042 | 0.39575 | 0.27794 | 0.18349 | 0.16196
WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | 8.5184 | 8.1255 | 7.8199 | 7.6277 | 6.6136 | 5.597 | 4.5665 | 3.4548 | 3.0145 | 2.5859 | 0.95645 | -1.3838 | -2.6251 | -3.4554 | 11.3275 | 11.2658 | 11.2074 | 11.116 | 10.7818 | 10.3208 | 9.8427 | 9.3321 | 9.0559 | 8.7657 | 7.7777 | 5.8217 | 4.5038 | 2.9028 | 9.43 | 8.9016 | 8.6038 | 8.3969 | 7.472 | 6.5366 | 5.5731 | 4.5456 | 4.0945 | 3.6422 | 2.1153 | 0.0023465 | -0.96626 | -1.5966
| DENBURN | CT |  |  | 8.5184 | 8.3539 | 8.2566 | 8.2142 | 7.2434 | 6.1863 | 5.6301 | 5.1517 | 4.6287 | 3.9796 | 1.9021 | -1.2663 | -2.6251 | -3.4554 | 11.3275 | 11.2658 | 11.2074 | 11.116 | 10.8661 | 10.3545 | 10.0258 | 9.7237 | 9.3957 | 9.0121 | 7.8223 | 5.8217 | 4.5038 | 2.9375 | 9.4823 | 9.1202 | 8.9823 | 8.8971 | 7.9938 | 7.0072 | 6.4563 | 5.984 | 5.4659 | 4.8444 | 2.9634 | 0.14366 | -0.96626 | -1.5966
| DENBURN | LW |  |  | 8.5416 | 8.1255 | 7.8199 | 7.6277 | 6.6136 | 5.597 | 4.5665 | 3.4548 | 3.0145 | 2.5859 | 0.95645 | -1.3838 | -2.3173 | -3.0189 | 11.35 | 11.3106 | 11.2561 | 11.1887 | 10.7818 | 10.3208 | 9.8427 | 9.3321 | 9.0559 | 8.7657 | 7.7777 | 6.4282 | 5.9825 | 5.6207 | 9.43 | 8.9016 | 8.6038 | 8.3969 | 7.472 | 6.5366 | 5.5731 | 4.5456 | 4.0945 | 3.6422 | 2.1153 | 0.0023465 | -0.72775 | -1.2453
| DENBURN | ST |  |  | 8.5965 | 8.567 | 8.5293 | 8.4914 | 8.4596 | 8.3989 | 8.3326 | 8.1537 | 8.1177 | 7.9492 | 7.3916 | 5.4943 | 3.8733 | 2.5526 | 11.3881 | 11.3607 | 11.3265 | 11.2908 | 11.2594 | 11.2069 | 11.1487 | 11.0675 | 10.9871 | 10.8587 | 10.3968 | 8.6918 | 7.0999 | 5.3477 | 9.5693 | 9.5414 | 9.5054 | 9.4688 | 9.3498 | 9.2127 | 9.0715 | 8.8884 | 8.838 | 8.6705 | 8.0895 | 6.2549 | 4.8703 | 3.842
| DENBURN | SP |  |  | 8.5994 | 8.5752 | 8.5475 | 8.5124 | 8.4876 | 8.4356 | 8.3809 | 8.3107 | 8.2294 | 8.1382 | 7.617 | 6.0245 | 4.4806 | 3.6791 | 11.3887 | 11.3645 | 11.3361 | 11.3006 | 11.2727 | 11.2244 | 11.172 | 11.1061 | 11.0292 | 10.9397 | 10.3714 | 8.5678 | 6.1093 | 2.9028 | 9.5718 | 9.5491 | 9.5227 | 9.4889 | 9.465 | 9.4162 | 9.3645 | 9.2443 | 9.1177 | 8.938 | 8.3162 | 6.6933 | 5.3272 | 4.7002
TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42445123 | YES | 0.25511 | 0.22264 | 0.19103 | 0.15419 | -0.073954 | -0.21354 | -0.31787 | -0.41201 | -0.5313 | -0.58441 | -0.76436 | -0.8071 | -0.71618 | -0.82547 | 1.8391 | 1.7944 | 1.7509 | 1.7154 | 1.6227 | 1.5611 | 1.5091 | 1.443 | 1.362 | 1.3045 | 1.0853 | 0.97265 | 1.0105 | 0.92264 | 0.83702 | 0.83054 | 0.77786 | 0.71174 | 0.52058 | 0.40256 | 0.31409 | 0.23918 | 0.13982 | 0.090036 | -0.080426 | -0.19477 | -0.12643 | -0.17508
| DERVAIG | CT |  |  | 0.25784 | 0.22977 | 0.2023 | 0.18333 | 0.13217 | 0.019521 | -0.11396 | -0.22959 | -0.33856 | -0.39407 | -0.56595 | -0.71658 | -0.66084 | -0.65396 | 1.8564 | 1.8242 | 1.7921 | 1.7654 | 1.6866 | 1.6251 | 1.564 | 1.5027 | 1.4401 | 1.389 | 1.1973 | 1.0279 | 1.0268 | 1.0099 | 0.83805 | 0.83254 | 0.82706 | 0.82166 | 0.70367 | 0.6118 | 0.49927 | 0.40296 | 0.30947 | 0.25822 | 0.097369 | -0.10002 | -0.075641 | -0.072043
| DERVAIG | LW |  |  | 0.25511 | 0.22264 | 0.19103 | 0.15419 | -0.073954 | -0.21354 | -0.31787 | -0.41201 | -0.5313 | -0.58441 | -0.76436 | -0.8071 | -0.69453 | -0.72404 | 1.8391 | 1.7944 | 1.7509 | 1.7154 | 1.6227 | 1.5611 | 1.5091 | 1.443 | 1.362 | 1.3045 | 1.0853 | 0.97265 | 1.0105 | 1.0004 | 0.83702 | 0.83054 | 0.77786 | 0.71174 | 0.52058 | 0.40256 | 0.31409 | 0.23918 | 0.13982 | 0.090036 | -0.080426 | -0.19477 | -0.12643 | -0.14487
| DERVAIG | ST |  |  | 0.26467 | 0.24996 | 0.23458 | 0.22277 | 0.21463 | 0.20797 | 0.19856 | 0.18834 | 0.18193 | 0.16608 | 0.10709 | -0.16144 | -0.2584 | -0.30191 | 1.8613 | 1.8448 | 1.8267 | 1.8084 | 1.7894 | 1.7721 | 1.7486 | 1.7269 | 1.7084 | 1.6779 | 1.5636 | 1.2751 | 1.17 | 1.134 | 0.83873 | 0.83517 | 0.83145 | 0.82897 | 0.82684 | 0.82517 | 0.82288 | 0.81344 | 0.80421 | 0.77759 | 0.68793 | 0.31693 | 0.18251 | 0.15412
| DERVAIG | SP |  |  | 0.27253 | 0.26242 | 0.25203 | 0.2474 | 0.2369 | 0.22656 | 0.21655 | 0.2054 | 0.19236 | 0.16959 | -0.019743 | -0.46444 | -0.71618 | -0.82547 | 1.8695 | 1.8577 | 1.8449 | 1.8354 | 1.8144 | 1.7922 | 1.7693 | 1.7454 | 1.7161 | 1.6743 | 1.5544 | 1.2344 | 1.0113 | 0.92264 | 0.83992 | 0.83704 | 0.83406 | 0.83279 | 0.83041 | 0.82818 | 0.82599 | 0.82362 | 0.80029 | 0.74342 | 0.57606 | 0.18878 | -0.091714 | -0.17508
BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | YES | 6.2101 | 6.1454 | 6.0196 | 5.8293 | 5.4692 | 4.9635 | 4.4534 | 3.8165 | 2.9938 | 2.329 | 0.4378 | -1.3906 | -2.2377 | -2.5473 | 7.7138 | 7.6709 | 7.6174 | 7.5465 | 7.3894 | 7.1216 | 6.8587 | 6.5063 | 6.0483 | 5.5936 | 4.3024 | 3.2895 | 2.8523 | 2.553 | 6.7782 | 6.5545 | 6.4228 | 6.2783 | 5.7918 | 5.3191 | 4.8574 | 4.2841 | 3.5464 | 2.9262 | 1.1462 | -0.51151 | -1.2603 | -1.532
| DINGWALL | CT |  |  | 6.2101 | 6.1454 | 6.0632 | 5.9568 | 5.6073 | 5.2366 | 4.7864 | 4.1263 | 3.452 | 2.8589 | 0.9137 | -1.3906 | -2.2377 | -2.5473 | 7.7138 | 7.6709 | 7.6174 | 7.5465 | 7.444 | 7.2299 | 6.9365 | 6.5945 | 6.2395 | 5.8809 | 4.6286 | 3.2895 | 2.8523 | 2.553 | 6.8439 | 6.7027 | 6.629 | 6.5487 | 6.0993 | 5.6666 | 5.1391 | 4.5554 | 3.9593 | 3.4176 | 1.6056 | -0.51151 | -1.2603 | -1.532
| DINGWALL | LW |  |  | 6.233 | 6.1607 | 6.0196 | 5.8293 | 5.4692 | 4.9635 | 4.4534 | 3.8165 | 2.9938 | 2.329 | 0.4378 | -1.122 | -1.5886 | -1.8405 | 7.7395 | 7.7 | 7.66 | 7.5963 | 7.3894 | 7.1216 | 6.8587 | 6.5063 | 6.0483 | 5.5936 | 4.3024 | 3.3643 | 3.1929 | 3.1012 | 6.7782 | 6.5545 | 6.4228 | 6.2783 | 5.7918 | 5.3191 | 4.8574 | 4.2841 | 3.5464 | 2.9262 | 1.1462 | -0.30942 | -0.71018 | -0.93133
| DINGWALL | ST |  |  | 6.2712 | 6.2396 | 6.2004 | 6.1633 | 6.1233 | 6.0662 | 5.9769 | 5.8273 | 5.6542 | 5.4277 | 4.6903 | 2.6239 | 1.6214 | 1.1533 | 7.7582 | 7.738 | 7.7131 | 7.6884 | 7.6632 | 7.6292 | 7.5807 | 7.5149 | 7.4341 | 7.2865 | 6.6888 | 5.0036 | 4.2963 | 3.9116 | 6.9346 | 6.8587 | 6.7737 | 6.6737 | 6.5887 | 6.5027 | 6.3989 | 6.2643 | 6.1278 | 5.9207 | 5.1957 | 3.0326 | 2.0968 | 1.6814
| DINGWALL | SP |  |  | 6.2752 | 6.2493 | 6.2154 | 6.1888 | 6.1582 | 6.1124 | 6.0555 | 5.9396 | 5.7859 | 5.5693 | 4.7415 | 2.7121 | 1.0813 | 0.68524 | 7.7632 | 7.7483 | 7.7283 | 7.7111 | 7.6919 | 7.6651 | 7.6299 | 7.5702 | 7.4758 | 7.3252 | 6.8172 | 5.404 | 4.0245 | 3.3542 | 6.9947 | 6.9609 | 6.9133 | 6.8682 | 6.7661 | 6.6362 | 6.503 | 6.3357 | 6.1393 | 5.9047 | 5.1487 | 3.2457 | 1.6497 | 1.2834
CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | 0.47411 | 1.0657 | 1.0552 | 1.0424 | 1.0058 | 0.9724 | 0.92008 | 0.86169 | 0.79168 | 0.74408 | 0.58569 | 0.50679 | 0.51176 | 0.47013 | 0.60663 | 1.1512 | 1.1445 | 1.1364 | 1.1158 | 1.0944 | 1.0651 | 1.0332 | 1.0026 | 0.97417 | 0.86793 | 0.80671 | 0.8139 | 0.79245 | 0.53968 | 1.0891 | 1.0796 | 1.0674 | 1.0265 | 0.9885 | 0.94168 | 0.8773 | 0.81481 | 0.77017 | 0.62014 | 0.54054 | 0.55266 | 0.51597
| DIPPEN | CT |  |  | 0.48999 | 1.0807 | 1.072 | 1.0492 | 1.0101 | 0.97368 | 0.92008 | 0.86169 | 0.79468 | 0.76002 | 0.63957 | 0.52725 | 0.53814 | 0.53717 | 0.61445 | 1.1585 | 1.1526 | 1.1383 | 1.1158 | 1.0944 | 1.0651 | 1.0332 | 1.0026 | 0.98187 | 0.90315 | 0.81665 | 0.8139 | 0.8089 | 0.55899 | 1.1011 | 1.0948 | 1.0822 | 1.0405 | 1.0018 | 0.94168 | 0.8773 | 0.81725 | 0.78491 | 0.67099 | 0.56007 | 0.56693 | 0.56649
| DIPPEN | LW |  |  | 0.47411 | 1.0657 | 1.0552 | 1.0424 | 1.0058 | 0.9724 | 0.93712 | 0.88175 | 0.79168 | 0.74408 | 0.58569 | 0.50679 | 0.53345 | 0.51529 | 0.60663 | 1.1512 | 1.1445 | 1.1364 | 1.1163 | 1.0978 | 1.0779 | 1.046 | 1.0032 | 0.97417 | 0.86793 | 0.80671 | 0.81507 | 0.80832 | 0.53968 | 1.0891 | 1.0796 | 1.0674 | 1.0265 | 0.9885 | 0.94946 | 0.89616 | 0.81481 | 0.77017 | 0.62014 | 0.54054 | 0.56238 | 0.54798
| DIPPEN | ST |  |  | 0.48488 | 1.0681 | 1.062 | 1.054 | 1.0503 | 1.0459 | 1.0425 | 1.0363 | 1.0257 | 1.0041 | 0.93401 | 0.74874 | 0.67727 | 0.66165 | 0.6127 | 1.1535 | 1.1495 | 1.1442 | 1.141 | 1.1374 | 1.1345 | 1.1294 | 1.1224 | 1.1085 | 1.0631 | 0.92682 | 0.87221 | 0.85875 | 0.55273 | 1.0922 | 1.0873 | 1.0814 | 1.079 | 1.0753 | 1.0723 | 1.0676 | 1.057 | 1.0358 | 0.96712 | 0.78172 | 0.70502 | 0.68568
| DIPPEN | SP |  |  | 0.48549 | 1.0694 | 1.0645 | 1.0596 | 1.045 | 1.0327 | 1.0192 | 1.0034 | 0.98134 | 0.9525 | 0.86348 | 0.6629 | 0.51176 | 0.47013 | 0.61272 | 1.1539 | 1.1505 | 1.1471 | 1.1389 | 1.1319 | 1.1243 | 1.1153 | 1.1022 | 1.0858 | 1.036 | 0.92714 | 0.81801 | 0.79245 | 0.55377 | 1.0939 | 1.0903 | 1.0867 | 1.0704 | 1.0563 | 1.0408 | 1.023 | 1.0001 | 0.9685 | 0.88018 | 0.69617 | 0.55266 | 0.51597
BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | -0.47588 | -0.60556 | -0.77407 | -0.89234 | -1.1017 | -1.3258 | -1.5387 | -1.7573 | -2.0469 | -2.1912 | -2.6254 | -2.8995 | -2.81 | -3.0304 | 1.1378 | 0.98456 | 0.79183 | 0.68971 | 0.56145 | 0.43164 | 0.31641 | 0.18929 | 0.034307 | -0.057406 | -0.31131 | -0.41206 | -0.39518 | -0.53685 | 0.77232 | 0.64401 | 0.47492 | 0.37527 | 0.27214 | 0.1581 | -0.041662 | -0.26611 | -0.56017 | -0.74288 | -1.3108 | -1.475 | -1.389 | -1.525
| DORNOCH | CT |  |  | -0.43104 | -0.5337 | -0.68321 | -0.79259 | -1.0003 | -1.1896 | -1.4331 | -1.6824 | -1.9245 | -2.0381 | -2.3611 | -2.6942 | -2.6957 | -2.7151 | 1.1521 | 1.0063 | 0.81892 | 0.7124 | 0.58316 | 0.4659 | 0.3386 | 0.20866 | 0.081562 | 0.004292 | -0.20531 | -0.3695 | -0.38046 | -0.41332 | 0.77232 | 0.64401 | 0.47492 | 0.37527 | 0.27214 | 0.17769 | 0.01798 | -0.20662 | -0.42569 | -0.5766 | -1.044 | -1.3676 | -1.3462 | -1.3537
| DORNOCH | LW |  |  | -0.47588 | -0.60556 | -0.77407 | -0.89234 | -1.1017 | -1.3258 | -1.5387 | -1.7573 | -2.0469 | -2.1912 | -2.6254 | -2.8995 | -2.81 | -2.8447 | 1.1378 | 0.98456 | 0.79183 | 0.68971 | 0.56145 | 0.43164 | 0.31641 | 0.18929 | 0.034307 | -0.057406 | -0.31131 | -0.41206 | -0.37472 | -0.39019 | 0.77787 | 0.64744 | 0.48037 | 0.39262 | 0.29269 | 0.1581 | -0.041662 | -0.26611 | -0.56017 | -0.74288 | -1.3108 | -1.475 | -1.389 | -1.4268
| DORNOCH | ST |  |  | -0.43029 | -0.53831 | -0.66895 | -0.73051 | -0.78337 | -0.82597 | -0.87156 | -0.92493 | -1.0034 | -1.107 | -1.4076 | -2.0405 | -2.3753 | -2.4591 | 1.1571 | 1.0127 | 0.83718 | 0.75929 | 0.69826 | 0.64614 | 0.60036 | 0.55415 | 0.49882 | 0.44092 | 0.28379 | -0.092086 | -0.2276 | -0.2806 | 0.78734 | 0.66602 | 0.51188 | 0.44542 | 0.39431 | 0.34992 | 0.30832 | 0.26597 | 0.21706 | 0.16433 | -0.02892 | -0.67845 | -0.96351 | -1.0193
| DORNOCH | SP |  |  | -0.41504 | -0.51519 | -0.63687 | -0.68711 | -0.76689 | -0.8324 | -0.90113 | -0.9749 | -1.0546 | -1.166 | -1.4913 | -2.2284 | -2.7996 | -3.0304 | 1.165 | 1.0246 | 0.85269 | 0.78168 | 0.71218 | 0.65234 | 0.60039 | 0.54585 | 0.48402 | 0.42357 | 0.25749 | -0.099442 | -0.39518 | -0.53685 | 0.79524 | 0.67832 | 0.52798 | 0.46953 | 0.41526 | 0.36785 | 0.32543 | 0.28032 | 0.22814 | 0.17796 | -0.0090458 | -0.76642 | -1.3475 | -1.525
CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | 2.157 | 2.1522 | 2.1364 | 2.1165 | 2.0691 | 2.0168 | 1.9639 | 1.9053 | 1.829 | 1.7889 | 1.6408 | 1.6172 | 1.6422 | 1.603 | 2.1962 | 2.1947 | 2.1927 | 2.1894 | 2.1741 | 2.1527 | 2.1298 | 2.1002 | 2.0673 | 2.0423 | 1.9401 | 1.9302 | 1.9358 | 1.9089 | 2.1431 | 2.1345 | 2.1216 | 2.104 | 2.0694 | 2.029 | 1.9865 | 1.9347 | 1.8756 | 1.8392 | 1.6946 | 1.6799 | 1.6962 | 1.6695
| DOUGLAS PIER | CT |  |  | 2.1583 | 2.1559 | 2.1511 | 2.1398 | 2.0993 | 2.0555 | 1.9959 | 1.933 | 1.8735 | 1.8417 | 1.7022 | 1.6551 | 1.6559 | 1.65 | 2.1962 | 2.1947 | 2.1927 | 2.1894 | 2.1761 | 2.1572 | 2.1343 | 2.1101 | 2.0864 | 2.0681 | 1.9648 | 1.9446 | 1.9415 | 1.9344 | 2.1511 | 2.1465 | 2.1367 | 2.1162 | 2.0804 | 2.0455 | 2.0012 | 1.9546 | 1.9098 | 1.8809 | 1.7385 | 1.707 | 1.709 | 1.7058
| DOUGLAS PIER | LW |  |  | 2.157 | 2.1522 | 2.1364 | 2.1165 | 2.0691 | 2.0168 | 1.9639 | 1.9053 | 1.829 | 1.7889 | 1.6408 | 1.6172 | 1.6422 | 1.6297 | 2.1967 | 2.1951 | 2.1934 | 2.1909 | 2.1741 | 2.1527 | 2.1298 | 2.1002 | 2.0673 | 2.0423 | 1.9401 | 1.9302 | 1.9385 | 1.9342 | 2.1431 | 2.1345 | 2.1216 | 2.104 | 2.0694 | 2.029 | 1.9865 | 1.9347 | 1.8756 | 1.8392 | 1.6946 | 1.6799 | 1.6962 | 1.6876
| DOUGLAS PIER | ST |  |  | 2.1597 | 2.1586 | 2.1574 | 2.1549 | 2.1538 | 2.1521 | 2.1434 | 2.1356 | 2.124 | 2.1037 | 2.0301 | 1.8545 | 1.8117 | 1.788 | 2.1977 | 2.197 | 2.1962 | 2.1951 | 2.1939 | 2.1926 | 2.1909 | 2.1891 | 2.1865 | 2.1748 | 2.1296 | 2.0084 | 1.9916 | 1.9796 | 2.1527 | 2.1496 | 2.1457 | 2.1393 | 2.1342 | 2.1282 | 2.1198 | 2.1125 | 2.1015 | 2.0824 | 2.0148 | 1.8486 | 1.8167 | 1.799
| DOUGLAS PIER | SP |  |  | 2.161 | 2.1607 | 2.1607 | 2.1604 | 2.1589 | 2.1568 | 2.147 | 2.1357 | 2.1201 | 2.0993 | 2.015 | 1.7886 | 1.6588 | 1.603 | 2.1977 | 2.1971 | 2.1966 | 2.1958 | 2.1953 | 2.1942 | 2.193 | 2.1917 | 2.1864 | 2.176 | 2.1375 | 2.0063 | 1.9358 | 1.9089 | 2.1543 | 2.1523 | 2.1514 | 2.1487 | 2.1424 | 2.1339 | 2.1251 | 2.115 | 2.0993 | 2.0812 | 2.0126 | 1.8115 | 1.7054 | 1.6695
DOUNREAY | DOUNREAY | MINIMUM HEADROOM | NC 98156665 | NO | 14.6467 | 14.6429 | 14.6382 | 14.6328 | 14.6268 | 14.6197 | 14.6107 | 14.6011 | 14.5903 | 14.5716 | 14.5145 | 14.4558 | 14.4538 | 14.451 | 16.0031 | 15.9994 | 15.995 | 15.9896 | 15.9837 | 15.9765 | 15.9678 | 15.9583 | 15.9477 | 15.9322 | 15.8878 | 15.842 | 15.8405 | 15.8386 | 15.314 | 15.3095 | 15.304 | 15.2971 | 15.2894 | 15.2802 | 15.2691 | 15.257 | 15.2437 | 15.2245 | 15.1698 | 15.1136 | 15.112 | 15.1096
| DOUNREAY | CT |  |  | 14.6467 | 14.6429 | 14.6382 | 14.6328 | 14.6268 | 14.6203 | 14.6132 | 14.6055 | 14.597 | 14.5856 | 14.5457 | 14.4997 | 14.4954 | 14.4923 | 16.0031 | 15.9994 | 15.995 | 15.9898 | 15.9839 | 15.9774 | 15.9704 | 15.9628 | 15.9544 | 15.9434 | 15.9116 | 15.876 | 15.8729 | 15.8707 | 15.314 | 15.3095 | 15.3041 | 15.2977 | 15.2901 | 15.2819 | 15.2729 | 15.2632 | 15.2525 | 15.239 | 15.1996 | 15.1557 | 15.1518 | 15.1493
| DOUNREAY | LW |  |  | 14.6475 | 14.6434 | 14.6387 | 14.633 | 14.627 | 14.6197 | 14.6107 | 14.6011 | 14.5903 | 14.5716 | 14.5145 | 14.4558 | 14.4538 | 14.451 | 16.0036 | 15.9997 | 15.9952 | 15.9896 | 15.9837 | 15.9765 | 15.9678 | 15.9583 | 15.9477 | 15.9322 | 15.8878 | 15.842 | 15.8405 | 15.8386 | 15.3146 | 15.3096 | 15.304 | 15.2971 | 15.2894 | 15.2802 | 15.2691 | 15.257 | 15.2437 | 15.2245 | 15.1698 | 15.1136 | 15.112 | 15.1096
| DOUNREAY | ST |  |  | 14.6502 | 14.6486 | 14.6466 | 14.6443 | 14.642 | 14.639 | 14.6356 | 14.6316 | 14.6268 | 14.6196 | 14.5919 | 14.5085 | 14.4747 | 14.4712 | 16.0064 | 16.0047 | 16.0029 | 16.0007 | 15.9984 | 15.9955 | 15.9923 | 15.9884 | 15.9837 | 15.9767 | 15.9501 | 15.8813 | 15.8554 | 15.8531 | 15.318 | 15.316 | 15.3137 | 15.311 | 15.3081 | 15.3046 | 15.3006 | 15.2958 | 15.29 | 15.2814 | 15.2485 | 15.1638 | 15.1317 | 15.1288
| DOUNREAY | SP |  |  | 14.6503 | 14.649 | 14.6474 | 14.6456 | 14.6438 | 14.6417 | 14.6391 | 14.6364 | 14.6333 | 14.6288 | 14.6138 | 14.5574 | 14.4993 | 14.4889 | 16.0064 | 16.0052 | 16.0037 | 16.0019 | 16.0002 | 15.9981 | 15.9956 | 15.993 | 15.9899 | 15.9856 | 15.971 | 15.9206 | 15.8759 | 15.8682 | 15.3181 | 15.3166 | 15.3147 | 15.3126 | 15.3104 | 15.3077 | 15.3047 | 15.3013 | 15.2975 | 15.2921 | 15.2736 | 15.211 | 15.1556 | 15.1461
ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | 1.7409 | 1.7562 | 1.743 | 1.7227 | 1.6538 | 1.591 | 1.5285 | 1.4573 | 1.3614 | 1.3069 | 1.1035 | 1.037 | 0.98357 | 0.9543 | 2.032 | 2.0286 | 2.0249 | 2.0186 | 2.0106 | 2.0027 | 1.9958 | 1.9884 | 1.978 | 1.9611 | 1.8206 | 1.7769 | 1.7569 | 1.7333 | 1.6845 | 1.6925 | 1.682 | 1.6656 | 1.6166 | 1.5717 | 1.5247 | 1.4651 | 1.3897 | 1.3404 | 1.1423 | 1.0821 | 1.0534 | 1.0326
| DRIMORE | CT |  |  | 1.7888 | 1.8006 | 1.7956 | 1.7723 | 1.704 | 1.6377 | 1.5619 | 1.4815 | 1.4045 | 1.3613 | 1.1904 | 1.0659 | 1.0546 | 1.0418 | 2.032 | 2.0286 | 2.0249 | 2.0186 | 2.0106 | 2.0027 | 1.9958 | 1.9884 | 1.9804 | 1.9694 | 1.8631 | 1.7847 | 1.7756 | 1.7642 | 1.7179 | 1.7265 | 1.7215 | 1.6994 | 1.6403 | 1.5897 | 1.5349 | 1.4769 | 1.4205 | 1.3819 | 1.2128 | 1.1022 | 1.0955 | 1.0879
| DRIMORE | LW |  |  | 1.7409 | 1.7562 | 1.743 | 1.7227 | 1.6538 | 1.591 | 1.5285 | 1.4573 | 1.3614 | 1.3069 | 1.1035 | 1.037 | 1.0711 | 1.0584 | 2.0331 | 2.0301 | 2.0266 | 2.0216 | 2.0152 | 2.0077 | 2 | 1.9893 | 1.978 | 1.9611 | 1.8206 | 1.7769 | 1.7872 | 1.7833 | 1.6845 | 1.6925 | 1.682 | 1.6656 | 1.6166 | 1.5717 | 1.5247 | 1.4651 | 1.3897 | 1.3404 | 1.1423 | 1.0821 | 1.1044 | 1.0957
| DRIMORE | ST |  |  | 1.7762 | 1.7724 | 1.7687 | 1.7653 | 1.7607 | 1.7546 | 1.7447 | 1.7362 | 1.7192 | 1.6917 | 1.5984 | 1.3375 | 1.2462 | 1.2059 | 2.036 | 2.0346 | 2.0332 | 2.031 | 2.0287 | 2.0261 | 2.0229 | 2.019 | 2.0146 | 2.0077 | 1.9822 | 1.8836 | 1.8315 | 1.8112 | 1.709 | 1.7057 | 1.7025 | 1.6984 | 1.6937 | 1.6882 | 1.6789 | 1.6702 | 1.6549 | 1.6301 | 1.545 | 1.2982 | 1.2214 | 1.1944
| DRIMORE | SP |  |  | 1.7737 | 1.7681 | 1.7633 | 1.7578 | 1.7222 | 1.6884 | 1.6498 | 1.6105 | 1.5679 | 1.5041 | 1.3832 | 1.1333 | 0.98357 | 0.9543 | 2.0361 | 2.0353 | 2.0341 | 2.0326 | 2.0313 | 2.0292 | 2.0268 | 2.0243 | 2.0209 | 2.0157 | 2.0019 | 1.8784 | 1.7569 | 1.7333 | 1.7072 | 1.7028 | 1.6991 | 1.6945 | 1.6709 | 1.6478 | 1.621 | 1.5936 | 1.5619 | 1.5146 | 1.4198 | 1.2088 | 1.0534 | 1.0326
CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | 3.853 | 3.8265 | 3.8096 | 3.7951 | 3.7763 | 3.679 | 3.5157 | 3.3198 | 3.0659 | 2.9259 | 2.566 | 2.475 | 2.5536 | 2.4064 | 5.0238 | 4.999 | 4.9834 | 4.9686 | 4.9584 | 4.9483 | 4.847 | 4.7372 | 4.5934 | 4.4792 | 4.1992 | 4.1267 | 4.1088 | 3.991 | 3.3248 | 3.3012 | 3.2878 | 3.2767 | 3.265 | 3.2262 | 3.0809 | 2.9351 | 2.7541 | 2.6719 | 2.4528 | 2.3671 | 2.3953 | 2.2491
| DRUMNADROCHIT | CT |  |  | 3.8586 | 3.8343 | 3.819 | 3.805 | 3.7853 | 3.7664 | 3.6203 | 3.4264 | 3.2343 | 3.1326 | 2.7712 | 2.5839 | 2.6138 | 2.6065 | 5.0238 | 4.999 | 4.9834 | 4.9686 | 4.9584 | 4.9483 | 4.8777 | 4.7852 | 4.6935 | 4.6159 | 4.2918 | 4.1618 | 4.1425 | 4.104 | 3.3257 | 3.3024 | 3.2888 | 3.2767 | 3.265 | 3.254 | 3.1725 | 3.0148 | 2.8624 | 2.7992 | 2.6158 | 2.4679 | 2.4823 | 2.4729
| DRUMNADROCHIT | LW |  |  | 3.853 | 3.8265 | 3.8096 | 3.7951 | 3.7763 | 3.679 | 3.5157 | 3.3198 | 3.0659 | 2.9259 | 2.566 | 2.475 | 2.5869 | 2.5489 | 5.0254 | 5.0003 | 4.986 | 4.9738 | 4.9648 | 4.9505 | 4.847 | 4.7372 | 4.5934 | 4.4792 | 4.1992 | 4.1267 | 4.1621 | 4.1505 | 3.3248 | 3.3012 | 3.2878 | 3.2769 | 3.2655 | 3.2262 | 3.0809 | 2.9351 | 2.7541 | 2.6719 | 2.4528 | 2.3671 | 2.4593 | 2.4292
| DRUMNADROCHIT | ST |  |  | 3.8591 | 3.8343 | 3.8214 | 3.8122 | 3.8066 | 3.8011 | 3.7951 | 3.7886 | 3.7808 | 3.771 | 3.7403 | 3.3192 | 3.1116 | 3.0349 | 5.0275 | 5.0045 | 4.9926 | 4.9831 | 4.9778 | 4.9725 | 4.9667 | 4.96 | 4.953 | 4.9443 | 4.8736 | 4.4426 | 4.3483 | 4.2891 | 3.3266 | 3.3034 | 3.2918 | 3.2833 | 3.2797 | 3.2765 | 3.2727 | 3.2688 | 3.2641 | 3.2582 | 3.2417 | 3.0295 | 2.807 | 2.7398
| DRUMNADROCHIT | SP |  |  | 3.8598 | 3.8353 | 3.8227 | 3.8137 | 3.8057 | 3.7977 | 3.7891 | 3.7798 | 3.7699 | 3.7584 | 3.5719 | 2.9326 | 2.5536 | 2.4064 | 5.0281 | 5.0055 | 4.9936 | 4.9848 | 4.9804 | 4.9753 | 4.9697 | 4.9633 | 4.9558 | 4.9485 | 4.8448 | 4.3926 | 4.1088 | 3.991 | 3.3274 | 3.3048 | 3.2935 | 3.2856 | 3.2807 | 3.2762 | 3.2711 | 3.2656 | 3.2597 | 3.2529 | 3.1257 | 2.6858 | 2.3953 | 2.2491
GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | 0.018768 | 1.5518 | 1.5479 | 1.5437 | 1.5325 | 1.5183 | 1.5069 | 1.4922 | 1.4677 | 1.4565 | 1.4069 | 1.3966 | 1.4007 | 1.3871 | 0.068302 | 1.4847 | 1.4827 | 1.4807 | 1.4752 | 1.4687 | 1.4634 | 1.4554 | 1.4435 | 1.437 | 1.4022 | 1.3972 | 1.3977 | 1.3914 | 0.037189 | 1.4533 | 1.4497 | 1.4459 | 1.4359 | 1.423 | 1.4128 | 1.3992 | 1.3769 | 1.3664 | 1.3191 | 1.3097 | 1.3135 | 1.3016
| DRUMRUNIE | CT |  |  | 0.023513 | 1.5575 | 1.5548 | 1.5498 | 1.5373 | 1.5277 | 1.511 | 1.4929 | 1.4766 | 1.4662 | 1.4237 | 1.4067 | 1.4069 | 1.4055 | 0.069904 | 1.4865 | 1.4847 | 1.4818 | 1.4752 | 1.4707 | 1.4634 | 1.4554 | 1.4481 | 1.4417 | 1.4111 | 1.4017 | 1.4011 | 1.3996 | 0.041316 | 1.4582 | 1.4557 | 1.451 | 1.4395 | 1.4309 | 1.4159 | 1.3997 | 1.3851 | 1.3753 | 1.3345 | 1.3189 | 1.3191 | 1.3179
| DRUMRUNIE | LW |  |  | 0.018768 | 1.5518 | 1.5479 | 1.5437 | 1.5325 | 1.5183 | 1.5069 | 1.4922 | 1.4677 | 1.4565 | 1.4069 | 1.3966 | 1.4025 | 1.3993 | 0.068302 | 1.4847 | 1.4827 | 1.4807 | 1.4759 | 1.4687 | 1.4637 | 1.4559 | 1.4435 | 1.437 | 1.4022 | 1.3972 | 1.3992 | 1.3981 | 0.037189 | 1.4533 | 1.4497 | 1.4459 | 1.4359 | 1.423 | 1.4128 | 1.3992 | 1.3769 | 1.3664 | 1.3191 | 1.3097 | 1.3149 | 1.3121
| DRUMRUNIE | ST |  |  | 0.022606 | 1.5554 | 1.5546 | 1.5526 | 1.5512 | 1.5495 | 1.5478 | 1.5437 | 1.5401 | 1.5335 | 1.512 | 1.4571 | 1.4419 | 1.4344 | 0.06999 | 1.4863 | 1.4858 | 1.4846 | 1.4836 | 1.4825 | 1.4815 | 1.4785 | 1.4765 | 1.4726 | 1.4594 | 1.4189 | 1.4123 | 1.4088 | 0.040627 | 1.4565 | 1.4558 | 1.4539 | 1.4525 | 1.4509 | 1.4493 | 1.4453 | 1.4421 | 1.4359 | 1.4156 | 1.3609 | 1.3482 | 1.342
| DRUMRUNIE | SP |  |  | 0.023556 | 1.5567 | 1.5562 | 1.5558 | 1.5524 | 1.5488 | 1.5454 | 1.5413 | 1.5363 | 1.5277 | 1.5043 | 1.4503 | 1.4007 | 1.3871 | 0.070439 | 1.4869 | 1.4865 | 1.4862 | 1.4846 | 1.4828 | 1.4813 | 1.4793 | 1.4767 | 1.4719 | 1.4605 | 1.4314 | 1.3977 | 1.3914 | 0.041487 | 1.4577 | 1.4572 | 1.4569 | 1.4537 | 1.4504 | 1.4474 | 1.4437 | 1.4391 | 1.4312 | 1.4099 | 1.3603 | 1.3135 | 1.3016
STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | 4.6528 | 4.6528 | 4.6263 | 4.5913 | 4.4786 | 4.3629 | 4.2265 | 4.0762 | 3.885 | 3.7202 | 3.2958 | 2.9319 | 2.7359 | 2.6588 | 4.925 | 4.9103 | 4.8897 | 4.8637 | 4.8285 | 4.7924 | 4.7347 | 4.6448 | 4.5464 | 4.4338 | 4.162 | 3.9659 | 3.8371 | 3.6713 | 4.5747 | 4.5687 | 4.5444 | 4.5125 | 4.4235 | 4.3311 | 4.2134 | 4.0789 | 3.9141 | 3.7529 | 3.3539 | 3.068 | 2.9075 | 2.8449
| DRYMEN | CT |  |  | 4.696 | 4.6952 | 4.6705 | 4.6231 | 4.5081 | 4.3999 | 4.2633 | 4.1138 | 3.9677 | 3.8151 | 3.337 | 2.9319 | 2.7359 | 2.6588 | 4.925 | 4.9103 | 4.8897 | 4.8637 | 4.8285 | 4.7924 | 4.7347 | 4.665 | 4.5965 | 4.4958 | 4.1744 | 3.9659 | 3.8371 | 3.7079 | 4.6001 | 4.5918 | 4.5653 | 4.5164 | 4.4254 | 4.3404 | 4.2378 | 4.123 | 4.0035 | 3.8593 | 3.4027 | 3.068 | 2.9075 | 2.8449
| DRYMEN | LW |  |  | 4.6528 | 4.6528 | 4.6263 | 4.5913 | 4.4786 | 4.3629 | 4.2265 | 4.0762 | 3.885 | 3.7202 | 3.2958 | 3.0207 | 2.9112 | 2.8534 | 4.9299 | 4.919 | 4.9049 | 4.8882 | 4.855 | 4.8117 | 4.7349 | 4.6448 | 4.5464 | 4.4338 | 4.162 | 4.0362 | 3.998 | 3.9775 | 4.5747 | 4.5687 | 4.5444 | 4.5125 | 4.4235 | 4.3311 | 4.2134 | 4.0789 | 3.9141 | 3.7529 | 3.3539 | 3.1319 | 3.0434 | 2.9974
| DRYMEN | ST |  |  | 4.6959 | 4.6863 | 4.6754 | 4.6645 | 4.6556 | 4.6388 | 4.6173 | 4.6004 | 4.5708 | 4.5154 | 4.3004 | 3.7724 | 3.5755 | 3.456 | 4.944 | 4.9367 | 4.9281 | 4.918 | 4.9083 | 4.896 | 4.8812 | 4.8648 | 4.8443 | 4.8111 | 4.6601 | 4.2416 | 4.1068 | 3.9681 | 4.6055 | 4.5967 | 4.586 | 4.5724 | 4.5623 | 4.5445 | 4.5214 | 4.5025 | 4.474 | 4.4213 | 4.2071 | 3.682 | 3.5401 | 3.4501
| DRYMEN | SP |  |  | 4.7015 | 4.6918 | 4.6837 | 4.6721 | 4.6319 | 4.5895 | 4.5439 | 4.4956 | 4.4348 | 4.3566 | 4.1674 | 3.6163 | 3.3777 | 3.3252 | 4.9453 | 4.9396 | 4.933 | 4.9248 | 4.9127 | 4.8998 | 4.8852 | 4.8691 | 4.8364 | 4.7924 | 4.6666 | 4.2275 | 3.9332 | 3.6713 | 4.6127 | 4.6043 | 4.5969 | 4.5853 | 4.5557 | 4.5218 | 4.4866 | 4.4485 | 4.3949 | 4.3321 | 4.1698 | 3.6264 | 3.3939 | 3.3538
DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | 1.606 | 1.5875 | 1.5507 | 1.4966 | 1.3673 | 1.2247 | 1.0839 | 0.93515 | 0.74334 | 0.61919 | 0.25446 | 0.17969 | 0.23757 | 0.13028 | 1.7959 | 1.7886 | 1.7753 | 1.7545 | 1.7088 | 1.6573 | 1.6096 | 1.5593 | 1.4695 | 1.384 | 1.1317 | 1.0927 | 1.1107 | 1.0383 | 1.5196 | 1.5022 | 1.4728 | 1.4227 | 1.3059 | 1.1764 | 1.0481 | 0.91186 | 0.73731 | 0.61964 | 0.27369 | 0.20524 | 0.2557 | 0.16486
| DRYNOCH | CT |  |  | 1.6494 | 1.6432 | 1.617 | 1.5664 | 1.4421 | 1.3292 | 1.1802 | 1.0216 | 0.86882 | 0.78505 | 0.41238 | 0.27627 | 0.27487 | 0.25811 | 1.8036 | 1.7949 | 1.7843 | 1.766 | 1.7214 | 1.6786 | 1.6279 | 1.574 | 1.5209 | 1.4759 | 1.1963 | 1.1233 | 1.1107 | 1.087 | 1.545 | 1.5342 | 1.5087 | 1.4618 | 1.3636 | 1.2659 | 1.1321 | 0.98951 | 0.85144 | 0.77285 | 0.4153 | 0.2916 | 0.29002 | 0.27499
| DRYNOCH | LW |  |  | 1.606 | 1.5875 | 1.5507 | 1.4966 | 1.3673 | 1.2247 | 1.0839 | 0.93515 | 0.74334 | 0.61919 | 0.25446 | 0.17969 | 0.23757 | 0.2071 | 1.7959 | 1.7886 | 1.7753 | 1.7545 | 1.7088 | 1.6573 | 1.6096 | 1.5593 | 1.4695 | 1.384 | 1.1317 | 1.0927 | 1.1107 | 1.0987 | 1.5196 | 1.5022 | 1.4728 | 1.4227 | 1.3059 | 1.1764 | 1.0481 | 0.91186 | 0.73731 | 0.61964 | 0.27369 | 0.20524 | 0.2557 | 0.22864
| DRYNOCH | ST |  |  | 1.6452 | 1.6341 | 1.6224 | 1.6071 | 1.594 | 1.577 | 1.5552 | 1.5378 | 1.5015 | 1.4489 | 1.2528 | 0.76345 | 0.62092 | 0.53595 | 1.8081 | 1.804 | 1.7996 | 1.7935 | 1.7889 | 1.7829 | 1.7752 | 1.7683 | 1.7554 | 1.7362 | 1.6642 | 1.3215 | 1.2442 | 1.1875 | 1.5482 | 1.5387 | 1.5281 | 1.5133 | 1.501 | 1.4848 | 1.4634 | 1.4477 | 1.415 | 1.3693 | 1.1872 | 0.72933 | 0.61358 | 0.53433
| DRYNOCH | SP |  |  | 1.655 | 1.6489 | 1.6424 | 1.636 | 1.6028 | 1.572 | 1.5333 | 1.4929 | 1.4453 | 1.3788 | 1.1648 | 0.60083 | 0.26593 | 0.13028 | 1.8115 | 1.8094 | 1.8071 | 1.8046 | 1.795 | 1.7857 | 1.7742 | 1.7619 | 1.7472 | 1.726 | 1.6566 | 1.3289 | 1.1187 | 1.0383 | 1.5562 | 1.551 | 1.5441 | 1.5374 | 1.5124 | 1.4895 | 1.4566 | 1.4198 | 1.3761 | 1.3155 | 1.1213 | 0.59629 | 0.28564 | 0.16486
KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | YES | 0.7681 | 0.76909 | 0.73618 | 0.70968 | 0.58843 | 0.36143 | 0.13706 | -0.10045 | -0.36359 | -0.5826 | -1.2864 | -1.9521 | -2.2504 | -2.355 | 2.8276 | 2.8156 | 2.7938 | 2.7681 | 2.7291 | 2.5858 | 2.4293 | 2.3423 | 2.2585 | 2.1748 | 1.9062 | 1.772 | 1.7592 | 1.7388 | 3.4214 | 3.4007 | 3.3638 | 3.321 | 3.2358 | 3.0434 | 2.8613 | 2.673 | 2.4349 | 2.238 | 1.6054 | 0.99805 | 0.72676 | 0.6316
| DUFFTOWN | CT |  |  | 0.78922 | 0.79018 | 0.76115 | 0.72194 | 0.60847 | 0.39546 | 0.13706 | -0.10045 | -0.33388 | -0.53598 | -1.266 | -1.9521 | -2.2504 | -2.355 | 2.8276 | 2.8156 | 2.7938 | 2.7681 | 2.7291 | 2.5858 | 2.4293 | 2.3423 | 2.2585 | 2.1825 | 1.9337 | 1.8021 | 1.7868 | 1.7708 | 3.4245 | 3.4044 | 3.3691 | 3.3237 | 3.2407 | 3.0515 | 2.8613 | 2.673 | 2.4598 | 2.2764 | 1.6205 | 0.99805 | 0.72676 | 0.6316
| DUFFTOWN | LW |  |  | 0.7681 | 0.76909 | 0.73618 | 0.70968 | 0.58843 | 0.36143 | 0.1424 | -0.083631 | -0.36359 | -0.5826 | -1.2864 | -1.8065 | -2.0064 | -2.0879 | 2.8325 | 2.8223 | 2.8024 | 2.7828 | 2.7461 | 2.604 | 2.4469 | 2.3508 | 2.2595 | 2.1748 | 1.9062 | 1.772 | 1.7674 | 1.7637 | 3.4214 | 3.4007 | 3.3638 | 3.321 | 3.2358 | 3.0434 | 2.8623 | 2.6888 | 2.4349 | 2.238 | 1.6054 | 1.1327 | 0.95011 | 0.87524
| DUFFTOWN | ST |  |  | 0.7929 | 0.78343 | 0.75748 | 0.74715 | 0.72217 | 0.59324 | 0.46782 | 0.38885 | 0.31545 | 0.22436 | -0.092588 | -0.76657 | -1.0813 | -1.2256 | 2.8418 | 2.8375 | 2.8252 | 2.8181 | 2.803 | 2.6843 | 2.5419 | 2.4708 | 2.4051 | 2.3435 | 2.1388 | 1.8669 | 1.7592 | 1.7388 | 3.4491 | 3.4397 | 3.421 | 3.4091 | 3.3867 | 3.2633 | 3.1371 | 3.0614 | 2.9871 | 2.9067 | 2.6282 | 2.0848 | 1.7994 | 1.6684
| DUFFTOWN | SP |  |  | 0.79975 | 0.79534 | 0.77214 | 0.76588 | 0.72509 | 0.58571 | 0.45091 | 0.35767 | 0.26155 | 0.16841 | -0.12151 | -0.72182 | -1.1048 | -1.2132 | 2.8433 | 2.8407 | 2.8294 | 2.8254 | 2.8126 | 2.6971 | 2.5592 | 2.4928 | 2.4279 | 2.3743 | 2.209 | 2.0063 | 1.8445 | 1.7772 | 3.4525 | 3.4464 | 3.4307 | 3.4224 | 3.398 | 3.275 | 3.1507 | 3.0776 | 3.0022 | 2.9176 | 2.6526 | 2.1197 | 1.7792 | 1.6809
BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | 1.9339 | 1.7495 | 1.5136 | 1.2275 | 0.60561 | -0.070098 | -0.85124 | -1.5197 | -2.2866 | -2.8847 | -4.5604 | -6.9991 | -8.3352 | -8.8089 | 4.4342 | 4.3176 | 4.1647 | 3.9737 | 3.6318 | 3.2404 | 2.7463 | 2.3529 | 1.9119 | 1.5306 | 0.50919 | -0.71576 | -1.4279 | -1.9966 | 2.6001 | 2.421 | 2.1949 | 1.9134 | 1.3406 | 0.70668 | -0.044423 | -0.67444 | -1.3914 | -1.9697 | -3.5582 | -5.6179 | -6.7162 | -7.1028
| DUNBLANE | CT |  |  | 2.0775 | 1.9441 | 1.735 | 1.5402 | 1.0104 | 0.47515 | -0.13094 | -0.71673 | -1.3281 | -2.0526 | -4.4172 | -6.9991 | -8.3352 | -8.8089 | 4.5061 | 4.4036 | 4.2455 | 4.0828 | 3.8033 | 3.5124 | 3.1836 | 2.8756 | 2.5501 | 2.1009 | 0.58849 | -0.71576 | -1.4279 | -1.9966 | 2.7338 | 2.5977 | 2.3891 | 2.1845 | 1.7073 | 1.2214 | 0.67742 | 0.15206 | -0.39776 | -1.0879 | -3.367 | -5.6179 | -6.7162 | -7.1028
| DUNBLANE | LW |  |  | 1.9339 | 1.7495 | 1.5136 | 1.2275 | 0.60561 | -0.070098 | -0.85124 | -1.5197 | -2.2866 | -2.8847 | -4.5604 | -6.3406 | -7.2533 | -7.5894 | 4.4342 | 4.3176 | 4.1647 | 3.9737 | 3.6318 | 3.2404 | 2.7463 | 2.3529 | 1.9119 | 1.5306 | 0.50919 | -0.37846 | -0.69564 | -0.81681 | 2.6001 | 2.421 | 2.1949 | 1.9134 | 1.3406 | 0.70668 | -0.044423 | -0.67444 | -1.3914 | -1.9697 | -3.5582 | -5.1412 | -5.882 | -6.1544
| DUNBLANE | ST |  |  | 2.1262 | 2.0769 | 2.0018 | 1.9319 | 1.8656 | 1.7822 | 1.6575 | 1.55 | 1.4408 | 1.2248 | 0.39357 | -1.9929 | -3.0686 | -3.7199 | 4.5344 | 4.4952 | 4.4325 | 4.3729 | 4.3171 | 4.2459 | 4.1389 | 4.0491 | 3.949 | 3.7767 | 3.094 | 1.2935 | 0.51916 | -0.14396 | 2.7778 | 2.7285 | 2.6555 | 2.5841 | 2.5167 | 2.4306 | 2.3078 | 2.1994 | 2.0849 | 1.8641 | 1.0032 | -1.3226 | -2.3009 | -2.8753
| DUNBLANE | SP |  |  | 2.1469 | 2.1161 | 2.0564 | 2.0028 | 1.8883 | 1.7618 | 1.5817 | 1.4132 | 1.2601 | 1.0592 | 0.40795 | -1.6332 | -2.8092 | -3.1296 | 4.5389 | 4.509 | 4.4519 | 4.3985 | 4.3216 | 4.2327 | 4.0982 | 3.9717 | 3.8574 | 3.7188 | 3.2433 | 1.5891 | 0.34361 | -0.67441 | 2.7932 | 2.7607 | 2.701 | 2.6436 | 2.5343 | 2.4114 | 2.2386 | 2.0713 | 1.9215 | 1.7325 | 1.1129 | -0.93629 | -2.0665 | -2.3608
DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | YES | 16.473 | 16.1757 | 16.1037 | 16.0287 | 15.6115 | 15.2438 | 14.8902 | 14.4216 | 13.9026 | 13.442 | 11.8998 | 9.5561 | 8.1952 | 7.6729 | 17.3825 | 17.2479 | 17.2104 | 17.1654 | 16.9788 | 16.8056 | 16.639 | 16.3864 | 16.1129 | 15.8551 | 14.9764 | 13.7647 | 13.0489 | 12.566 | 16.0257 | 15.7581 | 15.6948 | 15.6301 | 15.2273 | 14.8779 | 14.5445 | 14.1288 | 13.6606 | 13.2542 | 11.8522 | 9.6682 | 8.4068 | 7.9454
| DUNOON | CT |  |  | 16.6435 | 16.4481 | 16.4426 | 16.4407 | 16.0332 | 15.6515 | 15.268 | 14.854 | 14.4116 | 13.8894 | 12.2114 | 9.5561 | 8.1952 | 7.6729 | 17.4676 | 17.3708 | 17.3541 | 17.3248 | 17.1275 | 16.9382 | 16.7514 | 16.5407 | 16.3154 | 16.0423 | 15.153 | 13.7647 | 13.0489 | 12.566 | 16.1733 | 16.0056 | 16.0078 | 16.0273 | 15.6458 | 15.2902 | 14.9313 | 14.5493 | 14.1399 | 13.66 | 12.1214 | 9.6682 | 8.4068 | 7.9454
| DUNOON | LW |  |  | 16.473 | 16.1757 | 16.1037 | 16.0287 | 15.6115 | 15.2438 | 14.8902 | 14.4216 | 13.9026 | 13.442 | 11.8998 | 10.1033 | 9.2191 | 8.8759 | 17.3825 | 17.2479 | 17.2104 | 17.1654 | 16.9788 | 16.8056 | 16.639 | 16.3864 | 16.1129 | 15.8551 | 14.9764 | 14.0399 | 13.6746 | 13.526 | 16.0257 | 15.7581 | 15.6948 | 15.6301 | 15.2273 | 14.8779 | 14.5445 | 14.1288 | 13.6606 | 13.2542 | 11.8522 | 10.201 | 9.3796 | 9.07
| DUNOON | ST |  |  | 16.641 | 16.5363 | 16.4815 | 16.4089 | 16.3243 | 16.2352 | 16.1407 | 16.0492 | 16.0198 | 15.9019 | 15.4342 | 13.8413 | 12.8048 | 12.1881 | 17.4521 | 17.3949 | 17.3656 | 17.3235 | 17.276 | 17.2243 | 17.1674 | 17.1091 | 17.0722 | 16.9852 | 16.6432 | 15.562 | 14.843 | 14.3032 | 16.1878 | 16.1084 | 16.0576 | 15.9951 | 15.921 | 15.8442 | 15.7594 | 15.678 | 15.6556 | 15.5511 | 15.1347 | 13.6196 | 12.674 | 12.1425
| DUNOON | SP |  |  | 16.6908 | 16.6178 | 16.5901 | 16.5582 | 16.4655 | 16.3547 | 16.2478 | 16.1435 | 16.0161 | 15.8247 | 15.3076 | 14.1072 | 13.1026 | 12.8222 | 17.4731 | 17.4298 | 17.412 | 17.3907 | 17.3441 | 17.2872 | 17.2288 | 17.1702 | 17.0914 | 16.975 | 16.6243 | 15.7499 | 14.7139 | 13.8279 | 16.2373 | 16.189 | 16.1651 | 16.138 | 16.0516 | 15.9497 | 15.8522 | 15.758 | 15.6464 | 15.4712 | 15.0032 | 13.9179 | 12.9624 | 12.7119
DUNVEGAN | DUNVEGAN GRID | MINIMUM HEADROOM | NG 27604720 | YES | 4.7185 | 4.7132 | 4.7041 | 4.6813 | 4.6946 | 4.7105 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.3594 | 4.3575 | 4.3541 | 4.3458 | 4.3507 | 4.3565 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.3587 | 4.354 | 4.346 | 4.3261 | 4.3378 | 4.3517 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
| DUNVEGAN GRID | CT |  |  | 4.7185 | 4.7132 | 4.7041 | 4.6813 | 4.6946 | 4.7105 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.3594 | 4.3575 | 4.3541 | 4.3458 | 4.3507 | 4.3565 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.3587 | 4.354 | 4.346 | 4.3261 | 4.3378 | 4.3517 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
| DUNVEGAN GRID | LW |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
| DUNVEGAN GRID | ST |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
| DUNVEGAN GRID | SP |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | YES | 8.9913 | 8.9096 | 8.8113 | 8.6829 | 8.3977 | 7.9788 | 7.5823 | 7.1371 | 6.603 | 5.9513 | 3.7537 | 1.1095 | 0.70223 | 0.56395 | 11.0592 | 10.996 | 10.881 | 10.7156 | 10.4936 | 10.1513 | 9.8513 | 9.5064 | 9.0905 | 8.579 | 7.0127 | 5.3776 | 5.152 | 5.0639 | 9.9221 | 9.8447 | 9.7327 | 9.5418 | 9.3022 | 8.9028 | 8.4461 | 7.9559 | 7.3773 | 6.6977 | 4.6082 | 2.1745 | 1.8152 | 1.6934
| DYCE NORTH | CT |  |  | 8.9913 | 8.9096 | 8.8113 | 8.6829 | 8.3977 | 7.9788 | 7.5976 | 7.2149 | 6.7506 | 6.1954 | 4.5291 | 2.0019 | 1.4091 | 1.1895 | 11.0592 | 10.996 | 10.881 | 10.7156 | 10.4936 | 10.1513 | 9.8551 | 9.5583 | 9.1973 | 8.765 | 7.6027 | 6.2394 | 6.1087 | 6.045 | 9.9221 | 9.8447 | 9.7327 | 9.5418 | 9.3022 | 8.9028 | 8.5002 | 8.0772 | 7.5697 | 6.9737 | 5.3473 | 3.0634 | 2.5354 | 2.3398
| DYCE NORTH | LW |  |  | 9.0171 | 8.93 | 8.8435 | 8.7287 | 8.4595 | 8.0073 | 7.5823 | 7.1371 | 6.603 | 5.9513 | 3.7537 | 1.1095 | 0.70223 | 0.56395 | 11.0796 | 11.0129 | 10.9153 | 10.7634 | 10.5485 | 10.1805 | 9.8513 | 9.5064 | 9.0905 | 8.579 | 7.0127 | 5.3776 | 5.3187 | 5.2918 | 9.9468 | 9.8645 | 9.7744 | 9.6006 | 9.3637 | 8.9142 | 8.4461 | 7.9559 | 7.3773 | 6.6977 | 4.6082 | 2.1745 | 1.8152 | 1.6934
| DYCE NORTH | ST |  |  | 9.0838 | 9.0518 | 9.0147 | 8.9747 | 8.9108 | 8.7737 | 8.6696 | 8.4888 | 8.2376 | 7.8584 | 6.5088 | 3.1932 | 1.6988 | 1.5091 | 11.1303 | 11.1055 | 11.0767 | 11.0454 | 10.996 | 10.8315 | 10.7007 | 10.5058 | 10.2984 | 9.9931 | 8.9187 | 6.3141 | 5.152 | 5.0639 | 10.0098 | 9.9797 | 9.9448 | 9.9068 | 9.8468 | 9.7072 | 9.5586 | 9.3618 | 9.1516 | 8.7871 | 7.4888 | 4.1446 | 2.5656 | 2.3891
| DYCE NORTH | SP |  |  | 9.087 | 9.0607 | 9.0295 | 8.999 | 8.9507 | 8.8268 | 8.7393 | 8.6326 | 8.4805 | 8.2002 | 7.3486 | 4.9384 | 2.5602 | 2.0044 | 11.1325 | 11.112 | 11.0875 | 11.0635 | 11.0257 | 10.8932 | 10.7919 | 10.6527 | 10.4946 | 10.2678 | 9.587 | 7.694 | 5.8237 | 5.369 | 10.0128 | 9.9881 | 9.9586 | 9.9298 | 9.8843 | 9.7618 | 9.6708 | 9.518 | 9.3611 | 9.1177 | 8.2994 | 5.8485 | 3.4578 | 2.8943
THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | 0.93644 | 0.93938 | 0.93772 | 0.93297 | 0.917 | 0.90193 | 0.8818 | 0.86191 | 0.84344 | 0.83241 | 0.7844 | 0.76733 | 0.77081 | 0.76249 | 0.95723 | 0.95741 | 0.95711 | 0.95355 | 0.94541 | 0.9368 | 0.92755 | 0.91904 | 0.91095 | 0.90393 | 0.86786 | 0.85608 | 0.8571 | 0.85352 | 0.92224 | 0.92344 | 0.92289 | 0.91961 | 0.90683 | 0.89412 | 0.87917 | 0.86499 | 0.85194 | 0.8426 | 0.79833 | 0.78471 | 0.78821 | 0.78299
| EDAY | CT |  |  | 0.9438 | 0.94718 | 0.94473 | 0.9355 | 0.91842 | 0.90193 | 0.8818 | 0.86191 | 0.84344 | 0.83241 | 0.80591 | 0.76733 | 0.77496 | 0.77619 | 0.95928 | 0.96026 | 0.95881 | 0.95355 | 0.94541 | 0.9368 | 0.92755 | 0.91904 | 0.91095 | 0.90393 | 0.88748 | 0.85608 | 0.8571 | 0.85535 | 0.92522 | 0.92425 | 0.92289 | 0.91961 | 0.90683 | 0.89412 | 0.87917 | 0.86499 | 0.85194 | 0.8426 | 0.82092 | 0.78471 | 0.79104 | 0.7924
| EDAY | LW |  |  | 0.93644 | 0.94018 | 0.93772 | 0.93297 | 0.917 | 0.90343 | 0.89021 | 0.87279 | 0.84867 | 0.83741 | 0.7844 | 0.77152 | 0.77838 | 0.77136 | 0.95723 | 0.95839 | 0.95711 | 0.95473 | 0.94729 | 0.94103 | 0.93468 | 0.92464 | 0.91323 | 0.90637 | 0.86786 | 0.8589 | 0.86091 | 0.85821 | 0.92224 | 0.92477 | 0.92325 | 0.91987 | 0.90807 | 0.89851 | 0.8887 | 0.87413 | 0.85595 | 0.84674 | 0.79833 | 0.78896 | 0.79394 | 0.78883
| EDAY | ST |  |  | 0.94271 | 0.94226 | 0.9418 | 0.94119 | 0.94144 | 0.93972 | 0.93892 | 0.93786 | 0.93224 | 0.92547 | 0.90686 | 0.84632 | 0.82853 | 0.82006 | 0.95974 | 0.95945 | 0.9591 | 0.95841 | 0.95824 | 0.9566 | 0.95577 | 0.9543 | 0.95042 | 0.9463 | 0.93508 | 0.88866 | 0.87682 | 0.87071 | 0.92653 | 0.92616 | 0.92569 | 0.92494 | 0.92441 | 0.92324 | 0.92223 | 0.92075 | 0.91674 | 0.91111 | 0.8966 | 0.84273 | 0.83069 | 0.82566
| EDAY | SP |  |  | 0.94018 | 0.93938 | 0.93911 | 0.93893 | 0.93298 | 0.92743 | 0.92086 | 0.91377 | 0.90437 | 0.89316 | 0.86347 | 0.81121 | 0.77081 | 0.76249 | 0.95783 | 0.95741 | 0.95715 | 0.95697 | 0.95464 | 0.95241 | 0.94965 | 0.9467 | 0.94185 | 0.93714 | 0.92116 | 0.89274 | 0.86033 | 0.85352 | 0.92391 | 0.92344 | 0.92327 | 0.92323 | 0.91916 | 0.91532 | 0.91067 | 0.90562 | 0.89809 | 0.89005 | 0.86602 | 0.82516 | 0.78821 | 0.78299
FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | 5.0281 | 4.9326 | 4.8717 | 4.8073 | 4.7718 | 3.6792 | 2.321 | 0.69871 | -1.197 | -3.511 | -7.2216 | -8.9223 | -8.9369 | -8.9457 | 4.9029 | 4.7993 | 4.7349 | 4.667 | 4.6257 | 3.4513 | 1.9912 | 0.24273 | -1.7951 | -4.4451 | -8.7222 | -10.6631 | -10.6999 | -10.7387 | 4.9656 | 4.8577 | 4.785 | 4.7067 | 4.6281 | 3.4575 | 1.9911 | 0.26174 | -1.7582 | -4.1218 | -7.9988 | -9.8052 | -9.9551 | -10.024
| EDZELL | CT |  |  | 5.0281 | 4.9326 | 4.8717 | 4.8073 | 4.7718 | 3.6792 | 2.321 | 0.70032 | -1.1846 | -3.4755 | -7.1838 | -8.8753 | -8.8928 | -8.9012 | 4.9029 | 4.7993 | 4.7349 | 4.667 | 4.6257 | 3.4513 | 1.9912 | 0.24775 | -1.7791 | -4.4037 | -8.6851 | -10.6527 | -10.6999 | -10.7387 | 4.9708 | 4.8735 | 4.8049 | 4.7311 | 4.6493 | 3.5387 | 2.067 | 0.3361 | -1.6469 | -3.9691 | -7.8679 | -9.8021 | -9.9551 | -10.024
| EDZELL | LW |  |  | 5.0323 | 4.938 | 4.8806 | 4.8197 | 4.7866 | 3.6926 | 2.3298 | 0.69871 | -1.197 | -3.511 | -7.2216 | -8.9223 | -8.9369 | -8.9457 | 4.906 | 4.8021 | 4.7397 | 4.6737 | 4.6344 | 3.4584 | 1.9944 | 0.24273 | -1.7951 | -4.4451 | -8.7222 | -10.6631 | -10.6751 | -10.6893 | 4.9656 | 4.8577 | 4.785 | 4.7067 | 4.6281 | 3.4575 | 1.9911 | 0.26174 | -1.7582 | -4.1218 | -7.9988 | -9.8052 | -9.8415 | -9.8897
| EDZELL | ST |  |  | 5.0374 | 4.9489 | 4.8959 | 4.8407 | 4.8179 | 3.7343 | 2.3882 | 0.77825 | -1.0978 | -3.376 | -7.0326 | -8.8488 | -8.9077 | -8.9172 | 4.9149 | 4.8194 | 4.7648 | 4.708 | 4.6854 | 3.5275 | 2.0865 | 0.36134 | -1.6497 | -4.1894 | -8.4039 | -10.4513 | -10.539 | -10.5908 | 4.9822 | 4.8927 | 4.8403 | 4.7857 | 4.7599 | 3.6738 | 2.3187 | 0.68411 | -1.2446 | -3.5872 | -7.3416 | -9.1901 | -9.2489 | -9.2825
| EDZELL | SP |  |  | 5.0395 | 4.9513 | 4.8995 | 4.8468 | 4.8248 | 3.7443 | 2.3993 | 0.79165 | -1.0835 | -3.3563 | -6.982 | -8.7561 | -8.8829 | -8.9024 | 4.9169 | 4.8222 | 4.769 | 4.7149 | 4.6929 | 3.5376 | 2.0984 | 0.37624 | -1.6317 | -4.1833 | -8.3897 | -10.4353 | -10.5941 | -10.6795 | 4.9842 | 4.8952 | 4.8442 | 4.7922 | 4.7701 | 3.6843 | 2.3309 | 0.69641 | -1.2313 | -3.5685 | -7.2941 | -9.1029 | -9.3841 | -9.5338
MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | NO | 8.7162 | 8.6908 | 8.6539 | 8.5953 | 8.4664 | 8.3226 | 8.1396 | 7.9182 | 7.6369 | 7.4009 | 6.3433 | 4.6105 | 3.0061 | 1.7501 | 8.6494 | 8.6302 | 8.6039 | 8.5614 | 8.492 | 8.4181 | 8.3296 | 8.2263 | 8.084 | 7.951 | 7.3395 | 6.4541 | 5.5717 | 4.7427 | 8.2786 | 8.2583 | 8.2274 | 8.1724 | 8.057 | 7.9288 | 7.7659 | 7.5671 | 7.3118 | 7.0963 | 6.155 | 4.719 | 3.5142 | 2.6332
| EDZELL STREET | CT |  |  | 8.7196 | 8.6947 | 8.6564 | 8.5953 | 8.4664 | 8.3226 | 8.1396 | 7.9289 | 7.7041 | 7.434 | 6.3433 | 4.6105 | 3.0061 | 1.7501 | 8.6494 | 8.6302 | 8.6039 | 8.5614 | 8.492 | 8.4181 | 8.3296 | 8.2263 | 8.1156 | 7.9743 | 7.3532 | 6.4541 | 5.5717 | 4.7427 | 8.2801 | 8.2604 | 8.2278 | 8.1724 | 8.057 | 7.9288 | 7.7659 | 7.5777 | 7.3766 | 7.1333 | 6.155 | 4.719 | 3.5142 | 2.6332
| EDZELL STREET | LW |  |  | 8.7162 | 8.6908 | 8.6539 | 8.6102 | 8.4816 | 8.3271 | 8.1503 | 7.9182 | 7.6369 | 7.4009 | 6.3965 | 5.0479 | 3.5725 | 2.3661 | 8.6543 | 8.6357 | 8.6125 | 8.5846 | 8.5219 | 8.4463 | 8.3573 | 8.23 | 8.084 | 7.951 | 7.3395 | 6.6618 | 5.9151 | 5.2511 | 8.2786 | 8.2583 | 8.2274 | 8.1892 | 8.0754 | 7.938 | 7.7792 | 7.5671 | 7.3118 | 7.0963 | 6.1842 | 5.0954 | 4.0047 | 3.1672
| EDZELL STREET | ST |  |  | 8.7503 | 8.7261 | 8.7025 | 8.6754 | 8.6537 | 8.627 | 8.6009 | 8.5709 | 8.537 | 8.4674 | 8.1288 | 6.7577 | 5.3897 | 4.0669 | 8.6689 | 8.6522 | 8.6354 | 8.6143 | 8.5957 | 8.5732 | 8.5509 | 8.5244 | 8.4953 | 8.4434 | 8.2007 | 7.2921 | 6.4722 | 5.6197 | 8.3093 | 8.2907 | 8.2721 | 8.249 | 8.2306 | 8.2073 | 8.1842 | 8.1571 | 8.1264 | 8.0631 | 7.7718 | 6.5512 | 5.5118 | 4.5336
| EDZELL STREET | SP |  |  | 8.7411 | 8.7197 | 8.6976 | 8.6763 | 8.6454 | 8.6145 | 8.5786 | 8.539 | 8.486 | 8.4166 | 8.1215 | 7.1551 | 5.6705 | 4.5579 | 8.6601 | 8.6453 | 8.629 | 8.6124 | 8.5919 | 8.5705 | 8.5457 | 8.5179 | 8.4787 | 8.4274 | 8.2122 | 7.5182 | 6.4183 | 5.4193 | 8.2998 | 8.2839 | 8.2667 | 8.2494 | 8.2235 | 8.1973 | 8.1662 | 8.1315 | 8.0834 | 8.0215 | 7.776 | 6.9861 | 5.7529 | 4.9452
ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | YES | 8.0355 | 7.7413 | 7.3651 | 6.9795 | 6.5324 | 6.0714 | 5.5697 | 5.011 | 4.2874 | 3.628 | 1.6441 | -1.1231 | -2.2935 | -2.6708 | 9.2378 | 9.0118 | 8.719 | 8.3979 | 8.1064 | 7.8208 | 7.5232 | 7.1924 | 6.7644 | 6.3382 | 5.0704 | 3.4764 | 2.7921 | 2.3652 | 7.9089 | 7.6601 | 7.3337 | 6.9917 | 6.596 | 6.1857 | 5.7347 | 5.229 | 4.5749 | 3.97 | 2.1397 | -0.25946 | -1.2805 | -1.612
| ELGIN | CT |  |  | 8.0746 | 7.7939 | 7.424 | 7.022 | 6.5705 | 6.1174 | 5.6044 | 5.0421 | 4.463 | 3.8511 | 1.7626 | -1.1231 | -2.2935 | -2.6708 | 9.2416 | 9.0185 | 8.7213 | 8.3979 | 8.1064 | 7.8208 | 7.5232 | 7.2008 | 6.8685 | 6.4982 | 5.1999 | 3.4764 | 2.7921 | 2.3652 | 7.9408 | 7.7037 | 7.3815 | 7.0214 | 6.62 | 6.2164 | 5.7615 | 5.2614 | 4.7466 | 4.1951 | 2.2991 | -0.25946 | -1.2805 | -1.612
| ELGIN | LW |  |  | 8.0355 | 7.7413 | 7.3651 | 6.9795 | 6.5324 | 6.0714 | 5.5697 | 5.011 | 4.2874 | 3.628 | 1.6441 | -0.84107 | -1.7213 | -1.9904 | 9.2378 | 9.0118 | 8.719 | 8.417 | 8.1376 | 7.8537 | 7.5412 | 7.1924 | 6.7644 | 6.3382 | 5.0704 | 3.5523 | 3.1452 | 3.0201 | 7.9089 | 7.6601 | 7.3337 | 6.9917 | 6.596 | 6.1857 | 5.7347 | 5.229 | 4.5749 | 3.97 | 2.1397 | -0.051542 | -0.81346 | -1.0503
| ELGIN | ST |  |  | 8.1424 | 7.8891 | 7.5803 | 7.2829 | 7.0828 | 6.8897 | 6.7016 | 6.5125 | 6.3006 | 6.0218 | 5.0247 | 2.326 | 1.0643 | 0.57916 | 9.2927 | 9.095 | 8.8409 | 8.5892 | 8.4275 | 8.2736 | 8.1262 | 7.9799 | 7.8206 | 7.6185 | 6.8909 | 4.9035 | 4.002 | 3.5354 | 8.0067 | 7.7973 | 7.5337 | 7.2735 | 7.1018 | 6.9348 | 6.7723 | 6.609 | 6.4255 | 6.1775 | 5.2713 | 2.6949 | 1.5664 | 1.1707
| ELGIN | SP |  |  | 8.1459 | 7.8991 | 7.5964 | 7.3115 | 7.0887 | 6.8831 | 6.6753 | 6.4705 | 6.2353 | 5.9794 | 5.1595 | 2.9641 | 1.596 | 1.2928 | 9.2936 | 9.1008 | 8.8505 | 8.6091 | 8.442 | 8.2886 | 8.1374 | 7.992 | 7.8219 | 7.6418 | 7.0534 | 5.3655 | 4.0358 | 3.1893 | 8.0097 | 7.8067 | 7.5489 | 7.3013 | 7.1106 | 6.9345 | 6.7559 | 6.581 | 6.3769 | 6.1541 | 5.4407 | 3.3969 | 2.0449 | 1.765
ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | 0.88262 | 0.35956 | -0.038906 | -0.40359 | -0.75492 | -1.04 | -1.3616 | -1.6825 | -1.9982 | -2.2268 | -2.9052 | -3.8281 | -4.2897 | -4.4628 | 1.3877 | 0.84596 | 0.42412 | 0.040248 | -0.35532 | -0.60493 | -0.83762 | -1.0608 | -1.2728 | -1.4219 | -1.815 | -2.2239 | -2.4411 | -2.5787 | 1.515 | 0.99542 | 0.59752 | 0.23418 | -0.17846 | -0.45888 | -0.72718 | -0.99756 | -1.2977 | -1.5132 | -2.1351 | -2.9613 | -3.3614 | -3.5069
| ELLIOT DEPOT | CT |  |  | 0.88262 | 0.35956 | -0.038906 | -0.40359 | -0.75492 | -1.0316 | -1.3106 | -1.5873 | -1.8593 | -2.1163 | -2.9052 | -3.8281 | -4.2897 | -4.4628 | 1.3878 | 0.84652 | 0.42412 | 0.040248 | -0.35532 | -0.60493 | -0.82289 | -1.029 | -1.2227 | -1.3821 | -1.815 | -2.2239 | -2.4411 | -2.5787 | 1.515 | 0.99542 | 0.59752 | 0.23418 | -0.17846 | -0.45888 | -0.70307 | -0.93642 | -1.1691 | -1.4078 | -2.1351 | -2.9613 | -3.3614 | -3.5069
| ELLIOT DEPOT | LW |  |  | 0.88482 | 0.36235 | -0.034658 | -0.39719 | -0.74804 | -1.04 | -1.3616 | -1.6825 | -1.9982 | -2.2268 | -2.8777 | -3.537 | -3.9111 | -4.0652 | 1.3877 | 0.84596 | 0.42474 | 0.044369 | -0.34997 | -0.60356 | -0.83762 | -1.0608 | -1.2728 | -1.4219 | -1.8015 | -2.0969 | -2.2437 | -2.308 | 1.521 | 1.0038 | 0.60937 | 0.24576 | -0.16817 | -0.45695 | -0.72718 | -0.99756 | -1.2977 | -1.5132 | -2.1188 | -2.7128 | -3.0346 | -3.1636
| ELLIOT DEPOT | ST |  |  | 0.89116 | 0.3738 | -0.017272 | -0.36721 | -0.69542 | -0.87672 | -1.0338 | -1.1747 | -1.3006 | -1.3939 | -1.6151 | -1.9938 | -2.3474 | -2.5986 | 1.4007 | 0.86608 | 0.45474 | 0.089005 | -0.24929 | -0.43395 | -0.59754 | -0.74471 | -0.8753 | -0.97511 | -1.2106 | -1.5221 | -1.7324 | -1.9202 | 1.524 | 1.0105 | 0.62074 | 0.27275 | -0.050627 | -0.22785 | -0.3823 | -0.52082 | -0.64433 | -0.7354 | -0.94942 | -1.3392 | -1.6543 | -1.8708
| ELLIOT DEPOT | SP |  |  | 0.89145 | 0.37512 | -0.014902 | -0.36288 | -0.689 | -0.86813 | -1.023 | -1.1612 | -1.2838 | -1.3695 | -1.5559 | -1.8009 | -2.115 | -2.2128 | 1.4033 | 0.87069 | 0.46119 | 0.098987 | -0.24111 | -0.42783 | -0.59401 | -0.74345 | -0.87722 | -0.97474 | -1.1955 | -1.4289 | -1.674 | -1.8944 | 1.5252 | 1.0132 | 0.62496 | 0.27981 | -0.041575 | -0.21679 | -0.36926 | -0.50537 | -0.62622 | -0.71008 | -0.89405 | -1.1475 | -1.4446 | -1.5291
DYCE | ELLON 11 kV | MINIMUM HEADROOM | NJ 95510 30054 | YES | -0.62712 | -1.391 | -2.1123 | 8.2114 | 7.1589 | 6.0917 | 4.9035 | 3.6988 | 2.3107 | 1.085 | -2.5234 | -6.1029 | -7.5841 | -8.086 | 2.202 | 1.492 | 0.8513 | 10.6523 | 9.8489 | 9.1517 | 8.3394 | 7.5299 | 6.6576 | 5.8221 | 3.2882 | 1.2098 | 0.35363 | -0.29161 | 0.17993 | -0.5241 | -1.1781 | 8.5909 | 7.5745 | 6.5798 | 5.468 | 4.3518 | 3.0757 | 1.9343 | -1.5124 | -4.7116 | -6.0132 | -6.4524
| ELLON 11 kV | CT |  |  | -0.57378 | -1.3292 | -2.0593 | 8.2578 | 7.2376 | 6.2836 | 5.1876 | 4.0574 | 2.9439 | 1.7324 | -2.3242 | -6.1029 | -7.5841 | -8.086 | 2.202 | 1.492 | 0.8513 | 10.6523 | 9.8489 | 9.1676 | 8.434 | 7.6953 | 6.9793 | 6.1724 | 3.4007 | 1.2098 | 0.35363 | -0.29161 | 0.22044 | -0.47677 | -1.1424 | 8.6167 | 7.6288 | 6.7411 | 5.7304 | 4.6991 | 3.6868 | 2.5697 | -1.2912 | -4.7116 | -6.0132 | -6.4524
| ELLON 11 kV | LW |  |  | -0.62712 | -1.391 | -2.1123 | 8.2114 | 7.1589 | 6.0917 | 4.9035 | 3.6988 | 2.3107 | 1.085 | -2.5234 | -5.4821 | -6.5237 | -6.9002 | 2.2046 | 1.4973 | 0.87688 | 10.6978 | 9.889 | 9.1517 | 8.3394 | 7.5299 | 6.6576 | 5.8221 | 3.2882 | 1.5495 | 1.1344 | 0.98402 | 0.17993 | -0.5241 | -1.1781 | 8.5909 | 7.5745 | 6.5798 | 5.468 | 4.3518 | 3.0757 | 1.9343 | -1.5124 | -4.2038 | -5.1156 | -5.4448
| ELLON 11 kV | ST |  |  | -0.44742 | -1.1678 | -1.7872 | 8.7085 | 8.1729 | 7.7161 | 7.2398 | 6.7541 | 6.2595 | 5.6168 | 3.4555 | -0.32572 | -1.7888 | -2.5001 | 2.3015 | 1.6311 | 1.0715 | 10.9935 | 10.4374 | 10.0084 | 9.5664 | 9.1239 | 8.6917 | 8.1651 | 6.3407 | 3.6274 | 2.5641 | 1.8261 | 0.34743 | -0.30989 | -0.86567 | 9.0675 | 8.524 | 8.0914 | 7.6413 | 7.19 | 6.7342 | 6.1369 | 4.023 | 0.41994 | -0.92153 | -1.5476
| ELLON 11 kV | SP |  |  | -0.44387 | -1.1488 | -1.7539 | 8.752 | 8.1397 | 7.6283 | 7.079 | 6.5127 | 5.9581 | 5.3303 | 3.4209 | 0.25993 | -1.5946 | -1.9705 | 2.2988 | 1.6372 | 1.0843 | 11.0154 | 10.4306 | 9.9841 | 9.5151 | 9.0442 | 8.5873 | 8.0858 | 6.4582 | 4.1156 | 2.3362 | 1.0817 | 0.34895 | -0.29372 | -0.83629 | 9.1081 | 8.4978 | 8.0188 | 7.5051 | 6.9835 | 6.4747 | 5.8999 | 4.0525 | 1.0628 | -0.72557 | -1.0728
TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | 0.13435 | 0.13361 | 0.13251 | 0.13095 | 0.12736 | 0.12398 | 0.11912 | 0.1129 | 0.10402 | 0.098332 | 0.076978 | 0.071279 | 0.071384 | 0.064897 | 0.14956 | 0.14906 | 0.14843 | 0.14751 | 0.14555 | 0.14338 | 0.14041 | 0.13698 | 0.13244 | 0.12923 | 0.11561 | 0.11321 | 0.11192 | 0.108 | 0.13029 | 0.12956 | 0.12835 | 0.1267 | 0.12266 | 0.11875 | 0.11372 | 0.10769 | 0.098604 | 0.093324 | 0.073144 | 0.068051 | 0.068289 | 0.062534
| EREDINE | CT |  |  | 0.13601 | 0.13595 | 0.13541 | 0.13371 | 0.12885 | 0.12456 | 0.11912 | 0.1129 | 0.10712 | 0.10233 | 0.083011 | 0.074956 | 0.071384 | 0.069088 | 0.15031 | 0.15018 | 0.14978 | 0.14864 | 0.14584 | 0.14338 | 0.14041 | 0.13698 | 0.13389 | 0.13101 | 0.11818 | 0.11458 | 0.11274 | 0.11091 | 0.13232 | 0.13236 | 0.13183 | 0.13027 | 0.12522 | 0.12066 | 0.11454 | 0.10769 | 0.10146 | 0.096972 | 0.078913 | 0.071437 | 0.068327 | 0.066338
| EREDINE | LW |  |  | 0.13435 | 0.13361 | 0.13251 | 0.13095 | 0.12736 | 0.12398 | 0.11919 | 0.1135 | 0.10402 | 0.098332 | 0.076978 | 0.071279 | 0.07325 | 0.072698 | 0.14956 | 0.14906 | 0.14843 | 0.14751 | 0.14555 | 0.14373 | 0.14098 | 0.13762 | 0.13244 | 0.12923 | 0.11561 | 0.11321 | 0.11386 | 0.11365 | 0.13029 | 0.12956 | 0.12835 | 0.1267 | 0.12266 | 0.11875 | 0.11372 | 0.10794 | 0.098604 | 0.093324 | 0.073144 | 0.068051 | 0.0698 | 0.069339
| EREDINE | ST |  |  | 0.13575 | 0.13553 | 0.13517 | 0.13462 | 0.13378 | 0.13302 | 0.13121 | 0.13054 | 0.12891 | 0.12617 | 0.11689 | 0.092828 | 0.08557 | 0.081801 | 0.15027 | 0.15013 | 0.14988 | 0.14948 | 0.14893 | 0.14843 | 0.14724 | 0.14678 | 0.14579 | 0.1441 | 0.13829 | 0.12211 | 0.11797 | 0.11534 | 0.13195 | 0.13168 | 0.1313 | 0.13082 | 0.13003 | 0.12927 | 0.12765 | 0.12697 | 0.12523 | 0.12246 | 0.11324 | 0.090384 | 0.081743 | 0.077461
| EREDINE | SP |  |  | 0.13575 | 0.13551 | 0.13532 | 0.13495 | 0.13351 | 0.13246 | 0.13098 | 0.1294 | 0.12721 | 0.12377 | 0.1145 | 0.087807 | 0.071476 | 0.064897 | 0.15027 | 0.15011 | 0.14998 | 0.14971 | 0.1489 | 0.14834 | 0.1475 | 0.14659 | 0.14528 | 0.14322 | 0.13782 | 0.12152 | 0.11192 | 0.108 | 0.13195 | 0.13166 | 0.13144 | 0.13104 | 0.12946 | 0.12822 | 0.12658 | 0.12485 | 0.1226 | 0.11914 | 0.10929 | 0.083281 | 0.068289 | 0.062534
INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | NO | 1.6575 | 1.6536 | 1.6487 | 1.643 | 1.6289 | 1.6134 | 1.5978 | 1.5756 | 1.5453 | 1.5281 | 1.4594 | 1.4425 | 1.4486 | 1.4294 | 1.5455 | 1.5434 | 1.5411 | 1.5382 | 1.5318 | 1.5246 | 1.5159 | 1.5047 | 1.4905 | 1.4805 | 1.4329 | 1.4254 | 1.4222 | 1.4052 | 1.526 | 1.5225 | 1.518 | 1.5128 | 1.5001 | 1.4862 | 1.4721 | 1.4517 | 1.4241 | 1.4081 | 1.3421 | 1.3278 | 1.3331 | 1.3168
| ERROGIE | CT |  |  | 1.6631 | 1.6614 | 1.658 | 1.6513 | 1.6368 | 1.6236 | 1.6007 | 1.5756 | 1.5517 | 1.5382 | 1.4801 | 1.4537 | 1.4486 | 1.4442 | 1.5479 | 1.5465 | 1.5443 | 1.54 | 1.5325 | 1.526 | 1.5159 | 1.5047 | 1.4936 | 1.4856 | 1.4432 | 1.4284 | 1.4234 | 1.4164 | 1.5311 | 1.5294 | 1.5262 | 1.5198 | 1.5066 | 1.4946 | 1.4741 | 1.4517 | 1.4302 | 1.4175 | 1.3616 | 1.3382 | 1.3338 | 1.33
| ERROGIE | LW |  |  | 1.6575 | 1.6536 | 1.6487 | 1.643 | 1.6289 | 1.6134 | 1.5978 | 1.5783 | 1.5453 | 1.5281 | 1.4594 | 1.4425 | 1.4489 | 1.4455 | 1.5455 | 1.5434 | 1.5411 | 1.5382 | 1.5318 | 1.5246 | 1.5172 | 1.5067 | 1.4905 | 1.4805 | 1.4329 | 1.4254 | 1.4275 | 1.4263 | 1.526 | 1.5225 | 1.518 | 1.5128 | 1.5001 | 1.4862 | 1.4721 | 1.4541 | 1.4241 | 1.4081 | 1.3421 | 1.3278 | 1.3331 | 1.3304
| ERROGIE | ST |  |  | 1.6618 | 1.6605 | 1.6593 | 1.6567 | 1.6543 | 1.6521 | 1.6483 | 1.6452 | 1.6388 | 1.6297 | 1.5988 | 1.5192 | 1.4945 | 1.4826 | 1.5473 | 1.5465 | 1.5458 | 1.544 | 1.5424 | 1.5409 | 1.5382 | 1.536 | 1.5324 | 1.5271 | 1.5073 | 1.4515 | 1.4383 | 1.4285 | 1.5299 | 1.5287 | 1.5276 | 1.5251 | 1.5229 | 1.5208 | 1.5172 | 1.5142 | 1.5083 | 1.4999 | 1.471 | 1.3938 | 1.372 | 1.3616
| ERROGIE | SP |  |  | 1.6651 | 1.6644 | 1.6636 | 1.6631 | 1.6596 | 1.6564 | 1.653 | 1.6491 | 1.6428 | 1.6352 | 1.6015 | 1.5189 | 1.4532 | 1.4294 | 1.5496 | 1.5491 | 1.5483 | 1.5479 | 1.546 | 1.5442 | 1.5424 | 1.5402 | 1.5364 | 1.532 | 1.5148 | 1.4654 | 1.4222 | 1.4052 | 1.5331 | 1.5324 | 1.5316 | 1.5312 | 1.528 | 1.525 | 1.522 | 1.5184 | 1.5125 | 1.5055 | 1.4749 | 1.3985 | 1.3371 | 1.3168
ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | YES | 3.9026 | 3.8416 | 3.7606 | 3.657 | 3.4131 | 3.1259 | 2.8137 | 2.4876 | 2.0709 | 1.763 | 1.0014 | 0.34441 | -0.002243 | -0.13967 | 3.0331 | 2.9951 | 2.9465 | 2.8826 | 2.7561 | 2.6027 | 2.4292 | 2.2478 | 2.0256 | 1.8335 | 1.3859 | 1.0309 | 0.8193 | 0.63243 | 2.8152 | 2.755 | 2.677 | 2.5753 | 2.3557 | 2.0932 | 1.7989 | 1.4917 | 1.1059 | 0.80211 | 0.073911 | -0.47633 | -0.76291 | -0.87576
| ERROL | CT |  |  | 3.9466 | 3.9058 | 3.8328 | 3.7385 | 3.5052 | 3.2678 | 2.9818 | 2.6767 | 2.3756 | 2.1119 | 1.1445 | 0.34441 | -0.002243 | -0.13967 | 3.0469 | 3.0144 | 2.962 | 2.8971 | 2.7739 | 2.65 | 2.5109 | 2.3631 | 2.2148 | 2.0588 | 1.4488 | 1.0309 | 0.8193 | 0.63243 | 2.8513 | 2.8078 | 2.7331 | 2.6379 | 2.4279 | 2.2161 | 1.964 | 1.6957 | 1.43 | 1.1784 | 0.22104 | -0.47633 | -0.76291 | -0.87576
| ERROL | LW |  |  | 3.9026 | 3.8416 | 3.7606 | 3.657 | 3.4131 | 3.1259 | 2.8137 | 2.4876 | 2.0709 | 1.763 | 1.0014 | 0.44158 | 0.25418 | 0.1467 | 3.0331 | 2.9951 | 2.9465 | 2.8826 | 2.7561 | 2.6027 | 2.4292 | 2.2478 | 2.0256 | 1.8335 | 1.3859 | 1.1059 | 1.0348 | 0.99266 | 2.8152 | 2.755 | 2.677 | 2.5753 | 2.3557 | 2.0932 | 1.7989 | 1.4917 | 1.1059 | 0.80211 | 0.073911 | -0.4163 | -0.56908 | -0.65582
| ERROL | ST |  |  | 3.9727 | 3.9528 | 3.9282 | 3.9012 | 3.8681 | 3.8251 | 3.7875 | 3.7479 | 3.6794 | 3.5705 | 3.1664 | 2.0921 | 1.685 | 1.4501 | 3.0688 | 3.0538 | 3.0347 | 3.0134 | 2.9881 | 2.9552 | 2.9245 | 2.8922 | 2.8451 | 2.7732 | 2.493 | 1.7504 | 1.4729 | 1.2358 | 2.8794 | 2.8593 | 2.8344 | 2.8062 | 2.7741 | 2.7319 | 2.6922 | 2.6507 | 2.5833 | 2.4764 | 2.0697 | 1.0121 | 0.6461 | 0.43877
| ERROL | SP |  |  | 4.001 | 3.9885 | 3.9727 | 3.9553 | 3.9034 | 3.8427 | 3.7849 | 3.719 | 3.6467 | 3.5539 | 3.1876 | 2.1039 | 1.4496 | 1.2281 | 3.087 | 3.0757 | 3.0607 | 3.0441 | 3.0123 | 2.9727 | 2.9341 | 2.8898 | 2.8412 | 2.7822 | 2.5622 | 1.8193 | 1.2859 | 0.90414 | 2.9084 | 2.895 | 2.8781 | 2.8586 | 2.8112 | 2.7543 | 2.6976 | 2.6326 | 2.5616 | 2.4739 | 2.1358 | 1.0601 | 0.43973 | 0.24795
TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | 0.060111 | 0.059771 | 0.058901 | 0.057644 | 0.05501 | 0.051053 | 0.047401 | 0.041035 | 0.034201 | 0.029821 | 0.011049 | 0.0057208 | 0.0049442 | -0.00076179 | 0.067118 | 0.066911 | 0.066466 | 0.065758 | 0.064166 | 0.062454 | 0.060052 | 0.057308 | 0.053923 | 0.051338 | 0.038838 | 0.036665 | 0.03642 | 0.034434 | 0.056558 | 0.05624 | 0.055445 | 0.054279 | 0.051931 | 0.048269 | 0.044785 | 0.0391 | 0.032892 | 0.028781 | 0.010889 | 0.0062843 | 0.0056455 | 0.00060659
| FINCASTLE | CT |  |  | 0.061582 | 0.061686 | 0.061326 | 0.060238 | 0.056235 | 0.053252 | 0.047401 | 0.041035 | 0.034201 | 0.030736 | 0.014437 | 0.0077668 | 0.0049442 | 0.0032129 | 0.067623 | 0.067563 | 0.067283 | 0.06649 | 0.064166 | 0.062611 | 0.060052 | 0.057308 | 0.053979 | 0.052039 | 0.040522 | 0.037975 | 0.037014 | 0.036424 | 0.057838 | 0.057905 | 0.057552 | 0.056494 | 0.052756 | 0.05002 | 0.044785 | 0.0391 | 0.032892 | 0.02968 | 0.013865 | 0.0082123 | 0.0057384 | 0.004221
| FINCASTLE | LW |  |  | 0.060111 | 0.059771 | 0.058901 | 0.057644 | 0.05501 | 0.051053 | 0.048195 | 0.043954 | 0.034547 | 0.029821 | 0.011049 | 0.0057208 | 0.0069599 | 0.0065581 | 0.067118 | 0.066911 | 0.066466 | 0.065758 | 0.06463 | 0.062454 | 0.061139 | 0.058721 | 0.053923 | 0.051338 | 0.038838 | 0.036665 | 0.037087 | 0.036951 | 0.056558 | 0.05624 | 0.055445 | 0.054279 | 0.051931 | 0.048269 | 0.045698 | 0.041751 | 0.033146 | 0.028781 | 0.010889 | 0.0062843 | 0.0073704 | 0.0070182
| FINCASTLE | ST |  |  | 0.061426 | 0.061074 | 0.060673 | 0.060368 | 0.05969 | 0.059144 | 0.057513 | 0.05675 | 0.055176 | 0.052771 | 0.043724 | 0.023765 | 0.015656 | 0.011747 | 0.067729 | 0.067525 | 0.067272 | 0.067056 | 0.066617 | 0.066303 | 0.065115 | 0.064622 | 0.063863 | 0.062555 | 0.057117 | 0.04355 | 0.0406 | 0.039268 | 0.057743 | 0.057416 | 0.057037 | 0.056742 | 0.056098 | 0.05559 | 0.054001 | 0.053277 | 0.051851 | 0.049632 | 0.041154 | 0.021463 | 0.014868 | 0.011682
| FINCASTLE | SP |  |  | 0.061483 | 0.061273 | 0.060829 | 0.060545 | 0.059636 | 0.058772 | 0.057522 | 0.056088 | 0.054466 | 0.051461 | 0.042785 | 0.019172 | 0.0049787 | -0.00076179 | 0.067749 | 0.067661 | 0.067367 | 0.067194 | 0.066844 | 0.06651 | 0.065895 | 0.065153 | 0.064309 | 0.062509 | 0.058281 | 0.0441 | 0.03642 | 0.034434 | 0.057793 | 0.057607 | 0.057183 | 0.056917 | 0.056117 | 0.055356 | 0.05422 | 0.052906 | 0.051419 | 0.048596 | 0.040718 | 0.018678 | 0.0056455 | 0.00060659
SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | 5.3716 | 5.4952 | 5.1435 | 4.7759 | 4.3933 | 3.9621 | 3.5266 | 3.0443 | 2.5277 | 1.9773 | 0.19942 | -0.55325 | -0.53192 | -0.56669 | 4.9692 | 5.6054 | 5.2384 | 4.8563 | 4.468 | 4.034 | 3.5799 | 3.0887 | 2.5604 | 1.984 | 0.1593 | -0.5841 | -0.56291 | -0.58841 | 4.773 | 5.4316 | 5.0885 | 4.7166 | 4.3308 | 3.9084 | 3.4795 | 3.0068 | 2.4999 | 1.9576 | 0.24289 | -0.47728 | -0.43936 | -0.47744
| FIRTH | CT |  |  | 5.3716 | 5.4952 | 5.1465 | 4.7759 | 4.3933 | 3.9621 | 3.5266 | 3.0443 | 2.555 | 2.002 | 0.28944 | -0.44346 | -0.44167 | -0.44282 | 4.9701 | 5.607 | 5.2385 | 4.8563 | 4.468 | 4.034 | 3.5799 | 3.0887 | 2.5832 | 2.0039 | 0.18314 | -0.49368 | -0.48407 | -0.48088 | 4.7772 | 5.4345 | 5.0895 | 4.7166 | 4.3308 | 3.9084 | 3.4795 | 3.0068 | 2.5264 | 1.9815 | 0.32881 | -0.36856 | -0.34201 | -0.33358
| FIRTH | LW |  |  | 5.3732 | 5.4969 | 5.1435 | 4.7862 | 4.3984 | 3.9806 | 3.5415 | 3.0561 | 2.5277 | 1.9773 | 0.19942 | -0.55325 | -0.52651 | -0.53222 | 4.9692 | 5.6054 | 5.2384 | 4.8668 | 4.4697 | 4.042 | 3.5911 | 3.0957 | 2.5604 | 1.984 | 0.1593 | -0.5841 | -0.56291 | -0.56797 | 4.773 | 5.4316 | 5.0885 | 4.7388 | 4.3446 | 3.925 | 3.4938 | 3.0177 | 2.4999 | 1.9576 | 0.24289 | -0.47728 | -0.43936 | -0.45088
| FIRTH | ST |  |  | 5.3774 | 5.5109 | 5.1774 | 4.8322 | 4.4598 | 4.0744 | 3.6508 | 3.1972 | 2.7152 | 2.1763 | 0.45115 | -0.41189 | -0.53192 | -0.5384 | 4.9774 | 5.6285 | 5.2652 | 4.9005 | 4.5129 | 4.1085 | 3.6676 | 3.1968 | 2.6979 | 2.123 | 0.29054 | -0.46109 | -0.55124 | -0.55417 | 4.7876 | 5.4659 | 5.1381 | 4.806 | 4.4534 | 4.0824 | 3.6724 | 3.2328 | 2.7669 | 2.2474 | 0.59795 | -0.22267 | -0.33995 | -0.34309
| FIRTH | SP |  |  | 5.3777 | 5.5123 | 5.1787 | 4.8364 | 4.4638 | 4.0786 | 3.6564 | 3.2043 | 2.7383 | 2.1925 | 0.50886 | -0.27868 | -0.50686 | -0.56669 | 4.978 | 5.6299 | 5.267 | 4.9039 | 4.517 | 4.1137 | 3.6747 | 3.2061 | 2.7145 | 2.1348 | 0.31223 | -0.40896 | -0.54478 | -0.58841 | 4.7902 | 5.4704 | 5.1444 | 4.818 | 4.4593 | 4.0911 | 3.6849 | 3.2512 | 2.7934 | 2.2719 | 0.63935 | -0.16916 | -0.41587 | -0.47744
THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | 2.7983 | 2.7983 | 2.7964 | 2.7934 | 2.7851 | 2.7769 | 2.767 | 2.7548 | 2.7439 | 2.7372 | 2.7046 | 2.6948 | 2.6979 | 2.6914 | 2.642 | 2.6418 | 2.6409 | 2.6387 | 2.635 | 2.6302 | 2.6252 | 2.6196 | 2.6148 | 2.6107 | 2.5878 | 2.5813 | 2.582 | 2.5803 | -1.5006 | -1.5015 | -1.5028 | -1.5052 | -1.5074 | -1.5103 | -1.5165 | -1.525 | -1.5329 | -1.5369 | -1.5682 | -1.5769 | -1.5747 | -1.5783
| FLOTTA | CT |  |  | 2.8011 | 2.8016 | 2.7998 | 2.7945 | 2.7866 | 2.7778 | 2.767 | 2.7548 | 2.7439 | 2.7379 | 2.7207 | 2.6971 | 2.6995 | 2.699 | 2.6429 | 2.6428 | 2.6418 | 2.6387 | 2.635 | 2.6302 | 2.6252 | 2.6196 | 2.6148 | 2.6111 | 2.6003 | 2.5822 | 2.5823 | 2.5814 | -1.5006 | -1.5015 | -1.5028 | -1.5052 | -1.5074 | -1.5103 | -1.5165 | -1.525 | -1.5329 | -1.5369 | -1.5506 | -1.5752 | -1.5738 | -1.5743
| FLOTTA | LW |  |  | 2.7983 | 2.7983 | 2.7964 | 2.7934 | 2.7851 | 2.7769 | 2.7697 | 2.7594 | 2.7448 | 2.7372 | 2.7046 | 2.6948 | 2.6979 | 2.6938 | 2.642 | 2.6418 | 2.6409 | 2.6394 | 2.6355 | 2.6316 | 2.6283 | 2.6225 | 2.6154 | 2.6107 | 2.5878 | 2.5813 | 2.582 | 2.5803 | -1.4998 | -1.5005 | -1.5013 | -1.5027 | -1.5048 | -1.5089 | -1.5145 | -1.5211 | -1.531 | -1.5357 | -1.5682 | -1.5769 | -1.5747 | -1.5777
| FLOTTA | ST |  |  | 2.8007 | 2.8003 | 2.7998 | 2.7989 | 2.7981 | 2.7971 | 2.7962 | 2.7955 | 2.7916 | 2.7882 | 2.775 | 2.7384 | 2.7239 | 2.7175 | 2.643 | 2.6428 | 2.6424 | 2.6419 | 2.6412 | 2.6404 | 2.6398 | 2.6391 | 2.6365 | 2.6346 | 2.6265 | 2.5988 | 2.5914 | 2.588 | -1.4995 | -1.4997 | -1.5 | -1.5006 | -1.501 | -1.5016 | -1.5021 | -1.5028 | -1.5041 | -1.5055 | -1.5112 | -1.5441 | -1.5555 | -1.5614
| FLOTTA | SP |  |  | 2.801 | 2.8008 | 2.8008 | 2.8005 | 2.7985 | 2.7964 | 2.7942 | 2.7915 | 2.7872 | 2.7824 | 2.7657 | 2.7323 | 2.7003 | 2.6914 | 2.6431 | 2.643 | 2.6429 | 2.6427 | 2.6418 | 2.6409 | 2.64 | 2.6388 | 2.6363 | 2.6341 | 2.6254 | 2.6073 | 2.5851 | 2.5808 | -1.4994 | -1.4994 | -1.4996 | -1.4998 | -1.4999 | -1.5001 | -1.5003 | -1.5007 | -1.5015 | -1.5023 | -1.5121 | -1.5405 | -1.5717 | -1.5783
ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | YES | 7.9929 | 7.8955 | 7.7777 | 7.6157 | 7.4093 | 7.1809 | 6.5657 | 5.8325 | 5.3697 | 4.8079 | 3.0661 | 1.6789 | 1.5498 | 1.4857 | 8.403 | 8.328 | 8.238 | 8.114 | 7.9623 | 7.7932 | 7.2158 | 6.5199 | 6.1231 | 5.6383 | 4.1445 | 3.0859 | 3.055 | 3.0398 | 7.7238 | 7.661 | 7.5865 | 7.482 | 7.3435 | 7.1247 | 6.5355 | 5.8333 | 5.363 | 4.8104 | 3.1108 | 1.7857 | 1.6705 | 1.6133
| FOCHABERS | CT |  |  | 7.9929 | 7.8955 | 7.7777 | 7.6157 | 7.4093 | 7.1809 | 6.5657 | 5.8325 | 5.383 | 4.8901 | 3.3735 | 2.0964 | 1.683 | 1.5248 | 8.403 | 8.328 | 8.238 | 8.114 | 7.9623 | 7.7932 | 7.2158 | 6.5199 | 6.1278 | 5.6969 | 4.4057 | 3.5214 | 3.4461 | 3.4214 | 7.7238 | 7.661 | 7.5865 | 7.482 | 7.3435 | 7.1247 | 6.5355 | 5.8333 | 5.4028 | 4.9292 | 3.4565 | 2.2112 | 1.9478 | 1.8528
| FOCHABERS | LW |  |  | 8.0126 | 7.9169 | 7.8081 | 7.6605 | 7.4705 | 7.246 | 6.6226 | 5.8665 | 5.3697 | 4.8079 | 3.0661 | 1.6789 | 1.5498 | 1.4857 | 8.422 | 8.3502 | 8.2689 | 8.1578 | 8.0196 | 7.8554 | 7.2685 | 6.5502 | 6.1231 | 5.6383 | 4.1445 | 3.0859 | 3.055 | 3.0398 | 7.7425 | 7.6842 | 7.6188 | 7.5289 | 7.4053 | 7.1907 | 6.5927 | 5.867 | 5.363 | 4.8104 | 3.1108 | 1.7857 | 1.6705 | 1.6133
| FOCHABERS | ST |  |  | 8.0815 | 8.0397 | 7.9929 | 7.935 | 7.874 | 7.8033 | 7.3249 | 6.7318 | 6.4204 | 6.0506 | 4.783 | 2.9123 | 2.112 | 2.0099 | 8.4723 | 8.441 | 8.4057 | 8.3618 | 8.3158 | 8.2623 | 7.7798 | 7.1804 | 6.8846 | 6.5443 | 5.4009 | 3.9382 | 3.3345 | 3.2599 | 7.7804 | 7.7531 | 7.7228 | 7.6847 | 7.6455 | 7.6004 | 7.1463 | 6.5818 | 6.3118 | 6.006 | 4.8214 | 3.0151 | 2.2457 | 2.1493
| FOCHABERS | SP |  |  | 8.0861 | 8.0531 | 8.0141 | 7.9684 | 7.9182 | 7.8638 | 7.4059 | 6.8389 | 6.5601 | 6.2507 | 5.2598 | 3.9217 | 2.7498 | 2.4847 | 8.4754 | 8.4507 | 8.4212 | 8.3866 | 8.3501 | 8.3102 | 7.8446 | 7.2663 | 6.996 | 6.7028 | 5.7786 | 4.7365 | 3.842 | 3.6375 | 7.7821 | 7.7604 | 7.7343 | 7.7042 | 7.6732 | 7.6399 | 7.1999 | 6.6522 | 6.4004 | 6.132 | 5.2846 | 3.9959 | 2.8663 | 2.6129
NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | YES | 3.9629 | 3.5218 | 2.9662 | 2.363 | 1.3533 | 0.30608 | -0.78069 | -2.0016 | -3.4595 | -4.8225 | -8.806 | -12.4761 | -13.8804 | -14.3333 | 7.3773 | 7.0521 | 6.6563 | 6.1906 | 5.5369 | 4.8517 | 4.1476 | 3.4079 | 2.4689 | 1.5053 | -1.5954 | -4.8407 | -4.9555 | -4.9857 | 4.7622 | 4.3652 | 3.8707 | 3.3276 | 2.427 | 1.4858 | 0.50214 | -0.62131 | -1.9613 | -3.2297 | -6.9747 | -10.3666 | -11.5265 | -11.9235
| FORRES | CT |  |  | 4.0551 | 3.6506 | 3.1325 | 2.5215 | 1.4921 | 0.43243 | -0.69306 | -1.8596 | -3.0714 | -4.3632 | -8.1932 | -12.4761 | -13.8804 | -14.3333 | 7.3885 | 7.071 | 6.674 | 6.1906 | 5.5369 | 4.8517 | 4.1476 | 3.4079 | 2.6316 | 1.6935 | -0.82526 | -3.5397 | -4.2103 | -4.7069 | 4.8379 | 4.4722 | 4.0075 | 3.448 | 2.5242 | 1.5691 | 0.55625 | -0.5028 | -1.6052 | -2.7944 | -6.3628 | -10.2902 | -11.5265 | -11.9235
| FORRES | LW |  |  | 3.9629 | 3.5218 | 2.9662 | 2.363 | 1.3533 | 0.30608 | -0.78069 | -2.0016 | -3.4595 | -4.8225 | -8.806 | -12.4696 | -13.3548 | -13.6874 | 7.3773 | 7.0521 | 6.6563 | 6.2144 | 5.5957 | 4.9315 | 4.2285 | 3.412 | 2.4689 | 1.5053 | -1.5954 | -4.8407 | -4.9555 | -4.9857 | 4.7622 | 4.3652 | 3.8707 | 3.3276 | 2.427 | 1.4858 | 0.50214 | -0.62131 | -1.9613 | -3.2297 | -6.9747 | -10.3666 | -11.1373 | -11.429
| FORRES | ST |  |  | 4.2019 | 3.8943 | 3.5168 | 3.1184 | 2.6911 | 2.2338 | 1.7396 | 1.2332 | 0.68734 | -0.053827 | -2.428 | -7.9476 | -10.4247 | -10.5972 | 7.505 | 7.264 | 6.9706 | 6.6552 | 6.32 | 5.9604 | 5.5674 | 5.1584 | 4.7148 | 4.0366 | 1.8841 | -2.4097 | -4.297 | -4.4282 | 4.9817 | 4.7109 | 4.382 | 4.0312 | 3.6588 | 3.2569 | 2.8166 | 2.3577 | 1.8605 | 1.1777 | -0.80751 | -6.0355 | -8.42 | -8.5824
| FORRES | SP |  |  | 4.236 | 3.9525 | 3.6019 | 3.2344 | 2.7566 | 2.2576 | 1.7335 | 1.1911 | 0.58775 | -0.13603 | -1.9149 | -5.4441 | -8.5091 | -9.2672 | 7.5213 | 7.2942 | 7.0159 | 6.7237 | 6.3818 | 6.019 | 5.6337 | 5.2175 | 4.7382 | 4.1727 | 2.8324 | -0.075708 | -2.7985 | -3.4101 | 5.0126 | 4.7642 | 4.4603 | 4.1399 | 3.7265 | 3.2915 | 2.8301 | 2.3437 | 1.7971 | 1.1403 | -0.49457 | -3.8162 | -6.5593 | -7.2887
DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | NO | 2.0382 | 2.0263 | 2.0095 | 1.9886 | 1.9437 | 1.8931 | 1.838 | 1.7793 | 1.6979 | 1.6351 | 1.4121 | 1.1976 | 1.2096 | 1.2072 | 2.1834 | 2.1763 | 2.1668 | 2.1546 | 2.1333 | 2.1082 | 2.0794 | 2.0481 | 2.006 | 1.9621 | 1.79 | 1.6293 | 1.6337 | 1.6327 | -2.001 | -2.0086 | -2.0177 | -2.0303 | -2.0462 | -2.0624 | -2.0789 | -2.0994 | -2.1231 | -2.1546 | -2.2722 | -2.3437 | -2.3287 | -2.3565
| FORSS | CT |  |  | 2.0538 | 2.0496 | 2.0396 | 2.0241 | 1.9782 | 1.9356 | 1.8766 | 1.8134 | 1.7528 | 1.7144 | 1.5465 | 1.3582 | 1.3384 | 1.3285 | 2.1883 | 2.184 | 2.1766 | 2.1651 | 2.1411 | 2.1195 | 2.0918 | 2.0621 | 2.0328 | 2.002 | 1.8803 | 1.7466 | 1.7373 | 1.7336 | -2.001 | -2.0086 | -2.0177 | -2.0303 | -2.0462 | -2.0624 | -2.0776 | -2.0939 | -2.1117 | -2.1343 | -2.2057 | -2.293 | -2.3136 | -2.326
| FORSS | LW |  |  | 2.0382 | 2.0263 | 2.0095 | 1.9886 | 1.9437 | 1.8931 | 1.838 | 1.7793 | 1.6979 | 1.6351 | 1.4121 | 1.1976 | 1.2096 | 1.2072 | 2.1834 | 2.1763 | 2.1668 | 2.1546 | 2.1333 | 2.1082 | 2.0794 | 2.0481 | 2.006 | 1.9621 | 1.79 | 1.6293 | 1.6337 | 1.6327 | -1.9994 | -2.0074 | -2.0165 | -2.0289 | -2.0435 | -2.0607 | -2.0789 | -2.0994 | -2.1231 | -2.1546 | -2.2722 | -2.3437 | -2.3287 | -2.3308
| FORSS | ST |  |  | 2.0543 | 2.0492 | 2.0439 | 2.0384 | 2.031 | 2.0206 | 2.011 | 2 | 1.9823 | 1.9581 | 1.8402 | 1.4868 | 1.3286 | 1.3085 | 2.1912 | 2.1881 | 2.1849 | 2.181 | 2.1762 | 2.1693 | 2.163 | 2.1557 | 2.1453 | 2.1313 | 2.0617 | 1.8048 | 1.698 | 1.6914 | -1.9931 | -1.9961 | -1.9994 | -2.0036 | -2.0082 | -2.0141 | -2.0208 | -2.0285 | -2.0379 | -2.0518 | -2.1076 | -2.2546 | -2.3092 | -2.308
| FORSS | SP |  |  | 2.0575 | 2.0541 | 2.0509 | 2.047 | 2.035 | 2.0228 | 2.0084 | 1.992 | 1.9754 | 1.9506 | 1.8565 | 1.6182 | 1.3689 | 1.3075 | 2.1928 | 2.1908 | 2.1885 | 2.1858 | 2.1799 | 2.1737 | 2.1661 | 2.157 | 2.148 | 2.1345 | 2.0858 | 1.9332 | 1.7601 | 1.7261 | -1.9923 | -1.9945 | -1.997 | -1.9999 | -2.0033 | -2.0073 | -2.012 | -2.0176 | -2.0236 | -2.0328 | -2.0637 | -2.1679 | -2.3038 | -2.3565
BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | NO | 5.3772 | 5.3196 | 5.2478 | 5.1887 | 5.0967 | 4.9886 | 4.8678 | 4.7219 | 4.514 | 4.3549 | 3.9116 | 3.5057 | 3.2998 | 3.2225 | 5.48 | 5.4552 | 5.4215 | 5.3951 | 5.3541 | 5.3011 | 5.2352 | 5.1491 | 5.0317 | 4.9305 | 4.6531 | 4.45 | 4.3416 | 4.2616 | 5.2258 | 5.1836 | 5.1284 | 5.0806 | 4.9957 | 4.8964 | 4.7865 | 4.6547 | 4.465 | 4.3213 | 3.9191 | 3.5394 | 3.3466 | 3.2745
| FORTEVIOT | CT |  |  | 5.3911 | 5.3389 | 5.2721 | 5.2093 | 5.1235 | 5.0342 | 4.9086 | 4.7651 | 4.6238 | 4.4896 | 3.9794 | 3.5057 | 3.2998 | 3.2225 | 5.48 | 5.4552 | 5.4215 | 5.3951 | 5.3541 | 5.3092 | 5.2528 | 5.181 | 5.108 | 5.0286 | 4.7043 | 4.45 | 4.3416 | 4.2616 | 5.2388 | 5.2016 | 5.151 | 5.1003 | 5.0212 | 4.9389 | 4.8229 | 4.6908 | 4.5604 | 4.4379 | 3.9772 | 3.5394 | 3.3466 | 3.2745
| FORTEVIOT | LW |  |  | 5.3772 | 5.3196 | 5.2478 | 5.1887 | 5.0967 | 4.9886 | 4.8678 | 4.7219 | 4.514 | 4.3549 | 3.9116 | 3.5938 | 3.4671 | 3.4134 | 5.482 | 5.4581 | 5.4255 | 5.4018 | 5.3573 | 5.3011 | 5.2352 | 5.1491 | 5.0317 | 4.9305 | 4.6531 | 4.4917 | 4.4434 | 4.4222 | 5.2258 | 5.1836 | 5.1284 | 5.0806 | 4.9957 | 4.8964 | 4.7865 | 4.6547 | 4.465 | 4.3213 | 3.9191 | 3.6231 | 3.5041 | 3.4536
| FORTEVIOT | ST |  |  | 5.4012 | 5.3531 | 5.2983 | 5.2606 | 5.249 | 5.229 | 5.2061 | 5.1845 | 5.1503 | 5.0984 | 4.9005 | 4.3382 | 4.1346 | 4.0123 | 5.487 | 5.4667 | 5.4385 | 5.4214 | 5.4145 | 5.4053 | 5.3948 | 5.3776 | 5.354 | 5.3189 | 5.1777 | 4.7635 | 4.6509 | 4.5537 | 5.2478 | 5.2142 | 5.1744 | 5.1465 | 5.1363 | 5.1193 | 5.1 | 5.0819 | 5.0519 | 5.0055 | 4.8283 | 4.3108 | 4.1274 | 4.0192
| FORTEVIOT | SP |  |  | 5.4069 | 5.3614 | 5.3088 | 5.2764 | 5.2554 | 5.23 | 5.1999 | 5.167 | 5.1285 | 5.0835 | 4.9166 | 4.4402 | 4.0787 | 3.9876 | 5.4877 | 5.4681 | 5.4403 | 5.4248 | 5.4188 | 5.4113 | 5.3999 | 5.3786 | 5.3523 | 5.3238 | 5.2228 | 4.8931 | 4.5985 | 4.4475 | 5.2531 | 5.222 | 5.1844 | 5.161 | 5.1421 | 5.1198 | 5.0937 | 5.0651 | 5.0315 | 4.9911 | 4.8396 | 4.4107 | 4.079 | 3.9971
INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | NO | 2.664 | 2.6541 | 2.6436 | 2.6316 | 2.6049 | 2.5741 | 2.5419 | 2.5006 | 2.4607 | 2.4362 | 2.3595 | 2.3172 | 2.3324 | 2.3275 | 2.4541 | 2.4501 | 2.4456 | 2.4401 | 2.4302 | 2.4179 | 2.4043 | 2.3821 | 2.36 | 2.3445 | 2.2934 | 2.2608 | 2.267 | 2.2644 | 2.3963 | 2.3883 | 2.3796 | 2.3695 | 2.348 | 2.3228 | 2.2962 | 2.2605 | 2.2254 | 2.2031 | 2.1309 | 2.0887 | 2.1008 | 2.099
| FOYERS | CT |  |  | 2.6705 | 2.666 | 2.6586 | 2.6491 | 2.6171 | 2.5853 | 2.5558 | 2.5252 | 2.4972 | 2.4787 | 2.413 | 2.3438 | 2.3339 | 2.3275 | 2.4562 | 2.4541 | 2.4502 | 2.4445 | 2.4311 | 2.4183 | 2.4062 | 2.3924 | 2.3774 | 2.3654 | 2.3211 | 2.275 | 2.2688 | 2.2644 | 2.4015 | 2.3976 | 2.3911 | 2.3825 | 2.356 | 2.33 | 2.3057 | 2.2799 | 2.2559 | 2.2387 | 2.1765 | 2.1118 | 2.1038 | 2.099
| FOYERS | LW |  |  | 2.664 | 2.6541 | 2.6436 | 2.6316 | 2.6049 | 2.5741 | 2.5419 | 2.5006 | 2.4607 | 2.4362 | 2.3595 | 2.3172 | 2.3324 | 2.3302 | 2.4541 | 2.4501 | 2.4456 | 2.4401 | 2.4302 | 2.4179 | 2.4043 | 2.3821 | 2.36 | 2.3445 | 2.2934 | 2.2608 | 2.267 | 2.2661 | 2.3963 | 2.3883 | 2.3796 | 2.3695 | 2.348 | 2.3228 | 2.2962 | 2.2605 | 2.2254 | 2.2031 | 2.1309 | 2.0887 | 2.1008 | 2.099
| FOYERS | ST |  |  | 2.6712 | 2.6688 | 2.6662 | 2.6623 | 2.6583 | 2.6544 | 2.6489 | 2.6418 | 2.6334 | 2.6222 | 2.5786 | 2.4693 | 2.4247 | 2.4084 | 2.457 | 2.4557 | 2.4544 | 2.4521 | 2.45 | 2.448 | 2.4446 | 2.4404 | 2.4355 | 2.4292 | 2.402 | 2.3278 | 2.3047 | 2.2978 | 2.4022 | 2.4001 | 2.3978 | 2.3944 | 2.3909 | 2.3876 | 2.3826 | 2.3763 | 2.3687 | 2.3588 | 2.3187 | 2.2155 | 2.1774 | 2.1648
| FOYERS | SP |  |  | 2.6746 | 2.6735 | 2.6721 | 2.6705 | 2.6659 | 2.6607 | 2.6547 | 2.6473 | 2.6389 | 2.6283 | 2.581 | 2.4667 | 2.3789 | 2.3472 | 2.4589 | 2.4583 | 2.4574 | 2.4563 | 2.4544 | 2.4522 | 2.4492 | 2.445 | 2.4403 | 2.4348 | 2.4103 | 2.3443 | 2.2911 | 2.2732 | 2.4053 | 2.4044 | 2.4031 | 2.4016 | 2.3979 | 2.3936 | 2.3885 | 2.3819 | 2.3745 | 2.3653 | 2.3241 | 2.2213 | 2.1417 | 2.1156
FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | 20.0712 | 19.8015 | 19.5648 | 19.2779 | 18.5267 | 17.1062 | 15.5076 | 13.4817 | 11.0467 | 8.6712 | 3.3569 | -2.0762 | -4.0774 | -4.7628 | 23.6738 | 23.4926 | 23.3435 | 23.1199 | 22.7295 | 21.7312 | 20.5022 | 19.0508 | 17.3408 | 15.3752 | 11.3948 | 8.1512 | 7.0841 | 6.3434 | 20.8769 | 20.6394 | 20.4303 | 20.1726 | 19.5046 | 18.202 | 16.7049 | 14.8417 | 12.6005 | 10.3758 | 5.4179 | 0.53506 | -1.2204 | -1.8197
| FRASERBURGH | CT |  |  | 20.1318 | 19.901 | 19.6913 | 19.381 | 18.6432 | 17.2637 | 15.5076 | 13.4817 | 11.2778 | 8.92 | 3.4091 | -2.0762 | -4.0774 | -4.7628 | 23.6773 | 23.5038 | 23.3521 | 23.1199 | 22.7295 | 21.7312 | 20.5022 | 19.0508 | 17.3906 | 15.468 | 11.4604 | 8.1512 | 7.0841 | 6.3434 | 20.9262 | 20.7218 | 20.5339 | 20.2466 | 19.5839 | 18.3137 | 16.7049 | 14.8417 | 12.8108 | 10.6185 | 5.5132 | 0.53506 | -1.2204 | -1.8197
| FRASERBURGH | LW |  |  | 20.0712 | 19.8015 | 19.5648 | 19.2779 | 18.5267 | 17.1062 | 15.5141 | 13.532 | 11.0467 | 8.6712 | 3.3569 | -0.99971 | -2.41 | -2.9852 | 23.6738 | 23.4926 | 23.3435 | 23.1574 | 22.7921 | 21.7985 | 20.6405 | 19.1564 | 17.3408 | 15.3752 | 11.3948 | 8.6455 | 8.091 | 7.8571 | 20.8769 | 20.6394 | 20.4303 | 20.1726 | 19.5046 | 18.202 | 16.7379 | 14.8977 | 12.6005 | 10.3758 | 5.4179 | 1.4386 | 0.21165 | -0.29106
| FRASERBURGH | ST |  |  | 20.2268 | 20.0605 | 19.9334 | 19.776 | 19.6637 | 18.9164 | 17.9723 | 16.8357 | 15.5123 | 13.8466 | 10.4615 | 6.1017 | 4.0982 | 3.0378 | 23.7453 | 23.6152 | 23.5192 | 23.3975 | 23.3058 | 22.6065 | 21.728 | 20.6651 | 19.3564 | 17.7308 | 14.5772 | 11.4034 | 10.0349 | 9.0861 | 21.0173 | 20.874 | 20.7646 | 20.6249 | 20.5272 | 19.827 | 18.9424 | 17.8769 | 16.6345 | 15.0676 | 11.8866 | 7.6942 | 5.8286 | 4.9132
| FRASERBURGH | SP |  |  | 20.2796 | 20.1477 | 20.0549 | 19.9558 | 19.8081 | 19.0343 | 18.0628 | 16.9002 | 15.5294 | 13.8569 | 10.553 | 6.7229 | 4.5388 | 3.8405 | 23.7648 | 23.6508 | 23.5698 | 23.4829 | 23.387 | 22.6893 | 21.8126 | 20.7366 | 19.4126 | 17.8068 | 14.8425 | 11.8863 | 9.8823 | 8.2725 | 21.0637 | 20.9516 | 20.873 | 20.7881 | 20.6622 | 19.9427 | 19.0379 | 17.953 | 16.6693 | 15.1018 | 12.0267 | 8.4612 | 6.3046 | 5.6515
LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | NO | 2.4973 | 2.4651 | 2.4227 | 2.3722 | 2.2428 | 2.103 | 1.9469 | 1.7854 | 1.5337 | 1.3546 | 0.86159 | 0.3088 | -0.021818 | -0.15056 | 3.0975 | 3.0744 | 3.0454 | 3.0102 | 2.9385 | 2.8597 | 2.7578 | 2.6546 | 2.5122 | 2.361 | 1.9825 | 1.7482 | 1.603 | 1.5098 | 2.2768 | 2.2397 | 2.1918 | 2.1343 | 2.0023 | 1.857 | 1.6819 | 1.5033 | 1.2404 | 1.0239 | 0.45577 | -0.03376 | -0.32281 | -0.43337
| FRIOCKHEIM | CT |  |  | 2.5297 | 2.515 | 2.4863 | 2.4387 | 2.3234 | 2.2061 | 2.0167 | 1.8115 | 1.6104 | 1.4514 | 0.91693 | 0.3088 | -0.021818 | -0.15056 | 3.1026 | 3.0847 | 3.0563 | 3.0116 | 2.9429 | 2.8748 | 2.7784 | 2.6785 | 2.5785 | 2.4784 | 2.0266 | 1.7482 | 1.603 | 1.5098 | 2.3003 | 2.2782 | 2.2392 | 2.177 | 2.0542 | 1.9313 | 1.7438 | 1.5449 | 1.3486 | 1.178 | 0.5218 | -0.03376 | -0.32281 | -0.43337
| FRIOCKHEIM | LW |  |  | 2.4973 | 2.4651 | 2.4227 | 2.3722 | 2.2428 | 2.103 | 1.9469 | 1.7854 | 1.5337 | 1.3546 | 0.86159 | 0.42164 | 0.22657 | 0.13935 | 3.0975 | 3.0744 | 3.0454 | 3.0102 | 2.9385 | 2.8597 | 2.7578 | 2.6546 | 2.5122 | 2.361 | 1.9825 | 1.7994 | 1.7327 | 1.7031 | 2.2768 | 2.2397 | 2.1918 | 2.1343 | 2.0023 | 1.857 | 1.6819 | 1.5033 | 1.2404 | 1.0239 | 0.45577 | 0.073976 | -0.090281 | -0.16206
| FRIOCKHEIM | ST |  |  | 2.5382 | 2.5274 | 2.5161 | 2.5015 | 2.4867 | 2.4682 | 2.4443 | 2.4225 | 2.3867 | 2.3288 | 2.1231 | 1.5885 | 1.2501 | 1.0382 | 3.1198 | 3.1109 | 3.1007 | 3.0866 | 3.0732 | 3.0551 | 3.0332 | 3.0126 | 2.9859 | 2.942 | 2.7696 | 2.2471 | 2.0926 | 1.9759 | 2.3189 | 2.3063 | 2.2921 | 2.273 | 2.2543 | 2.2295 | 2.2002 | 2.172 | 2.1312 | 2.0639 | 1.812 | 1.1356 | 0.85359 | 0.68437
| FRIOCKHEIM | SP |  |  | 2.543 | 2.5368 | 2.5301 | 2.5231 | 2.497 | 2.4711 | 2.4369 | 2.4038 | 2.3632 | 2.309 | 2.0833 | 1.5421 | 1.1683 | 1.0157 | 3.1186 | 3.113 | 3.1048 | 3.0963 | 3.0795 | 3.0614 | 3.0377 | 3.0144 | 2.9814 | 2.9432 | 2.7992 | 2.3287 | 1.9876 | 1.825 | 2.3203 | 2.3131 | 2.3032 | 2.2932 | 2.2649 | 2.2356 | 2.1987 | 2.1613 | 2.1113 | 2.0508 | 1.8114 | 1.1525 | 0.72363 | 0.58804
KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | YES | 3.3977 | 3.3485 | 3.2918 | 3.2239 | 3.0474 | 2.8276 | 2.5918 | 2.3423 | 2.0151 | 1.8073 | 1.2518 | 0.91811 | 1.0127 | 0.93701 | 3.5505 | 3.5298 | 3.5041 | 3.4713 | 3.4286 | 3.3511 | 3.2473 | 3.1075 | 2.9357 | 2.7889 | 2.4352 | 2.2014 | 2.2325 | 2.2233 | 3.2422 | 3.195 | 3.1398 | 3.0699 | 2.8811 | 2.6423 | 2.3516 | 2.0635 | 1.7011 | 1.4459 | 0.91339 | 0.71358 | 0.81674 | 0.60784
| FYVIE | CT |  |  | 3.4452 | 3.4259 | 3.3945 | 3.3595 | 3.1978 | 3.0074 | 2.7558 | 2.4788 | 2.2079 | 2.0279 | 1.5798 | 1.1841 | 1.1202 | 1.0666 | 3.5505 | 3.5298 | 3.5041 | 3.4713 | 3.4286 | 3.356 | 3.2749 | 3.1674 | 3.0206 | 2.8915 | 2.5964 | 2.3583 | 2.3331 | 2.3117 | 3.2874 | 3.265 | 3.2267 | 3.185 | 3.0203 | 2.8306 | 2.568 | 2.2728 | 1.9988 | 1.7688 | 1.1901 | 0.89651 | 0.84859 | 0.80222
| FYVIE | LW |  |  | 3.3977 | 3.3485 | 3.2918 | 3.2239 | 3.0474 | 2.8276 | 2.5918 | 2.3423 | 2.0151 | 1.8073 | 1.2518 | 0.91811 | 1.0127 | 0.98665 | 3.5526 | 3.5312 | 3.5069 | 3.4743 | 3.4298 | 3.3511 | 3.2473 | 3.1075 | 2.9357 | 2.7889 | 2.4352 | 2.2014 | 2.2325 | 2.2233 | 3.2422 | 3.195 | 3.1398 | 3.0699 | 2.8811 | 2.6423 | 2.3516 | 2.0635 | 1.7011 | 1.4459 | 0.91339 | 0.71358 | 0.81674 | 0.78789
| FYVIE | ST |  |  | 3.4435 | 3.4272 | 3.4084 | 3.3916 | 3.3716 | 3.3261 | 3.2736 | 3.2081 | 3.1143 | 2.9856 | 2.6264 | 1.9883 | 1.629 | 1.4896 | 3.568 | 3.5602 | 3.5499 | 3.5375 | 3.524 | 3.482 | 3.4328 | 3.374 | 3.3047 | 3.2133 | 2.9757 | 2.5735 | 2.4312 | 2.3803 | 3.2816 | 3.2651 | 3.2448 | 3.2279 | 3.2072 | 3.1574 | 3.1081 | 3.0463 | 2.9566 | 2.8302 | 2.4211 | 1.7005 | 1.4487 | 1.3245
| FYVIE | SP |  |  | 3.4574 | 3.4486 | 3.4399 | 3.4302 | 3.3952 | 3.3378 | 3.2717 | 3.1951 | 3.1106 | 2.9927 | 2.5938 | 1.7918 | 1.2021 | 0.93701 | 3.5683 | 3.5619 | 3.554 | 3.545 | 3.5334 | 3.495 | 3.4478 | 3.3925 | 3.3298 | 3.2505 | 3.0763 | 2.6815 | 2.3715 | 2.2596 | 3.2924 | 3.286 | 3.2771 | 3.2667 | 3.2281 | 3.1667 | 3.0927 | 3.0089 | 2.9192 | 2.7977 | 2.377 | 1.3696 | 0.85375 | 0.60784
GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
| GARBAT FOREST | CT |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
| GARBAT FOREST | LW |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
| GARBAT FOREST | ST |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
| GARBAT FOREST | SP |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | -0.4359 | 1.3415 | 1.3204 | 1.3 | 1.2383 | 1.1785 | 1.1242 | 1.0709 | 1.0086 | 0.97777 | 0.83319 | 0.77329 | 0.80201 | 0.75697 | -0.17515 | 1.458 | 1.4434 | 1.4286 | 1.3999 | 1.3673 | 1.3383 | 1.3022 | 1.2634 | 1.2349 | 1.1127 | 1.0738 | 1.0755 | 1.0672 | -0.27326 | 1.362 | 1.353 | 1.3346 | 1.2717 | 1.2062 | 1.1504 | 1.0927 | 1.0164 | 0.97365 | 0.80973 | 0.74758 | 0.76814 | 0.73542
| GISLA | CT |  |  | -0.39507 | 1.3867 | 1.3742 | 1.3569 | 1.2957 | 1.2398 | 1.1817 | 1.1202 | 1.0618 | 1.0378 | 0.92592 | 0.81265 | 0.80358 | 0.79013 | -0.17515 | 1.458 | 1.4482 | 1.4381 | 1.4057 | 1.3739 | 1.3443 | 1.3136 | 1.2839 | 1.2582 | 1.1738 | 1.082 | 1.0755 | 1.0672 | -0.27176 | 1.3632 | 1.354 | 1.3482 | 1.3156 | 1.2532 | 1.1937 | 1.1313 | 1.0676 | 1.029 | 0.91132 | 0.77964 | 0.76814 | 0.75567
| GISLA | LW |  |  | -0.4359 | 1.3415 | 1.3204 | 1.3 | 1.2383 | 1.1785 | 1.1242 | 1.0709 | 1.0086 | 0.97777 | 0.83319 | 0.77329 | 0.80201 | 0.78555 | -0.17444 | 1.4586 | 1.4434 | 1.4286 | 1.3999 | 1.3673 | 1.3383 | 1.3022 | 1.2634 | 1.2349 | 1.1127 | 1.0738 | 1.0809 | 1.0752 | -0.27326 | 1.362 | 1.353 | 1.3346 | 1.2717 | 1.2062 | 1.1504 | 1.0927 | 1.0164 | 0.97365 | 0.80973 | 0.74758 | 0.77088 | 0.75793
| GISLA | ST |  |  | -0.40817 | 1.3584 | 1.3469 | 1.3443 | 1.3401 | 1.3336 | 1.3276 | 1.3238 | 1.314 | 1.2973 | 1.2459 | 1.0714 | 0.94779 | 0.87819 | -0.17335 | 1.461 | 1.4529 | 1.4493 | 1.4457 | 1.4379 | 1.4302 | 1.4238 | 1.4148 | 1.3998 | 1.3466 | 1.1836 | 1.1352 | 1.1088 | -0.2717 | 1.3631 | 1.3553 | 1.3528 | 1.3509 | 1.3489 | 1.3476 | 1.3466 | 1.3365 | 1.3144 | 1.2399 | 1.0207 | 0.92313 | 0.86918
| GISLA | SP |  |  | -0.40873 | 1.3567 | 1.3457 | 1.3406 | 1.3129 | 1.2872 | 1.2598 | 1.2315 | 1.2032 | 1.1611 | 1.0784 | 0.92888 | 0.80862 | 0.75697 | -0.17329 | 1.4612 | 1.4534 | 1.4507 | 1.4413 | 1.4297 | 1.4184 | 1.4052 | 1.3896 | 1.3695 | 1.3211 | 1.2179 | 1.0951 | 1.0692 | -0.27147 | 1.3634 | 1.3559 | 1.3539 | 1.3507 | 1.3361 | 1.3114 | 1.2857 | 1.2598 | 1.2219 | 1.1276 | 0.93811 | 0.78282 | 0.73542
ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | 2.2468 | 2.2521 | 2.2451 | 2.2342 | 2.1913 | 2.1476 | 2.1044 | 2.0408 | 1.899 | 1.8149 | 1.5656 | 1.4969 | 1.4879 | 1.4121 | 3.1875 | 3.185 | 3.1772 | 3.1671 | 3.1407 | 3.1018 | 3.0619 | 3.0119 | 2.9465 | 2.8962 | 2.7449 | 2.7049 | 2.6731 | 2.606 | 2.7326 | 2.7371 | 2.7216 | 2.699 | 2.6231 | 2.5442 | 2.4653 | 2.3746 | 2.2468 | 2.1678 | 1.9333 | 1.8696 | 1.8634 | 1.7968
| GLASTULLICH | CT |  |  | 2.2652 | 2.2706 | 2.2659 | 2.2523 | 2.2091 | 2.1703 | 2.1135 | 2.0552 | 1.9478 | 1.8915 | 1.683 | 1.5397 | 1.5352 | 1.5229 | 3.198 | 3.1974 | 3.1922 | 3.1832 | 3.1499 | 3.1132 | 3.0652 | 3.0158 | 2.9669 | 2.9348 | 2.8038 | 2.7164 | 2.7017 | 2.6794 | 2.7707 | 2.7792 | 2.7712 | 2.7465 | 2.6654 | 2.5929 | 2.4929 | 2.3897 | 2.2909 | 2.2386 | 2.0416 | 1.9085 | 1.9042 | 1.8938
| GLASTULLICH | LW |  |  | 2.2468 | 2.2521 | 2.2451 | 2.2342 | 2.1913 | 2.1476 | 2.1044 | 2.0408 | 1.899 | 1.8149 | 1.5656 | 1.4969 | 1.5464 | 1.5245 | 3.1875 | 3.185 | 3.1772 | 3.1671 | 3.1407 | 3.1018 | 3.0619 | 3.0119 | 2.9465 | 2.8962 | 2.7449 | 2.7049 | 2.7228 | 2.7143 | 2.7326 | 2.7371 | 2.7216 | 2.699 | 2.6231 | 2.5442 | 2.4653 | 2.3746 | 2.2468 | 2.1678 | 1.9333 | 1.8696 | 1.9134 | 1.8945
| GLASTULLICH | ST |  |  | 2.2594 | 2.257 | 2.2551 | 2.2536 | 2.2549 | 2.2547 | 2.2533 | 2.2528 | 2.2448 | 2.229 | 2.1751 | 1.9482 | 1.8425 | 1.7914 | 3.1978 | 3.195 | 3.1922 | 3.1895 | 3.1864 | 3.1822 | 3.1772 | 3.1721 | 3.1631 | 3.1442 | 3.0702 | 2.8735 | 2.815 | 2.7785 | 2.7606 | 2.7552 | 2.7503 | 2.7457 | 2.7419 | 2.7358 | 2.7272 | 2.7196 | 2.7006 | 2.6665 | 2.5501 | 2.2684 | 2.1737 | 2.1293
| GLASTULLICH | SP |  |  | 2.2618 | 2.2603 | 2.2598 | 2.2596 | 2.2463 | 2.2338 | 2.2199 | 2.2041 | 2.187 | 2.1584 | 2.0692 | 1.7025 | 1.4879 | 1.4121 | 3.1982 | 3.1956 | 3.1932 | 3.1908 | 3.1817 | 3.1728 | 3.1631 | 3.1466 | 3.1273 | 3.0983 | 3.0192 | 2.8156 | 2.6731 | 2.606 | 2.7626 | 2.7576 | 2.7541 | 2.7513 | 2.7237 | 2.6976 | 2.6691 | 2.6366 | 2.6009 | 2.5459 | 2.4005 | 2.063 | 1.8634 | 1.7968
SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | 1.3421 | 1.3419 | 1.3412 | 1.3399 | 1.3361 | 1.3294 | 1.2675 | 1.1905 | 1.0531 | 0.982 | 0.70627 | 0.64369 | 0.66012 | 0.58707 | 1.8424 | 1.8371 | 1.8299 | 1.8172 | 1.7896 | 1.7619 | 1.7252 | 1.6808 | 1.6101 | 1.5654 | 1.3718 | 1.3342 | 1.3326 | 1.2888 | 1.5639 | 1.5585 | 1.544 | 1.522 | 1.4576 | 1.3907 | 1.3195 | 1.2325 | 1.0923 | 1.0198 | 0.74553 | 0.67599 | 0.69389 | 0.61374
| GLEDFIELD | CT |  |  | 1.343 | 1.3428 | 1.3422 | 1.3401 | 1.3365 | 1.333 | 1.2957 | 1.2049 | 1.0998 | 1.0455 | 0.80774 | 0.69488 | 0.69126 | 0.68206 | 1.8492 | 1.8451 | 1.8386 | 1.8183 | 1.7896 | 1.763 | 1.7252 | 1.6859 | 1.634 | 1.5995 | 1.4268 | 1.3567 | 1.3505 | 1.3388 | 1.5895 | 1.5901 | 1.5825 | 1.5577 | 1.4962 | 1.4385 | 1.3459 | 1.2485 | 1.1409 | 1.0857 | 0.85211 | 0.73246 | 0.72589 | 0.71462
| GLEDFIELD | LW |  |  | 1.3421 | 1.3419 | 1.3412 | 1.3399 | 1.3361 | 1.3294 | 1.2675 | 1.1905 | 1.0531 | 0.982 | 0.70627 | 0.64369 | 0.67912 | 0.66598 | 1.8424 | 1.8371 | 1.8299 | 1.8172 | 1.7901 | 1.7619 | 1.7289 | 1.6808 | 1.6101 | 1.5654 | 1.3718 | 1.3342 | 1.3463 | 1.3416 | 1.5639 | 1.5585 | 1.544 | 1.522 | 1.4576 | 1.3907 | 1.3195 | 1.2325 | 1.0923 | 1.0198 | 0.74553 | 0.67599 | 0.71412 | 0.70037
| GLEDFIELD | ST |  |  | 1.3427 | 1.3425 | 1.3421 | 1.3416 | 1.3415 | 1.3411 | 1.3404 | 1.3398 | 1.3352 | 1.3324 | 1.2802 | 0.97817 | 0.89668 | 0.85951 | 1.8487 | 1.8459 | 1.8423 | 1.8358 | 1.832 | 1.826 | 1.8161 | 1.8075 | 1.7894 | 1.7668 | 1.6845 | 1.4595 | 1.4191 | 1.3982 | 1.5814 | 1.5765 | 1.571 | 1.5637 | 1.5596 | 1.5524 | 1.5408 | 1.5307 | 1.5017 | 1.465 | 1.3394 | 1.0378 | 0.94557 | 0.90341
| GLEDFIELD | SP |  |  | 1.3435 | 1.3434 | 1.3434 | 1.3432 | 1.3424 | 1.3414 | 1.3406 | 1.3394 | 1.3339 | 1.331 | 1.2317 | 0.90171 | 0.66012 | 0.58707 | 1.8545 | 1.8524 | 1.8511 | 1.8476 | 1.8402 | 1.8313 | 1.8236 | 1.8133 | 1.7858 | 1.7657 | 1.6942 | 1.4948 | 1.3326 | 1.2888 | 1.5902 | 1.587 | 1.5855 | 1.5819 | 1.5642 | 1.5456 | 1.5275 | 1.5056 | 1.4635 | 1.4236 | 1.2809 | 0.94098 | 0.69389 | 0.61374
FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | 0.11185 | 0.11185 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11183 | 0.11182 | 0.11175 | 0.11163 | 0.11149 | 0.1054 | 0.10537 | 0.10533 | 0.10529 | 0.10526 | 0.10523 | 0.10519 | 0.10515 | 0.1051 | 0.10506 | 0.10487 | 0.10432 | 0.10315 | 0.10094 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.10348 | 0.10344 | 0.10336 | 0.10327
| GLEN LAOGH | CT |  |  | 0.11185 | 0.11185 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11183 | 0.11182 | 0.11175 | 0.11163 | 0.11149 | 0.1054 | 0.10538 | 0.10535 | 0.10531 | 0.10528 | 0.10525 | 0.10522 | 0.10517 | 0.10513 | 0.10509 | 0.10495 | 0.10447 | 0.10361 | 0.10218 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.10348 | 0.10344 | 0.10336 | 0.10327
| GLEN LAOGH | LW |  |  | 0.11185 | 0.11185 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11183 | 0.11182 | 0.11175 | 0.11163 | 0.11149 | 0.10542 | 0.10542 | 0.10542 | 0.10542 | 0.10542 | 0.10542 | 0.10542 | 0.10542 | 0.10541 | 0.10541 | 0.1054 | 0.10536 | 0.10529 | 0.10522 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.10348 | 0.10344 | 0.10336 | 0.10327
| GLEN LAOGH | ST |  |  | 0.11185 | 0.11185 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11183 | 0.11182 | 0.11175 | 0.11163 | 0.11149 | 0.1054 | 0.10538 | 0.10535 | 0.10531 | 0.10528 | 0.10525 | 0.10522 | 0.10517 | 0.10513 | 0.10509 | 0.10495 | 0.10447 | 0.10361 | 0.10219 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.10348 | 0.10344 | 0.10336 | 0.10327
| GLEN LAOGH | SP |  |  | 0.11185 | 0.11185 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11184 | 0.11183 | 0.11182 | 0.11175 | 0.11163 | 0.11149 | 0.1054 | 0.10537 | 0.10533 | 0.10529 | 0.10526 | 0.10523 | 0.10519 | 0.10515 | 0.1051 | 0.10506 | 0.10487 | 0.10432 | 0.10315 | 0.10094 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.1035 | 0.10348 | 0.10344 | 0.10336 | 0.10327
KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | 5.6823 | 5.6679 | 5.6385 | 5.5812 | 5.477 | 5.3683 | 5.2579 | 5.1384 | 4.994 | 4.8982 | 4.601 | 4.5259 | 4.5859 | 4.5205 | 6.2305 | 6.2202 | 6.2039 | 6.1712 | 6.1187 | 6.0634 | 6.0062 | 5.9407 | 5.8684 | 5.8051 | 5.6015 | 5.5503 | 5.5569 | 5.4985 | 5.7951 | 5.7812 | 5.7542 | 5.7034 | 5.6076 | 5.5011 | 5.3932 | 5.2765 | 5.146 | 5.0536 | 4.762 | 4.6911 | 4.7393 | 4.6906
| GLENCOE | CT |  |  | 5.7134 | 5.7053 | 5.681 | 5.6211 | 5.5132 | 5.412 | 5.3045 | 5.1969 | 5.0953 | 5.0292 | 4.7388 | 4.583 | 4.5859 | 4.5744 | 6.2419 | 6.2339 | 6.218 | 6.1816 | 6.127 | 6.0753 | 6.0218 | 5.9678 | 5.916 | 5.8727 | 5.6684 | 5.5661 | 5.5569 | 5.5375 | 5.8219 | 5.8134 | 5.7904 | 5.7364 | 5.6389 | 5.547 | 5.4419 | 5.3366 | 5.2372 | 5.1722 | 4.8878 | 4.737 | 4.7398 | 4.7314
| GLENCOE | LW |  |  | 5.6823 | 5.6679 | 5.6385 | 5.5812 | 5.477 | 5.3683 | 5.2579 | 5.1384 | 4.994 | 4.8982 | 4.601 | 4.5259 | 4.5889 | 4.5653 | 6.2305 | 6.2202 | 6.2039 | 6.1712 | 6.1187 | 6.0634 | 6.0062 | 5.9407 | 5.8684 | 5.8051 | 5.6015 | 5.5503 | 5.5702 | 5.5621 | 5.7951 | 5.7812 | 5.7542 | 5.7034 | 5.6076 | 5.5011 | 5.3932 | 5.2765 | 5.146 | 5.0536 | 4.762 | 4.6911 | 4.7393 | 4.7208
| GLENCOE | ST |  |  | 5.7143 | 5.7076 | 5.7006 | 5.6734 | 5.6648 | 5.6548 | 5.6408 | 5.6271 | 5.6029 | 5.5602 | 5.4119 | 5.0091 | 4.8986 | 4.8623 | 6.2465 | 6.2422 | 6.2375 | 6.2203 | 6.2131 | 6.2052 | 6.1944 | 6.1836 | 6.1677 | 6.1401 | 6.041 | 5.7495 | 5.674 | 5.6431 | 5.8238 | 5.8176 | 5.8111 | 5.7875 | 5.779 | 5.7693 | 5.7557 | 5.7424 | 5.7197 | 5.6795 | 5.5386 | 5.1427 | 5.0276 | 4.9893
| GLENCOE | SP |  |  | 5.7182 | 5.7141 | 5.71 | 5.688 | 5.6606 | 5.6361 | 5.6037 | 5.5734 | 5.5325 | 5.4788 | 5.3189 | 4.9344 | 4.6207 | 4.5205 | 6.2479 | 6.2451 | 6.2416 | 6.2277 | 6.2134 | 6.2009 | 6.1827 | 6.1667 | 6.1428 | 6.1138 | 6.0242 | 5.7879 | 5.5675 | 5.4985 | 5.8273 | 5.8235 | 5.8194 | 5.8009 | 5.7761 | 5.7541 | 5.7244 | 5.697 | 5.6593 | 5.6075 | 5.4503 | 5.073 | 4.7698 | 4.6906
DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | 0.17631 | 0.5622 | 0.55146 | 0.54066 | 0.51201 | 0.4764 | 0.43819 | 0.40546 | 0.37483 | 0.33189 | 0.29289 | 0.27966 | 0.2891 | 0.26825 | 0.20436 | 0.56167 | 0.55521 | 0.54885 | 0.53542 | 0.51845 | 0.49902 | 0.48391 | 0.46969 | 0.437 | 0.41835 | 0.41154 | 0.41166 | 0.39959 | 0.17729 | 0.53372 | 0.52295 | 0.51162 | 0.48388 | 0.45165 | 0.41673 | 0.38725 | 0.35964 | 0.31804 | 0.2827 | 0.27058 | 0.27917 | 0.26075
| GLENDARUEL | CT |  |  | 0.18722 | 0.57493 | 0.56705 | 0.55985 | 0.53323 | 0.50935 | 0.4793 | 0.45106 | 0.42067 | 0.40393 | 0.33516 | 0.30465 | 0.29779 | 0.29132 | 0.20957 | 0.56762 | 0.56244 | 0.55797 | 0.54324 | 0.53162 | 0.5181 | 0.50593 | 0.49145 | 0.48149 | 0.43357 | 0.42033 | 0.41616 | 0.41113 | 0.19069 | 0.54964 | 0.54198 | 0.53516 | 0.50571 | 0.48092 | 0.45396 | 0.42879 | 0.40131 | 0.38567 | 0.32011 | 0.29294 | 0.28691 | 0.28123
| GLENDARUEL | LW |  |  | 0.17631 | 0.5622 | 0.55146 | 0.54066 | 0.51201 | 0.4764 | 0.43819 | 0.40546 | 0.37483 | 0.33189 | 0.29289 | 0.27966 | 0.29411 | 0.29018 | 0.20436 | 0.56167 | 0.55521 | 0.54885 | 0.53542 | 0.51845 | 0.49902 | 0.48391 | 0.46969 | 0.437 | 0.41835 | 0.41154 | 0.41629 | 0.41483 | 0.17729 | 0.53372 | 0.52295 | 0.51162 | 0.48388 | 0.45165 | 0.41673 | 0.38725 | 0.35964 | 0.31804 | 0.2827 | 0.27058 | 0.28324 | 0.27979
| GLENDARUEL | ST |  |  | 0.18722 | 0.57336 | 0.5708 | 0.56974 | 0.56715 | 0.56105 | 0.55792 | 0.55517 | 0.54973 | 0.53943 | 0.50318 | 0.41535 | 0.38385 | 0.36506 | 0.21029 | 0.56789 | 0.56623 | 0.56543 | 0.56367 | 0.55969 | 0.55764 | 0.55572 | 0.55224 | 0.54579 | 0.52204 | 0.46096 | 0.44611 | 0.43622 | 0.18948 | 0.54604 | 0.5435 | 0.54246 | 0.53985 | 0.53421 | 0.53085 | 0.52796 | 0.52229 | 0.51182 | 0.47591 | 0.38883 | 0.36118 | 0.34549
| GLENDARUEL | SP |  |  | 0.1871 | 0.57447 | 0.57221 | 0.56963 | 0.56134 | 0.5533 | 0.53987 | 0.528 | 0.51632 | 0.49763 | 0.45573 | 0.33942 | 0.2891 | 0.26825 | 0.21017 | 0.5686 | 0.56709 | 0.56535 | 0.56086 | 0.55644 | 0.54856 | 0.54244 | 0.53725 | 0.52862 | 0.50977 | 0.44136 | 0.41166 | 0.39959 | 0.18945 | 0.54697 | 0.54475 | 0.54226 | 0.53279 | 0.5237 | 0.51 | 0.49831 | 0.48786 | 0.47104 | 0.43353 | 0.32544 | 0.27917 | 0.26075
ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | 2.1391 | 2.1036 | 2.0546 | 1.9724 | 1.8378 | 1.6833 | 1.5086 | 1.3534 | 1.1702 | 1.0449 | 0.83858 | 0.67619 | 0.68775 | 0.56674 | 2.54 | 2.5147 | 2.4851 | 2.4267 | 2.3585 | 2.2776 | 2.1796 | 2.0972 | 1.9973 | 1.9167 | 1.8056 | 1.6765 | 1.6117 | 1.4993 | 3.3258 | 3.293 | 3.248 | 3.1735 | 3.0564 | 2.9205 | 2.7609 | 2.6221 | 2.4555 | 2.3347 | 2.1568 | 2.0188 | 2.024 | 1.9243
| GLENDEVON | CT |  |  | 2.1831 | 2.1621 | 2.1256 | 2.0572 | 1.9342 | 1.8085 | 1.6669 | 1.528 | 1.3934 | 1.2765 | 0.99745 | 0.78034 | 0.71957 | 0.68 | 2.5553 | 2.5346 | 2.5074 | 2.4534 | 2.392 | 2.3276 | 2.2562 | 2.1881 | 2.1206 | 2.0443 | 1.8612 | 1.705 | 1.6376 | 1.5785 | 3.3618 | 3.3409 | 3.3051 | 3.2418 | 3.1367 | 3.0294 | 2.9091 | 2.7909 | 2.6727 | 2.5615 | 2.2899 | 2.1072 | 2.0548 | 2.0215
| GLENDEVON | LW |  |  | 2.1391 | 2.1036 | 2.0546 | 1.9724 | 1.8378 | 1.6833 | 1.5086 | 1.3534 | 1.1702 | 1.0449 | 0.83858 | 0.67619 | 0.69287 | 0.66061 | 2.54 | 2.5147 | 2.4851 | 2.4267 | 2.3585 | 2.2776 | 2.1796 | 2.0972 | 1.9973 | 1.9167 | 1.8056 | 1.6765 | 1.6572 | 1.6338 | 3.3258 | 3.293 | 3.248 | 3.1735 | 3.0564 | 2.9205 | 2.7609 | 2.6221 | 2.4555 | 2.3347 | 2.1568 | 2.0188 | 2.0305 | 2.004
| GLENDEVON | ST |  |  | 2.1776 | 2.1535 | 2.1325 | 2.0892 | 2.0619 | 2.0238 | 1.988 | 1.9534 | 1.9087 | 1.8473 | 1.646 | 1.1991 | 1.0339 | 0.95004 | 2.5573 | 2.5392 | 2.5239 | 2.4827 | 2.4621 | 2.4348 | 2.4091 | 2.3851 | 2.3569 | 2.3197 | 2.1914 | 1.8643 | 1.7538 | 1.6777 | 3.3597 | 3.3387 | 3.3198 | 3.2813 | 3.2576 | 3.2242 | 3.1938 | 3.1632 | 3.1246 | 3.07 | 2.8788 | 2.4486 | 2.31 | 2.2399
| GLENDEVON | SP |  |  | 2.1891 | 2.1674 | 2.1511 | 2.1081 | 2.0603 | 2.0032 | 1.9447 | 1.8869 | 1.8292 | 1.7578 | 1.5466 | 0.93428 | 0.68775 | 0.56674 | 2.5645 | 2.5469 | 2.5338 | 2.4925 | 2.4642 | 2.4293 | 2.394 | 2.3606 | 2.3271 | 2.2886 | 2.1765 | 1.7747 | 1.6117 | 1.4993 | 3.3713 | 3.3523 | 3.3377 | 3.2993 | 3.259 | 3.2096 | 3.1595 | 3.109 | 3.0591 | 2.9988 | 2.8157 | 2.2355 | 2.024 | 1.9243
FORT AUGUSTUS | GLENDOE PRIMARY | MINIMUM HEADROOM | NH 40060 08894 | YES | 6.765 | 6.7455 | 6.7269 | 6.7006 | 6.634 | 6.5607 | 6.4853 | 6.4072 | 6.3311 | 6.2829 | 6.1205 | 6.0427 | 6.0746 | 6.0599 | 6.8486 | 6.8389 | 6.8299 | 6.8162 | 6.7832 | 6.7471 | 6.7059 | 6.6617 | 6.6203 | 6.5929 | 6.4949 | 6.4414 | 6.4538 | 6.4496 | 6.7791 | 6.7594 | 6.7406 | 6.7151 | 6.652 | 6.5823 | 6.5101 | 6.4333 | 6.3616 | 6.3174 | 6.1617 | 6.0814 | 6.1062 | 6.0988
| GLENDOE PRIMARY | CT |  |  | 6.7744 | 6.7625 | 6.7484 | 6.7214 | 6.6493 | 6.5751 | 6.5045 | 6.4432 | 6.3824 | 6.3444 | 6.2218 | 6.0946 | 6.0746 | 6.0599 | 6.8527 | 6.8463 | 6.8389 | 6.8234 | 6.7876 | 6.7507 | 6.7138 | 6.68 | 6.6459 | 6.6223 | 6.5451 | 6.4678 | 6.457 | 6.4496 | 6.7891 | 6.7772 | 6.7632 | 6.7374 | 6.6687 | 6.5979 | 6.5306 | 6.4703 | 6.4103 | 6.3724 | 6.2495 | 6.1268 | 6.1097 | 6.0988
| GLENDOE PRIMARY | LW |  |  | 6.765 | 6.7455 | 6.7269 | 6.7006 | 6.634 | 6.5607 | 6.4853 | 6.4072 | 6.3311 | 6.2829 | 6.1205 | 6.0427 | 6.0763 | 6.0678 | 6.8486 | 6.8389 | 6.8299 | 6.8162 | 6.7832 | 6.7471 | 6.7059 | 6.6617 | 6.6203 | 6.5929 | 6.4949 | 6.4414 | 6.4538 | 6.4503 | 6.7791 | 6.7594 | 6.7406 | 6.7151 | 6.652 | 6.5823 | 6.5101 | 6.4333 | 6.3616 | 6.3174 | 6.1617 | 6.0814 | 6.1062 | 6.0996
| GLENDOE PRIMARY | ST |  |  | 6.7775 | 6.7733 | 6.7679 | 6.7567 | 6.7376 | 6.7182 | 6.6961 | 6.6833 | 6.6683 | 6.6452 | 6.566 | 6.3907 | 6.3153 | 6.2899 | 6.855 | 6.8527 | 6.8497 | 6.8431 | 6.8309 | 6.8185 | 6.8041 | 6.7965 | 6.7878 | 6.7746 | 6.7284 | 6.6167 | 6.5733 | 6.5604 | 6.7922 | 6.7878 | 6.7824 | 6.772 | 6.7554 | 6.7384 | 6.7185 | 6.7058 | 6.6909 | 6.6677 | 6.5881 | 6.41 | 6.3315 | 6.3046
| GLENDOE PRIMARY | SP |  |  | 6.7837 | 6.7824 | 6.7805 | 6.7728 | 6.7523 | 6.7309 | 6.7109 | 6.6982 | 6.6797 | 6.6589 | 6.5708 | 6.3639 | 6.2076 | 6.1406 | 6.8579 | 6.857 | 6.8555 | 6.8502 | 6.8378 | 6.8247 | 6.8126 | 6.8053 | 6.7944 | 6.783 | 6.7377 | 6.6207 | 6.525 | 6.4898 | 6.7981 | 6.7965 | 6.7943 | 6.7873 | 6.7693 | 6.7503 | 6.7326 | 6.7201 | 6.7018 | 6.681 | 6.5933 | 6.3869 | 6.2304 | 6.1707
BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | 3.1093 | 2.9317 | 11.3457 | 10.9643 | 10.3147 | 9.7201 | 9.1341 | 8.5138 | 7.8668 | 7.1215 | 5.1597 | 3.7938 | 3.2313 | 3.0263 | 5.1052 | 5.0085 | 13.0731 | 12.8009 | 12.401 | 12.0532 | 11.7058 | 11.3169 | 10.9407 | 10.4098 | 9.0268 | 8.2233 | 7.9085 | 7.6726 | 3.6414 | 3.4848 | 11.4789 | 11.1331 | 10.5282 | 9.986 | 9.4615 | 8.9078 | 8.3264 | 7.6542 | 5.8702 | 4.6076 | 4.0855 | 3.8947
| GLENEAGLES | CT |  |  | 3.1605 | 3.0238 | 11.4603 | 11.1181 | 10.4719 | 9.9234 | 9.3426 | 8.7919 | 8.2506 | 7.5945 | 5.4648 | 3.7938 | 3.2313 | 3.0263 | 5.1164 | 5.0318 | 13.0941 | 12.8196 | 12.4115 | 12.0814 | 11.748 | 11.4318 | 11.122 | 10.6756 | 9.1976 | 8.2233 | 7.9085 | 7.6726 | 3.6882 | 3.5695 | 11.5853 | 11.2788 | 10.6789 | 10.1804 | 9.6578 | 9.1619 | 8.6761 | 8.0786 | 6.1449 | 4.6076 | 4.0855 | 3.8947
| GLENEAGLES | LW |  |  | 3.1093 | 2.9317 | 11.3457 | 10.9643 | 10.3147 | 9.7201 | 9.1341 | 8.5138 | 7.8668 | 7.1215 | 5.1597 | 3.9735 | 3.687 | 3.5298 | 5.1052 | 5.0085 | 13.0731 | 12.8009 | 12.401 | 12.0532 | 11.7058 | 11.3169 | 10.9407 | 10.4098 | 9.0268 | 8.3013 | 8.1913 | 8.1309 | 3.6414 | 3.4848 | 11.4789 | 11.1331 | 10.5282 | 9.986 | 9.4615 | 8.9078 | 8.3264 | 7.6542 | 5.8702 | 4.7815 | 4.5143 | 4.365
| GLENEAGLES | ST |  |  | 3.229 | 3.1637 | 11.6912 | 11.4423 | 11.1779 | 10.9722 | 10.7515 | 10.5416 | 10.3364 | 9.9306 | 8.7117 | 6.7046 | 5.95 | 5.6346 | 5.169 | 5.1291 | 13.2517 | 13.0538 | 12.8356 | 12.678 | 12.5151 | 12.3635 | 12.2136 | 11.9027 | 10.9629 | 9.4768 | 8.953 | 8.6745 | 3.7512 | 3.6987 | 11.7979 | 11.5748 | 11.3317 | 11.1535 | 10.9687 | 10.7911 | 10.6184 | 10.2531 | 9.145 | 7.2646 | 6.5674 | 6.2906
| GLENEAGLES | SP |  |  | 3.2739 | 3.231 | 11.7767 | 11.5576 | 11.28 | 11.0575 | 10.8168 | 10.6028 | 10.3684 | 9.9636 | 8.8258 | 7.0248 | 5.8083 | 5.4757 | 5.1924 | 5.1635 | 13.2936 | 13.1134 | 12.8969 | 12.7389 | 12.5726 | 12.426 | 12.2638 | 11.9623 | 11.1056 | 9.8631 | 8.8511 | 8.313 | 3.7932 | 3.7619 | 11.8787 | 11.6828 | 11.4262 | 11.2315 | 11.0276 | 10.8456 | 10.6471 | 10.2812 | 9.2418 | 7.611 | 6.4647 | 6.1603
RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | 0.27105 | 0.2687 | 0.26715 | 0.25692 | 0.24074 | 0.2347 | 0.21589 | 0.19697 | 0.16382 | 0.13092 | 0.062188 | -0.059606 | -0.14635 | -0.19373 | 0.27727 | 0.27678 | 0.27603 | 0.26466 | 0.25192 | 0.24955 | 0.23595 | 0.22226 | 0.19723 | 0.17172 | 0.11883 | 0.017592 | -0.045575 | -0.081797 | 0.26507 | 0.26306 | 0.26173 | 0.24766 | 0.2321 | 0.22678 | 0.20894 | 0.19101 | 0.15937 | 0.12781 | 0.061996 | -0.056117 | -0.13845 | -0.18376
| GLENETIVE | CT |  |  | 0.27105 | 0.27043 | 0.26825 | 0.25747 | 0.24074 | 0.23724 | 0.21913 | 0.20083 | 0.16803 | 0.15096 | 0.084411 | 0.014428 | 0.013718 | 0.013248 | 0.27727 | 0.27678 | 0.27603 | 0.26505 | 0.25192 | 0.25023 | 0.23704 | 0.22372 | 0.19891 | 0.18583 | 0.13446 | 0.080505 | 0.080103 | 0.07993 | 0.26507 | 0.26445 | 0.26235 | 0.24928 | 0.2321 | 0.22895 | 0.21176 | 0.19439 | 0.16308 | 0.14675 | 0.082973 | 0.015919 | 0.015265 | 0.014853
| GLENETIVE | LW |  |  | 0.2724 | 0.2687 | 0.26715 | 0.25692 | 0.2532 | 0.2347 | 0.21589 | 0.19697 | 0.16382 | 0.13092 | 0.062188 | -0.021891 | -0.020325 | -0.020792 | 0.28087 | 0.27709 | 0.27663 | 0.26466 | 0.26289 | 0.24955 | 0.23595 | 0.22226 | 0.19723 | 0.17172 | 0.11883 | 0.053033 | 0.053609 | 0.053437 | 0.26656 | 0.26306 | 0.26173 | 0.24766 | 0.24431 | 0.22678 | 0.20894 | 0.19101 | 0.15937 | 0.12781 | 0.061996 | -0.018747 | -0.017375 | -0.017784
| GLENETIVE | ST |  |  | 0.27408 | 0.27375 | 0.2733 | 0.27259 | 0.26988 | 0.26947 | 0.25806 | 0.24362 | 0.22801 | 0.19708 | 0.11942 | -0.059606 | -0.13982 | -0.14142 | 0.28158 | 0.28142 | 0.28114 | 0.28068 | 0.27678 | 0.2765 | 0.26541 | 0.25343 | 0.2413 | 0.21724 | 0.15691 | 0.017592 | -0.044323 | -0.044912 | 0.26805 | 0.26775 | 0.26733 | 0.26666 | 0.26407 | 0.26369 | 0.24946 | 0.23473 | 0.21976 | 0.1901 | 0.11565 | -0.056117 | -0.13294 | -0.13435
| GLENETIVE | SP |  |  | 0.27319 | 0.27301 | 0.27278 | 0.27257 | 0.2685 | 0.26746 | 0.25756 | 0.24236 | 0.22653 | 0.19548 | 0.14793 | -0.0020744 | -0.14635 | -0.19373 | 0.28076 | 0.28067 | 0.2805 | 0.28036 | 0.27687 | 0.27659 | 0.26525 | 0.25319 | 0.24109 | 0.21718 | 0.18127 | 0.066191 | -0.045575 | -0.081797 | 0.26714 | 0.26697 | 0.26675 | 0.26655 | 0.26271 | 0.26179 | 0.24874 | 0.23366 | 0.21852 | 0.1888 | 0.14344 | -0.00015772 | -0.13845 | -0.18376
FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | 0.044481 | 0.044579 | 0.041922 | 0.03779 | 0.027073 | 0.012148 | -0.00082484 | -0.013631 | -0.034849 | -0.044249 | -0.085977 | -0.092108 | -0.092898 | -0.10207 | 0.063364 | 0.063234 | 0.06173 | 0.05935 | 0.053444 | 0.046964 | 0.040851 | 0.034715 | 0.023982 | 0.018218 | -0.012081 | -0.015044 | -0.016234 | -0.020786 | 0.055011 | 0.055362 | 0.052492 | 0.048233 | 0.037615 | 0.023965 | 0.012238 | 0.00063569 | -0.018749 | -0.027534 | -0.06855 | -0.073793 | -0.0744 | -0.081889
| GLENUIG | CT |  |  | 0.048497 | 0.048451 | 0.046056 | 0.041764 | 0.02844 | 0.018279 | 0.0038747 | -0.01185 | -0.026692 | -0.036101 | -0.073123 | -0.087219 | -0.086031 | -0.08732 | 0.065232 | 0.064951 | 0.063448 | 0.060991 | 0.053444 | 0.047818 | 0.041837 | 0.035091 | 0.028615 | 0.022751 | -0.00496 | -0.012689 | -0.012927 | -0.014241 | 0.06017 | 0.059786 | 0.058083 | 0.054022 | 0.040152 | 0.029116 | 0.016196 | 0.0021673 | -0.011102 | -0.019986 | -0.056274 | -0.06918 | -0.068381 | -0.069408
| GLENUIG | LW |  |  | 0.044481 | 0.044579 | 0.041922 | 0.03779 | 0.027073 | 0.012148 | -0.00082484 | -0.013631 | -0.034849 | -0.044249 | -0.085977 | -0.092108 | -0.086163 | -0.089813 | 0.063364 | 0.063234 | 0.06173 | 0.05935 | 0.054439 | 0.046964 | 0.040851 | 0.034715 | 0.023982 | 0.018218 | -0.012081 | -0.015044 | -0.013052 | -0.014456 | 0.055011 | 0.055362 | 0.052492 | 0.048233 | 0.037615 | 0.023965 | 0.012238 | 0.00063569 | -0.018749 | -0.027534 | -0.06855 | -0.073793 | -0.06875 | -0.071764
| GLENUIG | ST |  |  | 0.04799 | 0.047444 | 0.046647 | 0.045668 | 0.044733 | 0.04362 | 0.042753 | 0.038422 | 0.036183 | 0.030882 | 0.012738 | -0.036794 | -0.047605 | -0.054179 | 0.065207 | 0.064855 | 0.064311 | 0.063639 | 0.062927 | 0.062132 | 0.061525 | 0.058477 | 0.057024 | 0.053558 | 0.041313 | 0.0059479 | 0.00077664 | -0.0024813 | 0.059191 | 0.058583 | 0.05781 | 0.056981 | 0.056191 | 0.05515 | 0.054233 | 0.050655 | 0.048247 | 0.042815 | 0.024402 | -0.02471 | -0.034797 | -0.040455
| GLENUIG | SP |  |  | 0.048259 | 0.047571 | 0.047428 | 0.046624 | 0.042791 | 0.039737 | 0.035088 | 0.030384 | 0.024818 | 0.014234 | -0.0069978 | -0.05307 | -0.092898 | -0.10207 | 0.065349 | 0.064905 | 0.064772 | 0.064197 | 0.06207 | 0.060413 | 0.057758 | 0.055743 | 0.053154 | 0.047624 | 0.037519 | 0.013028 | -0.016234 | -0.020786 | 0.059433 | 0.058692 | 0.058485 | 0.057722 | 0.053424 | 0.049859 | 0.044871 | 0.040547 | 0.035533 | 0.025823 | 0.0066505 | -0.035493 | -0.0744 | -0.081889
BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | 2.6436 | 2.6392 | 2.636 | 2.6141 | 2.5237 | 2.4062 | 2.2719 | 2.1461 | 1.9756 | 1.8868 | 1.6156 | 1.4693 | 1.534 | 1.4009 | 3.2396 | 3.2256 | 3.2104 | 3.164 | 3.0925 | 3.0288 | 2.9523 | 2.868 | 2.7644 | 2.6886 | 2.4608 | 2.3701 | 2.3612 | 2.2383 | 2.8199 | 2.8161 | 2.814 | 2.7932 | 2.705 | 2.5992 | 2.4776 | 2.3644 | 2.2123 | 2.131 | 1.8341 | 1.7148 | 1.7875 | 1.6635
| GOLSPIE | CT |  |  | 2.6436 | 2.6394 | 2.636 | 2.6141 | 2.5923 | 2.4924 | 2.335 | 2.1868 | 2.0495 | 1.9818 | 1.7724 | 1.5505 | 1.5529 | 1.5379 | 3.245 | 3.2347 | 3.2208 | 3.171 | 3.0965 | 3.0362 | 2.9523 | 2.8714 | 2.7951 | 2.7447 | 2.555 | 2.3899 | 2.3755 | 2.3437 | 2.8207 | 2.8179 | 2.8163 | 2.7958 | 2.7666 | 2.6741 | 2.5324 | 2.4002 | 2.2778 | 2.2158 | 2.0013 | 1.786 | 1.7975 | 1.7868
| GOLSPIE | LW |  |  | 2.6439 | 2.6398 | 2.6367 | 2.6155 | 2.5237 | 2.4062 | 2.2719 | 2.1461 | 1.9756 | 1.8868 | 1.6156 | 1.4693 | 1.534 | 1.5144 | 3.2396 | 3.2256 | 3.2104 | 3.164 | 3.0925 | 3.0288 | 2.9547 | 2.868 | 2.7644 | 2.6886 | 2.4608 | 2.3701 | 2.398 | 2.3875 | 2.8259 | 2.8258 | 2.8269 | 2.8088 | 2.705 | 2.5992 | 2.4776 | 2.3644 | 2.2123 | 2.131 | 1.8341 | 1.7148 | 1.7875 | 1.7633
| GOLSPIE | ST |  |  | 2.6436 | 2.6392 | 2.6361 | 2.6153 | 2.5986 | 2.5901 | 2.5802 | 2.5721 | 2.5641 | 2.5184 | 2.36 | 2.0404 | 1.8782 | 1.8171 | 3.2466 | 3.2354 | 3.226 | 3.1875 | 3.1559 | 3.1356 | 3.1122 | 3.0884 | 3.0588 | 3.024 | 2.9072 | 2.6196 | 2.5298 | 2.4829 | 2.8199 | 2.8161 | 2.814 | 2.7932 | 2.779 | 2.7738 | 2.7673 | 2.7627 | 2.7342 | 2.6917 | 2.545 | 2.2324 | 2.0881 | 2.0445
| GOLSPIE | SP |  |  | 2.6445 | 2.6405 | 2.638 | 2.6178 | 2.6005 | 2.5916 | 2.5812 | 2.5727 | 2.5538 | 2.4947 | 2.3022 | 1.8768 | 1.5484 | 1.4009 | 3.2509 | 3.2425 | 3.2361 | 3.2022 | 3.1667 | 3.144 | 3.1166 | 3.091 | 3.0588 | 3.0238 | 2.8979 | 2.6357 | 2.3612 | 2.2383 | 2.8224 | 2.8198 | 2.819 | 2.7992 | 2.7838 | 2.7775 | 2.7699 | 2.7593 | 2.7268 | 2.6725 | 2.4988 | 2.1142 | 1.7998 | 1.6635
BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | YES | 3.1233 | 3.0202 | 2.8948 | 2.7826 | 2.335 | 1.8513 | 1.3623 | 0.79546 | 0.32525 | -0.052777 | -1.614 | -4.2941 | -5.8148 | -6.6477 | 4.5264 | 4.4697 | 4.3907 | 4.3025 | 4.085 | 3.8394 | 3.6375 | 3.3449 | 3.0685 | 2.8143 | 1.9256 | 0.44194 | -0.48709 | -1.2853 | 3.2877 | 3.1934 | 3.0693 | 2.9523 | 2.5529 | 2.1104 | 1.656 | 1.103 | 0.62476 | 0.20499 | -1.2435 | -3.6777 | -4.9675 | -5.6043
| GOODLYBURN | CT |  |  | 3.1233 | 3.0337 | 2.9261 | 2.8268 | 2.402 | 1.9174 | 1.5337 | 1.1381 | 0.70619 | 0.21301 | -1.532 | -4.2941 | -5.8148 | -6.6477 | 4.5264 | 4.4697 | 4.3907 | 4.3025 | 4.085 | 3.8394 | 3.6375 | 3.414 | 3.1696 | 2.8854 | 1.9293 | 0.44194 | -0.48709 | -1.2853 | 3.2877 | 3.1983 | 3.0882 | 2.9673 | 2.5704 | 2.1214 | 1.7582 | 1.3668 | 0.94051 | 0.44737 | -1.1847 | -3.6777 | -4.9675 | -5.6043
| GOODLYBURN | LW |  |  | 3.1234 | 3.0202 | 2.8948 | 2.7826 | 2.335 | 1.8513 | 1.3623 | 0.79546 | 0.32525 | -0.052777 | -1.614 | -3.7239 | -5.0033 | -5.7849 | 4.5374 | 4.4798 | 4.3995 | 4.3233 | 4.1146 | 3.8819 | 3.6466 | 3.3449 | 3.0685 | 2.8143 | 1.9256 | 0.82491 | 0.21843 | -0.18766 | 3.2938 | 3.1934 | 3.0693 | 2.9523 | 2.5529 | 2.1104 | 1.656 | 1.103 | 0.62476 | 0.20499 | -1.2435 | -3.1272 | -4.2128 | -4.8193
| GOODLYBURN | ST |  |  | 3.2324 | 3.2069 | 3.1606 | 3.1188 | 3.0969 | 3.0713 | 3.044 | 3.0029 | 2.9834 | 2.896 | 2.3926 | 0.65765 | -0.64808 | -1.6652 | 4.5867 | 4.5649 | 4.5223 | 4.4826 | 4.4495 | 4.4122 | 4.3719 | 4.3216 | 4.2724 | 4.1813 | 3.8172 | 2.6617 | 1.7264 | 0.82232 | 3.3946 | 3.3669 | 3.3178 | 3.2664 | 3.2322 | 3.1929 | 3.1497 | 3.0915 | 3.0457 | 2.9325 | 2.4833 | 0.97444 | -0.11425 | -0.9395
| GOODLYBURN | SP |  |  | 3.2604 | 3.2545 | 3.2255 | 3.2116 | 3.1695 | 3.1234 | 3.0805 | 3.0338 | 2.9774 | 2.8806 | 2.4956 | 1.271 | -0.029639 | -0.65926 | 4.5902 | 4.5768 | 4.5407 | 4.5172 | 4.4798 | 4.4386 | 4.396 | 4.3469 | 4.2809 | 4.1864 | 3.8585 | 2.9046 | 1.6014 | 0.25158 | 3.4088 | 3.3977 | 3.3627 | 3.3407 | 3.2947 | 3.2443 | 3.1938 | 3.1361 | 3.0572 | 2.9419 | 2.5754 | 1.5296 | 0.47359 | 0.022231
CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | NO | 4.4965 | 4.3897 | 4.2922 | 3.99 | 3.5232 | 3.1582 | 2.8122 | 2.5156 | 2.0934 | 1.6456 | 0.71156 | -0.14069 | -0.50503 | -0.64504 | 4.666 | 4.5861 | 4.5095 | 4.2603 | 3.905 | 3.6451 | 3.3795 | 3.1707 | 2.8814 | 2.5343 | 1.8618 | 1.3686 | 1.1961 | 1.0747 | 4.2144 | 4.103 | 4.0018 | 3.7159 | 3.2909 | 2.9538 | 2.6067 | 2.3274 | 1.9462 | 1.5265 | 0.65376 | -0.063837 | -0.34851 | -0.45587
| GOURDIE | CT |  |  | 4.514 | 4.4225 | 4.335 | 4.05 | 3.589 | 3.2557 | 2.9549 | 2.6684 | 2.2801 | 1.8262 | 0.7729 | -0.14069 | -0.50503 | -0.64504 | 4.666 | 4.5865 | 4.5095 | 4.2633 | 3.9127 | 3.6801 | 3.4827 | 3.305 | 3.0427 | 2.6989 | 1.9011 | 1.3686 | 1.1961 | 1.0747 | 4.2207 | 4.1193 | 4.0204 | 3.7475 | 3.3313 | 3.0346 | 2.7739 | 2.5307 | 2.1899 | 1.7706 | 0.73125 | -0.063837 | -0.34851 | -0.45587
| GOURDIE | LW |  |  | 4.4965 | 4.3897 | 4.2922 | 3.99 | 3.5232 | 3.1582 | 2.8122 | 2.5156 | 2.0934 | 1.6456 | 0.71156 | 0.0013426 | -0.22389 | -0.31467 | 4.6685 | 4.5861 | 4.5118 | 4.2603 | 3.905 | 3.6451 | 3.3795 | 3.1707 | 2.8814 | 2.5343 | 1.8618 | 1.4363 | 1.3548 | 1.3199 | 4.2144 | 4.103 | 4.0018 | 3.7159 | 3.2909 | 2.9538 | 2.6067 | 2.3274 | 1.9462 | 1.5265 | 0.65376 | 0.03409 | -0.13944 | -0.20866
| GOURDIE | ST |  |  | 4.5564 | 4.4944 | 4.4446 | 4.2163 | 3.9041 | 3.7317 | 3.5922 | 3.4687 | 3.2332 | 2.9008 | 2.2026 | 1.2039 | 0.71303 | 0.53116 | 4.7114 | 4.6595 | 4.6198 | 4.4263 | 4.1676 | 4.0259 | 3.9057 | 3.8017 | 3.6111 | 3.341 | 2.7703 | 1.9298 | 1.6176 | 1.4925 | 4.2767 | 4.2103 | 4.1597 | 3.9542 | 3.6748 | 3.5144 | 3.3821 | 3.2654 | 3.0634 | 2.7732 | 2.1169 | 1.0639 | 0.63349 | 0.50237
| GOURDIE | SP |  |  | 4.5677 | 4.5131 | 4.469 | 4.2468 | 3.9291 | 3.7525 | 3.6086 | 3.4784 | 3.2455 | 2.9347 | 2.3008 | 1.4269 | 0.92581 | 0.72916 | 4.7212 | 4.6739 | 4.637 | 4.4468 | 4.1857 | 4.0423 | 3.9217 | 3.8122 | 3.625 | 3.3774 | 2.8996 | 2.1716 | 1.7305 | 1.4864 | 4.2907 | 4.2308 | 4.1845 | 3.9847 | 3.6999 | 3.535 | 3.3996 | 3.2731 | 3.0739 | 2.8125 | 2.2639 | 1.3476 | 0.8239 | 0.65348
BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | YES | 7.8145 | 7.8032 | 7.7891 | 7.7153 | 7.3114 | 6.8892 | 6.4902 | 6.0982 | 5.6178 | 5.4103 | 4.4369 | 4.1675 | 4.3728 | 4.2742 | 10.2646 | 10.1922 | 10.1125 | 10.0204 | 9.8315 | 9.6346 | 9.4331 | 9.1867 | 8.8953 | 8.6845 | 7.9872 | 7.7591 | 7.8314 | 7.5045 | 9.1127 | 9.0075 | 8.8891 | 8.7527 | 8.4465 | 8.1293 | 7.807 | 7.421 | 6.9621 | 6.6577 | 5.5925 | 5.2829 | 5.4881 | 5.3754
| GRANTOWN | CT |  |  | 7.8145 | 7.8032 | 7.7891 | 7.7724 | 7.5148 | 7.1567 | 6.725 | 6.309 | 5.9196 | 5.7531 | 4.9152 | 4.3629 | 4.4623 | 4.4755 | 10.281 | 10.2252 | 10.1533 | 10.047 | 9.8501 | 9.6716 | 9.4679 | 9.2563 | 9.0542 | 8.9038 | 8.2619 | 7.8555 | 7.8314 | 7.7583 | 9.1386 | 9.0583 | 8.9525 | 8.7951 | 8.4836 | 8.2009 | 7.8725 | 7.5362 | 7.2208 | 7.0046 | 6.0793 | 5.5051 | 5.5659 | 5.5609
| GRANTOWN | LW |  |  | 7.8156 | 7.8036 | 7.79 | 7.7153 | 7.3114 | 6.8892 | 6.4902 | 6.0982 | 5.6178 | 5.4103 | 4.4369 | 4.1675 | 4.3728 | 4.2936 | 10.2646 | 10.1922 | 10.1125 | 10.0204 | 9.8315 | 9.6346 | 9.4331 | 9.1867 | 8.8953 | 8.6845 | 7.9872 | 7.7591 | 7.8439 | 7.8129 | 9.1127 | 9.0075 | 8.8891 | 8.7527 | 8.4465 | 8.1293 | 7.807 | 7.421 | 6.9621 | 6.6577 | 5.5925 | 5.2829 | 5.4881 | 5.4149
| GRANTOWN | ST |  |  | 7.817 | 7.8089 | 7.7999 | 7.7914 | 7.7883 | 7.7864 | 7.7831 | 7.7794 | 7.7729 | 7.7195 | 7.1985 | 5.8927 | 5.573 | 5.4736 | 10.2985 | 10.2647 | 10.2275 | 10.182 | 10.1522 | 10.1221 | 10.0821 | 10.0394 | 9.9777 | 9.8833 | 9.5298 | 8.5554 | 8.2852 | 8.1633 | 9.1592 | 9.1134 | 9.0634 | 8.9987 | 8.9643 | 8.928 | 8.8788 | 8.8251 | 8.7423 | 8.6101 | 8.1148 | 6.8317 | 6.5512 | 6.479
| GRANTOWN | SP |  |  | 7.8204 | 7.8143 | 7.8071 | 7.8023 | 7.7984 | 7.7959 | 7.7929 | 7.7885 | 7.7809 | 7.7719 | 7.2232 | 5.8017 | 4.6303 | 4.2742 | 10.3191 | 10.2973 | 10.2705 | 10.2488 | 10.213 | 10.179 | 10.1418 | 10.0932 | 10.0225 | 9.9378 | 9.5924 | 8.693 | 7.8587 | 7.5045 | 9.1959 | 9.1709 | 9.1397 | 9.1155 | 9.0692 | 9.0239 | 8.9762 | 8.9111 | 8.8134 | 8.6942 | 8.1833 | 6.8792 | 5.7598 | 5.3754
WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | 16.106 | 15.3534 | 15.0742 | 14.7902 | 13.0078 | 11.0004 | 8.7657 | 6.6165 | 5.8137 | 4.939 | 1.9649 | -2.0941 | -3.1573 | -4.2615 | 17.7081 | 17.372 | 17.1163 | 16.8114 | 15.9736 | 14.9741 | 14.0587 | 13.1406 | 12.6558 | 12.0847 | 10.1307 | 7.2114 | 5.5867 | 3.753 | 15.6383 | 14.9692 | 14.5948 | 14.1665 | 12.5762 | 10.7921 | 8.835 | 6.9929 | 6.2349 | 5.387 | 2.5093 | -1.3588 | -2.1876 | -2.8901
| GREYFRIARS | CT |  |  | 16.2251 | 15.802 | 15.6568 | 15.3184 | 13.676 | 11.574 | 10.4119 | 9.5516 | 8.5631 | 7.3848 | 3.9105 | -1.2334 | -3.0931 | -4.2615 | 17.7081 | 17.3957 | 17.144 | 16.8345 | 15.9736 | 14.9741 | 14.2889 | 13.7925 | 13.2313 | 12.5589 | 10.5064 | 7.2114 | 5.5867 | 3.753 | 15.651 | 15.1885 | 14.897 | 14.5563 | 13.0407 | 11.1676 | 10.083 | 9.2961 | 8.4025 | 7.3302 | 4.1612 | -0.47618 | -1.989 | -2.8804
| GREYFRIARS | LW |  |  | 16.106 | 15.3534 | 15.0742 | 14.7902 | 13.0078 | 11.0004 | 8.7657 | 6.6165 | 5.8137 | 4.939 | 1.9649 | -2.0941 | -3.1573 | -4.0966 | 17.7543 | 17.372 | 17.1163 | 16.8114 | 16.0009 | 15.0822 | 14.0587 | 13.1406 | 12.6558 | 12.0847 | 10.1307 | 7.4799 | 6.9756 | 6.5433 | 15.6383 | 14.9692 | 14.5948 | 14.1665 | 12.5762 | 10.7921 | 8.835 | 6.9929 | 6.2349 | 5.387 | 2.5093 | -1.3588 | -2.1876 | -2.8901
| GREYFRIARS | ST |  |  | 16.5685 | 16.4774 | 16.3836 | 16.2768 | 16.1285 | 15.9476 | 15.7966 | 15.719 | 15.6291 | 15.3204 | 14.1722 | 10.515 | 7.8734 | 6.0246 | 18.0837 | 17.971 | 17.8463 | 17.6859 | 17.525 | 17.3608 | 17.19 | 17.0476 | 16.8978 | 16.6425 | 15.6807 | 12.8304 | 10.579 | 8.4461 | 16.2639 | 16.1173 | 15.9561 | 15.745 | 15.5279 | 15.3212 | 15.1222 | 14.9867 | 14.8726 | 14.5812 | 13.5026 | 10.1185 | 7.7681 | 6.2337
| GREYFRIARS | SP |  |  | 16.6033 | 16.5735 | 16.5432 | 16.5075 | 16.4041 | 16.2643 | 16.1358 | 15.9712 | 15.7652 | 15.439 | 14.3213 | 11.2885 | 8.8852 | 7.9609 | 18.1289 | 18.0488 | 17.9452 | 17.8265 | 17.6657 | 17.4795 | 17.298 | 17.1253 | 16.9156 | 16.6378 | 15.6525 | 12.8614 | 9.5539 | 5.8142 | 16.369 | 16.2927 | 16.1858 | 16.0654 | 15.8564 | 15.6121 | 15.4033 | 15.2194 | 15.004 | 14.7043 | 13.687 | 10.8934 | 8.6685 | 7.8889
GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309623 | YES | 23.2799 | 23.2798 | 23.2796 | 23.2792 | 23.2792 | 23.2792 | 23.2792 | 23.2793 | 23.2793 | 23.2796 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.0799 | 22.0799 | 22.0797 | 22.0797 | 22.0797 | 22.0797 | 22.0797 | 22.0798 | 22.0798 | 22.08 | 22.08 | 22.08 | 22.08 | 22.0799 | 22.0798 | 22.0797 | 22.0793 | 22.0793 | 22.0793 | 22.0793 | 22.0793 | 22.0794 | 22.0796 | 22.08 | 22.08 | 22.08 | 22.08
| GRUDIE BRIDGE | CT |  |  | 23.2799 | 23.2798 | 23.2796 | 23.2792 | 23.2792 | 23.2792 | 23.2792 | 23.2793 | 23.2793 | 23.2796 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.0799 | 22.0799 | 22.0797 | 22.0797 | 22.0797 | 22.0797 | 22.0797 | 22.0798 | 22.0798 | 22.08 | 22.08 | 22.08 | 22.08 | 22.0799 | 22.0798 | 22.0797 | 22.0793 | 22.0793 | 22.0793 | 22.0793 | 22.0793 | 22.0794 | 22.0796 | 22.08 | 22.08 | 22.08 | 22.08
| GRUDIE BRIDGE | LW |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| GRUDIE BRIDGE | ST |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| GRUDIE BRIDGE | SP |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | 4.019 | 4.0174 | 4.009 | 3.997 | 3.968 | 3.9391 | 3.9106 | 3.8746 | 3.8304 | 3.817 | 3.7738 | 3.7645 | 3.788 | 3.7675 | 3.8776 | 3.8752 | 3.8721 | 3.8671 | 3.8606 | 3.8537 | 3.8384 | 3.8145 | 3.7882 | 3.7741 | 3.6901 | 3.6769 | 3.6838 | 3.6712 | 3.7903 | 3.7889 | 3.7815 | 3.7708 | 3.7453 | 3.7199 | 3.695 | 3.67 | 3.6403 | 3.6238 | 3.5577 | 3.5239 | 3.5439 | 3.5308
| GUTCHER | CT |  |  | 4.0253 | 4.0246 | 4.0158 | 3.9974 | 3.9703 | 3.9453 | 3.9174 | 3.8838 | 3.8449 | 3.833 | 3.7987 | 3.7834 | 3.8164 | 3.8261 | 3.8776 | 3.8752 | 3.8721 | 3.8671 | 3.8606 | 3.8537 | 3.8436 | 3.8214 | 3.8009 | 3.7879 | 3.7225 | 3.6856 | 3.6921 | 3.6917 | 3.7958 | 3.7951 | 3.7874 | 3.7711 | 3.7473 | 3.7252 | 3.7007 | 3.6711 | 3.6449 | 3.6379 | 3.5966 | 3.5601 | 3.5821 | 3.5877
| GUTCHER | LW |  |  | 4.019 | 4.0174 | 4.009 | 3.997 | 3.968 | 3.9391 | 3.9106 | 3.8746 | 3.8304 | 3.817 | 3.7738 | 3.7645 | 3.788 | 3.7713 | 3.8793 | 3.8777 | 3.8754 | 3.8714 | 3.8651 | 3.8578 | 3.8384 | 3.8145 | 3.7882 | 3.7741 | 3.6901 | 3.6769 | 3.6838 | 3.679 | 3.7903 | 3.7889 | 3.7815 | 3.7708 | 3.7453 | 3.7199 | 3.695 | 3.67 | 3.6403 | 3.6238 | 3.5577 | 3.5239 | 3.5439 | 3.5308
| GUTCHER | ST |  |  | 4.0251 | 4.0242 | 4.0237 | 4.0202 | 4.0209 | 4.0214 | 4.0219 | 4.0226 | 4.02 | 4.014 | 3.9966 | 3.9638 | 3.9508 | 3.9443 | 3.8802 | 3.8794 | 3.8786 | 3.8769 | 3.8759 | 3.8749 | 3.8732 | 3.8717 | 3.8695 | 3.8658 | 3.8519 | 3.7444 | 3.7309 | 3.7253 | 3.7957 | 3.7949 | 3.7944 | 3.7913 | 3.7919 | 3.7923 | 3.7927 | 3.7932 | 3.7908 | 3.7854 | 3.7698 | 3.715 | 3.6855 | 3.6764
| GUTCHER | SP |  |  | 4.0279 | 4.0284 | 4.0299 | 4.0313 | 4.0271 | 4.0232 | 4.0188 | 4.0132 | 4.0061 | 3.9943 | 3.9553 | 3.8546 | 3.7966 | 3.7675 | 3.8803 | 3.8797 | 3.8794 | 3.8789 | 3.8786 | 3.8775 | 3.8768 | 3.8759 | 3.8738 | 3.8702 | 3.8504 | 3.7728 | 3.6865 | 3.6712 | 3.7982 | 3.7986 | 3.7999 | 3.8011 | 3.7973 | 3.7939 | 3.79 | 3.7851 | 3.7788 | 3.7683 | 3.736 | 3.6428 | 3.5665 | 3.5366
THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | 0.84112 | 0.75431 | 2.4386 | 2.3546 | 2.1864 | 2.0125 | 1.8243 | 1.626 | 1.3701 | 1.217 | 0.86489 | 0.74602 | 0.82129 | 0.69264 | 1.1522 | 1.0707 | 2.6439 | 2.5878 | 2.5045 | 2.4203 | 2.3249 | 2.2221 | 2.0891 | 1.9925 | 1.7861 | 1.7154 | 1.7327 | 1.6195 | 0.826 | 0.74644 | 2.305 | 2.2267 | 2.0786 | 1.9238 | 1.7543 | 1.5751 | 1.34 | 1.186 | 0.84054 | 0.72921 | 0.79512 | 0.68527
| HALKIRK | CT |  |  | 0.89515 | 0.8262 | 2.5245 | 2.448 | 2.2903 | 2.1424 | 1.9523 | 1.7416 | 1.5472 | 1.4474 | 1.0927 | 0.85969 | 0.8516 | 0.82994 | 1.1696 | 1.0941 | 2.6692 | 2.6124 | 2.5324 | 2.4587 | 2.3707 | 2.2692 | 2.1746 | 2.1151 | 1.8887 | 1.7528 | 1.7353 | 1.7022 | 0.87026 | 0.8057 | 2.3741 | 2.301 | 2.1607 | 2.0287 | 1.8643 | 1.6796 | 1.5087 | 1.4131 | 1.0504 | 0.83096 | 0.82361 | 0.80451
| HALKIRK | LW |  |  | 0.84112 | 0.75431 | 2.4386 | 2.3546 | 2.1864 | 2.0125 | 1.8243 | 1.626 | 1.3701 | 1.217 | 0.86489 | 0.74602 | 0.82129 | 0.79008 | 1.1522 | 1.0707 | 2.6439 | 2.5878 | 2.5045 | 2.4203 | 2.3249 | 2.2221 | 2.0891 | 1.9925 | 1.7861 | 1.7154 | 1.7438 | 1.7306 | 0.826 | 0.74644 | 2.305 | 2.2267 | 2.0786 | 1.9238 | 1.7543 | 1.5751 | 1.34 | 1.186 | 0.84054 | 0.72921 | 0.79512 | 0.76765
| HALKIRK | ST |  |  | 0.88829 | 0.81149 | 2.5279 | 2.4925 | 2.4666 | 2.4414 | 2.4016 | 2.3624 | 2.3077 | 2.2458 | 2.0269 | 1.503 | 1.3191 | 1.2289 | 1.1729 | 1.0979 | 2.6855 | 2.6535 | 2.6306 | 2.6104 | 2.5804 | 2.5515 | 2.5155 | 2.4802 | 2.3479 | 2.0218 | 1.9204 | 1.8574 | 0.86808 | 0.79889 | 2.3862 | 2.3528 | 2.3275 | 2.3025 | 2.2653 | 2.23 | 2.18 | 2.1223 | 1.9074 | 1.401 | 1.2351 | 1.155
| HALKIRK | SP |  |  | 0.89751 | 0.82568 | 2.5488 | 2.522 | 2.4693 | 2.4215 | 2.3605 | 2.2893 | 2.2188 | 2.1402 | 1.88 | 1.2452 | 0.84991 | 0.69264 | 1.1765 | 1.1037 | 2.6942 | 2.6669 | 2.6347 | 2.6065 | 2.5704 | 2.5281 | 2.4863 | 2.4474 | 2.3214 | 1.9667 | 1.7327 | 1.6195 | 0.87574 | 0.81094 | 2.4042 | 2.3789 | 2.3315 | 2.2876 | 2.2338 | 2.1702 | 2.1066 | 2.0366 | 1.8026 | 1.194 | 0.82473 | 0.68527
ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | YES | 9.0241 | 8.7433 | 8.5335 | 8.2497 | 7.5398 | 6.7776 | 6.0697 | 5.2808 | 4.6562 | 4.0922 | 2.2829 | -0.11919 | -1.2336 | -1.6464 | 5.6738 | 5.5268 | 5.3969 | 5.1234 | 4.785 | 4.4024 | 4.0888 | 3.6961 | 3.3246 | 2.9271 | 1.7188 | 0.50095 | 0.3095 | 0.22273 | 10.4681 | 10.3053 | 10.1566 | 9.8881 | 9.4895 | 8.8181 | 8.194 | 7.4818 | 6.902 | 6.3647 | 4.6141 | 2.478 | 1.532 | 1.1869
| HARBOUR | CT |  |  | 9.059 | 8.8275 | 8.6578 | 8.4039 | 7.7073 | 6.952 | 6.4149 | 5.8756 | 5.2962 | 4.6484 | 2.6 | -0.11919 | -1.2336 | -1.6464 | 5.6738 | 5.5268 | 5.3969 | 5.1234 | 4.785 | 4.4024 | 4.1194 | 3.8262 | 3.4788 | 3.1052 | 2.0321 | 0.81396 | 0.50346 | 0.37018 | 10.4681 | 10.3053 | 10.1566 | 9.8881 | 9.574 | 8.949 | 8.4738 | 7.9842 | 7.4603 | 6.8676 | 4.9553 | 2.478 | 1.532 | 1.1869
| HARBOUR | LW |  |  | 9.0241 | 8.7433 | 8.5335 | 8.2497 | 7.5398 | 6.7776 | 6.0697 | 5.2808 | 4.6562 | 4.0922 | 2.2829 | 0.23333 | -0.55609 | -0.89323 | 5.6871 | 5.5429 | 5.4259 | 5.1685 | 4.8314 | 4.4521 | 4.0888 | 3.6961 | 3.3246 | 2.9271 | 1.7188 | 0.50095 | 0.3095 | 0.22273 | 10.4814 | 10.3206 | 10.184 | 9.9266 | 9.4895 | 8.8181 | 8.194 | 7.4818 | 6.902 | 6.3647 | 4.6141 | 2.7056 | 2.0466 | 1.7674
| HARBOUR | ST |  |  | 9.1471 | 9.0049 | 8.858 | 8.6162 | 8.3609 | 8.1015 | 7.926 | 7.7542 | 7.5977 | 7.3815 | 6.6596 | 4.7921 | 3.7508 | 3.111 | 5.7227 | 5.608 | 5.5126 | 5.3107 | 5.0805 | 4.829 | 4.6591 | 4.4803 | 4.2853 | 4.0903 | 3.4074 | 1.8506 | 1.1461 | 0.98601 | 10.5175 | 10.3868 | 10.2735 | 10.0665 | 9.8347 | 9.5898 | 9.4185 | 9.2523 | 9.0778 | 8.9002 | 8.2845 | 6.3368 | 5.3648 | 5.0915
| HARBOUR | SP |  |  | 9.1494 | 9.0127 | 8.8907 | 8.6831 | 8.4506 | 8.1712 | 7.968 | 7.7715 | 7.5728 | 7.3388 | 6.6871 | 5.3292 | 4.2738 | 4.0458 | 5.7247 | 5.6149 | 5.5227 | 5.3288 | 5.1062 | 4.8638 | 4.7061 | 4.5585 | 4.399 | 4.2372 | 3.7593 | 2.7047 | 1.6251 | 1.3037 | 10.5195 | 10.3942 | 10.2843 | 10.0865 | 9.8632 | 9.628 | 9.4701 | 9.3197 | 9.1677 | 9.0199 | 8.5907 | 7.3153 | 6.015 | 5.691
STORNOWAY | HARRIS GRID | MINIMUM HEADROOM | NG 13495 94249 | YES | 35.0415 | 34.9958 | 34.9656 | 34.9399 | 34.905 | 34.8747 | 34.8491 | 34.8214 | 34.7894 | 34.7761 | 34.7297 | 34.712 | 34.7159 | 34.7106 | 32.488 | 32.4423 | 32.4109 | 32.3854 | 32.3631 | 32.3438 | 32.3288 | 32.3133 | 32.2931 | 32.2802 | 32.2449 | 32.2183 | 32.2187 | 32.2158 | 32.4112 | 32.3671 | 32.3385 | 32.3143 | 32.2822 | 32.2544 | 32.2309 | 32.2052 | 32.1756 | 32.1629 | 32.1183 | 32.1038 | 32.1078 | 32.1027
| HARRIS GRID | CT |  |  | 35.0561 | 35.0036 | 34.9725 | 34.9477 | 34.9129 | 34.8817 | 34.8533 | 34.8245 | 34.7958 | 34.7827 | 34.7427 | 34.7153 | 34.7213 | 34.7171 | 32.493 | 32.4425 | 32.4109 | 32.3854 | 32.3631 | 32.3438 | 32.3288 | 32.3133 | 32.295 | 32.2829 | 32.2542 | 32.2265 | 32.2238 | 32.2209 | 32.424 | 32.3785 | 32.3483 | 32.3234 | 32.2887 | 32.2599 | 32.2339 | 32.2075 | 32.1812 | 32.1688 | 32.1304 | 32.1038 | 32.113 | 32.1128
| HARRIS GRID | LW |  |  | 35.0415 | 34.9958 | 34.9656 | 34.9399 | 34.905 | 34.8747 | 34.8491 | 34.8214 | 34.7894 | 34.7761 | 34.7297 | 34.712 | 34.7159 | 34.7106 | 32.488 | 32.4423 | 32.4121 | 32.3871 | 32.3655 | 32.3462 | 32.3315 | 32.3136 | 32.2931 | 32.2802 | 32.2449 | 32.2183 | 32.2187 | 32.2158 | 32.4112 | 32.3671 | 32.3385 | 32.3143 | 32.2822 | 32.2544 | 32.2309 | 32.2052 | 32.1756 | 32.1629 | 32.1183 | 32.1044 | 32.1078 | 32.1027
| HARRIS GRID | ST |  |  | 35.0528 | 35.0002 | 34.9733 | 34.9554 | 34.9448 | 34.937 | 34.9291 | 34.9202 | 34.9103 | 34.9002 | 34.8695 | 34.7915 | 34.7438 | 34.7238 | 32.4929 | 32.4452 | 32.4186 | 32.3985 | 32.386 | 32.377 | 32.3678 | 32.358 | 32.3479 | 32.341 | 32.3218 | 32.2675 | 32.2318 | 32.2174 | 32.4213 | 32.3713 | 32.3457 | 32.3286 | 32.3183 | 32.3109 | 32.3033 | 32.2959 | 32.2868 | 32.2789 | 32.2551 | 32.1886 | 32.143 | 32.1242
| HARRIS GRID | SP |  |  | 35.0523 | 34.999 | 34.9725 | 34.9541 | 34.9328 | 34.9163 | 34.8991 | 34.8805 | 34.8619 | 34.8408 | 34.8108 | 34.7546 | 34.7252 | 34.7166 | 32.4928 | 32.4449 | 32.4193 | 32.3995 | 32.3852 | 32.3759 | 32.3663 | 32.3563 | 32.3456 | 32.3354 | 32.3209 | 32.2895 | 32.2558 | 32.2426 | 32.4209 | 32.3703 | 32.3451 | 32.3277 | 32.3081 | 32.2931 | 32.2774 | 32.2604 | 32.2435 | 32.2245 | 32.1971 | 32.1452 | 32.1155 | 32.1068
THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | 2.9502 | 2.9572 | 2.8922 | 2.7983 | 2.5305 | 2.2653 | 2.0029 | 1.7079 | 1.3333 | 1.0774 | 0.38872 | 0.19059 | 0.1641 | -0.010257 | 3.4456 | 3.434 | 3.4189 | 3.3739 | 3.252 | 3.1288 | 3.0048 | 2.8566 | 2.6711 | 2.5216 | 2.0704 | 1.9659 | 1.9304 | 1.8155 | 2.891 | 2.8945 | 2.8349 | 2.7484 | 2.5076 | 2.2686 | 2.0309 | 1.76 | 1.4172 | 1.1748 | 0.52506 | 0.34334 | 0.32357 | 0.16783
| HASTIGROW | CT |  |  | 3.0945 | 3.1212 | 3.0882 | 2.9847 | 2.7344 | 2.5121 | 2.2259 | 1.9243 | 1.6291 | 1.4579 | 0.7472 | 0.37678 | 0.29696 | 0.23424 | 3.4456 | 3.434 | 3.4189 | 3.384 | 3.3132 | 3.2056 | 3.0762 | 2.9381 | 2.7989 | 2.7028 | 2.231 | 2.0312 | 1.985 | 1.9352 | 3.0197 | 3.0459 | 3.0161 | 2.9214 | 2.6871 | 2.4793 | 2.2225 | 1.9513 | 1.6847 | 1.5246 | 0.85766 | 0.51071 | 0.44039 | 0.38516
| HASTIGROW | LW |  |  | 2.9502 | 2.9572 | 2.8922 | 2.7983 | 2.5305 | 2.2653 | 2.0029 | 1.7079 | 1.3333 | 1.0774 | 0.38872 | 0.19059 | 0.28601 | 0.23805 | 3.4549 | 3.4398 | 3.4236 | 3.3739 | 3.252 | 3.1288 | 3.0048 | 2.8566 | 2.6711 | 2.5216 | 2.0704 | 1.9659 | 1.9966 | 1.9786 | 2.891 | 2.8945 | 2.8349 | 2.7484 | 2.5076 | 2.2686 | 2.0309 | 1.76 | 1.4172 | 1.1748 | 0.52506 | 0.34334 | 0.42679 | 0.3845
| HASTIGROW | ST |  |  | 3.0635 | 3.0429 | 3.02 | 3.0043 | 2.9772 | 2.9351 | 2.885 | 2.8415 | 2.7771 | 2.6721 | 2.2745 | 1.2915 | 0.97393 | 0.79493 | 3.4624 | 3.4582 | 3.4523 | 3.4448 | 3.4334 | 3.4232 | 3.4022 | 3.3751 | 3.3387 | 3.2808 | 3.0556 | 2.3946 | 2.234 | 2.1323 | 2.9916 | 2.9727 | 2.9513 | 2.9358 | 2.9111 | 2.8733 | 2.8272 | 2.7879 | 2.7287 | 2.6315 | 2.2676 | 1.3762 | 1.0755 | 0.90753
| HASTIGROW | SP |  |  | 3.0618 | 3.0403 | 3.0231 | 3 | 2.8888 | 2.7853 | 2.6652 | 2.532 | 2.3911 | 2.2003 | 1.7657 | 0.69735 | 0.1641 | -0.010257 | 3.4626 | 3.4596 | 3.4555 | 3.4499 | 3.4258 | 3.3806 | 3.3261 | 3.264 | 3.1957 | 3.1078 | 2.8969 | 2.2981 | 1.9304 | 1.8155 | 2.9899 | 2.9706 | 2.9547 | 2.9329 | 2.8339 | 2.7415 | 2.6339 | 2.5138 | 2.3856 | 2.214 | 1.8197 | 0.82514 | 0.32357 | 0.16783
STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | 4.6344 | 4.5353 | 4.4148 | 4.2735 | 4.0266 | 3.7648 | 3.479 | 3.1812 | 2.7535 | 2.365 | 1.5136 | 0.89473 | 0.58296 | 0.46626 | 5.846 | 5.7647 | 5.6699 | 5.5499 | 5.3978 | 5.2428 | 5.0606 | 4.8728 | 4.6169 | 4.3485 | 3.789 | 3.4668 | 3.3057 | 3.1801 | 5.4518 | 5.3614 | 5.2508 | 5.1216 | 4.8972 | 4.6615 | 4.3982 | 4.1262 | 3.7369 | 3.3897 | 2.6169 | 2.0355 | 1.7608 | 1.6589
| HATTON | CT |  |  | 4.6553 | 4.5659 | 4.4447 | 4.2932 | 4.0625 | 3.8423 | 3.5535 | 3.233 | 2.9135 | 2.5872 | 1.6229 | 0.89473 | 0.58296 | 0.46626 | 5.8487 | 5.77 | 5.6699 | 5.5499 | 5.3978 | 5.2565 | 5.0868 | 4.9032 | 4.7198 | 4.5043 | 3.8615 | 3.4668 | 3.3057 | 3.1801 | 5.4711 | 5.3899 | 5.2792 | 5.1415 | 4.9317 | 4.7322 | 4.4654 | 4.1757 | 3.8894 | 3.5902 | 2.7119 | 2.0355 | 1.7608 | 1.6589
| HATTON | LW |  |  | 4.6344 | 4.5353 | 4.4148 | 4.2735 | 4.0266 | 3.7648 | 3.479 | 3.1812 | 2.7535 | 2.365 | 1.5136 | 1.0005 | 0.82109 | 0.73196 | 5.846 | 5.7647 | 5.67 | 5.5617 | 5.4041 | 5.2428 | 5.0606 | 4.8728 | 4.6169 | 4.3485 | 3.789 | 3.5184 | 3.4509 | 3.4171 | 5.4518 | 5.3614 | 5.2508 | 5.1216 | 4.8972 | 4.6615 | 4.3982 | 4.1262 | 3.7369 | 3.3897 | 2.6169 | 2.1368 | 1.9686 | 1.8849
| HATTON | ST |  |  | 4.6747 | 4.5937 | 4.5015 | 4.4047 | 4.2997 | 4.1934 | 4.0994 | 4.0014 | 3.8773 | 3.7156 | 3.2329 | 2.2606 | 1.9614 | 1.7848 | 5.8665 | 5.7977 | 5.7184 | 5.6342 | 5.5441 | 5.4561 | 5.3756 | 5.2923 | 5.1957 | 5.0759 | 4.7288 | 4.0145 | 3.8266 | 3.673 | 5.4889 | 5.4154 | 5.3312 | 5.2422 | 5.1484 | 5.0543 | 4.9693 | 4.8809 | 4.7707 | 4.6266 | 4.193 | 3.3233 | 3.0444 | 2.8792
| HATTON | SP |  |  | 4.6864 | 4.6139 | 4.5292 | 4.4419 | 4.3194 | 4.2035 | 4.0943 | 3.974 | 3.8351 | 3.6732 | 3.241 | 2.2474 | 1.7226 | 1.5768 | 5.8719 | 5.8081 | 5.7323 | 5.6543 | 5.5587 | 5.4694 | 5.3838 | 5.2903 | 5.1848 | 5.0665 | 4.77 | 4.0814 | 3.6488 | 3.3947 | 5.4995 | 5.434 | 5.3566 | 5.2767 | 5.1678 | 5.0651 | 4.9655 | 4.8556 | 4.7311 | 4.5866 | 4.1932 | 3.2999 | 2.8238 | 2.6878
PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | 16.4793 | 15.9109 | 15.5758 | 15.3403 | 14.5345 | 13.6941 | 12.7981 | 11.7187 | 11.0305 | 10.2882 | 7.7533 | 4.314 | 2.9284 | 2.0158 | 17.3063 | 17.0182 | 16.8313 | 16.6843 | 16.2946 | 15.883 | 15.4429 | 14.908 | 14.5188 | 14.0486 | 12.3842 | 10.2245 | 9.112 | 8.0363 | 16.2027 | 15.7277 | 15.4474 | 15.2375 | 14.5195 | 13.7644 | 12.933 | 11.9442 | 11.3266 | 10.6344 | 8.2447 | 5.0704 | 4.0088 | 3.3047
| HAUDAGAIN | CT |  |  | 16.5199 | 16.0836 | 15.8589 | 15.6954 | 14.8675 | 13.9527 | 13.3296 | 12.7014 | 12.0149 | 11.188 | 8.6221 | 4.5852 | 2.9284 | 2.0158 | 17.3063 | 17.065 | 16.9123 | 16.7774 | 16.3599 | 15.8995 | 15.562 | 15.1905 | 14.787 | 14.2907 | 12.7406 | 10.2523 | 9.112 | 8.0363 | 16.2337 | 15.874 | 15.6886 | 15.5364 | 14.7939 | 13.97 | 13.4021 | 12.8242 | 12.1927 | 11.4275 | 9.0595 | 5.3887 | 4.0088 | 3.3047
| HAUDAGAIN | LW |  |  | 16.4793 | 15.9109 | 15.5758 | 15.3403 | 14.5345 | 13.6941 | 12.7981 | 11.7187 | 11.0305 | 10.2882 | 7.7533 | 4.314 | 3.1095 | 2.334 | 17.3065 | 17.0182 | 16.8313 | 16.6843 | 16.2946 | 15.883 | 15.4429 | 14.908 | 14.5188 | 14.0486 | 12.3842 | 10.2245 | 9.6777 | 9.2999 | 16.2027 | 15.7277 | 15.4474 | 15.2375 | 14.5195 | 13.7644 | 12.933 | 11.9442 | 11.3266 | 10.6344 | 8.2447 | 5.0704 | 4.0991 | 3.515
| HAUDAGAIN | ST |  |  | 16.7852 | 16.5259 | 16.2946 | 16.097 | 15.9148 | 15.7639 | 15.5911 | 15.41 | 15.2879 | 15.0343 | 14.0618 | 11.0219 | 8.9412 | 7.722 | 17.4433 | 17.2914 | 17.1547 | 17.0368 | 16.9279 | 16.8299 | 16.715 | 16.5932 | 16.4711 | 16.2676 | 15.4764 | 13.1491 | 11.5236 | 10.3216 | 16.4764 | 16.2779 | 16.094 | 15.9247 | 15.7635 | 15.6254 | 15.4664 | 15.2994 | 15.1812 | 14.9395 | 14.014 | 11.1686 | 9.3359 | 8.3596
| HAUDAGAIN | SP |  |  | 16.8555 | 16.6458 | 16.4565 | 16.3163 | 16.1504 | 15.9736 | 15.8101 | 15.6477 | 15.4688 | 15.2149 | 14.3744 | 12.0057 | 9.7672 | 8.9083 | 17.4725 | 17.3428 | 17.2241 | 17.1317 | 17.0298 | 16.9214 | 16.8121 | 16.6997 | 16.5675 | 16.3704 | 15.6858 | 13.6977 | 11.2788 | 9.1139 | 16.538 | 16.3838 | 16.2375 | 16.1204 | 15.9754 | 15.8171 | 15.6696 | 15.5223 | 15.356 | 15.1203 | 14.3432 | 12.1504 | 10.1071 | 9.416
WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | 16.1591 | 15.667 | 15.3412 | 15.0186 | 14.0326 | 12.9405 | 11.8001 | 10.6512 | 10.05 | 9.453 | 7.3004 | 4.0733 | 2.0323 | 0.78028 | 16.772 | 16.5508 | 16.3906 | 16.2246 | 15.7779 | 15.2895 | 14.7687 | 14.2562 | 13.9485 | 13.5846 | 12.2012 | 10.0045 | 8.6193 | 7.2537 | 15.8081 | 15.4097 | 15.1828 | 14.9857 | 14.1341 | 13.2413 | 12.3331 | 11.324 | 10.7921 | 10.27 | 8.4448 | 5.6627 | 3.9695 | 3.0505
| HAYTON | CT |  |  | 16.1883 | 15.83 | 15.5977 | 15.3437 | 14.3522 | 13.2623 | 12.5281 | 11.9415 | 11.3038 | 10.5294 | 8.0606 | 4.0733 | 2.0323 | 0.78028 | 16.772 | 16.5876 | 16.4518 | 16.2942 | 15.8252 | 15.306 | 14.9218 | 14.5949 | 14.2427 | 13.803 | 12.3753 | 10.0045 | 8.6193 | 7.2537 | 15.8701 | 15.6091 | 15.4866 | 15.3896 | 14.5711 | 13.6773 | 13.0781 | 12.5558 | 11.9831 | 11.2965 | 9.1325 | 5.6627 | 3.9695 | 3.0505
| HAYTON | LW |  |  | 16.1591 | 15.667 | 15.3412 | 15.0186 | 14.0326 | 12.9405 | 11.8001 | 10.6512 | 10.05 | 9.453 | 7.3004 | 4.1705 | 2.6577 | 1.5783 | 16.7793 | 16.5508 | 16.3906 | 16.2246 | 15.7779 | 15.2895 | 14.7687 | 14.2562 | 13.9485 | 13.5846 | 12.2012 | 10.3427 | 9.644 | 9.1094 | 15.8081 | 15.4097 | 15.1828 | 14.9857 | 14.1341 | 13.2413 | 12.3331 | 11.324 | 10.7921 | 10.27 | 8.4448 | 5.8053 | 4.6127 | 3.8159
| HAYTON | ST |  |  | 16.5437 | 16.4311 | 16.3253 | 16.1793 | 16.026 | 15.8642 | 15.7087 | 15.5545 | 15.4696 | 15.2668 | 14.501 | 11.9421 | 9.8615 | 8.291 | 16.9474 | 16.8794 | 16.8157 | 16.7308 | 16.6416 | 16.5447 | 16.4475 | 16.3479 | 16.2741 | 16.1395 | 15.5803 | 13.6644 | 12.0931 | 10.6043 | 16.1283 | 16.0504 | 15.979 | 15.8818 | 15.777 | 15.6735 | 15.5795 | 15.483 | 15.464 | 15.3523 | 14.9704 | 12.8773 | 11.1306 | 9.9034
| HAYTON | SP |  |  | 16.608 | 16.5374 | 16.4665 | 16.3872 | 16.2449 | 16.0715 | 15.925 | 15.7857 | 15.6272 | 15.4157 | 14.6596 | 12.5834 | 10.5276 | 9.4508 | 16.9727 | 16.9218 | 16.871 | 16.8133 | 16.7261 | 16.6205 | 16.5228 | 16.4241 | 16.3098 | 16.1578 | 15.5938 | 13.823 | 11.476 | 8.9633 | 16.1959 | 16.1592 | 16.1217 | 16.0825 | 15.9786 | 15.8532 | 15.7577 | 15.6662 | 15.5751 | 15.4414 | 14.9725 | 13.4995 | 11.7157 | 10.8968
BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | 2.8616 | 2.861 | 2.8526 | 2.8419 | 2.7722 | 2.7108 | 2.6477 | 2.5815 | 2.4738 | 2.4278 | 2.2699 | 2.1612 | 2.1848 | 2.1336 | 2.6989 | 2.6965 | 2.6906 | 2.6833 | 2.6429 | 2.6116 | 2.5628 | 2.509 | 2.4545 | 2.4094 | 2.2515 | 2.1674 | 2.1719 | 2.1325 | 3.2195 | 3.2173 | 3.2144 | 3.2038 | 3.1802 | 3.1406 | 3.0711 | 2.9717 | 2.8611 | 2.7879 | 2.5513 | 2.4328 | 2.4618 | 2.4074
| HELMSDALE | CT |  |  | 2.882 | 2.8877 | 2.8865 | 2.8797 | 2.8198 | 2.7702 | 2.6799 | 2.5846 | 2.5009 | 2.4658 | 2.3727 | 2.1988 | 2.1848 | 2.173 | 2.7053 | 2.7048 | 2.7002 | 2.6852 | 2.6434 | 2.6117 | 2.5628 | 2.509 | 2.4651 | 2.4302 | 2.3149 | 2.1828 | 2.1719 | 2.1599 | 3.2195 | 3.2173 | 3.2144 | 3.2038 | 3.1802 | 3.1637 | 3.0711 | 2.9717 | 2.8873 | 2.8315 | 2.6585 | 2.471 | 2.4618 | 2.4523
| HELMSDALE | LW |  |  | 2.8616 | 2.861 | 2.8526 | 2.8419 | 2.7722 | 2.7108 | 2.6477 | 2.5815 | 2.4738 | 2.4278 | 2.2699 | 2.1612 | 2.1947 | 2.1838 | 2.6989 | 2.6965 | 2.6906 | 2.6833 | 2.6429 | 2.6116 | 2.5742 | 2.5188 | 2.4545 | 2.4094 | 2.2515 | 2.1674 | 2.1822 | 2.1771 | 3.2211 | 3.2196 | 3.2178 | 3.2157 | 3.189 | 3.1406 | 3.0738 | 2.9812 | 2.8611 | 2.7879 | 2.5513 | 2.4328 | 2.4679 | 2.4561
| HELMSDALE | ST |  |  | 2.8713 | 2.8682 | 2.8654 | 2.8642 | 2.8526 | 2.8496 | 2.8414 | 2.8344 | 2.8206 | 2.7996 | 2.7314 | 2.5263 | 2.39 | 2.352 | 2.7042 | 2.7021 | 2.6997 | 2.695 | 2.6771 | 2.6697 | 2.6552 | 2.6377 | 2.6225 | 2.6017 | 2.5264 | 2.3541 | 2.2606 | 2.2378 | 3.2224 | 3.2216 | 3.2205 | 3.2184 | 3.1982 | 3.1917 | 3.1741 | 3.1599 | 3.1522 | 3.1433 | 3.0573 | 2.8108 | 2.6709 | 2.6357
| HELMSDALE | SP |  |  | 2.8779 | 2.8778 | 2.8787 | 2.8799 | 2.8562 | 2.8426 | 2.8233 | 2.8047 | 2.7883 | 2.7614 | 2.6484 | 2.4322 | 2.2281 | 2.1336 | 2.7066 | 2.7057 | 2.7046 | 2.7036 | 2.684 | 2.6743 | 2.6571 | 2.6407 | 2.6234 | 2.6024 | 2.5252 | 2.3645 | 2.2017 | 2.1325 | 3.2226 | 3.222 | 3.2211 | 3.2202 | 3.2011 | 3.1952 | 3.1784 | 3.1661 | 3.1585 | 3.1507 | 3.0228 | 2.7479 | 2.5043 | 2.4074
INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | 11.5962 | 11.3966 | 11.2091 | 10.9989 | 10.1971 | 9.3346 | 8.3325 | 7.2794 | 6.2603 | 5.3124 | 2.2399 | -2.7554 | -5.1569 | -6.0934 | 14.1876 | 14.0645 | 13.9201 | 13.718 | 13.3188 | 12.8874 | 12.4037 | 11.8378 | 11.2695 | 10.651 | 8.6227 | 5.9656 | 4.6546 | 3.6212 | 11.8402 | 11.6484 | 11.459 | 11.2315 | 10.5626 | 9.8273 | 8.9487 | 8.0313 | 7.1278 | 6.2165 | 3.2485 | -1.0501 | -3.0186 | -3.7577
| HILTON | CT |  |  | 11.6349 | 11.4784 | 11.3173 | 11.1255 | 10.3671 | 9.5475 | 8.7146 | 7.9076 | 7.0559 | 5.9903 | 2.384 | -2.7554 | -5.1569 | -6.0934 | 14.1876 | 14.0645 | 13.9201 | 13.718 | 13.3188 | 12.8874 | 12.4369 | 12.0074 | 11.5578 | 10.9522 | 8.7873 | 5.9656 | 4.6546 | 3.6212 | 11.8488 | 11.6878 | 11.5082 | 11.2695 | 10.6205 | 9.9199 | 9.2035 | 8.5172 | 7.7966 | 6.8563 | 3.5514 | -1.0501 | -3.0186 | -3.7577
| HILTON | LW |  |  | 11.5962 | 11.3966 | 11.2091 | 10.9989 | 10.1971 | 9.3346 | 8.3325 | 7.2794 | 6.2603 | 5.3124 | 2.2399 | -1.4059 | -3.3201 | -4.1255 | 14.2064 | 14.0767 | 13.9433 | 13.7746 | 13.3867 | 12.9486 | 12.4037 | 11.8378 | 11.2695 | 10.651 | 8.6227 | 6.6177 | 5.9099 | 5.5894 | 11.8402 | 11.6484 | 11.459 | 11.2315 | 10.5626 | 9.8273 | 8.9487 | 8.0313 | 7.1278 | 6.2165 | 3.2485 | -0.058736 | -1.595 | -2.2201
| HILTON | ST |  |  | 11.832 | 11.7732 | 11.7093 | 11.6309 | 11.578 | 11.513 | 11.405 | 11.2944 | 11.2044 | 10.9586 | 9.9942 | 6.6484 | 4.8727 | 3.739 | 14.3249 | 14.2758 | 14.2201 | 14.1405 | 14.0728 | 13.994 | 13.8839 | 13.7668 | 13.6459 | 13.4242 | 12.5582 | 9.9029 | 8.5527 | 7.4315 | 12.045 | 11.9859 | 11.9197 | 11.8287 | 11.7593 | 11.6767 | 11.5555 | 11.43 | 11.3121 | 11.0435 | 9.9946 | 6.619 | 5.0685 | 4.147
| HILTON | SP |  |  | 11.8735 | 11.8461 | 11.8107 | 11.7663 | 11.6502 | 11.5184 | 11.3516 | 11.1712 | 10.9603 | 10.6669 | 9.8069 | 7.5293 | 5.5089 | 5.0672 | 14.3313 | 14.2952 | 14.2493 | 14.1929 | 14.109 | 14.0101 | 13.8855 | 13.7462 | 13.5697 | 13.3486 | 12.6183 | 10.541 | 8.1514 | 6.2701 | 12.0699 | 12.036 | 11.992 | 11.9365 | 11.8273 | 11.7007 | 11.544 | 11.3715 | 11.1592 | 10.8838 | 10.0437 | 7.7069 | 5.6833 | 5.3033
ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | YES | 14.6319 | 14.4776 | 14.3836 | 14.2808 | 13.6054 | 12.8763 | 12.113 | 11.1545 | 10.3726 | 9.7069 | 7.6058 | 4.2102 | 2.7378 | 2.232 | 15.7497 | 15.6693 | 15.6101 | 15.5213 | 15.2242 | 14.8897 | 14.6028 | 14.1502 | 13.7341 | 13.3097 | 11.9566 | 10.0333 | 9.1257 | 8.3846 | 14.3895 | 14.2609 | 14.1797 | 14.0893 | 13.4946 | 12.852 | 12.1771 | 11.3107 | 10.5949 | 9.9726 | 8.007 | 4.9533 | 3.6574 | 3.2196
| HUME STREET | CT |  |  | 14.6319 | 14.5 | 14.4223 | 14.3392 | 13.6953 | 12.9578 | 12.3555 | 11.7154 | 11.0383 | 10.257 | 7.8763 | 4.2102 | 2.7378 | 2.232 | 15.7497 | 15.6693 | 15.6101 | 15.5213 | 15.2242 | 14.8897 | 14.6028 | 14.2693 | 13.9097 | 13.4696 | 12.1138 | 10.0333 | 9.1257 | 8.3846 | 14.3895 | 14.2781 | 14.2104 | 14.1323 | 13.5615 | 12.9092 | 12.3745 | 11.7942 | 11.1799 | 10.4649 | 8.2852 | 4.9533 | 3.6574 | 3.2196
| HUME STREET | LW |  |  | 14.647 | 14.4776 | 14.3836 | 14.2808 | 13.6054 | 12.8763 | 12.113 | 11.1545 | 10.3726 | 9.7069 | 7.6058 | 4.8775 | 3.718 | 3.2221 | 15.7685 | 15.6803 | 15.6226 | 15.5557 | 15.2656 | 14.9496 | 14.6159 | 14.1502 | 13.7341 | 13.3097 | 11.9566 | 10.3583 | 9.9316 | 9.7498 | 14.4048 | 14.2609 | 14.1797 | 14.0893 | 13.4946 | 12.852 | 12.1771 | 11.3107 | 10.5949 | 9.9726 | 8.007 | 5.4892 | 4.4767 | 4.048
| HUME STREET | ST |  |  | 14.7885 | 14.7065 | 14.6343 | 14.5509 | 14.4889 | 14.4441 | 14.3749 | 14.3127 | 14.2572 | 14.0628 | 13.3338 | 10.0243 | 8.774 | 8.3833 | 15.8244 | 15.769 | 15.7175 | 15.6502 | 15.5869 | 15.5223 | 15.4384 | 15.3573 | 15.2692 | 15.0954 | 14.4446 | 12.0601 | 11.3115 | 10.7968 | 14.5303 | 14.4642 | 14.4029 | 14.3297 | 14.2752 | 14.235 | 14.1702 | 14.108 | 14.0495 | 13.8611 | 13.1532 | 9.5575 | 8.4598 | 8.1179
| HUME STREET | SP |  |  | 14.8612 | 14.8253 | 14.7893 | 14.7541 | 14.6721 | 14.5729 | 14.4765 | 14.3845 | 14.272 | 14.0816 | 13.3919 | 11.2172 | 9.5973 | 9.1934 | 15.849 | 15.8118 | 15.7723 | 15.7309 | 15.6646 | 15.5871 | 15.5023 | 15.4162 | 15.3008 | 15.1373 | 14.5416 | 12.894 | 11.2307 | 9.6358 | 14.5941 | 14.569 | 14.5396 | 14.5107 | 14.4402 | 14.3546 | 14.2689 | 14.1828 | 14.0745 | 13.895 | 13.244 | 10.79 | 9.2481 | 8.8645
KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | YES | 7.2211 | 6.8432 | 6.4384 | 6.0015 | 5.4454 | 5.0136 | 4.5808 | 4.1002 | 3.5511 | 3.0378 | 1.8392 | 0.57582 | -0.059855 | -0.28731 | 9.2747 | 8.9054 | 8.5252 | 8.1246 | 7.6791 | 7.3793 | 7.0741 | 6.7665 | 6.4481 | 6.1118 | 5.3626 | 4.6923 | 4.3513 | 4.1158 | 8.011 | 7.6442 | 7.2516 | 6.8314 | 6.302 | 5.8956 | 5.4896 | 5.0459 | 4.5394 | 4.073 | 2.9724 | 1.8146 | 1.2327 | 1.0247
| HUNTLY | CT |  |  | 7.2765 | 6.907 | 6.5033 | 6.0103 | 5.5013 | 5.0879 | 4.6206 | 4.1309 | 3.671 | 3.2639 | 1.9698 | 0.57582 | -0.059855 | -0.28731 | 9.2901 | 8.9201 | 8.539 | 8.128 | 7.6791 | 7.3793 | 7.0741 | 6.7665 | 6.4849 | 6.2266 | 5.4336 | 4.6923 | 4.3513 | 4.1158 | 8.0617 | 7.7021 | 7.3193 | 6.8963 | 6.361 | 5.967 | 5.5294 | 5.0745 | 4.647 | 4.2697 | 3.089 | 1.8146 | 1.2327 | 1.0247
| HUNTLY | LW |  |  | 7.2211 | 6.8432 | 6.4384 | 6.0015 | 5.4454 | 5.0136 | 4.5808 | 4.1002 | 3.5511 | 3.0378 | 1.8392 | 0.82124 | 0.43491 | 0.28871 | 9.2747 | 8.9054 | 8.5252 | 8.1246 | 7.6873 | 7.386 | 7.0922 | 6.7768 | 6.4481 | 6.1118 | 5.3626 | 4.8196 | 4.6688 | 4.6105 | 8.011 | 7.6442 | 7.2516 | 6.8314 | 6.302 | 5.8956 | 5.4896 | 5.0459 | 4.5394 | 4.073 | 2.9724 | 2.0338 | 1.6796 | 1.5456
| HUNTLY | ST |  |  | 7.3014 | 6.9325 | 6.5627 | 6.1899 | 5.8366 | 5.6013 | 5.3749 | 5.1653 | 4.9286 | 4.6955 | 3.9617 | 2.5617 | 1.9085 | 1.8326 | 9.3134 | 8.953 | 8.5922 | 8.2268 | 7.882 | 7.6716 | 7.489 | 7.3272 | 7.1642 | 7.0043 | 6.5235 | 5.6581 | 5.19 | 4.9245 | 8.0852 | 7.7263 | 7.367 | 7.0055 | 6.663 | 6.4479 | 6.2615 | 6.0969 | 5.9181 | 5.7294 | 5.1412 | 3.9579 | 3.1324 | 2.9594
| HUNTLY | SP |  |  | 7.3101 | 6.9449 | 6.5815 | 6.2139 | 5.8289 | 5.5953 | 5.3737 | 5.162 | 4.9593 | 4.7378 | 4.1608 | 3.057 | 2.2891 | 2.0167 | 9.3178 | 8.9597 | 8.6026 | 8.242 | 7.8868 | 7.68 | 7.4895 | 7.3123 | 7.1471 | 6.9771 | 6.5504 | 5.7924 | 5.1227 | 4.6373 | 8.0932 | 7.7379 | 7.3845 | 7.0274 | 6.6556 | 6.4313 | 6.2199 | 6.0193 | 5.829 | 5.6205 | 5.0832 | 4.0816 | 3.3884 | 3.148
BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | 1.6257 | 1.6059 | 1.5841 | 1.5468 | 1.4942 | 1.4369 | 1.4011 | 1.3628 | 1.3207 | 1.2671 | 1.0938 | 0.96114 | 0.93202 | 0.93229 | 1.8566 | 1.8463 | 1.8361 | 1.8109 | 1.7797 | 1.7507 | 1.7225 | 1.6891 | 1.6563 | 1.6121 | 1.4885 | 1.3597 | 1.3426 | 1.3417 | 1.6507 | 1.6316 | 1.6105 | 1.5744 | 1.5236 | 1.4682 | 1.4336 | 1.3967 | 1.356 | 1.3041 | 1.1367 | 1.0089 | 0.9805 | 0.98082
| INCHBARE | CT |  |  | 1.6257 | 1.6059 | 1.5841 | 1.5468 | 1.4942 | 1.4369 | 1.4011 | 1.3628 | 1.3207 | 1.2725 | 1.1266 | 1.0029 | 0.99834 | 0.9967 | 1.8566 | 1.8463 | 1.8361 | 1.8109 | 1.7797 | 1.7507 | 1.7225 | 1.6891 | 1.6563 | 1.6259 | 1.4962 | 1.4142 | 1.4089 | 1.4066 | 1.6507 | 1.6316 | 1.6105 | 1.5744 | 1.5236 | 1.4682 | 1.4336 | 1.3967 | 1.356 | 1.3095 | 1.1682 | 1.049 | 1.0447 | 1.0431
| INCHBARE | LW |  |  | 1.6326 | 1.6142 | 1.5941 | 1.558 | 1.5076 | 1.45 | 1.4126 | 1.3707 | 1.3238 | 1.2671 | 1.0938 | 0.96114 | 0.95898 | 0.95616 | 1.8575 | 1.8487 | 1.838 | 1.821 | 1.7937 | 1.761 | 1.7381 | 1.7053 | 1.6605 | 1.6121 | 1.4885 | 1.3597 | 1.3578 | 1.3552 | 1.6574 | 1.6396 | 1.6202 | 1.5853 | 1.5366 | 1.481 | 1.4448 | 1.4043 | 1.359 | 1.3041 | 1.1367 | 1.0089 | 1.0068 | 1.0041
| INCHBARE | ST |  |  | 1.6524 | 1.6473 | 1.642 | 1.6352 | 1.6263 | 1.6147 | 1.6015 | 1.5864 | 1.5678 | 1.5391 | 1.4166 | 1.1011 | 0.93202 | 0.93229 | 1.8666 | 1.8641 | 1.8612 | 1.8564 | 1.851 | 1.8419 | 1.833 | 1.8246 | 1.8103 | 1.7943 | 1.7158 | 1.5085 | 1.3426 | 1.3417 | 1.6765 | 1.6716 | 1.6664 | 1.6599 | 1.6513 | 1.6401 | 1.6273 | 1.6126 | 1.5948 | 1.567 | 1.4486 | 1.1436 | 0.9805 | 0.98082
| INCHBARE | SP |  |  | 1.655 | 1.6522 | 1.6492 | 1.6459 | 1.6402 | 1.6334 | 1.6258 | 1.6172 | 1.6053 | 1.5891 | 1.528 | 1.3244 | 1.1329 | 1.0748 | 1.8682 | 1.8668 | 1.8654 | 1.863 | 1.8587 | 1.8528 | 1.8471 | 1.8407 | 1.8253 | 1.8142 | 1.7651 | 1.5903 | 1.4871 | 1.4423 | 1.679 | 1.6763 | 1.6734 | 1.6702 | 1.6647 | 1.6582 | 1.6508 | 1.6425 | 1.631 | 1.6154 | 1.5563 | 1.3593 | 1.1746 | 1.1185
DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | 1.6755 | 1.6371 | 1.6132 | 1.5838 | 1.5053 | 1.4171 | 1.3393 | 1.2459 | 1.1206 | 1.0139 | 0.61732 | 0.1425 | -0.083816 | -0.16339 | 2.0108 | 1.9892 | 1.9761 | 1.9591 | 1.9164 | 1.8777 | 1.8362 | 1.7832 | 1.7144 | 1.6523 | 1.4107 | 1.1731 | 1.071 | 1.0186 | 1.7466 | 1.7174 | 1.6964 | 1.6702 | 1.5984 | 1.5189 | 1.4486 | 1.3614 | 1.2458 | 1.1494 | 0.79348 | 0.35269 | 0.14571 | 0.076225
| INNELLAN | CT |  |  | 1.6862 | 1.6521 | 1.6303 | 1.598 | 1.5174 | 1.4468 | 1.3636 | 1.2695 | 1.1686 | 1.0556 | 0.64216 | 0.1425 | -0.083816 | -0.16339 | 2.0141 | 1.9936 | 1.9801 | 1.9591 | 1.9164 | 1.8778 | 1.8362 | 1.7875 | 1.7348 | 1.6724 | 1.4359 | 1.1731 | 1.071 | 1.0186 | 1.7565 | 1.7312 | 1.7123 | 1.6841 | 1.6101 | 1.5453 | 1.4686 | 1.3821 | 1.2898 | 1.1862 | 0.8119 | 0.35269 | 0.14571 | 0.076225
| INNELLAN | LW |  |  | 1.6755 | 1.6371 | 1.6132 | 1.5838 | 1.5053 | 1.4171 | 1.3393 | 1.2459 | 1.1206 | 1.0139 | 0.61732 | 0.25642 | 0.10263 | 0.04959 | 2.0108 | 1.9892 | 1.9761 | 1.9593 | 1.9203 | 1.8777 | 1.8389 | 1.7832 | 1.7144 | 1.6523 | 1.4107 | 1.21 | 1.1524 | 1.1322 | 1.7466 | 1.7174 | 1.6964 | 1.6702 | 1.5984 | 1.5189 | 1.4486 | 1.3614 | 1.2458 | 1.1494 | 0.79348 | 0.46324 | 0.3181 | 0.26812
| INNELLAN | ST |  |  | 1.6945 | 1.6664 | 1.6565 | 1.6414 | 1.6284 | 1.6154 | 1.6002 | 1.5782 | 1.5595 | 1.5237 | 1.3896 | 0.95515 | 0.74189 | 0.64301 | 2.0198 | 2.0033 | 1.9971 | 1.9868 | 1.9779 | 1.9688 | 1.9583 | 1.9429 | 1.9294 | 1.9057 | 1.8155 | 1.5079 | 1.3808 | 1.3222 | 1.7644 | 1.7445 | 1.7366 | 1.7241 | 1.7133 | 1.7023 | 1.6895 | 1.6704 | 1.6542 | 1.6225 | 1.5034 | 1.1165 | 0.92033 | 0.82735
| INNELLAN | SP |  |  | 1.6991 | 1.6737 | 1.6659 | 1.657 | 1.6406 | 1.6236 | 1.6053 | 1.5861 | 1.5552 | 1.5201 | 1.4052 | 1.1121 | 0.83798 | 0.77934 | 2.0221 | 2.007 | 2.0019 | 1.9956 | 1.9864 | 1.9765 | 1.9659 | 1.9545 | 1.9349 | 1.9137 | 1.8416 | 1.6484 | 1.425 | 1.3441 | 1.7687 | 1.7514 | 1.7454 | 1.7385 | 1.7243 | 1.7094 | 1.6933 | 1.6762 | 1.6491 | 1.6176 | 1.5148 | 1.2529 | 1.0104 | 0.95754
KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | YES | -0.79025 | 6.0555 | 5.64 | 5.2123 | 4.5153 | 3.7971 | 2.9852 | 2.2429 | 1.3624 | 0.75984 | -0.40898 | -0.85778 | -0.62436 | -0.9912 | 2.3021 | 8.8841 | 8.5785 | 8.259 | 7.8466 | 7.4343 | 6.9575 | 6.5283 | 6.0249 | 5.6236 | 4.9027 | 4.6164 | 4.5842 | 4.1244 | 0.60385 | 7.1111 | 6.7309 | 6.3369 | 5.7034 | 5.049 | 4.2979 | 3.6165 | 2.8058 | 2.2386 | 1.1587 | 0.74304 | 0.94737 | 0.6361
| INSCH | CT |  |  | -0.66306 | 6.2703 | 5.9329 | 5.5773 | 4.9312 | 4.3197 | 3.6303 | 2.9296 | 2.2635 | 1.6899 | 0.30148 | -0.43825 | -0.58543 | -0.70911 | 2.3021 | 8.8897 | 8.6034 | 8.3041 | 7.9871 | 7.6283 | 7.2417 | 6.8495 | 6.4727 | 6.0797 | 5.1606 | 4.7217 | 4.5842 | 4.4031 | 0.71317 | 7.2969 | 6.9833 | 6.6514 | 6.0653 | 5.5104 | 4.8851 | 4.2459 | 3.6307 | 3.1029 | 1.7903 | 1.118 | 0.98812 | 0.87935
| INSCH | LW |  |  | -0.79025 | 6.0555 | 5.64 | 5.2123 | 4.5153 | 3.7971 | 2.9852 | 2.2429 | 1.3624 | 0.75984 | -0.40898 | -0.85778 | -0.62436 | -0.69137 | 2.3084 | 8.8841 | 8.5785 | 8.259 | 7.8466 | 7.4343 | 6.9575 | 6.5283 | 6.0249 | 5.6236 | 4.9027 | 4.6164 | 4.6973 | 4.6688 | 0.60385 | 7.1111 | 6.7309 | 6.3369 | 5.7034 | 5.049 | 4.2979 | 3.6165 | 2.8058 | 2.2386 | 1.1587 | 0.74304 | 0.94737 | 0.88825
| INSCH | ST |  |  | -0.63698 | 6.343 | 6.07 | 5.7926 | 5.5434 | 5.3251 | 5.1114 | 4.8833 | 4.6223 | 4.2818 | 3.2686 | 1.5881 | 0.92038 | 0.57972 | 2.3305 | 8.9371 | 8.6745 | 8.4095 | 8.1857 | 8.0011 | 7.818 | 7.6329 | 7.4442 | 7.2345 | 6.6471 | 5.5578 | 5.1713 | 4.8953 | 0.74267 | 7.3721 | 7.1218 | 6.8671 | 6.6359 | 6.4336 | 6.2332 | 6.0204 | 5.7779 | 5.4611 | 4.5081 | 2.9167 | 2.3171 | 2.0147
| INSCH | SP |  |  | -0.59383 | 6.4096 | 6.1643 | 5.9111 | 5.6249 | 5.3679 | 5.1023 | 4.8266 | 4.5471 | 4.2215 | 3.1671 | 0.83873 | -0.38929 | -0.9912 | 2.3332 | 8.9415 | 8.6823 | 8.4203 | 8.1997 | 8.0186 | 7.837 | 7.6536 | 7.47 | 7.2775 | 6.6868 | 5.3567 | 4.6201 | 4.1244 | 0.78131 | 7.4317 | 7.2066 | 6.9734 | 6.7105 | 6.4744 | 6.227 | 5.9706 | 5.711 | 5.4113 | 4.4427 | 2.2845 | 1.1691 | 0.6361
BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | 16.6805 | 16.3541 | 15.9714 | 15.7598 | 15.5618 | 15.272 | 15.1022 | 14.9123 | 14.7089 | 14.53 | 13.8787 | 12.7881 | 12.2671 | 12.0695 | 16.6231 | 16.2676 | 15.8516 | 15.6417 | 15.4587 | 15.1784 | 15.0258 | 14.8635 | 14.6928 | 14.5585 | 14.1531 | 13.7322 | 13.6903 | 13.65 | 16.584 | 16.2505 | 15.8599 | 15.6529 | 15.4657 | 15.186 | 15.0281 | 14.8581 | 14.6777 | 14.5251 | 13.9717 | 13.0399 | 12.5858 | 12.4185
| INVERALMOND | CT |  |  | 16.6805 | 16.3541 | 15.9714 | 15.7598 | 15.5618 | 15.272 | 15.1022 | 14.9123 | 14.7089 | 14.5334 | 13.9452 | 12.7881 | 12.2671 | 12.0695 | 16.6231 | 16.2676 | 15.8516 | 15.6417 | 15.4587 | 15.1784 | 15.0258 | 14.8635 | 14.6928 | 14.5585 | 14.2247 | 13.8549 | 13.7812 | 13.7137 | 16.584 | 16.2505 | 15.8599 | 15.6529 | 15.4657 | 15.186 | 15.0281 | 14.8581 | 14.6777 | 14.529 | 14.077 | 13.0399 | 12.5858 | 12.4185
| INVERALMOND | LW |  |  | 16.6905 | 16.3664 | 15.9886 | 15.7841 | 15.5938 | 15.3093 | 15.1387 | 14.9405 | 14.724 | 14.53 | 13.8787 | 12.9606 | 12.599 | 12.3662 | 16.6296 | 16.2756 | 15.8629 | 15.6581 | 15.4811 | 15.2052 | 15.0528 | 14.8835 | 14.7043 | 14.5585 | 14.1531 | 13.7322 | 13.6903 | 13.65 | 16.592 | 16.2603 | 15.8737 | 15.673 | 15.4928 | 15.2181 | 15.0598 | 14.8805 | 14.6889 | 14.5251 | 13.9717 | 13.178 | 12.8638 | 12.6656
| INVERALMOND | ST |  |  | 16.7133 | 16.4081 | 16.052 | 15.8857 | 15.755 | 15.544 | 15.4282 | 15.306 | 15.1781 | 15.0649 | 14.7277 | 13.8696 | 13.4201 | 13.2954 | 16.6442 | 16.3023 | 15.9033 | 15.7229 | 15.5832 | 15.3535 | 15.2347 | 15.1115 | 14.9844 | 14.8843 | 14.6141 | 14.0676 | 13.7792 | 13.6817 | 16.6104 | 16.294 | 15.9247 | 15.7548 | 15.6222 | 15.4063 | 15.291 | 15.1703 | 15.0448 | 14.9391 | 14.6366 | 13.8898 | 13.4207 | 13.3102
| INVERALMOND | SP |  |  | 16.7158 | 16.414 | 16.0609 | 15.9003 | 15.7761 | 15.5729 | 15.4673 | 15.3585 | 15.2437 | 15.1554 | 14.9389 | 14.3549 | 13.7606 | 13.5432 | 16.6457 | 16.3059 | 15.9089 | 15.7323 | 15.5971 | 15.3726 | 15.2606 | 15.1462 | 15.0272 | 14.943 | 14.7498 | 14.3467 | 13.9473 | 13.743 | 16.6123 | 16.2986 | 15.932 | 15.7669 | 15.6399 | 15.4308 | 15.3243 | 15.215 | 15.1 | 15.0152 | 14.8132 | 14.3354 | 13.7882 | 13.5712
CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | 2.1811 | 2.1805 | 2.1794 | 2.1777 | 2.1741 | 2.17 | 2.1657 | 2.161 | 2.1559 | 2.1525 | 2.1383 | 2.1274 | 2.121 | 2.1169 | 2.2096 | 2.2091 | 2.2083 | 2.207 | 2.2043 | 2.2012 | 2.198 | 2.1945 | 2.1907 | 2.1881 | 2.1774 | 2.1719 | 2.17 | 2.1682 | 2.1093 | 2.1086 | 2.1068 | 2.104 | 2.0979 | 2.0905 | 2.0828 | 2.0716 | 2.0604 | 2.0545 | 2.0296 | 2.0179 | 2.0123 | 2.0086
| INVERARAY | CT |  |  | 2.1816 | 2.1811 | 2.1801 | 2.1781 | 2.1741 | 2.17 | 2.1657 | 2.161 | 2.1559 | 2.1525 | 2.1407 | 2.1274 | 2.121 | 2.1169 | 2.2099 | 2.2095 | 2.2088 | 2.2073 | 2.2043 | 2.2012 | 2.198 | 2.1945 | 2.1907 | 2.1881 | 2.179 | 2.172 | 2.17 | 2.1682 | 2.1118 | 2.1114 | 2.1104 | 2.1082 | 2.1006 | 2.0932 | 2.0828 | 2.0716 | 2.0604 | 2.0545 | 2.0343 | 2.0179 | 2.0123 | 2.0086
| INVERARAY | LW |  |  | 2.1811 | 2.1805 | 2.1794 | 2.1777 | 2.1744 | 2.1702 | 2.1673 | 2.1635 | 2.1575 | 2.153 | 2.1383 | 2.1278 | 2.1302 | 2.1289 | 2.2096 | 2.2091 | 2.2083 | 2.207 | 2.2046 | 2.2015 | 2.1994 | 2.1965 | 2.192 | 2.1886 | 2.1774 | 2.1719 | 2.1721 | 2.1715 | 2.1093 | 2.1086 | 2.1068 | 2.104 | 2.0979 | 2.0905 | 2.0847 | 2.0776 | 2.0638 | 2.0555 | 2.0296 | 2.0182 | 2.0203 | 2.0191
| INVERARAY | ST |  |  | 2.1822 | 2.1819 | 2.1816 | 2.1811 | 2.1804 | 2.1798 | 2.1791 | 2.1779 | 2.1766 | 2.1743 | 2.1666 | 2.1474 | 2.1381 | 2.1329 | 2.2104 | 2.2102 | 2.2099 | 2.2095 | 2.2089 | 2.2085 | 2.208 | 2.207 | 2.206 | 2.2043 | 2.1984 | 2.1836 | 2.1763 | 2.1718 | 2.1119 | 2.1115 | 2.111 | 2.1106 | 2.1096 | 2.1088 | 2.1079 | 2.1062 | 2.1035 | 2.0995 | 2.0861 | 2.0559 | 2.0382 | 2.0288
| INVERARAY | SP |  |  | 2.1822 | 2.1819 | 2.1817 | 2.1814 | 2.1807 | 2.1799 | 2.1789 | 2.178 | 2.1766 | 2.1746 | 2.1687 | 2.1539 | 2.1343 | 2.1213 | 2.2104 | 2.2102 | 2.21 | 2.2097 | 2.2092 | 2.2086 | 2.2078 | 2.2071 | 2.206 | 2.2045 | 2.1999 | 2.1886 | 2.1764 | 2.1712 | 2.1118 | 2.1113 | 2.111 | 2.1105 | 2.1085 | 2.1067 | 2.1044 | 2.1022 | 2.0992 | 2.0948 | 2.0811 | 2.0514 | 2.0244 | 2.0129
LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | NO | 2.2501 | 2.2361 | 2.221 | 2.1973 | 2.15 | 2.0995 | 2.0466 | 1.9943 | 1.9155 | 1.838 | 1.7146 | 1.6501 | 1.643 | 1.6237 | 2.1862 | 2.1754 | 2.1626 | 2.142 | 2.1121 | 2.0768 | 2.05 | 2.0212 | 1.9874 | 1.9484 | 1.8157 | 1.6881 | 1.6852 | 1.677 | 2.1792 | 2.1625 | 2.1436 | 2.1138 | 2.0672 | 2.0122 | 1.9644 | 1.9128 | 1.8497 | 1.7881 | 1.6153 | 1.4631 | 1.4589 | 1.4474
| INVERARITY | CT |  |  | 2.26 | 2.2499 | 2.2365 | 2.2144 | 2.1684 | 2.1217 | 2.0612 | 1.9943 | 1.9287 | 1.891 | 1.747 | 1.6683 | 1.643 | 1.6237 | 2.1862 | 2.1754 | 2.1626 | 2.142 | 2.1121 | 2.0768 | 2.05 | 2.0212 | 1.9876 | 1.9574 | 1.8622 | 1.7514 | 1.7388 | 1.7281 | 2.1796 | 2.1643 | 2.1453 | 2.1162 | 2.0692 | 2.0152 | 1.9659 | 1.9128 | 1.8545 | 1.8065 | 1.6667 | 1.5314 | 1.5136 | 1.4987
| INVERARITY | LW |  |  | 2.2501 | 2.2361 | 2.221 | 2.1973 | 2.15 | 2.0995 | 2.0466 | 1.995 | 1.9155 | 1.838 | 1.7146 | 1.6501 | 1.6521 | 1.6402 | 2.1883 | 2.1781 | 2.1667 | 2.1469 | 2.1174 | 2.082 | 2.053 | 2.0225 | 1.9874 | 1.9484 | 1.8157 | 1.6881 | 1.6852 | 1.677 | 2.1792 | 2.1625 | 2.1436 | 2.1138 | 2.0672 | 2.0122 | 1.9644 | 1.9137 | 1.8497 | 1.7881 | 1.6153 | 1.4631 | 1.4589 | 1.4474
| INVERARITY | ST |  |  | 2.2635 | 2.2595 | 2.255 | 2.248 | 2.2423 | 2.233 | 2.2231 | 2.2144 | 2.1954 | 2.1725 | 2.0813 | 1.8822 | 1.7801 | 1.7078 | 2.1958 | 2.1921 | 2.1877 | 2.1821 | 2.1765 | 2.1694 | 2.1608 | 2.1512 | 2.1392 | 2.1226 | 2.0563 | 1.8732 | 1.7625 | 1.7145 | 2.1927 | 2.1867 | 2.1798 | 2.1714 | 2.1626 | 2.1516 | 2.1385 | 2.1235 | 2.1032 | 2.0752 | 1.9683 | 1.7013 | 1.5593 | 1.4914
| INVERARITY | SP |  |  | 2.2665 | 2.2639 | 2.2611 | 2.2573 | 2.2472 | 2.2387 | 2.229 | 2.2139 | 2.1993 | 2.1808 | 2.1028 | 1.8732 | 1.737 | 1.6613 | 2.1969 | 2.1943 | 2.1912 | 2.1874 | 2.1833 | 2.1792 | 2.1742 | 2.167 | 2.1584 | 2.1479 | 2.1075 | 1.9725 | 1.851 | 1.7981 | 2.1943 | 2.19 | 2.1852 | 2.1793 | 2.1715 | 2.1637 | 2.1545 | 2.1431 | 2.1306 | 2.1133 | 2.0464 | 1.8281 | 1.6711 | 1.5996
INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | NO | 2.2592 | 2.2548 | 2.2493 | 2.2428 | 2.2143 | 2.1652 | 2.0986 | 2.0225 | 1.9213 | 1.858 | 1.6774 | 1.6182 | 1.6437 | 1.5818 | 2.0891 | 2.085 | 2.0798 | 2.0738 | 2.0668 | 2.0595 | 2.0468 | 2.0325 | 2.0027 | 1.9747 | 1.8898 | 1.829 | 1.8381 | 1.8066 | 2.1365 | 2.1224 | 2.1029 | 2.0801 | 2.0309 | 1.9767 | 1.9194 | 1.8605 | 1.7756 | 1.7204 | 1.5625 | 1.5079 | 1.5305 | 1.4785
| INVERARNIE | CT |  |  | 2.2592 | 2.2548 | 2.2493 | 2.2428 | 2.2351 | 2.2051 | 2.1498 | 2.0775 | 1.9972 | 1.9492 | 1.7721 | 1.6769 | 1.6437 | 1.6205 | 2.0891 | 2.085 | 2.0798 | 2.0738 | 2.0668 | 2.0597 | 2.0517 | 2.0422 | 2.0275 | 2.0049 | 1.9263 | 1.8777 | 1.8612 | 1.8388 | 2.1425 | 2.1351 | 2.1249 | 2.1123 | 2.0738 | 2.0254 | 1.963 | 1.8966 | 1.8335 | 1.7962 | 1.6463 | 1.5609 | 1.5323 | 1.5123
| INVERARNIE | LW |  |  | 2.2599 | 2.2555 | 2.251 | 2.2446 | 2.2143 | 2.1652 | 2.0986 | 2.0225 | 1.9213 | 1.858 | 1.6774 | 1.6182 | 1.6485 | 1.6402 | 2.0899 | 2.0858 | 2.0814 | 2.0755 | 2.0682 | 2.0595 | 2.0468 | 2.0325 | 2.0027 | 1.9747 | 1.8898 | 1.829 | 1.8381 | 1.8357 | 2.1365 | 2.1224 | 2.1029 | 2.0801 | 2.0309 | 1.9767 | 1.9194 | 1.8605 | 1.7756 | 1.7204 | 1.5625 | 1.5079 | 1.5305 | 1.525
| INVERARNIE | ST |  |  | 2.2631 | 2.2612 | 2.2594 | 2.2565 | 2.254 | 2.2509 | 2.2463 | 2.2427 | 2.2383 | 2.23 | 2.1442 | 1.9484 | 1.8465 | 1.8021 | 2.093 | 2.0911 | 2.0894 | 2.0867 | 2.0842 | 2.0812 | 2.0771 | 2.0733 | 2.0689 | 2.061 | 2.0241 | 1.9236 | 1.8908 | 1.8873 | 2.1476 | 2.1435 | 2.1393 | 2.134 | 2.1281 | 2.1211 | 2.1128 | 2.1039 | 2.0872 | 2.0618 | 1.9761 | 1.7953 | 1.6891 | 1.6485
| INVERARNIE | SP |  |  | 2.264 | 2.2626 | 2.261 | 2.259 | 2.2566 | 2.2539 | 2.2507 | 2.2474 | 2.2429 | 2.2375 | 2.1521 | 1.8643 | 1.6739 | 1.5818 | 2.0936 | 2.0922 | 2.0906 | 2.0887 | 2.0865 | 2.0839 | 2.0811 | 2.0779 | 2.0739 | 2.0688 | 2.0521 | 1.965 | 1.8631 | 1.8066 | 2.1491 | 2.1459 | 2.1427 | 2.1389 | 2.1315 | 2.1238 | 2.1117 | 2.0974 | 2.0817 | 2.06 | 1.9667 | 1.7273 | 1.5593 | 1.4785
FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | YES | 3.6715 | 3.4975 | 3.353 | 3.1998 | 3.0293 | 2.8976 | 2.7565 | 2.6214 | 2.4636 | 2.3353 | 1.9662 | 1.6005 | 1.4341 | 1.3727 | 4.4594 | 4.306 | 4.174 | 4.0336 | 3.8984 | 3.8035 | 3.7098 | 3.6163 | 3.5145 | 3.4278 | 3.1822 | 2.9586 | 2.8338 | 2.7041 | 4.0505 | 3.8939 | 3.76 | 3.619 | 3.4636 | 3.3451 | 3.217 | 3.0951 | 2.953 | 2.8373 | 2.5063 | 2.1936 | 2.0484 | 1.9954
| INVERBERVIE | CT |  |  | 3.6809 | 3.5082 | 3.3639 | 3.2101 | 3.0423 | 2.9146 | 2.7803 | 2.6478 | 2.5206 | 2.3886 | 1.9851 | 1.6005 | 1.4341 | 1.3727 | 4.4607 | 4.3065 | 4.174 | 4.0336 | 3.8984 | 3.8035 | 3.7103 | 3.6212 | 3.5375 | 3.4485 | 3.1822 | 2.9586 | 2.8338 | 2.705 | 4.0585 | 3.9029 | 3.7689 | 3.6266 | 3.4733 | 3.3585 | 3.2382 | 3.12 | 3.0072 | 2.8887 | 2.5264 | 2.1936 | 2.0484 | 1.9954
| INVERBERVIE | LW |  |  | 3.6715 | 3.4975 | 3.353 | 3.1998 | 3.0293 | 2.8976 | 2.7565 | 2.6214 | 2.4636 | 2.3353 | 1.9662 | 1.6686 | 1.5623 | 1.5221 | 4.4594 | 4.306 | 4.176 | 4.0402 | 3.9058 | 3.8107 | 3.7098 | 3.6163 | 3.5145 | 3.4278 | 3.1866 | 3.0268 | 2.9855 | 2.9694 | 4.0505 | 3.8939 | 3.76 | 3.619 | 3.4636 | 3.3451 | 3.217 | 3.0951 | 2.953 | 2.8373 | 2.5063 | 2.2503 | 2.1581 | 2.1238
| INVERBERVIE | ST |  |  | 3.6855 | 3.5115 | 3.3721 | 3.2282 | 3.1027 | 3.0208 | 2.9444 | 2.8759 | 2.808 | 2.7337 | 2.5165 | 2.1621 | 2.0199 | 1.939 | 4.4659 | 4.314 | 4.1873 | 4.0562 | 3.9428 | 3.871 | 3.8042 | 3.7442 | 3.6871 | 3.6276 | 3.4595 | 3.1892 | 3.0565 | 2.919 | 4.0634 | 3.9074 | 3.7787 | 3.6465 | 3.532 | 3.4589 | 3.3907 | 3.3301 | 3.2705 | 3.2047 | 3.0138 | 2.6922 | 2.5641 | 2.4936
| INVERBERVIE | SP |  |  | 3.6896 | 3.517 | 3.3778 | 3.2337 | 3.0997 | 3.0128 | 2.9293 | 2.8521 | 2.777 | 2.7036 | 2.5058 | 2.1895 | 2.0277 | 1.989 | 4.4685 | 4.3175 | 4.1905 | 4.0603 | 3.9438 | 3.8711 | 3.8021 | 3.7391 | 3.6779 | 3.6194 | 3.4639 | 3.2023 | 2.9662 | 2.7041 | 4.0673 | 3.9128 | 3.7842 | 3.6522 | 3.5302 | 3.453 | 3.3788 | 3.3107 | 3.2444 | 3.1803 | 3.0103 | 2.7264 | 2.5723 | 2.5379
GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | 0.085513 | 0.22212 | 0.22001 | 0.21678 | 0.20396 | 0.19152 | 0.17937 | 0.16702 | 0.15106 | 0.1449 | 0.11526 | 0.11523 | 0.11192 | 0.1071 | 0.11504 | 0.24006 | 0.239 | 0.23739 | 0.23181 | 0.22632 | 0.22083 | 0.21496 | 0.20718 | 0.20357 | 0.18151 | 0.18127 | 0.1783 | 0.17411 | 0.092689 | 0.21866 | 0.21673 | 0.21378 | 0.20231 | 0.19116 | 0.18024 | 0.16905 | 0.15454 | 0.14878 | 0.12018 | 0.11995 | 0.11758 | 0.11357
| INVERBROOM | CT |  |  | 0.092048 | 0.22936 | 0.22818 | 0.2243 | 0.21076 | 0.20059 | 0.18725 | 0.17408 | 0.16307 | 0.15632 | 0.12787 | 0.1204 | 0.12596 | 0.12664 | 0.11737 | 0.24288 | 0.24206 | 0.23996 | 0.23374 | 0.2296 | 0.22373 | 0.21791 | 0.21345 | 0.2092 | 0.18785 | 0.18308 | 0.18382 | 0.18236 | 0.0984 | 0.22506 | 0.22392 | 0.22035 | 0.20816 | 0.19915 | 0.1872 | 0.17541 | 0.16567 | 0.15928 | 0.13191 | 0.12486 | 0.12897 | 0.12938
| INVERBROOM | LW |  |  | 0.085513 | 0.22212 | 0.22001 | 0.21678 | 0.20396 | 0.19152 | 0.17937 | 0.16702 | 0.15106 | 0.1449 | 0.11526 | 0.11523 | 0.12252 | 0.11842 | 0.11504 | 0.24006 | 0.239 | 0.23739 | 0.23181 | 0.22632 | 0.22083 | 0.21496 | 0.20718 | 0.20357 | 0.18151 | 0.18127 | 0.18363 | 0.18216 | 0.092689 | 0.21866 | 0.21673 | 0.21378 | 0.20231 | 0.19116 | 0.18024 | 0.16905 | 0.15454 | 0.14878 | 0.12018 | 0.11995 | 0.12587 | 0.12269
| INVERBROOM | ST |  |  | 0.089683 | 0.22497 | 0.2242 | 0.22389 | 0.2242 | 0.22379 | 0.22373 | 0.22302 | 0.22138 | 0.21841 | 0.20509 | 0.16953 | 0.16501 | 0.16132 | 0.11664 | 0.24175 | 0.24116 | 0.2407 | 0.24054 | 0.23999 | 0.23976 | 0.23877 | 0.23764 | 0.23603 | 0.22688 | 0.20037 | 0.19771 | 0.19477 | 0.096366 | 0.22134 | 0.22059 | 0.22024 | 0.22045 | 0.21999 | 0.21989 | 0.21909 | 0.21752 | 0.21479 | 0.20191 | 0.16641 | 0.16253 | 0.15939
| INVERBROOM | SP |  |  | 0.091109 | 0.22643 | 0.22635 | 0.22566 | 0.22065 | 0.21702 | 0.21204 | 0.2074 | 0.20133 | 0.19312 | 0.17485 | 0.13868 | 0.11192 | 0.1071 | 0.11764 | 0.24282 | 0.24269 | 0.24206 | 0.23976 | 0.23839 | 0.23613 | 0.23424 | 0.23115 | 0.22764 | 0.21874 | 0.19996 | 0.1783 | 0.17411 | 0.097749 | 0.22277 | 0.22268 | 0.22199 | 0.21748 | 0.21431 | 0.20984 | 0.20574 | 0.2002 | 0.19288 | 0.17635 | 0.14338 | 0.11758 | 0.11357
FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | 0.81135 | 0.81287 | 0.80574 | 0.7934 | 0.762 | 0.72744 | 0.6991 | 0.66949 | 0.63306 | 0.61075 | 0.52898 | 0.50571 | 0.51255 | 0.50401 | 0.87771 | 0.87685 | 0.8726 | 0.86488 | 0.84879 | 0.82959 | 0.8147 | 0.7984 | 0.77902 | 0.76473 | 0.70717 | 0.68594 | 0.6834 | 0.67383 | 0.76045 | 0.76145 | 0.75482 | 0.74324 | 0.71467 | 0.68283 | 0.65689 | 0.6296 | 0.5962 | 0.5751 | 0.49703 | 0.47505 | 0.48082 | 0.47581
| INVERGARRY | CT |  |  | 0.82729 | 0.82933 | 0.82473 | 0.81241 | 0.77814 | 0.74627 | 0.71489 | 0.68274 | 0.65218 | 0.63256 | 0.55721 | 0.51578 | 0.51255 | 0.50727 | 0.88331 | 0.88233 | 0.87858 | 0.87018 | 0.85164 | 0.83391 | 0.8181 | 0.80178 | 0.78613 | 0.77342 | 0.71913 | 0.69054 | 0.68598 | 0.68198 | 0.77438 | 0.77577 | 0.77126 | 0.75954 | 0.72809 | 0.69875 | 0.67024 | 0.641 | 0.6132 | 0.59466 | 0.52244 | 0.48384 | 0.48082 | 0.47605
| INVERGARRY | LW |  |  | 0.81135 | 0.81287 | 0.80574 | 0.7934 | 0.762 | 0.72744 | 0.6991 | 0.66949 | 0.63306 | 0.61075 | 0.52898 | 0.50571 | 0.51587 | 0.50913 | 0.87771 | 0.87685 | 0.8726 | 0.86488 | 0.84879 | 0.82959 | 0.8147 | 0.7984 | 0.77902 | 0.76473 | 0.70717 | 0.68594 | 0.6834 | 0.67957 | 0.76045 | 0.76145 | 0.75482 | 0.74324 | 0.71467 | 0.68283 | 0.65689 | 0.6296 | 0.5962 | 0.5751 | 0.49703 | 0.47505 | 0.48383 | 0.47776
| INVERGARRY | ST |  |  | 0.82515 | 0.82277 | 0.82085 | 0.81952 | 0.81741 | 0.81364 | 0.8099 | 0.80631 | 0.79821 | 0.78702 | 0.74544 | 0.63288 | 0.55804 | 0.53077 | 0.88426 | 0.88276 | 0.8815 | 0.88005 | 0.87827 | 0.87553 | 0.87292 | 0.86993 | 0.86444 | 0.85753 | 0.83051 | 0.74746 | 0.69295 | 0.67383 | 0.77291 | 0.77069 | 0.76889 | 0.76749 | 0.76541 | 0.76178 | 0.75822 | 0.75468 | 0.74697 | 0.7365 | 0.69724 | 0.58787 | 0.54194 | 0.52093
| INVERGARRY | SP |  |  | 0.82632 | 0.82406 | 0.82232 | 0.82059 | 0.80919 | 0.79836 | 0.78625 | 0.77326 | 0.76009 | 0.74025 | 0.69516 | 0.59768 | 0.52719 | 0.50401 | 0.88535 | 0.8842 | 0.88307 | 0.88198 | 0.87714 | 0.87237 | 0.86703 | 0.86108 | 0.85486 | 0.84574 | 0.82175 | 0.7646 | 0.71086 | 0.69238 | 0.77411 | 0.77207 | 0.77044 | 0.76883 | 0.75869 | 0.74902 | 0.73821 | 0.72655 | 0.71469 | 0.69686 | 0.65558 | 0.56509 | 0.49737 | 0.47581
ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | YES | 10.7446 | 10.4753 | 10.1548 | 10.009 | 9.7059 | 9.1623 | 8.4252 | 7.7742 | 7.0948 | 6.5586 | 4.8487 | 3.1432 | 2.6182 | 2.4288 | 2.2191 | 1.9553 | 1.6459 | 1.5078 | 1.2263 | 0.92101 | 0.59318 | 0.33855 | -0.13715 | -0.6026 | -2.0109 | -3.023 | -3.2924 | -3.4611 | 0.90071 | 0.59019 | 0.22525 | 0.033872 | -0.34897 | -0.9233 | -1.5416 | -2.1534 | -2.803 | -3.3541 | -5.2402 | -6.8551 | -7.3396 | -7.5147
| INVERGORDON | CT |  |  | 10.7582 | 10.4898 | 10.1712 | 10.0247 | 9.7178 | 9.3666 | 8.6341 | 7.9998 | 7.3555 | 6.7877 | 5.1224 | 3.1432 | 2.6182 | 2.4288 | 2.2233 | 1.9597 | 1.6503 | 1.5104 | 1.2263 | 0.92101 | 0.59364 | 0.34588 | -0.029139 | -0.4903 | -1.8771 | -3.0187 | -3.2924 | -3.4611 | 0.90071 | 0.59019 | 0.22525 | 0.033872 | -0.30686 | -0.82256 | -1.4312 | -1.9805 | -2.5491 | -3.0852 | -4.9679 | -6.8551 | -7.3396 | -7.5147
| INVERGORDON | LW |  |  | 10.7446 | 10.4753 | 10.1548 | 10.009 | 9.7059 | 9.1623 | 8.4252 | 7.7742 | 7.0948 | 6.5586 | 4.8487 | 3.1625 | 2.8947 | 2.729 | 2.2191 | 1.9553 | 1.6459 | 1.5078 | 1.2265 | 0.92184 | 0.59318 | 0.33855 | -0.13715 | -0.6026 | -2.0109 | -3.023 | -3.1616 | -3.2401 | 0.90749 | 0.59808 | 0.23944 | 0.064039 | -0.34897 | -0.9233 | -1.5416 | -2.1534 | -2.803 | -3.3541 | -5.2402 | -6.798 | -7.0825 | -7.2391
| INVERGORDON | ST |  |  | 10.7585 | 10.4867 | 10.1713 | 10.035 | 9.7593 | 9.4605 | 9.1365 | 8.8955 | 8.6546 | 8.4326 | 7.2647 | 5.2488 | 4.3727 | 4.0935 | 2.2256 | 1.962 | 1.6558 | 1.523 | 1.2545 | 0.96398 | 0.64964 | 0.41694 | 0.18651 | -0.023573 | -0.6821 | -2.115 | -2.6522 | -2.7707 | 0.91803 | 0.61751 | 0.26942 | 0.10761 | -0.19968 | -0.53317 | -0.89726 | -1.1814 | -1.5342 | -1.9145 | -3.1734 | -4.6294 | -5.149 | -5.4441
| INVERGORDON | SP |  |  | 10.7582 | 10.4861 | 10.1708 | 10.0339 | 9.7503 | 9.4452 | 9.1142 | 8.7685 | 8.3434 | 7.8698 | 6.7173 | 5.4674 | 4.5716 | 4.3602 | 2.2256 | 1.9622 | 1.6562 | 1.5239 | 1.2531 | 0.96093 | 0.64466 | 0.40954 | 0.17625 | -0.035175 | -0.85909 | -1.9038 | -2.4478 | -2.7827 | 0.91949 | 0.62121 | 0.27452 | 0.11997 | -0.18063 | -0.50812 | -0.96542 | -1.3532 | -1.7644 | -2.1984 | -3.3468 | -4.7205 | -5.3745 | -5.4858
FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | YES | 5.1006 | 5.0287 | 4.9296 | 4.7796 | 4.2169 | 3.5546 | 2.9694 | 2.4073 | 1.828 | 1.5105 | 0.54513 | 0.16314 | 0.52109 | 0.21493 | 6.6282 | 6.5574 | 6.466 | 6.3334 | 6.0328 | 5.7224 | 5.4534 | 5.1593 | 4.85 | 4.6128 | 3.864 | 3.4562 | 3.4773 | 2.9596 | 6.8227 | 6.7656 | 6.6995 | 6.5812 | 6.1572 | 5.5572 | 5.026 | 4.4965 | 3.953 | 3.6297 | 2.569 | 2.0405 | 2.3268 | 2.1623
| INVERLOCHY | CT |  |  | 5.1701 | 5.1115 | 5.0428 | 4.9133 | 4.5216 | 4.0166 | 3.4493 | 2.931 | 2.4344 | 2.1569 | 1.259 | 0.47794 | 0.55456 | 0.53327 | 6.7112 | 6.6601 | 6.594 | 6.4672 | 6.1424 | 5.8398 | 5.5786 | 5.3252 | 5.0721 | 4.8775 | 4.1829 | 3.5481 | 3.4773 | 3.3281 | 6.8347 | 6.7795 | 6.7147 | 6.5922 | 6.3463 | 5.9528 | 5.4386 | 4.9612 | 4.5009 | 4.2253 | 3.2317 | 2.3269 | 2.363 | 2.3387
| INVERLOCHY | LW |  |  | 5.1006 | 5.0287 | 4.9296 | 4.7796 | 4.2169 | 3.5546 | 2.9694 | 2.4073 | 1.828 | 1.5105 | 0.54513 | 0.16314 | 0.52109 | 0.42186 | 6.6282 | 6.5574 | 6.466 | 6.3334 | 6.0328 | 5.7224 | 5.4534 | 5.1593 | 4.85 | 4.6128 | 3.864 | 3.4562 | 3.5837 | 3.5436 | 6.8227 | 6.7656 | 6.6995 | 6.5812 | 6.1572 | 5.5572 | 5.026 | 4.4965 | 3.953 | 3.6297 | 2.569 | 2.0405 | 2.3268 | 2.2472
| INVERLOCHY | ST |  |  | 5.216 | 5.1758 | 5.142 | 5.1039 | 5.0893 | 5.0624 | 5.0213 | 4.9809 | 4.9368 | 4.8293 | 4.2534 | 2.6889 | 2.0256 | 1.8624 | 6.7331 | 6.6942 | 6.6587 | 6.6123 | 6.5778 | 6.5304 | 6.4675 | 6.4108 | 6.3448 | 6.2273 | 5.7781 | 4.6385 | 4.0051 | 3.8469 | 6.8859 | 6.8563 | 6.8312 | 6.7973 | 6.7824 | 6.759 | 6.7225 | 6.6841 | 6.6421 | 6.5538 | 6.0484 | 4.4299 | 3.698 | 3.5185
| INVERLOCHY | SP |  |  | 5.2434 | 5.2238 | 5.2097 | 5.1843 | 5.0937 | 4.9992 | 4.8955 | 4.7433 | 4.5152 | 4.1529 | 3.351 | 1.5774 | 0.5827 | 0.21493 | 6.7495 | 6.7204 | 6.6963 | 6.6601 | 6.5772 | 6.4857 | 6.3876 | 6.2842 | 6.1642 | 5.9904 | 5.5508 | 4.4327 | 3.5194 | 2.9596 | 6.9058 | 6.8888 | 6.8773 | 6.8554 | 6.8131 | 6.7661 | 6.7117 | 6.6412 | 6.4272 | 6.0957 | 5.3452 | 3.6122 | 2.5188 | 2.1623
PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | 2.3053 | 6.787 | 6.7843 | 6.7603 | 6.6615 | 6.5638 | 6.4711 | 6.401 | 6.3498 | 6.3282 | 6.2113 | 6.1564 | 6.1981 | 6.1856 | 2.1735 | 6.2983 | 6.2788 | 6.2559 | 6.2071 | 6.1583 | 6.1089 | 6.069 | 6.037 | 6.0093 | 5.9285 | 5.8993 | 5.9168 | 5.9076 | 2.0718 | 6.2111 | 6.208 | 6.2039 | 6.1883 | 6.1016 | 5.9991 | 5.918 | 5.8547 | 5.8055 | 5.6652 | 5.6264 | 5.6712 | 5.6602
| INVERNEIL | CT |  |  | 2.3053 | 6.787 | 6.7843 | 6.7811 | 6.6957 | 6.6106 | 6.5454 | 6.4913 | 6.4407 | 6.4184 | 6.2792 | 6.1886 | 6.2125 | 6.2181 | 2.1735 | 6.2987 | 6.2799 | 6.258 | 6.2071 | 6.1617 | 6.1243 | 6.0949 | 6.0665 | 6.0458 | 5.963 | 5.911 | 5.9168 | 5.9076 | 2.0718 | 6.2111 | 6.208 | 6.2039 | 6.1974 | 6.1217 | 6.0459 | 5.9862 | 5.9293 | 5.8922 | 5.7457 | 5.6602 | 5.6858 | 5.6907
| INVERNEIL | LW |  |  | 2.3064 | 6.7879 | 6.7855 | 6.7603 | 6.6615 | 6.5638 | 6.4711 | 6.401 | 6.3498 | 6.3282 | 6.2113 | 6.1564 | 6.1981 | 6.1856 | 2.1767 | 6.2983 | 6.2788 | 6.2559 | 6.2083 | 6.1583 | 6.1089 | 6.069 | 6.037 | 6.0093 | 5.9285 | 5.8993 | 5.921 | 5.9142 | 2.0759 | 6.2164 | 6.2149 | 6.2128 | 6.1883 | 6.1016 | 5.9991 | 5.918 | 5.8547 | 5.8055 | 5.6652 | 5.6264 | 5.6712 | 5.6602
| INVERNEIL | ST |  |  | 2.3072 | 6.7908 | 6.7904 | 6.7895 | 6.7891 | 6.7887 | 6.7881 | 6.7875 | 6.7869 | 6.7853 | 6.7603 | 6.5807 | 6.526 | 6.5123 | 2.1861 | 6.3245 | 6.3204 | 6.3134 | 6.308 | 6.3032 | 6.2969 | 6.2894 | 6.2827 | 6.2696 | 6.2237 | 6.1097 | 6.0712 | 6.051 | 2.0742 | 6.2163 | 6.2163 | 6.2156 | 6.2169 | 6.2183 | 6.2194 | 6.2204 | 6.2216 | 6.2217 | 6.2186 | 6.0262 | 5.9737 | 5.9614
| INVERNEIL | SP |  |  | 2.3074 | 6.7915 | 6.7915 | 6.7913 | 6.7912 | 6.7907 | 6.7905 | 6.79 | 6.7893 | 6.7881 | 6.7732 | 6.561 | 6.3849 | 6.3256 | 2.1873 | 6.3285 | 6.3272 | 6.3249 | 6.3212 | 6.3156 | 6.3113 | 6.3059 | 6.2986 | 6.2877 | 6.2395 | 6.0986 | 5.9928 | 5.9361 | 2.0755 | 6.2184 | 6.2194 | 6.2203 | 6.222 | 6.2233 | 6.225 | 6.2264 | 6.2274 | 6.2267 | 6.2214 | 6.0153 | 5.8489 | 5.789
INVERNESS | INVERNESS 11 kV | MINIMUM HEADROOM | NH 65302 42625 | NO | 5.3721 | 6.8905 | 6.8525 | 6.7918 | 6.7225 | 6.6569 | 6.5804 | 6.2554 | 5.7567 | 5.367 | 3.9244 | 2.1445 | 1.246 | 0.93434 | 7.8785 | 8.639 | 8.5915 | 8.5082 | 8.3543 | 8.1965 | 8.0157 | 7.8239 | 7.5732 | 7.3472 | 6.4557 | 5.4681 | 4.8964 | 4.3858 | 6.2951 | 7.0397 | 6.9656 | 6.8629 | 6.6158 | 6.3346 | 6.0168 | 5.6479 | 5.1954 | 4.8353 | 3.4859 | 1.9021 | 1.1134 | 0.84144
| INVERNESS 11 kV | CT |  |  | 5.3721 | 6.8905 | 6.8525 | 6.7918 | 6.7225 | 6.6569 | 6.5804 | 6.3344 | 5.9295 | 5.5117 | 3.9928 | 2.1445 | 1.246 | 0.93434 | 7.8856 | 8.6486 | 8.596 | 8.5082 | 8.3543 | 8.1965 | 8.0157 | 7.8239 | 7.6157 | 7.3844 | 6.4839 | 5.4681 | 4.8964 | 4.3858 | 6.3311 | 7.0903 | 7.0234 | 6.914 | 6.6537 | 6.382 | 6.0608 | 5.7198 | 5.3567 | 4.9759 | 3.5739 | 1.9021 | 1.1134 | 0.84144
| INVERNESS 11 kV | LW |  |  | 5.3846 | 6.8984 | 6.8647 | 6.8132 | 6.7544 | 6.6823 | 6.5954 | 6.2554 | 5.7567 | 5.367 | 3.9244 | 2.6665 | 2.0146 | 1.785 | 7.8785 | 8.639 | 8.5915 | 8.5226 | 8.3883 | 8.2324 | 8.0505 | 7.8326 | 7.5732 | 7.3472 | 6.4557 | 5.8334 | 5.5891 | 5.5012 | 6.2951 | 7.0397 | 6.9656 | 6.8629 | 6.6158 | 6.3346 | 6.0168 | 5.6479 | 5.1954 | 4.8353 | 3.4859 | 2.3466 | 1.7763 | 1.5763
| INVERNESS 11 kV | ST |  |  | 5.4024 | 6.9357 | 6.9169 | 6.8934 | 6.865 | 6.843 | 6.8047 | 6.7642 | 6.707 | 6.6353 | 6.3665 | 5.4273 | 4.7456 | 4.336 | 7.9178 | 8.6959 | 8.6704 | 8.6358 | 8.6016 | 8.5673 | 8.5159 | 8.4654 | 8.4006 | 8.3029 | 7.9306 | 6.783 | 6.2122 | 5.6488 | 6.3754 | 7.152 | 7.1251 | 7.0892 | 7.0553 | 7.0208 | 6.9665 | 6.9148 | 6.8445 | 6.7232 | 6.2685 | 4.8479 | 4.2101 | 3.8274
| INVERNESS 11 kV | SP |  |  | 5.4052 | 6.9408 | 6.9244 | 6.9066 | 6.8833 | 6.8668 | 6.8383 | 6.8046 | 6.7582 | 6.6981 | 6.5309 | 5.945 | 4.9892 | 4.8211 | 7.9247 | 8.7049 | 8.682 | 8.6554 | 8.6155 | 8.5754 | 8.5254 | 8.4641 | 8.3831 | 8.2787 | 7.9473 | 7.08 | 5.927 | 4.8876 | 6.3886 | 7.17 | 7.1496 | 7.1257 | 7.0726 | 7.021 | 6.9573 | 6.8808 | 6.7826 | 6.6541 | 6.2715 | 5.3325 | 4.4432 | 4.2875
KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | YES | 16.6578 | 16.216 | 15.7467 | 15.2664 | 14.2998 | 13.22 | 12.0705 | 10.8204 | 9.5218 | 8.3927 | 5.0004 | 1.1789 | -0.51745 | -1.1059 | 19.5816 | 19.3137 | 19.0109 | 18.6855 | 18.1827 | 17.6003 | 16.9762 | 16.2898 | 15.5657 | 14.8784 | 12.8246 | 10.5984 | 9.6232 | 8.8953 | 17.5823 | 17.2309 | 16.8477 | 16.4177 | 15.5577 | 14.5896 | 13.5543 | 12.4247 | 11.239 | 10.1929 | 7.136 | 3.6555 | 2.1597 | 1.6448
| INVERURIE | CT |  |  | 16.727 | 16.3495 | 15.9206 | 15.4782 | 14.5605 | 13.5627 | 12.5514 | 11.5061 | 10.4607 | 9.2258 | 5.586 | 1.1789 | -0.51745 | -1.1059 | 19.5855 | 19.334 | 19.0316 | 18.6975 | 18.2005 | 17.6546 | 17.1064 | 16.5369 | 15.9681 | 15.2421 | 13.1233 | 10.5984 | 9.6232 | 8.8953 | 17.6451 | 17.352 | 16.9898 | 16.5867 | 15.7676 | 14.8767 | 13.9745 | 13.0423 | 12.1044 | 10.9686 | 7.6678 | 3.6555 | 2.1597 | 1.6448
| INVERURIE | LW |  |  | 16.6578 | 16.216 | 15.7467 | 15.2664 | 14.2998 | 13.22 | 12.0705 | 10.8204 | 9.5218 | 8.3927 | 5.0004 | 1.428 | 0.39159 | -0.050411 | 19.5816 | 19.3137 | 19.0109 | 18.6855 | 18.1827 | 17.6003 | 16.9762 | 16.2898 | 15.5657 | 14.8784 | 12.8246 | 10.7228 | 10.2928 | 10.1194 | 17.5823 | 17.2309 | 16.8477 | 16.4177 | 15.5577 | 14.5896 | 13.5543 | 12.4247 | 11.239 | 10.1929 | 7.136 | 3.882 | 2.9086 | 2.514
| INVERURIE | ST |  |  | 16.9292 | 16.648 | 16.3282 | 16.0215 | 15.7818 | 15.5295 | 15.2624 | 14.977 | 14.6743 | 14.1942 | 12.4057 | 8.1951 | 6.299 | 5.4717 | 19.7143 | 19.5316 | 19.3118 | 19.0891 | 18.9229 | 18.7375 | 18.5416 | 18.3336 | 18.1177 | 17.7953 | 16.6155 | 13.7435 | 12.3558 | 11.5005 | 17.8281 | 17.6215 | 17.3749 | 17.1209 | 16.9178 | 16.7026 | 16.4732 | 16.2287 | 15.9748 | 15.5559 | 13.9944 | 10.055 | 8.2974 | 7.5686
| INVERURIE | SP |  |  | 16.9871 | 16.7467 | 16.4629 | 16.2029 | 15.9211 | 15.6076 | 15.2812 | 14.9368 | 14.5864 | 14.1399 | 12.6978 | 9.0977 | 6.674 | 6.1459 | 19.7379 | 19.5746 | 19.3707 | 19.1736 | 18.9949 | 18.7923 | 18.5784 | 18.3522 | 18.1137 | 17.8178 | 16.8765 | 14.4369 | 12.2009 | 10.6988 | 17.882 | 17.7129 | 17.4997 | 17.2857 | 17.0472 | 16.7809 | 16.5012 | 16.2063 | 15.8967 | 15.5023 | 14.2458 | 11.0063 | 8.6724 | 8.1781
DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | 2.304 | 2.2533 | 2.2114 | 2.1605 | 2.0397 | 1.9317 | 1.836 | 1.728 | 1.6106 | 1.5504 | 1.3051 | 1.2233 | 1.2936 | 1.2657 | 2.398 | 2.3712 | 2.351 | 2.3258 | 2.2712 | 2.2204 | 2.1746 | 2.1162 | 2.0573 | 2.0184 | 1.8457 | 1.7676 | 1.7889 | 1.7788 | 2.3183 | 2.282 | 2.2404 | 2.1918 | 2.0626 | 1.9511 | 1.8539 | 1.755 | 1.649 | 1.6006 | 1.3895 | 1.3071 | 1.369 | 1.345
| KAMES | CT |  |  | 2.332 | 2.292 | 2.2591 | 2.2104 | 2.0867 | 1.9829 | 1.8852 | 1.7981 | 1.7136 | 1.6632 | 1.492 | 1.2756 | 1.306 | 1.3069 | 2.4097 | 2.3875 | 2.3708 | 2.3433 | 2.2837 | 2.2325 | 2.1835 | 2.1393 | 2.0951 | 2.0617 | 1.9475 | 1.7922 | 1.7952 | 1.7892 | 2.3378 | 2.3306 | 2.304 | 2.2599 | 2.1487 | 2.0476 | 1.9445 | 1.8475 | 1.7548 | 1.7091 | 1.5566 | 1.3554 | 1.3819 | 1.383
| KAMES | LW |  |  | 2.304 | 2.2533 | 2.2114 | 2.1605 | 2.0397 | 1.9317 | 1.836 | 1.728 | 1.6106 | 1.5504 | 1.3051 | 1.2233 | 1.2936 | 1.2657 | 2.398 | 2.3712 | 2.351 | 2.3258 | 2.2712 | 2.2204 | 2.1746 | 2.1162 | 2.0573 | 2.0184 | 1.8457 | 1.7676 | 1.7889 | 1.7788 | 2.3183 | 2.282 | 2.2404 | 2.1918 | 2.0626 | 1.9511 | 1.8539 | 1.755 | 1.649 | 1.6006 | 1.3895 | 1.3071 | 1.369 | 1.345
| KAMES | ST |  |  | 2.3322 | 2.3021 | 2.2891 | 2.2698 | 2.2541 | 2.2377 | 2.221 | 2.2022 | 2.1859 | 2.1537 | 2.0404 | 1.7502 | 1.6464 | 1.6183 | 2.4112 | 2.3943 | 2.3868 | 2.3755 | 2.3653 | 2.3546 | 2.3434 | 2.3313 | 2.3198 | 2.2991 | 2.224 | 2.0158 | 1.9379 | 1.9168 | 2.339 | 2.3344 | 2.3275 | 2.3147 | 2.3005 | 2.2854 | 2.2698 | 2.2523 | 2.2368 | 2.2065 | 2.0989 | 1.8182 | 1.7186 | 1.6933
| KAMES | SP |  |  | 2.3435 | 2.3186 | 2.311 | 2.3024 | 2.2758 | 2.2496 | 2.2246 | 2.1981 | 2.1631 | 2.1123 | 1.9706 | 1.6752 | 1.4013 | 1.3193 | 2.4166 | 2.402 | 2.3968 | 2.3908 | 2.3775 | 2.3642 | 2.3514 | 2.3376 | 2.3174 | 2.2902 | 2.211 | 2.0394 | 1.8516 | 1.805 | 2.3412 | 2.3374 | 2.3365 | 2.3354 | 2.3192 | 2.2938 | 2.2688 | 2.2428 | 2.2157 | 2.1711 | 2.043 | 1.739 | 1.4724 | 1.3992
KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | YES | 7.4877 | 7.4524 | 7.3919 | 7.3122 | 7.1143 | 6.7858 | 6.4813 | 6.0499 | 5.6576 | 5.2126 | 3.803 | 2.1538 | 1.4872 | 1.2619 | 8.6387 | 8.6146 | 8.5776 | 8.5077 | 8.4138 | 8.1629 | 8.0294 | 7.786 | 7.5671 | 7.3186 | 6.4264 | 5.4698 | 5.1071 | 4.8765 | 7.7793 | 7.7524 | 7.7018 | 7.6336 | 7.4606 | 7.1429 | 6.865 | 6.4599 | 6.0965 | 5.6918 | 4.3913 | 2.84 | 2.2156 | 2.0048
| KEITH | CT |  |  | 7.5241 | 7.489 | 7.435 | 7.3185 | 7.1143 | 6.8001 | 6.4813 | 6.0499 | 5.6658 | 5.2993 | 3.8328 | 2.1538 | 1.4872 | 1.2619 | 8.6387 | 8.6146 | 8.5776 | 8.5077 | 8.4138 | 8.1629 | 8.0294 | 7.786 | 7.5671 | 7.3592 | 6.4502 | 5.4698 | 5.1071 | 4.8765 | 7.8135 | 7.7871 | 7.7426 | 7.6423 | 7.4606 | 7.1631 | 6.865 | 6.4599 | 6.1006 | 5.7612 | 4.4055 | 2.84 | 2.2156 | 2.0048
| KEITH | LW |  |  | 7.4877 | 7.4524 | 7.3919 | 7.3122 | 7.1214 | 6.7858 | 6.5533 | 6.156 | 5.6576 | 5.2126 | 3.803 | 2.5382 | 2.0644 | 1.896 | 8.6448 | 8.6193 | 8.578 | 8.5244 | 8.4327 | 8.1676 | 8.041 | 7.8218 | 7.5766 | 7.3186 | 6.4264 | 5.6735 | 5.4735 | 5.4003 | 7.7793 | 7.7524 | 7.7018 | 7.6336 | 7.4621 | 7.1429 | 6.9256 | 6.5586 | 6.0965 | 5.6918 | 4.3913 | 3.2057 | 2.7586 | 2.5997
| KEITH | ST |  |  | 7.5357 | 7.5018 | 7.4682 | 7.4215 | 7.3745 | 7.1903 | 7.1144 | 6.9647 | 6.8521 | 6.7093 | 6.0164 | 4.5391 | 3.9416 | 3.625 | 8.6539 | 8.6397 | 8.6249 | 8.6059 | 8.5814 | 8.3859 | 8.3052 | 8.1463 | 8.0465 | 7.9371 | 7.3748 | 6.4717 | 6.1322 | 5.8574 | 7.8239 | 7.7978 | 7.772 | 7.735 | 7.6995 | 7.5239 | 7.4535 | 7.3116 | 7.2071 | 7.0758 | 6.4313 | 5.0858 | 4.5325 | 4.2346
| KEITH | SP |  |  | 7.5432 | 7.515 | 7.4871 | 7.4557 | 7.3912 | 7.2029 | 7.1171 | 6.9437 | 6.797 | 6.6419 | 6.0026 | 4.7833 | 4.053 | 3.8809 | 8.6548 | 8.6424 | 8.6292 | 8.6144 | 8.5957 | 8.4047 | 8.3296 | 8.1766 | 8.0834 | 8 | 7.5208 | 6.6596 | 6.0497 | 5.6108 | 7.8311 | 7.8103 | 7.7899 | 7.7664 | 7.7138 | 7.5329 | 7.452 | 7.2876 | 7.1524 | 7.0098 | 6.41 | 5.2936 | 4.6377 | 4.4794
KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | YES | 10.4573 | 10.361 | 10.2343 | 10.0919 | 9.8753 | 9.6027 | 9.2844 | 8.9179 | 8.4359 | 7.9587 | 6.926 | 5.8166 | 5.2792 | 5.0912 | 11.1158 | 11.027 | 10.9197 | 10.7963 | 10.6451 | 10.4543 | 10.2208 | 9.9491 | 9.6251 | 9.2687 | 8.5751 | 7.9824 | 7.7133 | 7.5187 | 10.6125 | 10.5201 | 10.4007 | 10.266 | 10.0653 | 9.8116 | 9.5136 | 9.169 | 8.7216 | 8.2713 | 7.3223 | 6.3178 | 5.863 | 5.7062
| KEMNAY | CT |  |  | 10.4864 | 10.395 | 10.2704 | 10.1206 | 9.9088 | 9.6593 | 9.3268 | 8.9442 | 8.548 | 8.0891 | 6.926 | 5.8166 | 5.2792 | 5.0912 | 11.1224 | 11.0345 | 10.9238 | 10.7963 | 10.6451 | 10.4607 | 10.2384 | 9.9849 | 9.7203 | 9.3841 | 8.5923 | 7.9824 | 7.7133 | 7.5187 | 10.6368 | 10.5492 | 10.4308 | 10.2883 | 10.0916 | 9.8596 | 9.555 | 9.2069 | 8.8474 | 8.4135 | 7.3223 | 6.3178 | 5.863 | 5.7062
| KEMNAY | LW |  |  | 10.4573 | 10.361 | 10.2343 | 10.0919 | 9.8753 | 9.6027 | 9.2844 | 8.9179 | 8.4359 | 7.9587 | 6.9515 | 6.1425 | 5.7616 | 5.6332 | 11.1158 | 11.027 | 10.9197 | 10.8014 | 10.6509 | 10.4543 | 10.2208 | 9.9491 | 9.6251 | 9.2687 | 8.5751 | 8.1382 | 7.9968 | 7.9481 | 10.6125 | 10.5201 | 10.4007 | 10.266 | 10.0653 | 9.8116 | 9.5136 | 9.169 | 8.7216 | 8.2713 | 7.3299 | 6.5959 | 6.2633 | 6.152
| KEMNAY | ST |  |  | 10.5022 | 10.4123 | 10.3084 | 10.2025 | 10.0939 | 9.943 | 9.7798 | 9.6002 | 9.395 | 9.1332 | 8.5336 | 7.5852 | 7.2007 | 6.9643 | 11.1376 | 11.0564 | 10.962 | 10.8641 | 10.7634 | 10.625 | 10.4758 | 10.3099 | 10.1259 | 9.8971 | 9.3872 | 8.671 | 8.4211 | 8.2063 | 10.6537 | 10.5699 | 10.4728 | 10.3726 | 10.27 | 10.1273 | 9.974 | 9.8043 | 9.6116 | 9.3635 | 8.7862 | 7.8781 | 7.5335 | 7.3277
| KEMNAY | SP |  |  | 10.5072 | 10.4187 | 10.3179 | 10.2137 | 10.0839 | 9.921 | 9.7366 | 9.5301 | 9.3073 | 9.0387 | 8.4961 | 7.6704 | 7.2623 | 7.1777 | 11.1411 | 11.0611 | 10.9688 | 10.8731 | 10.7649 | 10.6255 | 10.4686 | 10.2919 | 10.1 | 9.8721 | 9.417 | 8.7496 | 8.3134 | 7.974 | 10.659 | 10.5767 | 10.4829 | 10.3851 | 10.2647 | 10.1139 | 9.9429 | 9.7501 | 9.5417 | 9.2912 | 8.7792 | 7.9774 | 7.5857 | 7.5106
TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | 0.3661 | 0.36644 | 0.36426 | 0.36136 | 0.35182 | 0.3414 | 0.33125 | 0.31914 | 0.29979 | 0.28694 | 0.23922 | 0.22822 | 0.22342 | 0.2131 | 0.3943 | 0.39414 | 0.39273 | 0.3909 | 0.38561 | 0.37966 | 0.37379 | 0.36659 | 0.35621 | 0.3487 | 0.31724 | 0.31223 | 0.30911 | 0.30276 | 0.35155 | 0.35225 | 0.34995 | 0.34689 | 0.33632 | 0.32513 | 0.31424 | 0.30182 | 0.28225 | 0.27026 | 0.22501 | 0.2151 | 0.21121 | 0.20216
| KENMORE | CT |  |  | 0.37198 | 0.37274 | 0.37143 | 0.36758 | 0.35709 | 0.34678 | 0.33347 | 0.32051 | 0.30626 | 0.29643 | 0.25283 | 0.23532 | 0.23131 | 0.22782 | 0.39724 | 0.3973 | 0.39625 | 0.39364 | 0.3877 | 0.38175 | 0.37438 | 0.36729 | 0.3597 | 0.35388 | 0.32415 | 0.31562 | 0.31317 | 0.31023 | 0.3581 | 0.35801 | 0.35713 | 0.35508 | 0.34368 | 0.33267 | 0.31788 | 0.30317 | 0.28832 | 0.27914 | 0.23796 | 0.22177 | 0.21829 | 0.21526
| KENMORE | LW |  |  | 0.3661 | 0.36644 | 0.36426 | 0.36136 | 0.35182 | 0.3414 | 0.33125 | 0.31914 | 0.29979 | 0.28694 | 0.23922 | 0.22822 | 0.2342 | 0.23219 | 0.3943 | 0.39414 | 0.39273 | 0.3909 | 0.38561 | 0.37966 | 0.37379 | 0.36659 | 0.35621 | 0.3487 | 0.31724 | 0.31223 | 0.31422 | 0.31351 | 0.35155 | 0.35225 | 0.34995 | 0.34689 | 0.33632 | 0.32513 | 0.31424 | 0.30182 | 0.28225 | 0.27026 | 0.22501 | 0.2151 | 0.22036 | 0.21864
| KENMORE | ST |  |  | 0.3704 | 0.36955 | 0.3688 | 0.36791 | 0.36684 | 0.36573 | 0.36378 | 0.36133 | 0.35836 | 0.35269 | 0.33275 | 0.27759 | 0.26467 | 0.25797 | 0.39665 | 0.39607 | 0.39552 | 0.39478 | 0.39394 | 0.3931 | 0.39172 | 0.38993 | 0.38804 | 0.38447 | 0.37172 | 0.33332 | 0.32547 | 0.32058 | 0.35642 | 0.35555 | 0.35477 | 0.35414 | 0.35322 | 0.35212 | 0.35033 | 0.34825 | 0.34505 | 0.33929 | 0.31943 | 0.26662 | 0.25155 | 0.2435
| KENMORE | SP |  |  | 0.37142 | 0.37069 | 0.36958 | 0.36903 | 0.36461 | 0.36094 | 0.35657 | 0.35177 | 0.34562 | 0.33756 | 0.31631 | 0.26098 | 0.22342 | 0.2131 | 0.39732 | 0.39685 | 0.39608 | 0.39565 | 0.39318 | 0.39115 | 0.38871 | 0.38597 | 0.38234 | 0.37772 | 0.36533 | 0.33429 | 0.30911 | 0.30276 | 0.35719 | 0.35636 | 0.35528 | 0.35466 | 0.34973 | 0.34552 | 0.3406 | 0.33526 | 0.32885 | 0.32015 | 0.29771 | 0.2466 | 0.21121 | 0.20216
STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | YES | 2.9248 | 4.5841 | 4.5271 | 4.4501 | 4.2564 | 4.0107 | 3.7615 | 3.5084 | 3.2239 | 2.9653 | 2.389 | 1.8943 | 1.6442 | 1.5474 | 4.3052 | 5.9714 | 5.9345 | 5.8839 | 5.7788 | 5.6538 | 5.5244 | 5.3876 | 5.2317 | 5.0587 | 4.6998 | 4.4199 | 4.273 | 4.151 | 3.3252 | 4.9843 | 4.9252 | 4.8464 | 4.6498 | 4.4251 | 4.1965 | 3.9629 | 3.6998 | 3.4521 | 2.9077 | 2.4609 | 2.2407 | 2.1562
| KEPCULLOCH | CT |  |  | 2.9705 | 4.6336 | 4.5836 | 4.5017 | 4.3041 | 4.1141 | 3.892 | 3.6782 | 3.4662 | 3.2608 | 2.5477 | 1.8943 | 1.6442 | 1.5474 | 4.3239 | 5.9899 | 5.9536 | 5.8954 | 5.7826 | 5.68 | 5.5689 | 5.4631 | 5.3562 | 5.2309 | 4.7768 | 4.4199 | 4.273 | 4.151 | 3.3785 | 5.0437 | 4.9944 | 4.914 | 4.7055 | 4.5145 | 4.3124 | 4.1182 | 3.9252 | 3.7323 | 3.0575 | 2.4609 | 2.2407 | 2.1562
| KEPCULLOCH | LW |  |  | 2.9248 | 4.5841 | 4.5271 | 4.4501 | 4.2564 | 4.0107 | 3.7615 | 3.5084 | 3.2239 | 2.9653 | 2.389 | 1.9658 | 1.8548 | 1.7774 | 4.3052 | 5.9714 | 5.9345 | 5.8839 | 5.7788 | 5.6538 | 5.5244 | 5.3876 | 5.2317 | 5.0587 | 4.6998 | 4.4639 | 4.4221 | 4.3932 | 3.3252 | 4.9843 | 4.9252 | 4.8464 | 4.6498 | 4.4251 | 4.1965 | 3.9629 | 3.6998 | 3.4521 | 2.9077 | 2.5161 | 2.419 | 2.3516
| KEPCULLOCH | ST |  |  | 2.9862 | 4.6616 | 4.6477 | 4.6263 | 4.6109 | 4.5845 | 4.5598 | 4.5326 | 4.4904 | 4.4175 | 4.1272 | 3.3316 | 3.0564 | 2.8963 | 4.3399 | 6.0189 | 6.008 | 5.9898 | 5.9757 | 5.9537 | 5.9329 | 5.9094 | 5.8764 | 5.8242 | 5.6121 | 5.0237 | 4.8362 | 4.6911 | 3.3918 | 5.0668 | 5.0525 | 5.0318 | 5.016 | 4.9894 | 4.9642 | 4.9367 | 4.894 | 4.8206 | 4.5324 | 3.7504 | 3.4908 | 3.3508
| KEPCULLOCH | SP |  |  | 2.9963 | 4.6758 | 4.6643 | 4.6514 | 4.6009 | 4.5515 | 4.4973 | 4.4329 | 4.3591 | 4.2526 | 3.9698 | 3.1692 | 2.7264 | 2.6275 | 4.3457 | 6.0272 | 6.017 | 6.0055 | 5.9749 | 5.9442 | 5.9106 | 5.8694 | 5.8204 | 5.7598 | 5.5892 | 5.0371 | 4.64 | 4.4072 | 3.4013 | 5.08 | 5.0682 | 5.055 | 5.0009 | 4.9481 | 4.8904 | 4.8231 | 4.747 | 4.6466 | 4.3848 | 3.6251 | 3.2003 | 3.1116
TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385
| KERRERA | CT |  |  | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385
| KERRERA | LW |  |  | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385
| KERRERA | ST |  |  | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385
| KERRERA | SP |  |  | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26862 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.26927 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385
GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | 5.3478 | 5.3524 | 5.3266 | 5.2906 | 5.1831 | 5.0644 | 4.946 | 4.8094 | 4.6217 | 4.5239 | 4.1486 | 4.0642 | 4.061 | 3.969 | 5.3501 | 5.3487 | 5.3358 | 5.3176 | 5.2717 | 5.2175 | 5.1556 | 5.0858 | 4.9998 | 4.9416 | 4.6798 | 4.6282 | 4.6129 | 4.5539 | 3.4647 | 3.4643 | 3.4619 | 3.4586 | 3.4367 | 3.3396 | 3.2452 | 3.1361 | 2.9729 | 2.8934 | 2.5973 | 2.5201 | 2.5205 | 2.443
| KERRY FALLS | CT |  |  | 5.4014 | 5.4114 | 5.3955 | 5.3499 | 5.2371 | 5.1279 | 4.9736 | 4.8159 | 4.6736 | 4.5979 | 4.2962 | 4.1131 | 4.1286 | 4.1222 | 5.3681 | 5.3683 | 5.3575 | 5.3304 | 5.2776 | 5.2252 | 5.1556 | 5.0858 | 5.0222 | 4.9772 | 4.7673 | 4.6438 | 4.6387 | 4.6224 | 3.4691 | 3.4695 | 3.4681 | 3.4642 | 3.4547 | 3.4086 | 3.2778 | 3.1396 | 3.0137 | 2.9518 | 2.715 | 2.5637 | 2.5727 | 2.5662
| KERRY FALLS | LW |  |  | 5.3478 | 5.3524 | 5.3266 | 5.2906 | 5.1831 | 5.0644 | 4.946 | 4.8094 | 4.6217 | 4.5239 | 4.1486 | 4.0642 | 4.1237 | 4.0927 | 5.3501 | 5.3487 | 5.3358 | 5.3176 | 5.2717 | 5.2175 | 5.1616 | 5.0898 | 4.9998 | 4.9416 | 4.6798 | 4.6282 | 4.6482 | 4.6378 | 3.4647 | 3.4643 | 3.4619 | 3.4586 | 3.4367 | 3.3396 | 3.2452 | 3.1361 | 2.9729 | 2.8934 | 2.5973 | 2.5201 | 2.5682 | 2.5438
| KERRY FALLS | ST |  |  | 5.3878 | 5.3811 | 5.3743 | 5.3647 | 5.358 | 5.3388 | 5.3189 | 5.2979 | 5.2675 | 5.2186 | 5.0495 | 4.6142 | 4.4813 | 4.427 | 5.3667 | 5.3629 | 5.3586 | 5.3508 | 5.3445 | 5.3313 | 5.318 | 5.3023 | 5.2844 | 5.2566 | 5.1516 | 4.8323 | 4.758 | 4.7247 | 3.4684 | 3.4676 | 3.4668 | 3.4656 | 3.4641 | 3.4604 | 3.4568 | 3.4528 | 3.449 | 3.4437 | 3.3706 | 2.984 | 2.8633 | 2.8159
| KERRY FALLS | SP |  |  | 5.3916 | 5.3853 | 5.3815 | 5.3777 | 5.3397 | 5.2959 | 5.2482 | 5.1959 | 5.1403 | 5.061 | 4.8508 | 4.3944 | 4.061 | 3.969 | 5.3683 | 5.3647 | 5.3616 | 5.3585 | 5.3423 | 5.3219 | 5.2998 | 5.2751 | 5.2466 | 5.2082 | 5.1031 | 4.8518 | 4.6129 | 4.5539 | 3.4685 | 3.4677 | 3.4669 | 3.4662 | 3.4628 | 3.4577 | 3.4523 | 3.4465 | 3.4165 | 3.3539 | 3.1813 | 2.7939 | 2.5205 | 2.443
TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | 0.57899 | 0.57091 | 0.56083 | 0.54455 | 0.51977 | 0.48388 | 0.42365 | 0.37383 | 0.31644 | 0.26899 | 0.16424 | 0.091679 | 0.10923 | 0.095174 | 0.57526 | 0.56871 | 0.56072 | 0.54448 | 0.52039 | 0.49196 | 0.4608 | 0.4331 | 0.40231 | 0.36246 | 0.28062 | 0.26048 | 0.26273 | 0.25194 | 0.54175 | 0.53225 | 0.51913 | 0.49514 | 0.45157 | 0.3965 | 0.3391 | 0.28619 | 0.22623 | 0.16942 | 0.044957 | 0.011629 | 0.028753 | 0.012469
| KILCHRENAN | CT |  |  | 0.57899 | 0.57091 | 0.56083 | 0.54455 | 0.51977 | 0.48388 | 0.4548 | 0.40247 | 0.35074 | 0.32095 | 0.22023 | 0.12959 | 0.11914 | 0.10887 | 0.57715 | 0.57153 | 0.56131 | 0.54695 | 0.52217 | 0.49714 | 0.4743 | 0.45148 | 0.42699 | 0.40433 | 0.29866 | 0.26865 | 0.26273 | 0.2542 | 0.54947 | 0.54296 | 0.52904 | 0.5087 | 0.46666 | 0.42255 | 0.37378 | 0.32439 | 0.27443 | 0.23977 | 0.093133 | 0.036139 | 0.030509 | 0.022911
| KILCHRENAN | LW |  |  | 0.58222 | 0.57476 | 0.56665 | 0.55052 | 0.52659 | 0.48442 | 0.42365 | 0.37383 | 0.31644 | 0.26899 | 0.16424 | 0.091679 | 0.10923 | 0.10052 | 0.57526 | 0.56871 | 0.56072 | 0.54448 | 0.52039 | 0.49196 | 0.4608 | 0.4331 | 0.40231 | 0.36246 | 0.28062 | 0.26048 | 0.26704 | 0.26272 | 0.54175 | 0.53225 | 0.51913 | 0.49514 | 0.45157 | 0.3965 | 0.3391 | 0.28619 | 0.22623 | 0.16942 | 0.044957 | 0.011629 | 0.028753 | 0.020294
| KILCHRENAN | ST |  |  | 0.58987 | 0.58776 | 0.58515 | 0.58208 | 0.57847 | 0.57354 | 0.56812 | 0.56178 | 0.54673 | 0.53467 | 0.47779 | 0.31792 | 0.20895 | 0.17381 | 0.58298 | 0.58065 | 0.57757 | 0.5737 | 0.57045 | 0.56478 | 0.55908 | 0.5527 | 0.54554 | 0.5317 | 0.47982 | 0.34116 | 0.30278 | 0.2861 | 0.5552 | 0.55179 | 0.54751 | 0.54233 | 0.53797 | 0.53047 | 0.52285 | 0.51443 | 0.50381 | 0.4837 | 0.4107 | 0.21438 | 0.14345 | 0.11466
| KILCHRENAN | SP |  |  | 0.59083 | 0.58963 | 0.5883 | 0.58663 | 0.5838 | 0.58121 | 0.57732 | 0.5731 | 0.56081 | 0.55388 | 0.48011 | 0.30503 | 0.15521 | 0.095174 | 0.58336 | 0.58177 | 0.57983 | 0.57767 | 0.57162 | 0.56673 | 0.55821 | 0.54969 | 0.54094 | 0.52947 | 0.49309 | 0.37237 | 0.2834 | 0.25194 | 0.5564 | 0.5542 | 0.55179 | 0.54914 | 0.53888 | 0.53022 | 0.5169 | 0.50332 | 0.48938 | 0.47017 | 0.3993 | 0.2013 | 0.061666 | 0.012469
STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | 2.8771 | 2.8627 | 2.821 | 2.7673 | 2.6401 | 2.4728 | 2.3053 | 2.1773 | 2.0039 | 1.8794 | 1.5697 | 1.1751 | 0.92937 | 0.83653 | 3.5963 | 3.5791 | 3.5514 | 3.5158 | 3.4466 | 3.3437 | 3.2399 | 3.1694 | 3.0747 | 3.0027 | 2.8127 | 2.625 | 2.4628 | 2.2963 | 3.2258 | 3.2078 | 3.1696 | 3.1203 | 3.0129 | 2.8628 | 2.7118 | 2.6032 | 2.4562 | 2.3481 | 2.0892 | 1.7877 | 1.5951 | 1.522
| KILLEARN | CT |  |  | 2.9202 | 2.9103 | 2.8757 | 2.8298 | 2.7227 | 2.6153 | 2.496 | 2.3685 | 2.2399 | 2.0803 | 1.58 | 1.1751 | 0.92937 | 0.83653 | 3.6036 | 3.5863 | 3.5567 | 3.5213 | 3.4668 | 3.4101 | 3.351 | 3.2876 | 3.224 | 3.1266 | 2.8127 | 2.625 | 2.4628 | 2.2963 | 3.2523 | 3.2376 | 3.2028 | 3.1589 | 3.0731 | 2.9859 | 2.8914 | 2.7903 | 2.6891 | 2.5484 | 2.1009 | 1.7877 | 1.5951 | 1.522
| KILLEARN | LW |  |  | 2.8771 | 2.8627 | 2.821 | 2.7673 | 2.6401 | 2.4728 | 2.3053 | 2.1773 | 2.0039 | 1.8794 | 1.5697 | 1.3025 | 1.1493 | 1.0921 | 3.5963 | 3.5791 | 3.5514 | 3.5158 | 3.4466 | 3.3437 | 3.2399 | 3.1694 | 3.0747 | 3.0027 | 2.8371 | 2.7333 | 2.6809 | 2.6602 | 3.2258 | 3.2078 | 3.1696 | 3.1203 | 3.0129 | 2.8628 | 2.7118 | 2.6032 | 2.4562 | 2.3481 | 2.0892 | 1.8832 | 1.7622 | 1.7164
| KILLEARN | ST |  |  | 2.9297 | 2.9113 | 2.8927 | 2.8789 | 2.8606 | 2.8372 | 2.8109 | 2.7885 | 2.7574 | 2.7022 | 2.4947 | 2.012 | 1.8204 | 1.684 | 3.6196 | 3.6058 | 3.5914 | 3.5775 | 3.5623 | 3.5442 | 3.5237 | 3.5042 | 3.4798 | 3.4402 | 3.281 | 2.9145 | 2.7654 | 2.5876 | 3.2678 | 3.2514 | 3.2347 | 3.2206 | 3.2037 | 3.1825 | 3.1584 | 3.1374 | 3.109 | 3.0583 | 2.858 | 2.4009 | 2.2552 | 2.1508
| KILLEARN | SP |  |  | 2.9199 | 2.8997 | 2.8813 | 2.8605 | 2.8075 | 2.7516 | 2.6924 | 2.629 | 2.5683 | 2.4939 | 2.3429 | 1.8252 | 1.7064 | 1.68 | 3.6128 | 3.5988 | 3.5848 | 3.5686 | 3.5407 | 3.5087 | 3.4758 | 3.4393 | 3.4038 | 3.3642 | 3.2609 | 2.8445 | 2.6317 | 2.3658 | 3.2587 | 3.2414 | 3.2254 | 3.2069 | 3.1646 | 3.1181 | 3.0698 | 3.0171 | 2.967 | 2.9085 | 2.7798 | 2.2837 | 2.1733 | 2.1529
KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | 1.807 | 1.8055 | 1.8038 | 1.8019 | 1.797 | 1.756 | 1.6744 | 1.5968 | 1.4843 | 1.4253 | 1.2223 | 1.1441 | 1.2056 | 1.1517 | 2.185 | 2.1668 | 2.1501 | 2.132 | 2.0861 | 2.0431 | 1.9997 | 1.9486 | 1.8826 | 1.8382 | 1.6929 | 1.6202 | 1.6294 | 1.5708 | 1.9738 | 1.9724 | 1.9708 | 1.9689 | 1.9109 | 1.8293 | 1.748 | 1.659 | 1.5425 | 1.4744 | 1.2502 | 1.1518 | 1.1986 | 1.1735
| KILLIN TOWN | CT |  |  | 1.807 | 1.8055 | 1.8038 | 1.8019 | 1.797 | 1.7924 | 1.7348 | 1.6419 | 1.5537 | 1.5037 | 1.3272 | 1.1792 | 1.2056 | 1.2051 | 2.185 | 2.1719 | 2.1567 | 2.1389 | 2.0942 | 2.0515 | 2.005 | 1.9593 | 1.9142 | 1.8744 | 1.743 | 1.6323 | 1.6294 | 1.6137 | 1.9738 | 1.9724 | 1.9708 | 1.9689 | 1.9456 | 1.8673 | 1.7791 | 1.6936 | 1.6111 | 1.5498 | 1.349 | 1.1856 | 1.1986 | 1.1956
| KILLIN TOWN | LW |  |  | 1.808 | 1.8061 | 1.8046 | 1.8029 | 1.7975 | 1.756 | 1.6744 | 1.5968 | 1.4843 | 1.4253 | 1.2223 | 1.1441 | 1.208 | 1.1819 | 2.1861 | 2.1668 | 2.1501 | 2.132 | 2.0861 | 2.0431 | 1.9997 | 1.9486 | 1.8826 | 1.8382 | 1.6929 | 1.6202 | 1.6414 | 1.6314 | 1.9747 | 1.9729 | 1.9716 | 1.97 | 1.9109 | 1.8293 | 1.748 | 1.659 | 1.5425 | 1.4744 | 1.2502 | 1.1518 | 1.1998 | 1.1802
| KILLIN TOWN | ST |  |  | 1.8079 | 1.8075 | 1.8072 | 1.8064 | 1.8059 | 1.8057 | 1.8048 | 1.8038 | 1.8027 | 1.8004 | 1.7922 | 1.5952 | 1.4587 | 1.4116 | 2.1919 | 2.1875 | 2.1831 | 2.1746 | 2.1667 | 2.1596 | 2.1481 | 2.1355 | 2.1213 | 2.0991 | 2.0189 | 1.8148 | 1.7393 | 1.7075 | 1.9746 | 1.9743 | 1.9739 | 1.9731 | 1.9727 | 1.9724 | 1.9715 | 1.9705 | 1.9693 | 1.9671 | 1.8537 | 1.5549 | 1.4443 | 1.4015
| KILLIN TOWN | SP |  |  | 1.8088 | 1.8089 | 1.8091 | 1.8092 | 1.8089 | 1.8087 | 1.8079 | 1.8074 | 1.8063 | 1.8044 | 1.7959 | 1.5516 | 1.2753 | 1.1517 | 2.1966 | 2.1952 | 2.1943 | 2.1922 | 2.1855 | 2.1791 | 2.1686 | 2.1608 | 2.1464 | 2.1276 | 2.0475 | 1.8438 | 1.6528 | 1.5708 | 1.9754 | 1.9754 | 1.9756 | 1.9756 | 1.9753 | 1.9751 | 1.9743 | 1.9738 | 1.9726 | 1.9709 | 1.8886 | 1.5549 | 1.2706 | 1.1735
TAYNUILT | KILMELFORD PS | MINIMUM HEADROOM | NM 84056 14437 | YES | 0.86123 | 0.84988 | 0.83297 | 0.80846 | 0.77132 | 0.72832 | 0.65854 | 0.57294 | 0.48298 | 0.43524 | 0.22762 | 0.17573 | 0.21099 | 0.16651 | 0.64307 | 0.6415 | 0.63917 | 0.6359 | 0.63359 | 0.6314 | 0.62346 | 0.59578 | 0.56351 | 0.55048 | 0.50891 | 0.49556 | 0.51279 | 0.49275 | 0.5355 | 0.53087 | 0.52511 | 0.51221 | 0.44658 | 0.37518 | 0.30374 | 0.22887 | 0.1435 | 0.10483 | -0.046285 | -0.089631 | -0.046251 | -0.09596
| KILMELFORD PS | CT |  |  | 0.86809 | 0.86264 | 0.84896 | 0.82477 | 0.7884 | 0.75161 | 0.70595 | 0.63236 | 0.56074 | 0.51522 | 0.32692 | 0.23133 | 0.23147 | 0.22465 | 0.64307 | 0.6415 | 0.63917 | 0.6359 | 0.63359 | 0.6314 | 0.62908 | 0.61291 | 0.58617 | 0.57503 | 0.54101 | 0.51645 | 0.52344 | 0.52308 | 0.5355 | 0.53087 | 0.52511 | 0.51516 | 0.48316 | 0.42264 | 0.34872 | 0.27504 | 0.20568 | 0.17304 | 0.047113 | -0.034182 | -0.018163 | -0.019349
| KILMELFORD PS | LW |  |  | 0.86123 | 0.84988 | 0.83297 | 0.80846 | 0.77132 | 0.72832 | 0.65854 | 0.57294 | 0.48298 | 0.43524 | 0.22762 | 0.17573 | 0.21099 | 0.19864 | 0.64326 | 0.64188 | 0.63972 | 0.63688 | 0.63453 | 0.63193 | 0.62346 | 0.59578 | 0.56351 | 0.55048 | 0.50891 | 0.49556 | 0.51279 | 0.50614 | 0.53612 | 0.53214 | 0.52692 | 0.51221 | 0.44658 | 0.37518 | 0.30374 | 0.22887 | 0.1435 | 0.10483 | -0.046285 | -0.089631 | -0.046251 | -0.062894
| KILMELFORD PS | ST |  |  | 0.86903 | 0.86535 | 0.85484 | 0.84467 | 0.83651 | 0.82853 | 0.81709 | 0.80698 | 0.79595 | 0.77569 | 0.70824 | 0.50894 | 0.44604 | 0.41646 | 0.64344 | 0.64235 | 0.64031 | 0.63826 | 0.63688 | 0.63576 | 0.6343 | 0.63331 | 0.63247 | 0.63095 | 0.62586 | 0.6097 | 0.60849 | 0.6083 | 0.53729 | 0.53491 | 0.53025 | 0.52552 | 0.52192 | 0.51862 | 0.51374 | 0.50963 | 0.50642 | 0.50001 | 0.44572 | 0.28378 | 0.22954 | 0.20375
| KILMELFORD PS | SP |  |  | 0.86912 | 0.86751 | 0.85987 | 0.85044 | 0.83794 | 0.82565 | 0.81315 | 0.79909 | 0.77989 | 0.76214 | 0.69536 | 0.43021 | 0.22972 | 0.16651 | 0.64354 | 0.64252 | 0.64068 | 0.6387 | 0.63732 | 0.63613 | 0.63496 | 0.63399 | 0.63256 | 0.6316 | 0.62805 | 0.57106 | 0.51877 | 0.49275 | 0.53738 | 0.53516 | 0.53114 | 0.52653 | 0.52327 | 0.51998 | 0.51683 | 0.5132 | 0.4962 | 0.4694 | 0.37107 | 0.14166 | -0.028787 | -0.09596
TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | 0.99288 | 0.98546 | 0.97211 | 0.94951 | 0.89507 | 1.141 | 1.0587 | 0.96864 | 0.86859 | 0.78541 | 0.49798 | 0.40755 | 0.43827 | 0.40648 | 1.5998 | 1.5944 | 1.5864 | 1.5672 | 1.5367 | 2.0332 | 1.9897 | 1.9433 | 1.8869 | 1.8303 | 1.6287 | 1.5624 | 1.5739 | 1.5458 | 1.1695 | 1.1659 | 1.1591 | 1.1454 | 1.1274 | 1.6067 | 1.5295 | 1.4411 | 1.3399 | 1.258 | 0.97545 | 0.88352 | 0.91274 | 0.88128
| KILNINVER | CT |  |  | 0.99909 | 0.99455 | 0.98162 | 0.94951 | 0.89507 | 1.1436 | 1.0587 | 0.96864 | 0.8827 | 0.82653 | 0.57823 | 0.44603 | 0.46245 | 0.46388 | 1.6017 | 1.5977 | 1.589 | 1.5672 | 1.5367 | 2.0332 | 1.9897 | 1.9433 | 1.8976 | 1.8597 | 1.6824 | 1.5851 | 1.582 | 1.5728 | 1.1695 | 1.1659 | 1.1591 | 1.1454 | 1.1274 | 1.6127 | 1.5295 | 1.4411 | 1.3566 | 1.3011 | 1.0578 | 0.9238 | 0.93401 | 0.93292
| KILNINVER | LW |  |  | 0.99288 | 0.98546 | 0.97211 | 0.95167 | 0.89937 | 1.141 | 1.078 | 0.99063 | 0.86859 | 0.78541 | 0.49798 | 0.40755 | 0.43827 | 0.41917 | 1.5998 | 1.5944 | 1.5864 | 1.5736 | 1.5469 | 2.0414 | 2.0071 | 1.954 | 1.8869 | 1.8303 | 1.6287 | 1.5624 | 1.5739 | 1.5661 | 1.1736 | 1.1716 | 1.1672 | 1.16 | 1.1393 | 1.6067 | 1.5447 | 1.4591 | 1.3399 | 1.258 | 0.97545 | 0.88352 | 0.91274 | 0.89546
| KILNINVER | ST |  |  | 1.001 | 0.99599 | 0.99106 | 0.9816 | 0.97665 | 1.269 | 1.2622 | 1.2534 | 1.2324 | 1.199 | 1.0783 | 0.74478 | 0.68071 | 0.65625 | 1.605 | 1.6013 | 1.5975 | 1.5905 | 1.5851 | 2.1028 | 2.0963 | 2.0882 | 2.0737 | 2.0515 | 1.9683 | 1.7197 | 1.674 | 1.6523 | 1.1733 | 1.1719 | 1.1702 | 1.1669 | 1.167 | 1.6911 | 1.6901 | 1.6885 | 1.6826 | 1.6627 | 1.5431 | 1.213 | 1.1434 | 1.1162
| KILNINVER | SP |  |  | 1.0077 | 1.0072 | 1.0056 | 1.0037 | 0.99566 | 1.2872 | 1.2777 | 1.2627 | 1.2384 | 1.2099 | 1.083 | 0.76338 | 0.48036 | 0.40648 | 1.608 | 1.6067 | 1.6042 | 1.6014 | 1.5961 | 2.1153 | 2.1087 | 2.0985 | 2.0814 | 2.0635 | 1.9886 | 1.7877 | 1.5945 | 1.5458 | 1.1766 | 1.177 | 1.1775 | 1.1774 | 1.177 | 1.7013 | 1.7005 | 1.6974 | 1.6919 | 1.6725 | 1.5472 | 1.2333 | 0.9551 | 0.88128
BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | 5.5352 | 5.5274 | 5.5047 | 5.4768 | 5.3793 | 5.2723 | 5.1358 | 4.9947 | 4.8006 | 4.6552 | 4.378 | 4.2815 | 4.29 | 4.1755 | 5.9863 | 5.9772 | 5.9622 | 5.9406 | 5.8927 | 5.8411 | 5.7672 | 5.6899 | 5.5916 | 5.4969 | 5.3362 | 5.2823 | 5.2595 | 5.1816 | 5.3246 | 5.3132 | 5.2882 | 5.2535 | 5.1619 | 5.0648 | 4.941 | 4.8128 | 4.6379 | 4.4998 | 4.2421 | 4.1533 | 4.1623 | 4.0616
| KILTARLITY | CT |  |  | 5.5755 | 5.5793 | 5.5703 | 5.5421 | 5.4466 | 5.3588 | 5.219 | 5.0689 | 4.9268 | 4.8168 | 4.5252 | 4.3611 | 4.3365 | 4.3129 | 5.9989 | 5.9932 | 5.9793 | 5.9543 | 5.9076 | 5.8655 | 5.8017 | 5.7322 | 5.665 | 5.593 | 5.4043 | 5.3113 | 5.2903 | 5.2629 | 5.3583 | 5.356 | 5.3387 | 5.3054 | 5.2187 | 5.1392 | 5.0157 | 4.8827 | 4.7568 | 4.6525 | 4.3762 | 4.2258 | 4.2043 | 4.184
| KILTARLITY | LW |  |  | 5.5352 | 5.5274 | 5.5047 | 5.4768 | 5.3793 | 5.2723 | 5.1358 | 4.9947 | 4.8006 | 4.6552 | 4.378 | 4.2815 | 4.3324 | 4.315 | 5.9863 | 5.9772 | 5.9622 | 5.9406 | 5.8927 | 5.8411 | 5.7672 | 5.6899 | 5.5916 | 5.4969 | 5.3362 | 5.2823 | 5.3008 | 5.2941 | 5.3246 | 5.3132 | 5.2882 | 5.2535 | 5.1619 | 5.0648 | 4.941 | 4.8128 | 4.6379 | 4.4998 | 4.2421 | 4.1533 | 4.1982 | 4.1832
| KILTARLITY | ST |  |  | 5.5651 | 5.5582 | 5.5512 | 5.547 | 5.5409 | 5.5323 | 5.5112 | 5.4871 | 5.4458 | 5.3937 | 5.2051 | 4.792 | 4.6509 | 4.5834 | 6.001 | 5.9947 | 5.9884 | 5.9816 | 5.9744 | 5.9635 | 5.9453 | 5.9288 | 5.9049 | 5.8746 | 5.7565 | 5.4788 | 5.4066 | 5.363 | 5.3538 | 5.3446 | 5.3357 | 5.3277 | 5.3189 | 5.3048 | 5.2815 | 5.2608 | 5.2249 | 5.1769 | 4.9999 | 4.6059 | 4.4802 | 4.4213
| KILTARLITY | SP |  |  | 5.5693 | 5.5643 | 5.5598 | 5.5556 | 5.5296 | 5.5048 | 5.4736 | 5.427 | 5.3698 | 5.3093 | 5.1067 | 4.5632 | 4.29 | 4.1755 | 6.0054 | 6.0017 | 5.9954 | 5.99 | 5.9749 | 5.9603 | 5.9381 | 5.9135 | 5.8806 | 5.8496 | 5.7466 | 5.421 | 5.2595 | 5.1816 | 5.361 | 5.3557 | 5.348 | 5.3415 | 5.3136 | 5.2871 | 5.2504 | 5.2101 | 5.1593 | 5.1048 | 4.9212 | 4.4132 | 4.1623 | 4.0616
REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | 3.8154 | 3.5654 | 3.4011 | 3.3131 | 2.7534 | 2.1265 | 1.3245 | 0.47853 | -0.3169 | -0.97797 | -3.1102 | -5.9372 | -7.4124 | -8.0501 | 5.8628 | 5.7548 | 5.6761 | 5.6217 | 5.2933 | 4.9086 | 4.3273 | 3.7694 | 3.2074 | 2.7816 | 1.4305 | -0.09791 | -0.93602 | -1.6063 | 4.6681 | 4.4597 | 4.3224 | 4.238 | 3.7429 | 3.1867 | 2.47 | 1.6925 | 0.953 | 0.321 | -1.7222 | -4.2326 | -5.4617 | -5.9677
| KINCORTH | CT |  |  | 3.8641 | 3.6773 | 3.5789 | 3.5066 | 2.946 | 2.2868 | 1.5503 | 0.84639 | 0.099312 | -0.62156 | -2.8855 | -5.9372 | -7.4124 | -8.0501 | 5.8752 | 5.7879 | 5.7297 | 5.6776 | 5.3451 | 4.9456 | 4.3876 | 3.8821 | 3.3388 | 2.8936 | 1.5195 | -0.09791 | -0.93602 | -1.6063 | 4.7078 | 4.5519 | 4.4682 | 4.389 | 3.8866 | 3.2975 | 2.6347 | 1.9903 | 1.3069 | 0.64047 | -1.4578 | -4.2326 | -5.4617 | -5.9677
| KINCORTH | LW |  |  | 3.8154 | 3.5654 | 3.4011 | 3.3131 | 2.7534 | 2.1265 | 1.3245 | 0.47853 | -0.3169 | -0.97797 | -3.1102 | -5.5207 | -6.6382 | -7.1398 | 5.8628 | 5.7548 | 5.6761 | 5.6217 | 5.2933 | 4.9086 | 4.3273 | 3.7694 | 3.2074 | 2.7816 | 1.4305 | 0.079776 | -0.36988 | -0.60158 | 4.6681 | 4.4597 | 4.3224 | 4.238 | 3.7429 | 3.1867 | 2.47 | 1.6925 | 0.953 | 0.321 | -1.7222 | -3.9729 | -4.8846 | -5.2764
| KINCORTH | ST |  |  | 3.9734 | 3.8727 | 3.7708 | 3.6986 | 3.4627 | 3.1744 | 2.7324 | 2.3622 | 2.0315 | 1.721 | 0.69406 | -1.2027 | -2.5803 | -3.3574 | 5.9307 | 5.8813 | 5.8327 | 5.7961 | 5.6033 | 5.3652 | 4.9329 | 4.5652 | 4.1947 | 3.9142 | 3.0116 | 1.7685 | 0.82104 | 0.074727 | 4.8023 | 4.7209 | 4.6378 | 4.5668 | 4.3471 | 4.0791 | 3.6697 | 3.3273 | 3.0153 | 2.7164 | 1.7204 | -0.13539 | -1.3568 | -2.018
| KINCORTH | SP |  |  | 4.0064 | 3.9253 | 3.8395 | 3.8015 | 3.565 | 3.2727 | 2.8363 | 2.4845 | 2.1129 | 1.8056 | 0.83791 | -0.56717 | -1.8213 | -2.3233 | 5.9437 | 5.9027 | 5.8608 | 5.838 | 5.6451 | 5.4061 | 4.977 | 4.6178 | 4.2351 | 3.9619 | 3.0988 | 2.1298 | 0.77243 | -0.52721 | 4.8313 | 4.7669 | 4.6977 | 4.6597 | 4.4416 | 4.1738 | 3.7732 | 3.4501 | 3.1031 | 2.814 | 1.9019 | 0.53014 | -0.63623 | -1.0375
FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | 0.046054 | 0.046127 | 0.045775 | 0.044818 | 0.043349 | 0.041381 | 0.0394 | 0.035993 | 0.032146 | 0.025846 | 0.0073024 | -0.010574 | -0.01017 | -0.010298 | 0.063915 | 0.063848 | 0.063575 | 0.062773 | 0.061676 | 0.060641 | 0.059223 | 0.057123 | 0.055778 | 0.051822 | 0.038149 | 0.024576 | 0.024716 | 0.02466 | 0.057966 | 0.058017 | 0.057587 | 0.056593 | 0.055174 | 0.052851 | 0.050869 | 0.047248 | 0.042883 | 0.03688 | 0.019245 | 0.0021722 | 0.0025262 | 0.0024146
| KINGAIRLOCH | CT |  |  | 0.046909 | 0.046616 | 0.046121 | 0.045086 | 0.043349 | 0.042015 | 0.0394 | 0.035993 | 0.033807 | 0.028996 | 0.016314 | 0.0019827 | 0.00097423 | 0.00043013 | 0.064306 | 0.064274 | 0.064092 | 0.062773 | 0.061676 | 0.060815 | 0.059223 | 0.057123 | 0.055778 | 0.052846 | 0.045055 | 0.034517 | 0.034069 | 0.03385 | 0.0587 | 0.058361 | 0.057884 | 0.056893 | 0.055364 | 0.053788 | 0.050869 | 0.047248 | 0.044537 | 0.039923 | 0.027868 | 0.014249 | 0.013353 | 0.012876
| KINGAIRLOCH | LW |  |  | 0.046054 | 0.046127 | 0.045775 | 0.044818 | 0.043664 | 0.041381 | 0.04008 | 0.037209 | 0.032146 | 0.025846 | 0.0073024 | -0.010574 | -0.01017 | -0.010298 | 0.063915 | 0.063848 | 0.063575 | 0.062851 | 0.062131 | 0.060641 | 0.059753 | 0.058288 | 0.05578 | 0.051822 | 0.038149 | 0.024576 | 0.024716 | 0.02466 | 0.057966 | 0.058017 | 0.057587 | 0.056593 | 0.055174 | 0.052851 | 0.051302 | 0.048115 | 0.042883 | 0.03688 | 0.019245 | 0.0021722 | 0.0025262 | 0.0024146
| KINGAIRLOCH | ST |  |  | 0.046742 | 0.046636 | 0.046532 | 0.046289 | 0.046183 | 0.044996 | 0.044648 | 0.044182 | 0.043441 | 0.042338 | 0.034738 | 0.0087211 | -0.002241 | -0.0034175 | 0.064319 | 0.064212 | 0.064105 | 0.063877 | 0.063752 | 0.062916 | 0.06262 | 0.062219 | 0.061685 | 0.060885 | 0.05723 | 0.037695 | 0.02998 | 0.029528 | 0.058806 | 0.058665 | 0.058527 | 0.05831 | 0.058065 | 0.057117 | 0.056728 | 0.056261 | 0.055411 | 0.054166 | 0.045991 | 0.020296 | 0.0099516 | 0.0089209
| KINGAIRLOCH | SP |  |  | 0.046662 | 0.046506 | 0.046369 | 0.046228 | 0.045611 | 0.04501 | 0.044362 | 0.043315 | 0.041326 | 0.039892 | 0.034989 | 0.019143 | 0.0018429 | -0.0011491 | 0.064279 | 0.064158 | 0.064033 | 0.063903 | 0.063542 | 0.063174 | 0.062781 | 0.062117 | 0.060836 | 0.059921 | 0.056706 | 0.04761 | 0.034765 | 0.032884 | 0.058712 | 0.058516 | 0.058339 | 0.058158 | 0.057413 | 0.056681 | 0.055894 | 0.054769 | 0.052868 | 0.051303 | 0.046172 | 0.030655 | 0.014188 | 0.011414
DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | YES | 2.2458 | 1.9249 | 1.5513 | 1.115 | 0.5503 | 0.042834 | -0.52418 | -1.1009 | -1.6643 | -2.0881 | -3.0047 | -3.6988 | -4.0754 | -4.2238 | 3.914 | 3.658 | 3.3597 | 3.0046 | 2.5844 | 2.2475 | 1.8752 | 1.5048 | 1.1676 | 0.89618 | 0.3278 | -0.073299 | -0.31135 | -0.51885 | 3.4598 | 3.1822 | 2.8533 | 2.4627 | 1.9503 | 1.4933 | 0.97877 | 0.45694 | -0.049925 | -0.43413 | -1.2603 | -1.8693 | -2.2191 | -2.3567
| KINGSEAT | CT |  |  | 2.2689 | 1.9654 | 1.5949 | 1.1785 | 0.6423 | 0.20557 | -0.28466 | -0.75542 | -1.1815 | -1.6276 | -2.917 | -3.6988 | -4.0754 | -4.2238 | 3.9153 | 3.6635 | 3.3597 | 3.0099 | 2.6048 | 2.3092 | 1.9964 | 1.7069 | 1.4515 | 1.1645 | 0.33772 | -0.073299 | -0.31135 | -0.51885 | 3.4729 | 3.2117 | 2.8871 | 2.5138 | 2.0288 | 1.64 | 1.2054 | 0.79094 | 0.40607 | 0.010778 | -1.1788 | -1.8693 | -2.2191 | -2.3567
| KINGSEAT | LW |  |  | 2.2458 | 1.9249 | 1.5513 | 1.115 | 0.5503 | 0.042834 | -0.52418 | -1.1009 | -1.6643 | -2.0881 | -3.0047 | -3.5522 | -3.753 | -3.8576 | 3.914 | 3.658 | 3.3597 | 3.0046 | 2.5844 | 2.2475 | 1.8752 | 1.5048 | 1.1676 | 0.89618 | 0.3278 | 0.054182 | -0.028558 | -0.072776 | 3.4598 | 3.1822 | 2.8533 | 2.4627 | 1.9503 | 1.4933 | 0.97877 | 0.45694 | -0.049925 | -0.43413 | -1.2603 | -1.7436 | -1.9176 | -2.0148
| KINGSEAT | ST |  |  | 2.3158 | 2.0424 | 1.7322 | 1.3853 | 1.044 | 0.81634 | 0.59166 | 0.37174 | 0.1693 | -0.063874 | -0.75995 | -1.8669 | -2.2437 | -2.484 | 3.9509 | 3.722 | 3.4591 | 3.1549 | 2.8311 | 2.6058 | 2.3895 | 2.1884 | 2.0325 | 1.8904 | 1.4688 | 0.72161 | 0.46281 | 0.21262 | 3.5225 | 3.2932 | 3.0246 | 2.7189 | 2.4114 | 2.2132 | 2.0182 | 1.8275 | 1.6523 | 1.4499 | 0.81575 | -0.23839 | -0.57302 | -0.78452
| KINGSEAT | SP |  |  | 2.33 | 2.0645 | 1.7641 | 1.4217 | 1.0631 | 0.80736 | 0.54978 | 0.29703 | 0.086779 | -0.1247 | -0.74518 | -2.0195 | -2.5566 | -2.7621 | 3.9573 | 3.7322 | 3.4739 | 3.1718 | 2.837 | 2.6111 | 2.3942 | 2.1929 | 2.0393 | 1.9061 | 1.5054 | 0.67099 | 0.21435 | -0.19006 | 3.5343 | 3.312 | 3.0536 | 2.7523 | 2.4299 | 2.206 | 1.9802 | 1.7594 | 1.5772 | 1.3932 | 0.83583 | -0.35506 | -0.85289 | -1.0352
BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | YES | 1.8482 | 1.8391 | 1.8283 | 1.7149 | 1.421 | 1.0978 | 0.79427 | 0.47656 | 0.10076 | -0.14765 | -0.86483 | -1.4292 | -1.3404 | -1.3728 | 3.7892 | 3.7373 | 3.6801 | 3.5969 | 3.4421 | 3.2776 | 3.1071 | 2.8979 | 2.6691 | 2.4611 | 1.8598 | 1.5073 | 1.565 | 1.3855 | 3.4838 | 3.4754 | 3.4645 | 3.4484 | 3.4084 | 3.1419 | 2.8635 | 2.5076 | 2.1128 | 1.8035 | 0.91091 | 0.44206 | 0.57482 | 0.5235
| KINGUSSIE | CT |  |  | 1.8482 | 1.8391 | 1.8283 | 1.8135 | 1.5534 | 1.2622 | 0.94188 | 0.61828 | 0.29933 | 0.10479 | -0.46664 | -1.0627 | -1.0694 | -1.0959 | 3.8009 | 3.7604 | 3.7072 | 3.6168 | 3.4544 | 3.2961 | 3.1285 | 2.9492 | 2.7707 | 2.6221 | 2.076 | 1.6433 | 1.6162 | 1.5543 | 3.4838 | 3.4754 | 3.4645 | 3.4484 | 3.4286 | 3.2622 | 2.9567 | 2.6378 | 2.329 | 2.1085 | 1.3051 | 0.69387 | 0.71926 | 0.71174
| KINGUSSIE | LW |  |  | 1.8487 | 1.8392 | 1.8289 | 1.7149 | 1.421 | 1.0978 | 0.79427 | 0.47656 | 0.10076 | -0.14765 | -0.86483 | -1.4292 | -1.3404 | -1.3728 | 3.7892 | 3.7373 | 3.6801 | 3.5969 | 3.4421 | 3.2776 | 3.1071 | 2.8979 | 2.6691 | 2.4611 | 1.8598 | 1.5073 | 1.565 | 1.5402 | 3.4942 | 3.4903 | 3.485 | 3.4767 | 3.4084 | 3.1419 | 2.8635 | 2.5076 | 2.1128 | 1.8035 | 0.91091 | 0.44206 | 0.57482 | 0.5235
| KINGUSSIE | ST |  |  | 1.8508 | 1.8442 | 1.8377 | 1.8297 | 1.8231 | 1.8168 | 1.8098 | 1.7549 | 1.6534 | 1.4976 | 0.98354 | -0.23632 | -0.81224 | -0.9032 | 3.8186 | 3.7947 | 3.7705 | 3.7382 | 3.7019 | 3.6643 | 3.6199 | 3.5659 | 3.5021 | 3.401 | 3.0613 | 2.2151 | 1.9228 | 1.8186 | 3.4874 | 3.4829 | 3.4788 | 3.4725 | 3.4729 | 3.4736 | 3.4735 | 3.4716 | 3.468 | 3.4591 | 3.0485 | 1.8471 | 1.4484 | 1.3529
| KINGUSSIE | SP |  |  | 1.853 | 1.8477 | 1.8422 | 1.8367 | 1.8292 | 1.8225 | 1.8152 | 1.7904 | 1.7005 | 1.5668 | 1.0853 | -0.046413 | -0.95806 | -1.3093 | 3.8314 | 3.8149 | 3.7976 | 3.7778 | 3.7376 | 3.6976 | 3.6516 | 3.5933 | 3.523 | 3.4315 | 3.1301 | 2.3592 | 1.6747 | 1.3855 | 3.4927 | 3.4909 | 3.4896 | 3.488 | 3.4871 | 3.4869 | 3.4864 | 3.4833 | 3.4785 | 3.4693 | 3.0735 | 1.8688 | 0.90476 | 0.61379
TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | 1.2878 | 1.2835 | 1.276 | 1.2592 | 1.2261 | 1.1955 | 1.1645 | 1.1289 | 1.0949 | 1.0403 | 0.81213 | 0.7357 | 0.76988 | 0.72004 | 1.9218 | 1.9196 | 1.9113 | 1.8997 | 1.8646 | 1.8297 | 1.786 | 1.7424 | 1.6873 | 1.6459 | 1.4869 | 1.4272 | 1.4341 | 1.3969 | 1.5458 | 1.5451 | 1.5306 | 1.5102 | 1.4532 | 1.3921 | 1.3193 | 1.2459 | 1.1566 | 1.0987 | 0.87889 | 0.80429 | 0.83419 | 0.79265
| KINLOCH | CT |  |  | 1.2908 | 1.2839 | 1.276 | 1.2592 | 1.2261 | 1.1955 | 1.1645 | 1.1289 | 1.0949 | 1.07 | 0.88755 | 0.74929 | 0.77067 | 0.77283 | 1.9341 | 1.932 | 1.9253 | 1.9095 | 1.8684 | 1.8299 | 1.786 | 1.7424 | 1.6993 | 1.6643 | 1.536 | 1.4333 | 1.4341 | 1.4252 | 1.5671 | 1.5665 | 1.5546 | 1.525 | 1.4549 | 1.3934 | 1.3193 | 1.2459 | 1.1754 | 1.1268 | 0.95067 | 0.81705 | 0.83544 | 0.83727
| KINLOCH | LW |  |  | 1.2878 | 1.2835 | 1.2772 | 1.2677 | 1.238 | 1.2109 | 1.1804 | 1.1467 | 1.1011 | 1.0403 | 0.81213 | 0.7357 | 0.76988 | 0.74957 | 1.9218 | 1.9196 | 1.9113 | 1.8997 | 1.8646 | 1.8297 | 1.7929 | 1.7472 | 1.6873 | 1.6459 | 1.4869 | 1.4272 | 1.4422 | 1.4332 | 1.5458 | 1.5451 | 1.5306 | 1.5102 | 1.4532 | 1.3921 | 1.3293 | 1.2533 | 1.1566 | 1.0987 | 0.87889 | 0.80429 | 0.83419 | 0.81633
| KINLOCH | ST |  |  | 1.2926 | 1.2916 | 1.2907 | 1.2878 | 1.2829 | 1.2832 | 1.2773 | 1.2747 | 1.2659 | 1.2513 | 1.2023 | 1.0729 | 0.98163 | 0.95402 | 1.9321 | 1.9303 | 1.9285 | 1.9254 | 1.9205 | 1.9186 | 1.9128 | 1.9023 | 1.8917 | 1.8715 | 1.7996 | 1.5936 | 1.5247 | 1.5001 | 1.5635 | 1.5606 | 1.5578 | 1.5514 | 1.5443 | 1.5406 | 1.533 | 1.5187 | 1.5047 | 1.4765 | 1.3777 | 1.1057 | 1.0194 | 0.99473
| KINLOCH | SP |  |  | 1.2945 | 1.2945 | 1.295 | 1.2954 | 1.2861 | 1.2817 | 1.2721 | 1.2658 | 1.2528 | 1.2346 | 1.1812 | 1.0156 | 0.78419 | 0.72004 | 1.9333 | 1.9318 | 1.931 | 1.9302 | 1.9178 | 1.9082 | 1.8955 | 1.8834 | 1.8665 | 1.8432 | 1.7675 | 1.6162 | 1.4486 | 1.3969 | 1.5652 | 1.5631 | 1.5619 | 1.5611 | 1.5427 | 1.5256 | 1.507 | 1.4855 | 1.4568 | 1.4179 | 1.3002 | 1.0739 | 0.8515 | 0.79265
TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | 1.9317 | 1.9345 | 1.9303 | 1.9235 | 1.8964 | 1.8697 | 1.8432 | 1.7994 | 1.7542 | 1.7233 | 1.6249 | 1.557 | 1.5658 | 1.5297 | 2.1192 | 2.1189 | 2.1161 | 2.1117 | 2.0987 | 2.0858 | 2.0678 | 2.0479 | 2.0271 | 2.0091 | 1.9488 | 1.9015 | 1.9048 | 1.8931 | -0.38637 | -0.38486 | -0.38817 | -0.39312 | -0.41246 | -0.43117 | -0.45084 | -0.4823 | -0.51685 | -0.54037 | -0.61702 | -0.66849 | -0.66485 | -0.6906
| KINLOCH RANNOCH | CT |  |  | 1.9438 | 1.947 | 1.9449 | 1.9367 | 1.9098 | 1.8846 | 1.8434 | 1.7994 | 1.7572 | 1.7334 | 1.656 | 1.5723 | 1.5694 | 1.5651 | 2.1229 | 2.1225 | 2.1201 | 2.1137 | 2.0998 | 2.0864 | 2.0678 | 2.0479 | 2.028 | 2.0138 | 1.9654 | 1.9091 | 1.9048 | 1.9008 | -0.37738 | -0.37531 | -0.3768 | -0.38328 | -0.40316 | -0.42151 | -0.45084 | -0.4823 | -0.51268 | -0.53064 | -0.59184 | -0.65965 | -0.66457 | -0.66856
| KINLOCH RANNOCH | LW |  |  | 1.9317 | 1.9345 | 1.9303 | 1.9235 | 1.8964 | 1.8697 | 1.8432 | 1.8111 | 1.7542 | 1.7233 | 1.6249 | 1.557 | 1.5721 | 1.565 | 2.1192 | 2.1189 | 2.1161 | 2.1117 | 2.0987 | 2.0858 | 2.0726 | 2.0547 | 2.0271 | 2.0091 | 1.9488 | 1.9015 | 1.9067 | 1.9038 | -0.38637 | -0.38486 | -0.38817 | -0.39312 | -0.41246 | -0.43117 | -0.45024 | -0.47489 | -0.51685 | -0.54037 | -0.61702 | -0.66849 | -0.65812 | -0.66249
| KINLOCH RANNOCH | ST |  |  | 1.9401 | 1.9384 | 1.9369 | 1.9352 | 1.9341 | 1.9317 | 1.9293 | 1.9267 | 1.918 | 1.9032 | 1.852 | 1.7288 | 1.6611 | 1.6408 | 2.1229 | 2.1218 | 2.1208 | 2.1188 | 2.1172 | 2.1148 | 2.1126 | 2.1098 | 2.1047 | 2.0959 | 2.0643 | 1.9804 | 1.9353 | 1.9245 | -0.38003 | -0.38132 | -0.38231 | -0.38403 | -0.38553 | -0.38805 | -0.39026 | -0.3928 | -0.3995 | -0.41088 | -0.45019 | -0.54756 | -0.60084 | -0.61556
| KINLOCH RANNOCH | SP |  |  | 1.9402 | 1.9387 | 1.9379 | 1.9363 | 1.9269 | 1.9184 | 1.9079 | 1.8967 | 1.8833 | 1.8634 | 1.8042 | 1.6734 | 1.5658 | 1.5297 | 2.1225 | 2.1216 | 2.1209 | 2.1195 | 2.1154 | 2.1117 | 2.1068 | 2.1015 | 2.0945 | 2.0848 | 2.0549 | 1.9837 | 1.9141 | 1.8931 | -0.38052 | -0.38176 | -0.38237 | -0.3838 | -0.39078 | -0.3971 | -0.40497 | -0.4134 | -0.42386 | -0.43875 | -0.48335 | -0.57995 | -0.66485 | -0.6906
GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | 0.57525 | 0.57283 | 0.56466 | 0.55399 | 0.52559 | 0.49519 | 0.46367 | 0.41861 | 0.3705 | 0.34042 | 0.21868 | 0.18667 | 0.20151 | 0.16528 | 0.67235 | 0.67054 | 0.66653 | 0.66117 | 0.6479 | 0.63435 | 0.61532 | 0.59592 | 0.57475 | 0.55681 | 0.47172 | 0.45192 | 0.45397 | 0.43435 | 0.58695 | 0.58458 | 0.57717 | 0.56745 | 0.5421 | 0.5148 | 0.48511 | 0.44491 | 0.40162 | 0.37343 | 0.25724 | 0.22734 | 0.2412 | 0.20916
| KINLOCHEWE | CT |  |  | 0.58417 | 0.58376 | 0.57849 | 0.56398 | 0.53468 | 0.50702 | 0.46367 | 0.41861 | 0.3773 | 0.35492 | 0.27908 | 0.19803 | 0.20448 | 0.20351 | 0.67487 | 0.67365 | 0.67057 | 0.66201 | 0.6479 | 0.63435 | 0.61532 | 0.59592 | 0.57792 | 0.56458 | 0.51654 | 0.45481 | 0.45397 | 0.44953 | 0.59459 | 0.59397 | 0.58909 | 0.57554 | 0.549 | 0.52389 | 0.48511 | 0.44491 | 0.40801 | 0.38707 | 0.31536 | 0.23764 | 0.24324 | 0.24241
| KINLOCHEWE | LW |  |  | 0.57525 | 0.57283 | 0.56466 | 0.55399 | 0.52559 | 0.49519 | 0.46424 | 0.42642 | 0.3705 | 0.34042 | 0.21868 | 0.18667 | 0.20314 | 0.19346 | 0.67235 | 0.67054 | 0.66653 | 0.66117 | 0.64894 | 0.63529 | 0.62091 | 0.60083 | 0.57475 | 0.55681 | 0.47172 | 0.45192 | 0.45747 | 0.45425 | 0.58695 | 0.58458 | 0.57717 | 0.56745 | 0.5421 | 0.5148 | 0.4869 | 0.4521 | 0.40162 | 0.37343 | 0.25724 | 0.22734 | 0.2418 | 0.23333
| KINLOCHEWE | ST |  |  | 0.58308 | 0.58131 | 0.57938 | 0.57565 | 0.57374 | 0.57041 | 0.56704 | 0.56351 | 0.55271 | 0.53918 | 0.49024 | 0.34938 | 0.30893 | 0.29393 | 0.67558 | 0.67455 | 0.67328 | 0.67072 | 0.66902 | 0.66635 | 0.66377 | 0.66092 | 0.65433 | 0.64684 | 0.61741 | 0.51084 | 0.48796 | 0.47859 | 0.59391 | 0.59228 | 0.59047 | 0.58691 | 0.585 | 0.58172 | 0.57844 | 0.57498 | 0.56485 | 0.55236 | 0.50654 | 0.36486 | 0.32799 | 0.31488
| KINLOCHEWE | SP |  |  | 0.58515 | 0.58395 | 0.58376 | 0.58292 | 0.57598 | 0.56918 | 0.56155 | 0.55255 | 0.54007 | 0.52298 | 0.46266 | 0.33165 | 0.20151 | 0.16528 | 0.67642 | 0.6755 | 0.67508 | 0.67415 | 0.67102 | 0.66775 | 0.66408 | 0.65967 | 0.65269 | 0.64399 | 0.61391 | 0.54437 | 0.45444 | 0.43435 | 0.59575 | 0.59459 | 0.59437 | 0.5935 | 0.58729 | 0.58115 | 0.57427 | 0.56613 | 0.55458 | 0.539 | 0.48416 | 0.36419 | 0.2412 | 0.20916
KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | YES | 2.0777 | 2.0775 | 2.0765 | 2.0752 | 1.9571 | 1.8471 | 1.769 | 1.6908 | 1.5951 | 1.5495 | 1.4116 | 1.3648 | 1.3981 | 1.3411 | 2.5491 | 2.5434 | 2.5319 | 2.5173 | 2.452 | 2.4052 | 2.3705 | 2.328 | 2.2808 | 2.2497 | 2.1505 | 2.0982 | 2.0738 | 1.9928 | 2.2749 | 2.2752 | 2.2747 | 2.2734 | 2.1919 | 2.0936 | 2.0229 | 1.948 | 1.8582 | 1.8114 | 1.6656 | 1.6117 | 1.6419 | 1.589
| KINLOCHLEVEN | CT |  |  | 2.0788 | 2.0786 | 2.0777 | 2.0761 | 2.0462 | 1.9517 | 1.8548 | 1.7663 | 1.6853 | 1.6444 | 1.5369 | 1.4046 | 1.4274 | 1.4273 | 2.5644 | 2.5616 | 2.5537 | 2.5412 | 2.4791 | 2.4355 | 2.3926 | 2.3513 | 2.3135 | 2.2873 | 2.2148 | 2.1088 | 2.105 | 2.0857 | 2.2752 | 2.2755 | 2.2747 | 2.2734 | 2.2592 | 2.1832 | 2.0954 | 2.0142 | 1.9393 | 1.8988 | 1.7889 | 1.6474 | 1.6732 | 1.6758
| KINLOCHLEVEN | LW |  |  | 2.0777 | 2.0775 | 2.0765 | 2.0752 | 1.9571 | 1.8471 | 1.769 | 1.6908 | 1.5951 | 1.5495 | 1.4116 | 1.3648 | 1.4344 | 1.4156 | 2.5491 | 2.5434 | 2.5319 | 2.5173 | 2.452 | 2.4052 | 2.3705 | 2.328 | 2.2808 | 2.2497 | 2.1505 | 2.0982 | 2.1254 | 2.1176 | 2.2774 | 2.2796 | 2.2807 | 2.2812 | 2.1919 | 2.0936 | 2.0229 | 1.948 | 1.8582 | 1.8114 | 1.6656 | 1.6117 | 1.6768 | 1.6588
| KINLOCHLEVEN | ST |  |  | 2.0785 | 2.0783 | 2.0781 | 2.0778 | 2.0685 | 2.066 | 2.0635 | 2.0607 | 2.0591 | 2.0566 | 2.015 | 1.8099 | 1.6964 | 1.6635 | 2.5616 | 2.5584 | 2.5557 | 2.5521 | 2.5325 | 2.5244 | 2.5151 | 2.5038 | 2.495 | 2.4782 | 2.4194 | 2.2843 | 2.214 | 2.1814 | 2.2749 | 2.2752 | 2.2757 | 2.2761 | 2.2686 | 2.2685 | 2.2682 | 2.2677 | 2.2662 | 2.2637 | 2.2225 | 2.0157 | 1.9126 | 1.8877
| KINLOCHLEVEN | SP |  |  | 2.0791 | 2.0791 | 2.0792 | 2.0793 | 2.0688 | 2.0652 | 2.0618 | 2.0582 | 2.0195 | 1.9604 | 1.8204 | 1.5522 | 1.3981 | 1.3411 | 2.5644 | 2.5622 | 2.561 | 2.5597 | 2.5308 | 2.5139 | 2.4974 | 2.4792 | 2.4579 | 2.4296 | 2.3547 | 2.2067 | 2.0738 | 1.9928 | 2.2766 | 2.2777 | 2.279 | 2.2804 | 2.271 | 2.2692 | 2.2675 | 2.2655 | 2.2427 | 2.1884 | 2.057 | 1.8032 | 1.6419 | 1.589
FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | 2.2973 | 2.2973 | 2.2962 | 2.2944 | 2.2902 | 2.2863 | 2.2825 | 2.2782 | 2.2709 | 2.2676 | 2.2509 | 2.25 | 2.2509 | 2.2487 | 2.1408 | 2.1407 | 2.1401 | 2.139 | 2.1365 | 2.1343 | 2.1323 | 2.1299 | 2.1259 | 2.1238 | 2.1113 | 2.1105 | 2.111 | 2.1101 | 2.1352 | 2.1353 | 2.1342 | 2.1324 | 2.1286 | 2.1241 | 2.1198 | 2.1154 | 2.1086 | 2.1055 | 2.0893 | 2.088 | 2.0888 | 2.0868
| KINLOCHMOIDART | CT |  |  | 2.2983 | 2.2981 | 2.2969 | 2.2952 | 2.2902 | 2.2863 | 2.2825 | 2.2782 | 2.2731 | 2.2697 | 2.2541 | 2.251 | 2.2529 | 2.2534 | 2.1413 | 2.1411 | 2.1403 | 2.1394 | 2.1365 | 2.1343 | 2.1323 | 2.1299 | 2.1276 | 2.1254 | 2.1137 | 2.1114 | 2.1121 | 2.1122 | 2.1367 | 2.1366 | 2.1354 | 2.1337 | 2.1286 | 2.1245 | 2.1202 | 2.1154 | 2.1108 | 2.1076 | 2.0928 | 2.0893 | 2.0908 | 2.0912
| KINLOCHMOIDART | LW |  |  | 2.2973 | 2.2973 | 2.2962 | 2.2944 | 2.2915 | 2.2867 | 2.2825 | 2.2786 | 2.2709 | 2.2676 | 2.2509 | 2.25 | 2.2518 | 2.2505 | 2.1408 | 2.1407 | 2.1401 | 2.139 | 2.1375 | 2.1347 | 2.1323 | 2.13 | 2.1259 | 2.1238 | 2.1113 | 2.1105 | 2.1112 | 2.1107 | 2.1352 | 2.1353 | 2.1342 | 2.1324 | 2.129 | 2.1241 | 2.1198 | 2.1157 | 2.1086 | 2.1055 | 2.0893 | 2.088 | 2.0899 | 2.0887
| KINLOCHMOIDART | ST |  |  | 2.2983 | 2.2982 | 2.2979 | 2.2975 | 2.2969 | 2.2968 | 2.2966 | 2.2948 | 2.2941 | 2.2919 | 2.285 | 2.2656 | 2.2641 | 2.2632 | 2.1414 | 2.1413 | 2.1411 | 2.1408 | 2.1404 | 2.1403 | 2.1401 | 2.1389 | 2.1384 | 2.137 | 2.1323 | 2.118 | 2.117 | 2.1165 | 2.1365 | 2.1364 | 2.1361 | 2.1357 | 2.1353 | 2.1352 | 2.1349 | 2.1335 | 2.1328 | 2.1307 | 2.124 | 2.1048 | 2.1028 | 2.1016
| KINLOCHMOIDART | SP |  |  | 2.2984 | 2.2983 | 2.2983 | 2.298 | 2.2969 | 2.2959 | 2.2941 | 2.2929 | 2.2916 | 2.2879 | 2.2818 | 2.2661 | 2.2509 | 2.2487 | 2.1414 | 2.1414 | 2.1413 | 2.1411 | 2.1404 | 2.1399 | 2.1389 | 2.1382 | 2.1375 | 2.1353 | 2.1317 | 2.1226 | 2.111 | 2.1101 | 2.1366 | 2.1365 | 2.1364 | 2.1362 | 2.1349 | 2.1337 | 2.1319 | 2.1305 | 2.1291 | 2.1255 | 2.119 | 2.104 | 2.0888 | 2.0868
ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | YES | 11.5311 | 11.4937 | 11.4451 | 11.3849 | 11.2286 | 11.0672 | 10.9162 | 10.7496 | 10.5323 | 10.3363 | 9.7636 | 9.2538 | 9.0367 | 8.9492 | 11.8182 | 11.8076 | 11.7945 | 11.7753 | 11.7398 | 11.7054 | 11.6784 | 11.6495 | 11.6128 | 11.5672 | 11.4148 | 11.2914 | 11.285 | 11.2644 | 11.178 | 11.1446 | 11.1008 | 11.0463 | 10.9009 | 10.7511 | 10.6124 | 10.4608 | 10.2606 | 10.0838 | 9.5644 | 9.093 | 8.892 | 8.8119
| KINLOSS | CT |  |  | 11.5593 | 11.5359 | 11.4977 | 11.4441 | 11.2905 | 11.1486 | 10.982 | 10.8105 | 10.6357 | 10.4798 | 9.9021 | 9.2538 | 9.0367 | 8.9492 | 11.8182 | 11.8076 | 11.7945 | 11.7753 | 11.7398 | 11.7054 | 11.6784 | 11.6499 | 11.6203 | 11.5864 | 11.4559 | 11.3299 | 11.3128 | 11.2644 | 11.2046 | 11.1843 | 11.1503 | 11.103 | 10.961 | 10.83 | 10.6757 | 10.5171 | 10.3549 | 10.2121 | 9.6876 | 9.093 | 8.892 | 8.8119
| KINLOSS | LW |  |  | 11.5311 | 11.4937 | 11.4451 | 11.3849 | 11.2286 | 11.0672 | 10.9162 | 10.7496 | 10.5323 | 10.3363 | 9.7636 | 9.3288 | 9.2232 | 9.1582 | 11.8213 | 11.8111 | 11.7994 | 11.7827 | 11.7492 | 11.7148 | 11.6853 | 11.6495 | 11.6128 | 11.5672 | 11.4148 | 11.2914 | 11.285 | 11.2783 | 11.178 | 11.1446 | 11.1008 | 11.0463 | 10.9009 | 10.7511 | 10.6124 | 10.4608 | 10.2606 | 10.0838 | 9.5644 | 9.1644 | 9.0665 | 9.0064
| KINLOSS | ST |  |  | 11.5716 | 11.5564 | 11.5398 | 11.5198 | 11.4923 | 11.4678 | 11.4391 | 11.4045 | 11.3658 | 11.2971 | 11.0403 | 10.3212 | 10.026 | 9.8761 | 11.8276 | 11.8226 | 11.8171 | 11.8095 | 11.7907 | 11.7794 | 11.7666 | 11.7481 | 11.7342 | 11.7134 | 11.6216 | 11.3992 | 11.3199 | 11.2838 | 11.2153 | 11.2021 | 11.1877 | 11.1707 | 11.1464 | 11.1253 | 11.1004 | 11.0694 | 11.0347 | 10.9727 | 10.7399 | 10.0942 | 9.8225 | 9.6833
| KINLOSS | SP |  |  | 11.5769 | 11.566 | 11.5552 | 11.5407 | 11.5006 | 11.4629 | 11.4215 | 11.3737 | 11.3196 | 11.2502 | 10.9968 | 10.3878 | 9.883 | 9.7503 | 11.8277 | 11.8235 | 11.819 | 11.8134 | 11.7965 | 11.7873 | 11.7772 | 11.7618 | 11.7502 | 11.7365 | 11.6741 | 11.5186 | 11.3709 | 11.3158 | 11.2206 | 11.2116 | 11.2027 | 11.1905 | 11.1539 | 11.1201 | 11.0829 | 11.0393 | 10.9907 | 10.9271 | 10.6947 | 10.1405 | 9.6873 | 9.5656
BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | 2.5018 | 2.4083 | 2.2964 | 2.1631 | 1.8066 | 1.4255 | 1.054 | 0.67809 | 0.2882 | -0.030919 | -0.71888 | -0.96353 | -0.77937 | -1.0996 | 4.64 | 4.5949 | 4.5417 | 4.4709 | 4.3313 | 4.1505 | 3.9577 | 3.7588 | 3.5454 | 3.3122 | 2.8546 | 2.574 | 2.2522 | 1.9584 | 3.362 | 3.2766 | 3.1745 | 3.0471 | 2.7362 | 2.4 | 2.0625 | 1.7195 | 1.36 | 1.0342 | 0.37021 | 0.13283 | 0.28064 | 0.043593
| KIPPEN | CT |  |  | 2.5801 | 2.5311 | 2.4521 | 2.3675 | 2.0429 | 1.7265 | 1.4064 | 1.0961 | 0.79845 | 0.58453 | -0.23218 | -0.68589 | -0.72995 | -0.78574 | 4.6513 | 4.6156 | 4.5643 | 4.4992 | 4.3726 | 4.2415 | 4.0938 | 3.944 | 3.7968 | 3.6507 | 3.0391 | 2.7451 | 2.6626 | 2.5418 | 3.4239 | 3.3748 | 3.2978 | 3.2078 | 2.9241 | 2.6465 | 2.3669 | 2.0934 | 1.8297 | 1.619 | 0.78901 | 0.37527 | 0.33189 | 0.28406
| KIPPEN | LW |  |  | 2.5018 | 2.4083 | 2.2964 | 2.1631 | 1.8066 | 1.4255 | 1.054 | 0.67809 | 0.2882 | -0.030919 | -0.71888 | -0.96353 | -0.77937 | -0.81935 | 4.64 | 4.5949 | 4.5417 | 4.4709 | 4.3313 | 4.1505 | 3.9577 | 3.7588 | 3.5454 | 3.3122 | 2.8546 | 2.574 | 2.599 | 2.587 | 3.362 | 3.2766 | 3.1745 | 3.0471 | 2.7362 | 2.4 | 2.0625 | 1.7195 | 1.36 | 1.0342 | 0.37021 | 0.13283 | 0.28064 | 0.24845
| KIPPEN | ST |  |  | 2.5917 | 2.5546 | 2.5188 | 2.492 | 2.4642 | 2.4251 | 2.3829 | 2.3325 | 2.2634 | 2.1394 | 1.6386 | 0.52401 | 0.13605 | -0.03454 | 4.6762 | 4.6557 | 4.6347 | 4.6134 | 4.5936 | 4.5645 | 4.5343 | 4.5012 | 4.4593 | 4.3843 | 3.9308 | 2.8185 | 2.2522 | 2.1678 | 3.4438 | 3.4108 | 3.3784 | 3.3498 | 3.3207 | 3.2795 | 3.2362 | 3.186 | 3.1189 | 3.0007 | 2.5153 | 1.3989 | 0.99684 | 0.84661
| KIPPEN | SP |  |  | 2.6149 | 2.5947 | 2.5706 | 2.5548 | 2.4818 | 2.409 | 2.3265 | 2.2312 | 2.1362 | 1.9976 | 1.4599 | 0.078543 | -0.76453 | -1.0996 | 4.6825 | 4.6689 | 4.6507 | 4.6359 | 4.6028 | 4.568 | 4.5271 | 4.4748 | 4.4231 | 4.3579 | 4.0699 | 3.1385 | 2.2577 | 1.9584 | 3.4621 | 3.4436 | 3.4205 | 3.4028 | 3.3367 | 3.2699 | 3.1941 | 3.104 | 3.0145 | 2.8909 | 2.4123 | 1.1034 | 0.32475 | 0.043593
THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | YES | 9.9625 | 9.6871 | 8.9775 | 7.9931 | 6.164 | 4.3147 | 2.5159 | 0.38644 | -1.1416 | -2.0903 | -4.8514 | -5.5134 | -4.6566 | -5.0154 | 13.0171 | 12.8458 | 12.5002 | 11.9431 | 10.9688 | 9.9489 | 8.8943 | 7.4759 | 6.4664 | 5.7143 | 3.4951 | 2.7165 | 2.821 | 2.0304 | 9.7537 | 9.5185 | 8.8773 | 7.98 | 6.3365 | 4.6698 | 3.0374 | 1.0782 | -0.33212 | -1.236 | -3.864 | -4.5483 | -3.7973 | -4.1111
| KIRKWALL | CT |  |  | 10.2161 | 10.0085 | 9.5098 | 8.3731 | 6.4194 | 4.6009 | 3.3028 | 1.4327 | -0.033816 | -0.87546 | -3.5969 | -4.9998 | -4.1786 | -3.9378 | 13.0171 | 12.8458 | 12.5002 | 11.9431 | 10.996 | 9.9801 | 9.1238 | 7.8482 | 6.906 | 6.2491 | 4.0688 | 2.8696 | 3.0206 | 2.8901 | 10.0758 | 9.8863 | 9.34 | 8.3032 | 6.5458 | 4.905 | 3.7161 | 1.998 | 0.65512 | -0.13856 | -2.7216 | -4.079 | -3.3647 | -3.1526
| KIRKWALL | LW |  |  | 9.9625 | 9.6871 | 8.9775 | 7.9931 | 6.164 | 4.3147 | 2.5159 | 0.38644 | -1.1416 | -2.0903 | -4.8514 | -5.5134 | -4.6566 | -5.0154 | 13.0403 | 12.8683 | 12.5268 | 11.9475 | 10.9688 | 9.9489 | 8.8943 | 7.4759 | 6.4664 | 5.7143 | 3.4951 | 2.7165 | 3.0262 | 2.8901 | 9.7537 | 9.5185 | 8.8773 | 7.98 | 6.3365 | 4.6698 | 3.0374 | 1.0782 | -0.33212 | -1.236 | -3.864 | -4.5483 | -3.7973 | -4.1111
| KIRKWALL | ST |  |  | 10.2881 | 10.1141 | 9.8023 | 9.3206 | 8.8386 | 8.2954 | 7.6888 | 6.7212 | 6.0706 | 5.3935 | 3.1082 | 0.54964 | -0.11876 | -0.33107 | 13.0746 | 12.9307 | 12.6151 | 12.1111 | 11.5684 | 10.9797 | 10.3188 | 9.2494 | 8.541 | 7.9765 | 6.1545 | 4.8096 | 4.1773 | 4.0372 | 10.1454 | 9.9746 | 9.6687 | 9.1585 | 8.7284 | 8.2084 | 7.6096 | 6.6507 | 6.0071 | 5.4442 | 3.2883 | 0.83299 | 0.11541 | -0.14926
| KIRKWALL | SP |  |  | 10.2915 | 10.1231 | 9.816 | 9.3584 | 8.7967 | 7.9934 | 7.0959 | 5.8387 | 4.8278 | 3.7219 | 0.89992 | -2.7522 | -4.4213 | -4.9465 | 13.0774 | 12.9378 | 12.6258 | 12.1326 | 11.5964 | 11.0191 | 10.3689 | 9.3056 | 8.6035 | 8.0681 | 6.2729 | 4.1765 | 2.821 | 2.0304 | 10.1487 | 9.9973 | 9.7005 | 9.253 | 8.6717 | 7.9337 | 7.1074 | 5.9389 | 5.0033 | 3.9949 | 1.3932 | -1.9626 | -3.5471 | -4.0241
BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | 1.1566 | 1.1505 | 1.1299 | 1.0929 | 1.0068 | 0.91525 | 0.81635 | 0.69592 | 0.53861 | 0.4558 | 0.15857 | 0.06139 | 0.10692 | 0.025494 | 1.4037 | 1.4003 | 1.3963 | 1.3787 | 1.3676 | 1.348 | 1.3107 | 1.2686 | 1.2024 | 1.1496 | 0.94561 | 0.87994 | 0.89509 | 0.84752 | 1.1532 | 1.1496 | 1.1326 | 1.1008 | 1.0268 | 0.94919 | 0.86849 | 0.77634 | 0.64928 | 0.58972 | 0.39734 | 0.3341 | 0.38062 | 0.29852
| KISHORNHILL | CT |  |  | 1.1827 | 1.1821 | 1.1685 | 1.1225 | 1.0445 | 0.96701 | 0.84469 | 0.70796 | 0.58656 | 0.51953 | 0.29974 | 0.10864 | 0.12452 | 0.12293 | 1.4037 | 1.4003 | 1.3963 | 1.3787 | 1.3676 | 1.3556 | 1.3266 | 1.2777 | 1.2256 | 1.1812 | 1.0281 | 0.89581 | 0.89509 | 0.88598 | 1.1742 | 1.1699 | 1.1642 | 1.1326 | 1.0651 | 1.0004 | 0.89715 | 0.78575 | 0.68603 | 0.63692 | 0.49048 | 0.37849 | 0.4055 | 0.40812
| KISHORNHILL | LW |  |  | 1.1566 | 1.1505 | 1.1299 | 1.0929 | 1.0068 | 0.91525 | 0.81635 | 0.69592 | 0.53861 | 0.4558 | 0.15857 | 0.06139 | 0.10692 | 0.084113 | 1.4047 | 1.4015 | 1.3979 | 1.3827 | 1.3727 | 1.348 | 1.3107 | 1.2686 | 1.2024 | 1.1496 | 0.94561 | 0.87994 | 0.89662 | 0.88815 | 1.1532 | 1.1496 | 1.1326 | 1.1008 | 1.0268 | 0.94919 | 0.86849 | 0.77634 | 0.64928 | 0.58972 | 0.39734 | 0.3341 | 0.38062 | 0.35629
| KISHORNHILL | ST |  |  | 1.1773 | 1.1719 | 1.1667 | 1.1478 | 1.1388 | 1.1281 | 1.1064 | 1.0772 | 1.0439 | 0.99309 | 0.85142 | 0.50151 | 0.3819 | 0.34666 | 1.4077 | 1.4065 | 1.4052 | 1.3929 | 1.388 | 1.3827 | 1.3732 | 1.3613 | 1.3514 | 1.3382 | 1.3034 | 1.0597 | 0.9856 | 0.96455 | 1.1704 | 1.1661 | 1.1623 | 1.147 | 1.1427 | 1.1369 | 1.1251 | 1.1099 | 1.088 | 1.0534 | 0.95557 | 0.74943 | 0.6644 | 0.63456
| KISHORNHILL | SP |  |  | 1.1846 | 1.1823 | 1.1812 | 1.1705 | 1.1499 | 1.129 | 1.0989 | 1.0583 | 1.0125 | 0.95541 | 0.78722 | 0.42977 | 0.11462 | 0.025494 | 1.408 | 1.4072 | 1.4061 | 1.395 | 1.391 | 1.3865 | 1.3785 | 1.3679 | 1.358 | 1.3472 | 1.2977 | 1.1041 | 0.89882 | 0.84752 | 1.1773 | 1.1763 | 1.1767 | 1.1664 | 1.1504 | 1.1334 | 1.1107 | 1.0822 | 1.0514 | 1.0082 | 0.87242 | 0.5936 | 0.3813 | 0.29852
BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | YES | 4.1689 | 4.1661 | 4.1433 | 2.8114 | 2.7054 | 2.5922 | 2.4694 | 2.3428 | 2.186 | 2.0877 | 1.7711 | 1.6724 | 1.7453 | 1.718 | 4.9485 | 4.943 | 4.9289 | 3.609 | 3.5507 | 3.4878 | 3.4244 | 3.359 | 3.2728 | 3.2101 | 2.9891 | 2.9022 | 2.9085 | 2.869 | 4.5514 | 4.547 | 4.5206 | 3.1841 | 3.0646 | 2.9407 | 2.8198 | 2.6777 | 2.511 | 2.421 | 2.1243 | 2.0282 | 2.0998 | 2.0697
| KYLE | CT |  |  | 4.199 | 4.1973 | 4.1787 | 2.8347 | 2.7151 | 2.5994 | 2.4772 | 2.3538 | 2.2384 | 2.1687 | 1.9279 | 1.7071 | 1.7453 | 1.7483 | 4.9612 | 4.9561 | 4.9439 | 3.6148 | 3.5507 | 3.4878 | 3.4244 | 3.359 | 3.2965 | 3.2472 | 3.0845 | 2.913 | 2.9085 | 2.8914 | 4.5876 | 4.586 | 4.5658 | 3.2192 | 3.0874 | 2.9598 | 2.8256 | 2.6907 | 2.5659 | 2.4945 | 2.2712 | 2.0606 | 2.0998 | 2.106
| KYLE | LW |  |  | 4.1689 | 4.1661 | 4.1433 | 2.8114 | 2.7054 | 2.5922 | 2.4694 | 2.3428 | 2.186 | 2.0877 | 1.7711 | 1.6724 | 1.7542 | 1.718 | 4.9485 | 4.943 | 4.9289 | 3.609 | 3.5542 | 3.496 | 3.4388 | 3.3611 | 3.2728 | 3.2101 | 2.9891 | 2.9022 | 2.9304 | 2.9164 | 4.5514 | 4.547 | 4.5206 | 3.1841 | 3.0646 | 2.9407 | 2.8198 | 2.6777 | 2.511 | 2.421 | 2.1243 | 2.0282 | 2.1039 | 2.0697
| KYLE | ST |  |  | 4.1942 | 4.1893 | 4.1848 | 2.8766 | 2.8759 | 2.8719 | 2.8645 | 2.8571 | 2.8326 | 2.7855 | 2.6382 | 2.2932 | 2.1927 | 2.1704 | 4.9632 | 4.9595 | 4.9556 | 3.6484 | 3.644 | 3.6375 | 3.6277 | 3.618 | 3.5992 | 3.5657 | 3.4563 | 3.1738 | 3.0778 | 3.0473 | 4.5822 | 4.5764 | 4.571 | 3.2628 | 3.2613 | 3.2563 | 3.2468 | 3.2385 | 3.2137 | 3.166 | 3.0127 | 2.6603 | 2.5413 | 2.5111
| KYLE | SP |  |  | 4.2018 | 4.1997 | 4.2002 | 2.8997 | 2.8745 | 2.8518 | 2.8244 | 2.7951 | 2.7503 | 2.6823 | 2.5008 | 2.1435 | 1.8166 | 1.72 | 4.9663 | 4.9638 | 4.9623 | 3.6599 | 3.6458 | 3.633 | 3.6163 | 3.5992 | 3.5711 | 3.5313 | 3.4198 | 3.1897 | 2.9469 | 2.869 | 4.5901 | 4.5872 | 4.587 | 3.2858 | 3.2568 | 3.2302 | 3.1977 | 3.1643 | 3.1183 | 3.0473 | 2.8553 | 2.4712 | 2.1619 | 2.0755
LAIRG | LAIRG GRID | MINIMUM HEADROOM | NC 58798 07111 | YES | 2.9499 | 2.9486 | 2.9463 | 2.9404 | 2.9447 | 2.9493 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.725 | 2.7245 | 2.7236 | 2.7215 | 2.7231 | 2.7248 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.7249 | 2.7238 | 2.7218 | 2.7166 | 2.7204 | 2.7244 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725
| LAIRG GRID | CT |  |  | 2.9499 | 2.9486 | 2.9463 | 2.9404 | 2.9447 | 2.9493 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.725 | 2.7245 | 2.7236 | 2.7215 | 2.7231 | 2.7248 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.7249 | 2.7238 | 2.7218 | 2.7166 | 2.7204 | 2.7244 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725
| LAIRG GRID | LW |  |  | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725
| LAIRG GRID | ST |  |  | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725
| LAIRG GRID | SP |  |  | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725 | 2.725
MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | 2.6713 | 2.6601 | 2.6239 | 2.5808 | 2.4174 | 2.2625 | 2.1029 | 1.9282 | 1.6742 | 1.5369 | 1.0179 | 0.86056 | 0.88216 | 0.71305 | 3.1933 | 3.1855 | 3.1679 | 3.1471 | 3.0609 | 2.9877 | 2.9097 | 2.8177 | 2.6956 | 2.6186 | 2.2953 | 2.2097 | 2.2046 | 2.1115 | 2.7279 | 2.7171 | 2.6843 | 2.6452 | 2.4984 | 2.3615 | 2.2196 | 2.0603 | 1.8307 | 1.7038 | 1.2149 | 1.0707 | 1.0929 | 0.94391
| LATHERON | CT |  |  | 2.7369 | 2.7455 | 2.7289 | 2.6918 | 2.5281 | 2.387 | 2.1883 | 1.9845 | 1.7918 | 1.6809 | 1.268 | 0.9811 | 0.92452 | 0.8825 | 3.2152 | 3.2145 | 3.202 | 3.1771 | 3.0844 | 3.0127 | 2.9234 | 2.8331 | 2.7459 | 2.6812 | 2.4188 | 2.256 | 2.2254 | 2.195 | 2.7849 | 2.7915 | 2.7753 | 2.7399 | 2.591 | 2.4655 | 2.2902 | 2.1089 | 1.9365 | 1.8335 | 1.4437 | 1.1789 | 1.1292 | 1.0925
| LATHERON | LW |  |  | 2.6713 | 2.6601 | 2.6239 | 2.5808 | 2.4174 | 2.2625 | 2.1029 | 1.9282 | 1.6742 | 1.5369 | 1.0179 | 0.86056 | 0.92903 | 0.90806 | 3.1933 | 3.1855 | 3.1679 | 3.1471 | 3.0609 | 2.9877 | 2.9097 | 2.8177 | 2.6956 | 2.6186 | 2.2953 | 2.2097 | 2.2347 | 2.2269 | 2.7279 | 2.7171 | 2.6843 | 2.6452 | 2.4984 | 2.3615 | 2.2196 | 2.0603 | 1.8307 | 1.7038 | 1.2149 | 1.0707 | 1.1309 | 1.1126
| LATHERON | ST |  |  | 2.7191 | 2.7076 | 2.6958 | 2.6842 | 2.6353 | 2.5996 | 2.5609 | 2.5214 | 2.4707 | 2.3991 | 2.1571 | 1.5769 | 1.3335 | 1.2214 | 3.2125 | 3.2065 | 3.2 | 3.1918 | 3.1507 | 3.1269 | 3.1008 | 3.072 | 3.043 | 3.0026 | 2.8598 | 2.4876 | 2.3711 | 2.3149 | 2.7702 | 2.7598 | 2.7489 | 2.7379 | 2.6921 | 2.6614 | 2.6274 | 2.5904 | 2.5441 | 2.4781 | 2.2536 | 1.7044 | 1.4866 | 1.3885
| LATHERON | SP |  |  | 2.7245 | 2.7162 | 2.7092 | 2.7011 | 2.6273 | 2.5695 | 2.5048 | 2.445 | 2.3755 | 2.2814 | 1.9902 | 1.3773 | 0.88216 | 0.71305 | 3.2147 | 3.2104 | 3.2062 | 3.2008 | 3.1536 | 3.1234 | 3.0891 | 3.0581 | 3.0203 | 2.9715 | 2.8271 | 2.5049 | 2.2046 | 2.1115 | 2.7751 | 2.7675 | 2.7611 | 2.7534 | 2.6868 | 2.6371 | 2.5807 | 2.5273 | 2.4639 | 2.3783 | 2.1153 | 1.5546 | 1.0929 | 0.94391
FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | YES | 1.0539 | 0.94088 | 0.81214 | 0.67652 | 0.35812 | -0.20027 | -0.81508 | -1.5354 | -2.3809 | -3.2046 | -4.8063 | -5.8707 | -6.2837 | -6.4525 | 3.7118 | 3.6259 | 3.5321 | 3.4272 | 3.2596 | 2.8953 | 2.4712 | 1.9528 | 1.3953 | 0.76597 | -0.37215 | -1.0494 | -1.2717 | -1.452 | 1.7443 | 1.6407 | 1.5188 | 1.3855 | 1.102 | 0.6034 | 0.045493 | -0.62288 | -1.3735 | -2.1454 | -3.6456 | -4.5843 | -4.9343 | -5.077
| LAURENCEKIRK | CT |  |  | 1.1118 | 1.0176 | 0.9079 | 0.79506 | 0.51178 | 0.014797 | -0.61314 | -1.3081 | -2.0647 | -2.8579 | -4.6047 | -5.8707 | -6.2837 | -6.4525 | 3.7158 | 3.6307 | 3.5354 | 3.4272 | 3.2691 | 2.94 | 2.5432 | 2.1009 | 1.6097 | 1.0186 | -0.27027 | -1.0494 | -1.2717 | -1.452 | 1.7834 | 1.6923 | 1.5822 | 1.4593 | 1.2048 | 0.76648 | 0.22127 | -0.37881 | -1.0452 | -1.7864 | -3.4494 | -4.5843 | -4.9343 | -5.077
| LAURENCEKIRK | LW |  |  | 1.0539 | 0.94088 | 0.81214 | 0.67652 | 0.35812 | -0.20027 | -0.81508 | -1.5354 | -2.3809 | -3.2046 | -4.8063 | -5.7618 | -5.9546 | -6.0687 | 3.7118 | 3.6259 | 3.5321 | 3.4304 | 3.2596 | 2.8953 | 2.4712 | 1.9528 | 1.3953 | 0.76597 | -0.37215 | -0.97704 | -1.051 | -1.0943 | 1.7443 | 1.6407 | 1.5188 | 1.3855 | 1.102 | 0.6034 | 0.045493 | -0.62288 | -1.3735 | -2.1454 | -3.6456 | -4.5042 | -4.6669 | -4.7626
| LAURENCEKIRK | ST |  |  | 1.1258 | 1.0241 | 0.93654 | 0.86666 | 0.79156 | 0.49783 | 0.14615 | -0.26583 | -0.75721 | -1.3638 | -2.572 | -3.9903 | -4.4884 | -4.7712 | 3.7485 | 3.6776 | 3.6119 | 3.5501 | 3.4859 | 3.2475 | 2.9623 | 2.5347 | 2.0087 | 1.3729 | 0.25836 | -0.69947 | -1.0026 | -1.0719 | 1.812 | 1.7266 | 1.6489 | 1.5819 | 1.5105 | 1.2497 | 0.9382 | 0.575 | 0.1436 | -0.41579 | -1.5582 | -2.9818 | -3.4085 | -3.6519
| LAURENCEKIRK | SP |  |  | 1.1356 | 1.041 | 0.96219 | 0.89089 | 0.77386 | 0.44042 | 0.045932 | -0.41197 | -0.92595 | -1.5444 | -2.7482 | -4.2301 | -4.9095 | -5.1592 | 3.7488 | 3.6813 | 3.6192 | 3.5609 | 3.4871 | 3.2364 | 2.938 | 2.55 | 2.0315 | 1.4104 | 0.36185 | -0.4096 | -0.85865 | -1.2285 | 1.8176 | 1.7385 | 1.6682 | 1.6031 | 1.5009 | 1.2089 | 0.86366 | 0.46366 | 0.004145 | -0.56133 | -1.6666 | -3.1065 | -3.7629 | -3.9814
STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | 1.0651 | 1.088 | 1.0453 | 0.98207 | 0.78384 | 0.5904 | 0.40427 | 0.19593 | -0.043596 | -0.17185 | -0.68305 | -0.81951 | -0.85867 | -0.95954 | 1.6408 | 1.6441 | 1.6234 | 1.5922 | 1.5071 | 1.4205 | 1.3356 | 1.2299 | 1.1125 | 1.0365 | 0.70498 | 0.61511 | 0.60622 | 0.53057 | 1.3035 | 1.3156 | 1.2809 | 1.2293 | 1.0771 | 0.92564 | 0.77815 | 0.60023 | 0.38614 | 0.26161 | -0.25716 | -0.3927 | -0.41165 | -0.50022
| LAXAY | CT |  |  | 1.1947 | 1.2281 | 1.2112 | 1.1415 | 0.93439 | 0.74747 | 0.5455 | 0.33606 | 0.13783 | 0.029796 | -0.37546 | -0.70402 | -0.71463 | -0.74082 | 1.682 | 1.682 | 1.6688 | 1.6265 | 1.5443 | 1.457 | 1.3663 | 1.2731 | 1.1838 | 1.1199 | 0.85878 | 0.65185 | 0.63567 | 0.60903 | 1.3952 | 1.4141 | 1.3974 | 1.3339 | 1.1696 | 1.0198 | 0.86109 | 0.69669 | 0.54048 | 0.43739 | 0.028764 | -0.29671 | -0.31055 | -0.33377
| LAXAY | LW |  |  | 1.0651 | 1.088 | 1.0453 | 0.98207 | 0.78384 | 0.5904 | 0.40427 | 0.19593 | -0.043596 | -0.17185 | -0.68305 | -0.81951 | -0.72552 | -0.76582 | 1.6408 | 1.6441 | 1.6234 | 1.5922 | 1.5071 | 1.4205 | 1.3356 | 1.2299 | 1.1125 | 1.0365 | 0.70498 | 0.61511 | 0.64866 | 0.6325 | 1.3035 | 1.3156 | 1.2809 | 1.2293 | 1.0771 | 0.92564 | 0.77815 | 0.60023 | 0.38614 | 0.26161 | -0.25716 | -0.3927 | -0.31716 | -0.34946
| LAXAY | ST |  |  | 1.1586 | 1.1443 | 1.1318 | 1.122 | 1.1084 | 1.0874 | 1.061 | 1.0394 | 1.0004 | 0.93129 | 0.69157 | 0.05 | -0.1967 | -0.31474 | 1.6788 | 1.671 | 1.6639 | 1.6546 | 1.6446 | 1.6314 | 1.6139 | 1.5952 | 1.5731 | 1.5343 | 1.3876 | 0.92525 | 0.80165 | 0.74997 | 1.374 | 1.3616 | 1.3507 | 1.3386 | 1.3244 | 1.3046 | 1.2792 | 1.2556 | 1.2209 | 1.1588 | 0.93575 | 0.29427 | 0.085814 | -0.0032201
| LAXAY | SP |  |  | 1.1561 | 1.1391 | 1.1276 | 1.1147 | 1.0261 | 0.94436 | 0.85264 | 0.75669 | 0.64791 | 0.49495 | 0.18338 | -0.4275 | -0.85867 | -0.95954 | 1.6778 | 1.6698 | 1.6633 | 1.6557 | 1.6199 | 1.5865 | 1.5488 | 1.5088 | 1.4577 | 1.3903 | 1.2389 | 0.91628 | 0.60622 | 0.53057 | 1.3719 | 1.3584 | 1.3483 | 1.3368 | 1.2701 | 1.2084 | 1.1392 | 1.066 | 0.97803 | 0.85762 | 0.59549 | 0.036948 | -0.41165 | -0.50022
COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | 4.1559 | 4.1163 | 4.068 | 4.0004 | 3.837 | 3.6446 | 3.4218 | 3.1977 | 2.894 | 2.6604 | 2.0458 | 1.4295 | 1.1088 | 0.98668 | 4.9107 | 4.8834 | 4.8497 | 4.7996 | 4.7157 | 4.6099 | 4.4779 | 4.3498 | 4.1741 | 4.0165 | 3.625 | 3.3218 | 3.1467 | 2.9995 | 4.2263 | 4.191 | 4.1478 | 4.0872 | 3.9389 | 3.7645 | 3.5651 | 3.3637 | 3.0914 | 2.8646 | 2.2687 | 1.7522 | 1.4763 | 1.366
| LEOCH | CT |  |  | 4.171 | 4.1422 | 4.0974 | 4.0341 | 3.8843 | 3.7223 | 3.5329 | 3.3189 | 3.106 | 2.8844 | 2.1159 | 1.4295 | 1.1088 | 0.98668 | 4.9112 | 4.8858 | 4.8497 | 4.7996 | 4.7158 | 4.6266 | 4.5345 | 4.4264 | 4.3184 | 4.179 | 3.6671 | 3.3218 | 3.1467 | 2.9995 | 4.2399 | 4.2143 | 4.1745 | 4.1181 | 3.9821 | 3.8347 | 3.6621 | 3.4678 | 3.2743 | 3.0761 | 2.3495 | 1.7522 | 1.4763 | 1.366
| LEOCH | LW |  |  | 4.1559 | 4.1163 | 4.068 | 4.0004 | 3.837 | 3.6446 | 3.4218 | 3.1977 | 2.894 | 2.6604 | 2.0458 | 1.5664 | 1.3564 | 1.2644 | 4.9107 | 4.8834 | 4.8513 | 4.8044 | 4.7157 | 4.6099 | 4.4779 | 4.3498 | 4.1741 | 4.0165 | 3.625 | 3.3971 | 3.3233 | 3.2901 | 4.2263 | 4.191 | 4.1478 | 4.0872 | 3.9389 | 3.7645 | 3.5651 | 3.3637 | 3.0914 | 2.8646 | 2.2687 | 1.8497 | 1.6791 | 1.605
| LEOCH | ST |  |  | 4.1998 | 4.1848 | 4.1696 | 4.1503 | 4.1343 | 4.1134 | 4.0903 | 4.0621 | 4.0195 | 3.9461 | 3.6479 | 2.8015 | 2.4748 | 2.2984 | 4.9355 | 4.923 | 4.9099 | 4.8926 | 4.8765 | 4.8562 | 4.8339 | 4.8075 | 4.7732 | 4.7179 | 4.4821 | 3.8526 | 3.6292 | 3.4565 | 4.2658 | 4.2526 | 4.2393 | 4.2224 | 4.2087 | 4.1906 | 4.1706 | 4.146 | 4.1083 | 4.0431 | 3.7485 | 2.9312 | 2.6354 | 2.4807
| LEOCH | SP |  |  | 4.2114 | 4.2036 | 4.1957 | 4.185 | 4.1591 | 4.13 | 4.0982 | 4.0578 | 4.0128 | 3.9535 | 3.7118 | 2.9388 | 2.4447 | 2.3026 | 4.9411 | 4.9326 | 4.9232 | 4.911 | 4.8916 | 4.8687 | 4.844 | 4.8123 | 4.7765 | 4.7326 | 4.5683 | 3.9844 | 3.541 | 3.2386 | 4.2765 | 4.2699 | 4.2632 | 4.2542 | 4.2314 | 4.206 | 4.1782 | 4.1428 | 4.1034 | 4.0506 | 3.8342 | 3.0814 | 2.612 | 2.4844
NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | 1.1214 | 1.1032 | 1.0812 | 1.0506 | 1.0069 | 0.95168 | 0.82623 | 0.67908 | 0.49834 | 0.33018 | 0.033252 | -0.064497 | -0.039813 | -0.13541 | 1.6884 | 1.6748 | 1.6579 | 1.6318 | 1.5906 | 1.5447 | 1.4872 | 1.415 | 1.3376 | 1.2408 | 1.0962 | 1.0066 | 1.0138 | 1.0006 | 1.3369 | 1.3106 | 1.2769 | 1.2308 | 1.1369 | 1.0333 | 0.91919 | 0.78848 | 0.62055 | 0.47991 | 0.21087 | 0.10834 | 0.13564 | 0.0476
| LETHEN | CT |  |  | 1.1214 | 1.1042 | 1.0829 | 1.052 | 1.0082 | 0.96079 | 0.88959 | 0.73938 | 0.607 | 0.50381 | 0.15568 | 0.0074407 | -0.039813 | -0.073754 | 1.6947 | 1.6831 | 1.6684 | 1.6405 | 1.5995 | 1.5614 | 1.5095 | 1.4483 | 1.3966 | 1.3406 | 1.1421 | 1.0862 | 1.0653 | 1.0449 | 1.3629 | 1.3484 | 1.3261 | 1.2866 | 1.1954 | 1.1066 | 0.97973 | 0.83822 | 0.71171 | 0.62271 | 0.32987 | 0.18107 | 0.13564 | 0.10277
| LETHEN | LW |  |  | 1.1221 | 1.1032 | 1.0812 | 1.0506 | 1.0069 | 0.95168 | 0.82623 | 0.67908 | 0.49834 | 0.33018 | 0.033252 | -0.064497 | -0.026024 | -0.039792 | 1.6884 | 1.6748 | 1.6579 | 1.6318 | 1.5906 | 1.5447 | 1.4872 | 1.415 | 1.3376 | 1.2408 | 1.0962 | 1.0066 | 1.0138 | 1.0082 | 1.3369 | 1.3106 | 1.2769 | 1.2308 | 1.1369 | 1.0333 | 0.91919 | 0.78848 | 0.62055 | 0.47991 | 0.21087 | 0.10834 | 0.14705 | 0.13343
| LETHEN | ST |  |  | 1.1375 | 1.1303 | 1.1215 | 1.1108 | 1.0995 | 1.0853 | 1.0692 | 1.0514 | 1.028 | 0.99419 | 0.86351 | 0.43232 | 0.26313 | 0.17492 | 1.7016 | 1.697 | 1.6901 | 1.6813 | 1.6729 | 1.6599 | 1.6469 | 1.6363 | 1.6171 | 1.5921 | 1.48 | 1.2245 | 1.127 | 1.0904 | 1.3674 | 1.359 | 1.3482 | 1.3357 | 1.3224 | 1.3038 | 1.2848 | 1.2673 | 1.231 | 1.183 | 0.99812 | 0.60127 | 0.43194 | 0.34574
| LETHEN | SP |  |  | 1.1382 | 1.1328 | 1.1262 | 1.1185 | 1.1086 | 1.0968 | 1.0849 | 1.0693 | 1.0531 | 1.0308 | 0.88699 | 0.30702 | 0.0031238 | -0.13541 | 1.7017 | 1.6987 | 1.6933 | 1.6883 | 1.6781 | 1.6633 | 1.6516 | 1.631 | 1.6115 | 1.5889 | 1.5006 | 1.199 | 1.0647 | 1.0006 | 1.3704 | 1.3653 | 1.3581 | 1.3512 | 1.3296 | 1.3039 | 1.2805 | 1.2466 | 1.2128 | 1.1694 | 0.9817 | 0.47347 | 0.18499 | 0.0476
GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | 0.11073 | 0.11071 | 0.11068 | 0.11051 | 0.11027 | 0.11 | 0.10968 | 0.1093 | 0.10889 | 0.10831 | 0.10637 | 0.10431 | 0.10431 | 0.10431 | 0.10394 | 0.10392 | 0.1039 | 0.10387 | 0.10384 | 0.10368 | 0.10342 | 0.10313 | 0.1028 | 0.10235 | 0.10079 | 0.099169 | 0.09917 | 0.09917 | 0.10296 | 0.10294 | 0.10291 | 0.10287 | 0.10283 | 0.10277 | 0.10244 | 0.10206 | 0.10163 | 0.10104 | 0.099131 | 0.097147 | 0.097149 | 0.097149
| LETTEREWE | CT |  |  | 0.11074 | 0.11072 | 0.11069 | 0.11051 | 0.11028 | 0.11002 | 0.10974 | 0.10945 | 0.10912 | 0.10867 | 0.10745 | 0.10591 | 0.10591 | 0.10591 | 0.10394 | 0.10392 | 0.1039 | 0.10388 | 0.10384 | 0.10369 | 0.10348 | 0.10324 | 0.10299 | 0.10263 | 0.10164 | 0.10043 | 0.10043 | 0.10043 | 0.10296 | 0.10295 | 0.10292 | 0.10289 | 0.10284 | 0.10279 | 0.10251 | 0.10221 | 0.10188 | 0.10141 | 0.10017 | 0.098684 | 0.098683 | 0.098683
| LETTEREWE | LW |  |  | 0.11073 | 0.11071 | 0.11068 | 0.11051 | 0.11027 | 0.11 | 0.10968 | 0.1093 | 0.10889 | 0.10831 | 0.10637 | 0.10431 | 0.10431 | 0.10431 | 0.10394 | 0.10392 | 0.1039 | 0.10387 | 0.10384 | 0.10368 | 0.10342 | 0.10313 | 0.1028 | 0.10235 | 0.10079 | 0.099169 | 0.09917 | 0.09917 | 0.10296 | 0.10294 | 0.10291 | 0.10287 | 0.10283 | 0.10277 | 0.10244 | 0.10206 | 0.10163 | 0.10104 | 0.099131 | 0.097147 | 0.097149 | 0.097149
| LETTEREWE | ST |  |  | 0.11075 | 0.11074 | 0.11073 | 0.11072 | 0.1107 | 0.11068 | 0.1106 | 0.11044 | 0.11025 | 0.10996 | 0.1089 | 0.10603 | 0.10494 | 0.10494 | 0.10396 | 0.10395 | 0.10394 | 0.10393 | 0.10392 | 0.1039 | 0.10388 | 0.10386 | 0.10383 | 0.10365 | 0.10281 | 0.10052 | 0.099669 | 0.099668 | 0.10298 | 0.10297 | 0.10296 | 0.10294 | 0.10293 | 0.10291 | 0.10289 | 0.10286 | 0.10283 | 0.10274 | 0.10165 | 0.098804 | 0.097758 | 0.097757
| LETTEREWE | SP |  |  | 0.11076 | 0.11074 | 0.11073 | 0.11072 | 0.1107 | 0.11068 | 0.11065 | 0.11062 | 0.11052 | 0.11035 | 0.10978 | 0.10784 | 0.10598 | 0.10577 | 0.10396 | 0.10395 | 0.10394 | 0.10393 | 0.10392 | 0.10391 | 0.10389 | 0.10387 | 0.10385 | 0.10383 | 0.10352 | 0.10197 | 0.10049 | 0.10032 | 0.10298 | 0.10297 | 0.10296 | 0.10295 | 0.10293 | 0.10291 | 0.10288 | 0.10286 | 0.10283 | 0.10279 | 0.10254 | 0.10055 | 0.098753 | 0.09855
ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | YES | 5.1824 | 5.1507 | 5.1046 | 5.0491 | 4.9405 | 4.8154 | 4.6778 | 4.5222 | 4.3027 | 4.1234 | 3.6582 | 3.0597 | 2.7588 | 2.6503 | 5.7378 | 5.7153 | 5.6858 | 5.6412 | 5.5867 | 5.5281 | 5.4548 | 5.3753 | 5.2658 | 5.1394 | 4.8456 | 4.5463 | 4.3974 | 4.2869 | 5.2085 | 5.1807 | 5.1407 | 5.0913 | 4.9933 | 4.8795 | 4.7524 | 4.6062 | 4.402 | 4.2201 | 3.7836 | 3.2454 | 2.9908 | 2.9001
| LHANBRYDE | CT |  |  | 5.201 | 5.1722 | 5.1297 | 5.0648 | 4.9582 | 4.8441 | 4.6901 | 4.5225 | 4.3547 | 4.2008 | 3.6781 | 3.0597 | 2.7588 | 2.6503 | 5.7391 | 5.7154 | 5.6858 | 5.6412 | 5.5867 | 5.5281 | 5.4548 | 5.3753 | 5.2948 | 5.206 | 4.8705 | 4.5463 | 4.3974 | 4.2869 | 5.2218 | 5.1958 | 5.1577 | 5.0972 | 4.9998 | 4.8955 | 4.7579 | 4.6084 | 4.4582 | 4.312 | 3.8038 | 3.2454 | 2.9908 | 2.9001
| LHANBRYDE | LW |  |  | 5.1824 | 5.1507 | 5.1046 | 5.0491 | 4.9405 | 4.8154 | 4.6778 | 4.5222 | 4.3027 | 4.1234 | 3.6582 | 3.2267 | 3.0292 | 2.9363 | 5.7378 | 5.7153 | 5.6874 | 5.6532 | 5.6012 | 5.5391 | 5.4675 | 5.3819 | 5.2658 | 5.1394 | 4.8456 | 4.6227 | 4.5517 | 4.5199 | 5.2085 | 5.1807 | 5.1407 | 5.0913 | 4.9933 | 4.8795 | 4.7524 | 4.6062 | 4.402 | 4.2201 | 3.7836 | 3.3866 | 3.21 | 3.1334
| LHANBRYDE | ST |  |  | 5.2151 | 5.1905 | 5.1655 | 5.1364 | 5.1285 | 5.1154 | 5.1007 | 5.0829 | 5.0566 | 5.0106 | 4.8271 | 4.2438 | 3.9996 | 3.8553 | 5.7526 | 5.736 | 5.7185 | 5.6972 | 5.6882 | 5.6753 | 5.661 | 5.6431 | 5.6222 | 5.5884 | 5.4497 | 5.0219 | 4.861 | 4.7321 | 5.2381 | 5.2184 | 5.1981 | 5.1731 | 5.1637 | 5.1493 | 5.1333 | 5.1136 | 5.0868 | 5.0403 | 4.8583 | 4.3405 | 4.1161 | 3.9819
| LHANBRYDE | SP |  |  | 5.2155 | 5.1938 | 5.1729 | 5.1492 | 5.1263 | 5.1041 | 5.0764 | 5.0432 | 5.0026 | 4.9505 | 4.7793 | 4.2921 | 3.9506 | 3.8651 | 5.7502 | 5.7352 | 5.72 | 5.7021 | 5.6881 | 5.6741 | 5.6561 | 5.6337 | 5.6046 | 5.5702 | 5.4541 | 5.0886 | 4.7667 | 4.5494 | 5.237 | 5.2201 | 5.2037 | 5.1841 | 5.1625 | 5.1418 | 5.1156 | 5.0837 | 5.0435 | 4.9936 | 4.8289 | 4.3743 | 4.0706 | 3.9932
FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | 0.09458 | 0.093359 | 0.09184 | 0.089503 | 0.083528 | 0.077773 | 0.071328 | 0.064805 | 0.057977 | 0.054684 | 0.040885 | 0.040246 | 0.043043 | 0.039275 | 0.092579 | 0.091819 | 0.090993 | 0.089659 | 0.086908 | 0.084471 | 0.081386 | 0.07824 | 0.075046 | 0.072848 | 0.062635 | 0.062259 | 0.063279 | 0.061841 | 0.088413 | 0.087277 | 0.085624 | 0.083239 | 0.077798 | 0.072669 | 0.066826 | 0.060906 | 0.054737 | 0.05163 | 0.038077 | 0.037466 | 0.039895 | 0.036572
| LIDDESDALE | CT |  |  | 0.095731 | 0.094946 | 0.09369 | 0.091239 | 0.086717 | 0.08238 | 0.076695 | 0.070563 | 0.064638 | 0.061643 | 0.047761 | 0.04468 | 0.046551 | 0.046873 | 0.093138 | 0.092624 | 0.091902 | 0.090525 | 0.088062 | 0.086037 | 0.08364 | 0.08102 | 0.078302 | 0.076478 | 0.065783 | 0.064292 | 0.064981 | 0.0651 | 0.089943 | 0.089287 | 0.088108 | 0.085721 | 0.080849 | 0.07667 | 0.071606 | 0.066134 | 0.060795 | 0.057976 | 0.044226 | 0.041435 | 0.043075 | 0.043357
| LIDDESDALE | LW |  |  | 0.09458 | 0.093359 | 0.09184 | 0.089503 | 0.083528 | 0.077773 | 0.071328 | 0.064805 | 0.057977 | 0.054684 | 0.040885 | 0.040246 | 0.043043 | 0.04151 | 0.092579 | 0.091819 | 0.090993 | 0.089659 | 0.086908 | 0.084471 | 0.081386 | 0.07824 | 0.075046 | 0.072848 | 0.062635 | 0.062259 | 0.063279 | 0.062715 | 0.088413 | 0.087277 | 0.085624 | 0.083239 | 0.077798 | 0.072669 | 0.066826 | 0.060906 | 0.054737 | 0.05163 | 0.038077 | 0.037466 | 0.039895 | 0.038551
| LIDDESDALE | ST |  |  | 0.095994 | 0.095377 | 0.095068 | 0.094145 | 0.09372 | 0.093443 | 0.092325 | 0.091648 | 0.091178 | 0.088681 | 0.081886 | 0.064842 | 0.061972 | 0.060288 | 0.093372 | 0.092988 | 0.092804 | 0.092248 | 0.091964 | 0.091783 | 0.091071 | 0.090618 | 0.090311 | 0.088638 | 0.084012 | 0.071798 | 0.070673 | 0.070053 | 0.089975 | 0.089394 | 0.089065 | 0.088205 | 0.087794 | 0.08748 | 0.086453 | 0.085796 | 0.085264 | 0.082842 | 0.075991 | 0.059128 | 0.056599 | 0.055123
| LIDDESDALE | SP |  |  | 0.096402 | 0.096088 | 0.095828 | 0.095724 | 0.094146 | 0.093288 | 0.091996 | 0.089986 | 0.088552 | 0.085778 | 0.078017 | 0.055283 | 0.043269 | 0.039275 | 0.093591 | 0.093378 | 0.093188 | 0.093098 | 0.09216 | 0.091683 | 0.090933 | 0.089724 | 0.088897 | 0.087479 | 0.083991 | 0.07022 | 0.063326 | 0.061841 | 0.090399 | 0.090115 | 0.089899 | 0.089811 | 0.088214 | 0.087222 | 0.085847 | 0.083846 | 0.082294 | 0.079718 | 0.072746 | 0.051275 | 0.040075 | 0.036572
KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | 1.2154 | 1.1917 | 1.158 | 1.1157 | 1.0198 | 0.92157 | 0.81035 | 0.6898 | 0.51022 | 0.36884 | 0.086435 | -0.012676 | 0.02379 | -0.10813 | 1.7025 | 1.6988 | 1.6942 | 1.6856 | 1.6799 | 1.6624 | 1.6302 | 1.5903 | 1.5249 | 1.4717 | 1.3222 | 1.208 | 1.2188 | 1.1978 | 1.4926 | 1.4706 | 1.4396 | 1.4003 | 1.3133 | 1.2243 | 1.1224 | 1.0114 | 0.84713 | 0.71281 | 0.45012 | 0.36096 | 0.3932 | 0.27798
| LIMEHILLOCKS | CT |  |  | 1.2464 | 1.2356 | 1.2138 | 1.1736 | 1.0916 | 1.0133 | 0.88654 | 0.74912 | 0.61884 | 0.54093 | 0.22556 | 0.084108 | 0.030958 | -0.0049836 | 1.7025 | 1.6988 | 1.6942 | 1.6856 | 1.6799 | 1.675 | 1.6598 | 1.6107 | 1.5584 | 1.5201 | 1.3808 | 1.2942 | 1.2755 | 1.2601 | 1.5192 | 1.5081 | 1.487 | 1.4479 | 1.3734 | 1.3026 | 1.1885 | 1.0648 | 0.94723 | 0.87447 | 0.5742 | 0.44841 | 0.40206 | 0.37086
| LIMEHILLOCKS | LW |  |  | 1.2154 | 1.1917 | 1.158 | 1.1157 | 1.0198 | 0.92157 | 0.81035 | 0.6898 | 0.51022 | 0.36884 | 0.086435 | -0.012676 | 0.02379 | 0.011777 | 1.7039 | 1.7012 | 1.6979 | 1.693 | 1.6862 | 1.6624 | 1.6302 | 1.5903 | 1.5249 | 1.4717 | 1.3222 | 1.208 | 1.2188 | 1.2143 | 1.4926 | 1.4706 | 1.4396 | 1.4003 | 1.3133 | 1.2243 | 1.1224 | 1.0114 | 0.84713 | 0.71281 | 0.45012 | 0.36096 | 0.3932 | 0.38297
| LIMEHILLOCKS | ST |  |  | 1.2466 | 1.2363 | 1.2253 | 1.21 | 1.1955 | 1.1718 | 1.1506 | 1.1282 | 1.0917 | 1.0465 | 0.85558 | 0.44944 | 0.27935 | 0.19461 | 1.7055 | 1.7042 | 1.7028 | 1.6999 | 1.6983 | 1.6942 | 1.691 | 1.6877 | 1.6838 | 1.6796 | 1.6352 | 1.4245 | 1.3202 | 1.2892 | 1.5207 | 1.5112 | 1.5009 | 1.4862 | 1.4728 | 1.4503 | 1.4303 | 1.4092 | 1.3755 | 1.334 | 1.1546 | 0.77062 | 0.61985 | 0.54552
| LIMEHILLOCKS | SP |  |  | 1.2509 | 1.245 | 1.2372 | 1.2288 | 1.2026 | 1.1775 | 1.1464 | 1.1107 | 1.0661 | 1.0214 | 0.83405 | 0.28772 | 0.024173 | -0.10813 | 1.7054 | 1.7048 | 1.7035 | 1.7019 | 1.7 | 1.6981 | 1.6948 | 1.6908 | 1.6846 | 1.6811 | 1.6419 | 1.4091 | 1.2726 | 1.1978 | 1.5245 | 1.519 | 1.5116 | 1.5036 | 1.4798 | 1.457 | 1.4283 | 1.3953 | 1.3536 | 1.3128 | 1.1431 | 0.63198 | 0.3943 | 0.27798
ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | YES | 16.5175 | 16.5203 | 16.5145 | 16.5042 | 16.4696 | 16.4366 | 16.409 | 16.3795 | 16.3381 | 16.3153 | 16.2283 | 16.2041 | 16.1983 | 16.1875 | 16.6892 | 16.6886 | 16.6855 | 16.6796 | 16.6617 | 16.6442 | 16.6303 | 16.6145 | 16.5928 | 16.5792 | 16.5202 | 16.5051 | 16.4977 | 16.4897 | 16.5985 | 16.6005 | 16.5952 | 16.5857 | 16.5541 | 16.5238 | 16.4987 | 16.4717 | 16.4338 | 16.4124 | 16.3299 | 16.3075 | 16.3018 | 16.2921
| LOCH CARNAN | CT |  |  | 16.5381 | 16.542 | 16.5401 | 16.5306 | 16.4947 | 16.4605 | 16.4271 | 16.3925 | 16.3574 | 16.3376 | 16.269 | 16.2112 | 16.1983 | 16.1875 | 16.6964 | 16.6961 | 16.6941 | 16.6876 | 16.6689 | 16.6503 | 16.6341 | 16.6174 | 16.5996 | 16.5875 | 16.5416 | 16.5051 | 16.4977 | 16.4897 | 16.6164 | 16.6195 | 16.6174 | 16.6084 | 16.5756 | 16.5442 | 16.514 | 16.4827 | 16.4508 | 16.4322 | 16.3672 | 16.3134 | 16.3018 | 16.2921
| LOCH CARNAN | LW |  |  | 16.5175 | 16.5203 | 16.5145 | 16.5042 | 16.4696 | 16.4366 | 16.409 | 16.3795 | 16.3381 | 16.3153 | 16.2283 | 16.2041 | 16.2133 | 16.2069 | 16.6892 | 16.6886 | 16.6855 | 16.6796 | 16.6617 | 16.6442 | 16.6303 | 16.6145 | 16.5928 | 16.5792 | 16.5202 | 16.5063 | 16.5084 | 16.5048 | 16.5985 | 16.6005 | 16.5952 | 16.5857 | 16.5541 | 16.5238 | 16.4987 | 16.4717 | 16.4338 | 16.4124 | 16.3299 | 16.3075 | 16.3154 | 16.3096
| LOCH CARNAN | ST |  |  | 16.5323 | 16.5305 | 16.5284 | 16.5273 | 16.5251 | 16.521 | 16.5148 | 16.5117 | 16.5031 | 16.4923 | 16.45 | 16.3396 | 16.2862 | 16.2494 | 16.6952 | 16.6943 | 16.6931 | 16.6915 | 16.6899 | 16.6872 | 16.683 | 16.6806 | 16.6753 | 16.6693 | 16.6433 | 16.5653 | 16.5357 | 16.5126 | 16.6116 | 16.61 | 16.608 | 16.6068 | 16.6046 | 16.6008 | 16.5949 | 16.5918 | 16.5838 | 16.5738 | 16.5342 | 16.4269 | 16.3798 | 16.3468
| LOCH CARNAN | SP |  |  | 16.5313 | 16.5285 | 16.5261 | 16.5231 | 16.5084 | 16.4958 | 16.4811 | 16.4661 | 16.4469 | 16.4249 | 16.3777 | 16.2736 | 16.2141 | 16.1907 | 16.695 | 16.6937 | 16.6924 | 16.6907 | 16.6845 | 16.6795 | 16.6734 | 16.6673 | 16.6574 | 16.6481 | 16.6247 | 16.5653 | 16.5207 | 16.5025 | 16.6107 | 16.6082 | 16.6061 | 16.6033 | 16.5902 | 16.5791 | 16.566 | 16.5528 | 16.5352 | 16.5157 | 16.4729 | 16.3764 | 16.3196 | 16.2979
GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435
| LOCH GLASCARNOCH | CT |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435
| LOCH GLASCARNOCH | LW |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435
| LOCH GLASCARNOCH | ST |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435
| LOCH GLASCARNOCH | SP |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435
FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | 4.2662 | 4.2652 | 4.2615 | 4.2565 | 4.2465 | 4.2259 | 4.1927 | 4.1567 | 4.1241 | 4.1109 | 4.0597 | 4.0372 | 4.0473 | 4.0294 | 4.4733 | 4.4741 | 4.4719 | 4.4676 | 4.4566 | 4.4461 | 4.4318 | 4.4161 | 4.4016 | 4.3936 | 4.3529 | 4.3399 | 4.3407 | 4.3277 | 4.3912 | 4.3922 | 4.3878 | 4.3816 | 4.3649 | 4.348 | 4.3294 | 4.302 | 4.2766 | 4.2645 | 4.2166 | 4.1882 | 4.1978 | 4.1809
| LOCHALINE | CT |  |  | 4.27 | 4.2684 | 4.2658 | 4.2616 | 4.2478 | 4.2263 | 4.1927 | 4.1567 | 4.1241 | 4.1109 | 4.0604 | 4.0372 | 4.055 | 4.0596 | 4.4758 | 4.4748 | 4.4737 | 4.4676 | 4.4566 | 4.4461 | 4.4318 | 4.4161 | 4.4016 | 4.3936 | 4.357 | 4.3399 | 4.3443 | 4.3425 | 4.398 | 4.3961 | 4.394 | 4.3881 | 4.3715 | 4.3552 | 4.3294 | 4.302 | 4.2766 | 4.2645 | 4.2276 | 4.1978 | 4.2031 | 4.2029
| LOCHALINE | LW |  |  | 4.2662 | 4.2652 | 4.2615 | 4.2565 | 4.2465 | 4.2259 | 4.206 | 4.1835 | 4.1394 | 4.1225 | 4.0597 | 4.0435 | 4.0575 | 4.0462 | 4.4733 | 4.4741 | 4.4719 | 4.4679 | 4.4596 | 4.4496 | 4.4408 | 4.4285 | 4.4076 | 4.3972 | 4.3529 | 4.3423 | 4.3475 | 4.3432 | 4.3912 | 4.3922 | 4.3878 | 4.3816 | 4.3649 | 4.348 | 4.3314 | 4.3143 | 4.2817 | 4.2662 | 4.2166 | 4.1882 | 4.1978 | 4.1915
| LOCHALINE | ST |  |  | 4.271 | 4.2697 | 4.2685 | 4.2672 | 4.2655 | 4.2636 | 4.2606 | 4.2585 | 4.2537 | 4.2462 | 4.2209 | 4.1597 | 4.1333 | 4.1264 | 4.476 | 4.4756 | 4.4753 | 4.4742 | 4.4733 | 4.4727 | 4.4703 | 4.4702 | 4.467 | 4.461 | 4.4421 | 4.393 | 4.3805 | 4.3743 | 4.398 | 4.3969 | 4.3958 | 4.3945 | 4.3934 | 4.3918 | 4.3892 | 4.3875 | 4.3824 | 4.374 | 4.3467 | 4.284 | 4.2563 | 4.2484
| LOCHALINE | SP |  |  | 4.2709 | 4.2698 | 4.2687 | 4.2676 | 4.2634 | 4.2595 | 4.255 | 4.2497 | 4.2444 | 4.2319 | 4.191 | 4.1006 | 4.0473 | 4.0294 | 4.4763 | 4.476 | 4.4759 | 4.4757 | 4.4729 | 4.4705 | 4.4673 | 4.4629 | 4.4583 | 4.4504 | 4.4296 | 4.3781 | 4.3407 | 4.3277 | 4.3983 | 4.3972 | 4.3962 | 4.3953 | 4.3899 | 4.3843 | 4.3778 | 4.3704 | 4.3629 | 4.3507 | 4.3176 | 4.2439 | 4.1978 | 4.1809
TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | 0.36331 | 0.357 | 0.35359 | 0.34645 | 0.32247 | 0.2959 | 0.25937 | 0.21772 | 0.17756 | 0.14311 | 0.017024 | -0.040793 | -0.028975 | -0.054964 | 0.52159 | 0.51915 | 0.51521 | 0.50856 | 0.49134 | 0.47525 | 0.45702 | 0.43527 | 0.412 | 0.38793 | 0.29938 | 0.25625 | 0.26047 | 0.24222 | 0.45079 | 0.44471 | 0.4415 | 0.43484 | 0.42075 | 0.40247 | 0.38846 | 0.35261 | 0.30742 | 0.27737 | 0.16521 | 0.10534 | 0.11808 | 0.07078
| LOCHDONHEAD | CT |  |  | 0.36331 | 0.357 | 0.35359 | 0.34645 | 0.32247 | 0.2959 | 0.25937 | 0.21772 | 0.17756 | 0.14864 | 0.040869 | -0.02775 | -0.020114 | -0.019303 | 0.52361 | 0.52117 | 0.51747 | 0.50856 | 0.49134 | 0.47525 | 0.45702 | 0.43527 | 0.41349 | 0.39339 | 0.31636 | 0.26557 | 0.26514 | 0.26209 | 0.45079 | 0.44471 | 0.4415 | 0.43484 | 0.42075 | 0.40247 | 0.38846 | 0.35261 | 0.30742 | 0.28048 | 0.18787 | 0.11997 | 0.12535 | 0.1248
| LOCHDONHEAD | LW |  |  | 0.36417 | 0.35889 | 0.3564 | 0.35046 | 0.32762 | 0.29825 | 0.27341 | 0.23633 | 0.17842 | 0.14311 | 0.017024 | -0.040793 | -0.028975 | -0.03775 | 0.52159 | 0.51915 | 0.51521 | 0.51012 | 0.4982 | 0.48134 | 0.46787 | 0.44464 | 0.412 | 0.38793 | 0.29938 | 0.25625 | 0.26047 | 0.2569 | 0.4516 | 0.44644 | 0.44407 | 0.4406 | 0.42767 | 0.41265 | 0.39768 | 0.3721 | 0.31046 | 0.27737 | 0.16521 | 0.10534 | 0.11808 | 0.10921
| LOCHDONHEAD | ST |  |  | 0.36473 | 0.36402 | 0.36342 | 0.36175 | 0.35663 | 0.35626 | 0.35087 | 0.34181 | 0.33162 | 0.31491 | 0.25574 | 0.10203 | 0.059206 | 0.043785 | 0.52419 | 0.52243 | 0.52083 | 0.51758 | 0.51318 | 0.51032 | 0.50589 | 0.49776 | 0.49059 | 0.47928 | 0.43787 | 0.32339 | 0.29546 | 0.2861 | 0.45219 | 0.45149 | 0.45087 | 0.44926 | 0.44417 | 0.44381 | 0.43837 | 0.4318 | 0.42464 | 0.41487 | 0.38286 | 0.23798 | 0.16649 | 0.15
| LOCHDONHEAD | SP |  |  | 0.3662 | 0.3663 | 0.36636 | 0.36643 | 0.36096 | 0.35982 | 0.35329 | 0.34411 | 0.33153 | 0.31192 | 0.25276 | 0.10183 | -0.019645 | -0.054964 | 0.52577 | 0.525 | 0.52351 | 0.52244 | 0.51856 | 0.51433 | 0.50959 | 0.50347 | 0.49487 | 0.48201 | 0.44624 | 0.34938 | 0.26555 | 0.24222 | 0.45353 | 0.45356 | 0.45352 | 0.4535 | 0.44822 | 0.44708 | 0.44141 | 0.43494 | 0.42754 | 0.41772 | 0.3878 | 0.24644 | 0.12547 | 0.07078
KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | 3.4429 | 3.417 | 3.3822 | 3.3387 | 3.2226 | 3.0917 | 2.9541 | 2.8162 | 2.6238 | 2.5026 | 2.2115 | 2.1425 | 2.2079 | 2.1019 | 3.6032 | 3.5886 | 3.5703 | 3.5467 | 3.4932 | 3.431 | 3.3632 | 3.2958 | 3.1968 | 3.1136 | 2.9263 | 2.8862 | 2.887 | 2.8105 | 1.6367 | 1.6329 | 1.6191 | 1.5921 | 1.5064 | 1.408 | 1.3137 | 1.2177 | 1.0862 | 1.0224 | 0.8334 | 0.74234 | 0.79897 | 0.72146
| LOCHEARNHEAD | CT |  |  | 3.4694 | 3.4571 | 3.4316 | 3.3955 | 3.2811 | 3.1728 | 3.0406 | 2.9002 | 2.7652 | 2.688 | 2.3688 | 2.2197 | 2.2138 | 2.1968 | 3.6105 | 3.6005 | 3.5836 | 3.56 | 3.5064 | 3.4572 | 3.3998 | 3.3368 | 3.2742 | 3.228 | 2.9977 | 2.9114 | 2.8968 | 2.8717 | 1.6367 | 1.6329 | 1.6276 | 1.6201 | 1.5604 | 1.4779 | 1.3732 | 1.2652 | 1.1594 | 1.1135 | 0.96101 | 0.8258 | 0.81822 | 0.80228
| LOCHEARNHEAD | LW |  |  | 3.4429 | 3.417 | 3.3822 | 3.3387 | 3.2226 | 3.0917 | 2.9541 | 2.8162 | 2.6238 | 2.5026 | 2.2115 | 2.1425 | 2.2079 | 2.1882 | 3.6032 | 3.5886 | 3.5703 | 3.5467 | 3.4932 | 3.431 | 3.3632 | 3.2958 | 3.1968 | 3.1136 | 2.9263 | 2.8862 | 2.9082 | 2.9014 | 1.6383 | 1.6345 | 1.6191 | 1.5921 | 1.5064 | 1.408 | 1.3137 | 1.2177 | 1.0862 | 1.0224 | 0.8334 | 0.74234 | 0.79897 | 0.78263
| LOCHEARNHEAD | ST |  |  | 3.4718 | 3.4624 | 3.453 | 3.4415 | 3.4336 | 3.4224 | 3.4075 | 3.3918 | 3.3597 | 3.3093 | 3.1342 | 2.7206 | 2.6022 | 2.5442 | 3.6168 | 3.6108 | 3.6046 | 3.5962 | 3.5899 | 3.5813 | 3.5699 | 3.5583 | 3.5389 | 3.5091 | 3.3947 | 3.0924 | 3.0304 | 2.9899 | 1.6407 | 1.6391 | 1.6374 | 1.6346 | 1.6324 | 1.6293 | 1.6252 | 1.6217 | 1.6165 | 1.5882 | 1.4833 | 1.2622 | 1.1188 | 1.0646
| LOCHEARNHEAD | SP |  |  | 3.4788 | 3.4741 | 3.4706 | 3.4639 | 3.4418 | 3.417 | 3.391 | 3.3582 | 3.3207 | 3.27 | 3.0791 | 2.5445 | 2.2302 | 2.1019 | 3.6189 | 3.615 | 3.6115 | 3.6053 | 3.5943 | 3.5806 | 3.5663 | 3.5475 | 3.5253 | 3.4983 | 3.4049 | 3.0766 | 2.887 | 2.8105 | 1.6404 | 1.6391 | 1.6378 | 1.6354 | 1.6336 | 1.6305 | 1.6273 | 1.6111 | 1.5911 | 1.553 | 1.4156 | 1.0785 | 0.84286 | 0.72146
LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | 16.7971 | 16.6438 | 16.4875 | 16.4253 | 16.1733 | 15.9311 | 15.7031 | 15.4553 | 15.3302 | 15.2114 | 14.7841 | 13.9385 | 13.0361 | 12.2254 | 17.4181 | 17.3913 | 17.3446 | 17.3165 | 17.2733 | 17.2281 | 17.1801 | 17.128 | 17.0835 | 17.0301 | 16.759 | 16.0141 | 15.1333 | 13.2909 | 16.1798 | 16.0529 | 15.9326 | 15.8787 | 15.6569 | 15.4435 | 15.2427 | 15.0232 | 14.9107 | 14.8036 | 14.4332 | 13.7671 | 13.137 | 12.5944
| LOCHEE | CT |  |  | 16.8099 | 16.6933 | 16.5824 | 16.5527 | 16.3092 | 16.0715 | 15.916 | 15.7788 | 15.6421 | 15.4851 | 14.9661 | 13.9385 | 13.0361 | 12.2254 | 17.4181 | 17.3913 | 17.3446 | 17.3165 | 17.2733 | 17.2281 | 17.1801 | 17.128 | 17.0835 | 17.0301 | 16.759 | 16.0141 | 15.1964 | 14.1814 | 16.1904 | 16.0955 | 16.0148 | 15.9884 | 15.7734 | 15.5636 | 15.4262 | 15.3046 | 15.183 | 15.0434 | 14.5964 | 13.7671 | 13.137 | 12.5944
| LOCHEE | LW |  |  | 16.7971 | 16.6438 | 16.4875 | 16.4253 | 16.1733 | 15.9311 | 15.7031 | 15.4553 | 15.3302 | 15.2114 | 14.7841 | 13.9927 | 13.1965 | 12.4075 | 17.4248 | 17.402 | 17.3608 | 17.3432 | 17.3014 | 17.2603 | 17.2161 | 17.1651 | 17.122 | 17.07 | 16.8448 | 16.371 | 15.9203 | 15.4605 | 16.1798 | 16.0529 | 15.9326 | 15.8787 | 15.6569 | 15.4435 | 15.2427 | 15.0232 | 14.9107 | 14.8036 | 14.4332 | 13.8097 | 13.2737 | 12.7412
| LOCHEE | ST |  |  | 16.8681 | 16.8166 | 16.7259 | 16.6887 | 16.6415 | 16.5988 | 16.5415 | 16.4736 | 16.4464 | 16.3903 | 16.1609 | 15.3786 | 14.451 | 13.5256 | 17.4287 | 17.4075 | 17.3678 | 17.3556 | 17.3319 | 17.3091 | 17.2713 | 17.2385 | 17.2109 | 17.1739 | 17.0275 | 16.5743 | 15.7128 | 14.6556 | 16.2425 | 16.2051 | 16.1427 | 16.1113 | 16.0706 | 16.0339 | 15.9839 | 15.9253 | 15.9017 | 15.8528 | 15.6643 | 15.0426 | 14.371 | 13.7079
| LOCHEE | SP |  |  | 16.8894 | 16.8523 | 16.7731 | 16.7565 | 16.714 | 16.6686 | 16.6169 | 16.5702 | 16.5309 | 16.4694 | 16.2261 | 15.4797 | 14.5481 | 13.7098 | 17.4287 | 17.4084 | 17.3691 | 17.3581 | 17.3353 | 17.3132 | 17.2769 | 17.2459 | 17.2201 | 17.1841 | 17.0523 | 16.4228 | 15.1333 | 13.2909 | 16.2611 | 16.2365 | 16.1842 | 16.1713 | 16.1349 | 16.0961 | 16.0514 | 16.0118 | 15.9781 | 15.9249 | 15.7279 | 15.1445 | 14.4638 | 13.8729
PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | YES | 16.0401 | 15.8332 | 15.4212 | 14.939 | 14.1029 | 13.3849 | 12.6885 | 12.0652 | 11.5228 | 11.2427 | 10.0233 | 9.6043 | 9.8873 | 9.7981 | 18.4064 | 18.0911 | 17.6463 | 17.1823 | 16.4958 | 16.0058 | 15.5805 | 15.1663 | 14.8032 | 14.5527 | 13.7624 | 13.4973 | 13.6399 | 13.3314 | 15.7079 | 15.4804 | 15.0343 | 14.567 | 13.8394 | 13.1705 | 12.4862 | 11.8346 | 11.2642 | 10.9449 | 9.9401 | 9.711 | 10.0682 | 9.9587
| LOCHGILPHEAD | CT |  |  | 16.077 | 15.89 | 15.5744 | 15.113 | 14.2735 | 13.6465 | 13.1045 | 12.6064 | 12.1279 | 11.8241 | 10.6833 | 9.8813 | 10.0433 | 10.0812 | 18.4493 | 18.1536 | 17.7222 | 17.2698 | 16.5807 | 16.1203 | 15.7255 | 15.3716 | 15.0551 | 14.8251 | 14.0834 | 13.6086 | 13.6399 | 13.5651 | 15.7085 | 15.4841 | 15.0565 | 14.6108 | 13.8906 | 13.4091 | 12.8803 | 12.3312 | 11.8365 | 11.5372 | 10.5889 | 9.9866 | 10.2165 | 10.266
| LOCHGILPHEAD | LW |  |  | 16.0401 | 15.8332 | 15.4212 | 14.939 | 14.1029 | 13.3849 | 12.6885 | 12.0652 | 11.5228 | 11.2427 | 10.0233 | 9.6043 | 9.8873 | 9.7981 | 18.4064 | 18.0911 | 17.6463 | 17.1823 | 16.4958 | 16.0058 | 15.5805 | 15.1663 | 14.8032 | 14.5527 | 13.7624 | 13.4973 | 13.6442 | 13.596 | 15.7079 | 15.4804 | 15.0343 | 14.567 | 13.8394 | 13.1705 | 12.4862 | 11.8346 | 11.2642 | 10.9449 | 9.9401 | 9.711 | 10.0682 | 9.9587
| LOCHGILPHEAD | ST |  |  | 16.0762 | 15.8997 | 15.6493 | 15.3938 | 15.0426 | 14.8406 | 14.6552 | 14.4741 | 14.3144 | 14.0918 | 13.3554 | 11.9018 | 11.5101 | 11.426 | 18.4713 | 18.1998 | 17.8195 | 17.4322 | 17.0071 | 16.7775 | 16.5735 | 16.3884 | 16.2305 | 16.056 | 15.507 | 14.6668 | 14.3723 | 14.2315 | 15.7121 | 15.5439 | 15.1605 | 14.7749 | 14.3587 | 14.1426 | 13.9541 | 13.7883 | 13.6493 | 13.5053 | 13.0386 | 12.2425 | 11.913 | 11.814
| LOCHGILPHEAD | SP |  |  | 16.0838 | 15.918 | 15.6768 | 15.4356 | 15.1029 | 14.8434 | 14.6068 | 14.3794 | 14.1456 | 13.8681 | 13.0697 | 11.5246 | 10.3374 | 10.0211 | 18.4898 | 18.2313 | 17.864 | 17.4968 | 17.0402 | 16.7814 | 16.5514 | 16.343 | 16.1494 | 15.9463 | 15.3674 | 14.4717 | 13.7237 | 13.3314 | 15.7149 | 15.5542 | 15.207 | 14.84 | 14.4078 | 14.1772 | 13.9778 | 13.7856 | 13.6108 | 13.4159 | 12.8726 | 11.4104 | 10.4255 | 10.0827
CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | 0.48894 | 0.48811 | 0.48696 | 0.485 | 0.4826 | 0.47936 | 0.47391 | 0.45018 | 0.40744 | 0.38726 | 0.29702 | 0.28909 | 0.28615 | 0.27699 | 1.3279 | 1.3273 | 1.3266 | 1.3252 | 1.3236 | 1.3221 | 1.3205 | 1.3189 | 1.3162 | 1.3128 | 1.297 | 1.2929 | 1.2928 | 1.2927 | 0.63598 | 0.64184 | 0.63911 | 0.63443 | 0.61052 | 0.58752 | 0.56514 | 0.5404 | 0.50656 | 0.49349 | 0.44352 | 0.44166 | 0.43704 | 0.42972
| LOCHGOILHEAD | CT |  |  | 0.48894 | 0.48811 | 0.48696 | 0.485 | 0.4826 | 0.48023 | 0.47487 | 0.45152 | 0.4195 | 0.40288 | 0.32264 | 0.30003 | 0.31377 | 0.3166 | 1.3279 | 1.3273 | 1.3266 | 1.3252 | 1.3236 | 1.3221 | 1.3205 | 1.3189 | 1.317 | 1.3143 | 1.3001 | 1.2958 | 1.2955 | 1.2953 | 0.64885 | 0.65371 | 0.65224 | 0.64528 | 0.62008 | 0.59768 | 0.56901 | 0.54084 | 0.51445 | 0.50342 | 0.45966 | 0.44674 | 0.46463 | 0.46919
| LOCHGOILHEAD | LW |  |  | 0.48918 | 0.48848 | 0.48762 | 0.48651 | 0.48458 | 0.47936 | 0.47391 | 0.45018 | 0.40744 | 0.38726 | 0.29702 | 0.28909 | 0.30678 | 0.29864 | 1.3282 | 1.3277 | 1.3271 | 1.3264 | 1.3255 | 1.3242 | 1.3226 | 1.3195 | 1.3162 | 1.3128 | 1.297 | 1.2929 | 1.2928 | 1.2927 | 0.63598 | 0.64184 | 0.63911 | 0.63443 | 0.61052 | 0.58752 | 0.56514 | 0.5404 | 0.50656 | 0.49349 | 0.44352 | 0.44166 | 0.45979 | 0.45105
| LOCHGOILHEAD | ST |  |  | 0.48967 | 0.48936 | 0.48887 | 0.4882 | 0.48748 | 0.48664 | 0.4856 | 0.48454 | 0.48313 | 0.48082 | 0.47096 | 0.42183 | 0.41146 | 0.4048 | 1.3284 | 1.3282 | 1.3279 | 1.3274 | 1.3268 | 1.3262 | 1.3254 | 1.3246 | 1.3236 | 1.322 | 1.3156 | 1.2968 | 1.2948 | 1.2946 | 0.64374 | 0.64295 | 0.64233 | 0.64242 | 0.64401 | 0.64462 | 0.64455 | 0.64583 | 0.64337 | 0.63704 | 0.61496 | 0.56666 | 0.56133 | 0.55691
| LOCHGOILHEAD | SP |  |  | 0.48991 | 0.48977 | 0.48945 | 0.48904 | 0.48846 | 0.48783 | 0.48688 | 0.48465 | 0.48159 | 0.47718 | 0.45274 | 0.34637 | 0.28615 | 0.27699 | 1.3286 | 1.3285 | 1.3283 | 1.328 | 1.3277 | 1.3273 | 1.3268 | 1.3262 | 1.3252 | 1.3238 | 1.3197 | 1.3062 | 1.2946 | 1.2938 | 0.64508 | 0.64443 | 0.64441 | 0.64446 | 0.63567 | 0.62755 | 0.61799 | 0.60819 | 0.59744 | 0.57959 | 0.54414 | 0.46879 | 0.43704 | 0.42972
GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | 1.4606 | 1.3392 | 1.1525 | 1.0584 | 0.91959 | 0.77414 | 0.65709 | 0.52907 | 0.36631 | 0.29463 | 0.089966 | 0.0032776 | 0.055714 | 0.0043954 | 1.6872 | 1.5601 | 1.3778 | 1.2955 | 1.2149 | 1.1305 | 1.073 | 1.0108 | 0.94124 | 0.89117 | 0.69429 | 0.63582 | 0.6551 | 0.62672 | 1.5416 | 1.4422 | 1.2875 | 1.2038 | 1.0858 | 0.96991 | 0.84498 | 0.71618 | 0.57222 | 0.47668 | 0.15018 | 0.060089 | 0.10608 | 0.062707
| LOCHINVER | CT |  |  | 1.489 | 1.3725 | 1.1929 | 1.099 | 0.96245 | 0.82565 | 0.67963 | 0.52907 | 0.38818 | 0.32631 | 0.17448 | 0.0441 | 0.077242 | 0.073754 | 1.6872 | 1.5601 | 1.3794 | 1.2997 | 1.2181 | 1.1336 | 1.0737 | 1.0117 | 0.94918 | 0.90449 | 0.75885 | 0.6413 | 0.6551 | 0.65413 | 1.5554 | 1.4552 | 1.2995 | 1.2038 | 1.0858 | 0.96991 | 0.84498 | 0.71618 | 0.59221 | 0.51573 | 0.25725 | 0.077155 | 0.11206 | 0.11801
| LOCHINVER | LW |  |  | 1.4606 | 1.3392 | 1.1525 | 1.0584 | 0.91959 | 0.77414 | 0.65709 | 0.53425 | 0.36631 | 0.29463 | 0.089966 | 0.0032776 | 0.055714 | 0.027992 | 1.6888 | 1.5614 | 1.3778 | 1.2955 | 1.2149 | 1.1305 | 1.073 | 1.0108 | 0.94124 | 0.89117 | 0.69429 | 0.63582 | 0.6551 | 0.64323 | 1.5416 | 1.4422 | 1.2875 | 1.211 | 1.0924 | 0.97722 | 0.86775 | 0.73394 | 0.57222 | 0.47668 | 0.15018 | 0.060089 | 0.10608 | 0.079487
| LOCHINVER | ST |  |  | 1.4832 | 1.3616 | 1.1907 | 1.1196 | 1.0666 | 1.0212 | 0.98693 | 0.94176 | 0.89531 | 0.84543 | 0.71733 | 0.50408 | 0.39174 | 0.33726 | 1.6912 | 1.5665 | 1.3892 | 1.3168 | 1.2597 | 1.2124 | 1.1779 | 1.1306 | 1.0904 | 1.0552 | 0.9714 | 0.82218 | 0.75334 | 0.72425 | 1.5527 | 1.4505 | 1.3074 | 1.2429 | 1.1979 | 1.1584 | 1.1237 | 1.0926 | 1.0488 | 0.99577 | 0.8479 | 0.48718 | 0.39308 | 0.36086
| LOCHINVER | SP |  |  | 1.4898 | 1.3714 | 1.2051 | 1.1381 | 1.0671 | 1.0065 | 0.95748 | 0.89433 | 0.84021 | 0.78 | 0.61492 | 0.31092 | 0.10307 | 0.0043954 | 1.6919 | 1.5677 | 1.3909 | 1.3197 | 1.2641 | 1.2166 | 1.18 | 1.132 | 1.0928 | 1.0604 | 0.98772 | 0.86555 | 0.67387 | 0.62672 | 1.5617 | 1.4636 | 1.3247 | 1.2697 | 1.2153 | 1.1685 | 1.1287 | 1.0838 | 1.0261 | 0.96705 | 0.79231 | 0.4487 | 0.14472 | 0.062707
LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | 7.1791 | 6.5768 | 5.9789 | 5.3753 | 4.4824 | 3.8167 | 3.192 | 2.4937 | 1.703 | 0.96604 | -1.122 | -3.7232 | -4.8887 | -5.2971 | 8.8489 | 8.3435 | 7.7588 | 7.0988 | 6.3564 | 5.9047 | 5.4901 | 5.1046 | 4.6808 | 4.2228 | 2.8011 | 1.3764 | 0.71407 | 0.21215 | 7.7184 | 7.1685 | 6.6072 | 6.0329 | 5.2029 | 4.6005 | 4.0365 | 3.399 | 2.6787 | 1.9998 | 0.060167 | -2.2691 | -3.2899 | -3.6413
| LOCHSIDE | CT |  |  | 7.1949 | 6.6106 | 6.0362 | 5.4406 | 4.5638 | 3.9203 | 3.2796 | 2.6211 | 1.9074 | 1.1408 | -1.1143 | -3.7232 | -4.8887 | -5.2971 | 8.8489 | 8.3469 | 7.7588 | 7.0988 | 6.3564 | 5.9047 | 5.4901 | 5.1046 | 4.6904 | 4.2573 | 2.8301 | 1.3764 | 0.71407 | 0.21215 | 7.7337 | 7.2003 | 6.6585 | 6.0842 | 5.2637 | 4.6807 | 4.1028 | 3.5068 | 2.8609 | 2.164 | 0.093847 | -2.2691 | -3.2899 | -3.6413
| LOCHSIDE | LW |  |  | 7.1791 | 6.5768 | 5.9789 | 5.3753 | 4.4824 | 3.8167 | 3.192 | 2.4937 | 1.703 | 0.96604 | -1.122 | -3.1577 | -4.0523 | -4.3824 | 8.8497 | 8.3435 | 7.7779 | 7.1258 | 6.3853 | 5.9323 | 5.5234 | 5.1198 | 4.6808 | 4.2228 | 2.8011 | 1.6419 | 1.2972 | 1.1643 | 7.7184 | 7.1685 | 6.6072 | 6.0329 | 5.2029 | 4.6005 | 4.0365 | 3.399 | 2.6787 | 1.9998 | 0.060167 | -1.8054 | -2.5832 | -2.8657
| LOCHSIDE | ST |  |  | 7.2486 | 6.6977 | 6.1193 | 5.5241 | 4.91 | 4.5623 | 4.2289 | 3.9193 | 3.6102 | 3.2427 | 2.1969 | 0.51564 | -0.47141 | -1.0053 | 8.8825 | 8.4031 | 7.8305 | 7.1943 | 6.5315 | 6.1751 | 5.85 | 5.5624 | 5.2559 | 4.934 | 4.0481 | 2.8748 | 2.1676 | 1.7568 | 7.7839 | 7.2831 | 6.7429 | 6.1783 | 5.5965 | 5.2707 | 4.9674 | 4.6862 | 4.4039 | 4.0666 | 3.0861 | 1.4649 | 0.5356 | 0.082118
| LOCHSIDE | SP |  |  | 7.2827 | 6.7497 | 6.1877 | 5.6051 | 4.9672 | 4.6009 | 4.2551 | 3.9387 | 3.5934 | 3.2128 | 2.246 | 0.95538 | 0.010315 | -0.22191 | 8.8983 | 8.4269 | 7.852 | 7.2216 | 6.557 | 6.2005 | 5.8803 | 5.5977 | 5.2915 | 4.9787 | 4.1763 | 3.3641 | 2.2138 | 1.1861 | 7.815 | 7.33 | 6.8041 | 6.2542 | 5.6542 | 5.3128 | 4.9984 | 4.7133 | 4.3994 | 4.0539 | 3.1606 | 1.9393 | 0.9897 | 0.76207
BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | 5.0383 | 5.0299 | 5.0208 | 5.0082 | 4.979 | 1.995 | 1.9597 | 1.9198 | 1.8494 | 1.8064 | 1.7032 | 1.6485 | 1.6643 | 1.6201 | 4.2013 | 4.1962 | 4.1914 | 4.1837 | 4.1703 | 1.4286 | 1.4108 | 1.3889 | 1.352 | 1.3239 | 1.263 | 1.2306 | 1.2359 | 1.2033 | 4.0328 | 4.0228 | 4.0115 | 3.9974 | 3.9741 | 1.2226 | 1.1934 | 1.1611 | 1.113 | 1.0736 | 0.95908 | 0.86368 | 0.87144 | 0.86871
| LOGIE PERT | CT |  |  | 5.0459 | 5.0432 | 5.0382 | 5.0298 | 5.0017 | 2.0251 | 1.9768 | 1.9245 | 1.8758 | 1.8474 | 1.7535 | 1.684 | 1.6699 | 1.6588 | 4.2031 | 4.2005 | 4.1967 | 4.19 | 4.1756 | 1.4377 | 1.416 | 1.3924 | 1.37 | 1.3523 | 1.2883 | 1.2472 | 1.2376 | 1.2267 | 4.0369 | 4.0306 | 4.0221 | 4.011 | 3.9887 | 1.2409 | 1.2065 | 1.1691 | 1.1327 | 1.1039 | 1.0199 | 0.93272 | 0.92189 | 0.91486
| LOGIE PERT | LW |  |  | 5.0383 | 5.0299 | 5.0208 | 5.0082 | 4.979 | 1.995 | 1.9597 | 1.9198 | 1.8494 | 1.8064 | 1.7032 | 1.6485 | 1.6643 | 1.6583 | 4.2013 | 4.1962 | 4.1914 | 4.1837 | 4.1703 | 1.4286 | 1.4108 | 1.3889 | 1.352 | 1.3239 | 1.263 | 1.2306 | 1.2359 | 1.2334 | 4.0328 | 4.0228 | 4.0115 | 3.9974 | 3.9741 | 1.2226 | 1.1934 | 1.1611 | 1.113 | 1.0736 | 0.95908 | 0.86368 | 0.87144 | 0.86871
| LOGIE PERT | ST |  |  | 5.0457 | 5.0428 | 5.0389 | 5.0352 | 5.032 | 2.078 | 2.0723 | 2.0669 | 2.054 | 2.0364 | 1.9742 | 1.8423 | 1.7767 | 1.7489 | 4.2046 | 4.2027 | 4.1998 | 4.1968 | 4.1943 | 1.4663 | 1.4615 | 1.4575 | 1.4499 | 1.4397 | 1.4003 | 1.3091 | 1.275 | 1.2579 | 4.0413 | 4.0377 | 4.0334 | 4.0286 | 4.0235 | 1.2923 | 1.285 | 1.2765 | 1.2633 | 1.2447 | 1.1779 | 1.0201 | 0.94753 | 0.9312
| LOGIE PERT | SP |  |  | 5.0482 | 5.047 | 5.0455 | 5.0426 | 5.0361 | 2.0797 | 2.0731 | 2.0644 | 2.0543 | 2.0398 | 1.9698 | 1.7945 | 1.6761 | 1.6201 | 4.2057 | 4.2047 | 4.2032 | 4.2003 | 4.1967 | 1.4679 | 1.4641 | 1.4587 | 1.4523 | 1.4437 | 1.408 | 1.3029 | 1.2362 | 1.2033 | 4.0425 | 4.0399 | 4.037 | 4.0333 | 4.0273 | 1.2961 | 1.2892 | 1.2813 | 1.2721 | 1.259 | 1.204 | 1.0545 | 0.93268 | 0.8953
MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | 12.4212 | 12.5971 | 11.8662 | 11.094 | 9.8329 | 8.5893 | 7.0854 | 5.4687 | 3.9456 | 2.8031 | -0.57113 | -4.4971 | -6.3904 | -7.2324 | 13.4593 | 13.733 | 13.1265 | 12.482 | 11.6154 | 10.7757 | 9.7034 | 8.5485 | 7.4483 | 6.616 | 4.1817 | 1.8329 | 0.68246 | -0.30353 | 12.2091 | 12.4031 | 11.7336 | 11.0328 | 9.886 | 8.7561 | 7.3709 | 5.8747 | 4.464 | 3.3993 | 0.26118 | -3.2367 | -4.8512 | -5.5309
| LONGHAUGH | CT |  |  | 12.4411 | 12.666 | 11.9776 | 11.2766 | 10.0497 | 8.8202 | 7.4067 | 6.0043 | 4.6141 | 3.3942 | -0.39091 | -4.4971 | -6.3904 | -7.2324 | 13.4593 | 13.7376 | 13.1364 | 12.4943 | 11.6173 | 10.7757 | 9.718 | 8.6651 | 7.642 | 6.7948 | 4.1921 | 1.8329 | 0.68246 | -0.30353 | 12.224 | 12.4605 | 11.827 | 11.184 | 10.0631 | 8.9435 | 7.638 | 6.3393 | 5.0571 | 3.9351 | 0.44733 | -3.2367 | -4.8512 | -5.5309
| LONGHAUGH | LW |  |  | 12.4212 | 12.5971 | 11.8662 | 11.094 | 9.8329 | 8.5893 | 7.0854 | 5.4687 | 3.9456 | 2.8031 | -0.57113 | -3.7262 | -5.1412 | -5.833 | 13.4662 | 13.733 | 13.1265 | 12.482 | 11.6154 | 10.7857 | 9.7034 | 8.5485 | 7.4483 | 6.616 | 4.1817 | 2.3439 | 1.7304 | 1.4016 | 12.2091 | 12.4031 | 11.7336 | 11.0328 | 9.886 | 8.7561 | 7.3709 | 5.8747 | 4.464 | 3.3993 | 0.26118 | -2.5927 | -3.7808 | -4.3292
| LONGHAUGH | ST |  |  | 12.5758 | 12.8805 | 12.2647 | 11.601 | 10.9379 | 10.3275 | 9.4626 | 8.6237 | 7.8613 | 7.2356 | 5.2544 | 2.5448 | 0.84545 | -0.26946 | 13.5316 | 13.8527 | 13.2942 | 12.698 | 12.0693 | 11.4955 | 10.6676 | 9.863 | 9.0766 | 8.4609 | 6.5582 | 4.5899 | 3.339 | 2.224 | 12.3475 | 12.6571 | 12.0911 | 11.4887 | 10.8722 | 10.3048 | 9.487 | 8.6932 | 7.972 | 7.3825 | 5.5122 | 3.0074 | 1.5337 | 0.5933
| LONGHAUGH | SP |  |  | 12.6223 | 12.9578 | 12.3713 | 11.7418 | 11.0571 | 10.426 | 9.5513 | 8.7169 | 7.9158 | 7.3028 | 5.3848 | 3.1229 | 1.6062 | 0.95999 | 13.5469 | 13.8808 | 13.3342 | 12.7571 | 12.1214 | 11.5425 | 10.7143 | 9.9061 | 9.0991 | 8.5091 | 6.694 | 4.7793 | 3.0525 | 1.1083 | 12.388 | 12.7251 | 12.1854 | 11.6151 | 10.9809 | 10.3973 | 9.5733 | 8.7855 | 8.0302 | 7.4557 | 5.662 | 3.5675 | 2.228 | 1.7164
ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | YES | 7.6655 | 7.6255 | 7.5715 | 7.4836 | 7.277 | 7.0554 | 6.7381 | 6.3832 | 6.0142 | 5.584 | 4.1536 | 1.8948 | 0.89231 | 0.53994 | 8.8756 | 8.8417 | 8.7993 | 8.7277 | 8.6059 | 8.477 | 8.313 | 8.127 | 7.9263 | 7.6688 | 6.7143 | 5.5543 | 5.0441 | 4.6906 | 7.4831 | 7.4461 | 7.396 | 7.3117 | 7.1221 | 6.9196 | 6.6332 | 6.3123 | 5.9737 | 5.5857 | 4.2497 | 2.2254 | 1.3554 | 1.0583
| LOSSIEMOUTH | CT |  |  | 7.6655 | 7.6255 | 7.5715 | 7.4836 | 7.277 | 7.0554 | 6.7381 | 6.3832 | 6.0161 | 5.584 | 4.1536 | 1.8948 | 0.89231 | 0.53994 | 8.8756 | 8.8417 | 8.7993 | 8.7277 | 8.6059 | 8.477 | 8.313 | 8.127 | 7.935 | 7.6895 | 6.8478 | 5.5543 | 5.0441 | 4.6906 | 7.4831 | 7.4461 | 7.396 | 7.3117 | 7.1221 | 6.9196 | 6.6332 | 6.3123 | 5.9805 | 5.5857 | 4.2749 | 2.2254 | 1.3554 | 1.0583
| LOSSIEMOUTH | LW |  |  | 7.6728 | 7.6406 | 7.5971 | 7.5371 | 7.3451 | 7.1076 | 6.8478 | 6.508 | 6.0142 | 5.6037 | 4.1667 | 2.4954 | 1.7043 | 1.4095 | 8.8837 | 8.8554 | 8.8215 | 8.7755 | 8.6746 | 8.5476 | 8.4077 | 8.2 | 7.9263 | 7.6688 | 6.7143 | 5.7765 | 5.4878 | 5.3742 | 7.4906 | 7.461 | 7.421 | 7.365 | 7.1917 | 6.9763 | 6.7399 | 6.4253 | 5.9737 | 5.5929 | 4.2497 | 2.7332 | 2.0529 | 1.8062
| LOSSIEMOUTH | ST |  |  | 7.7041 | 7.6816 | 7.6559 | 7.6225 | 7.6022 | 7.5748 | 7.5428 | 7.495 | 7.438 | 7.3171 | 6.8577 | 5.3319 | 4.4647 | 4.0455 | 8.904 | 8.887 | 8.867 | 8.8377 | 8.8131 | 8.7832 | 8.7493 | 8.7029 | 8.6484 | 8.5458 | 8.1577 | 6.9148 | 6.2669 | 5.888 | 7.5204 | 7.5014 | 7.4791 | 7.4483 | 7.4293 | 7.4036 | 7.3731 | 7.3276 | 7.2738 | 7.1593 | 6.7246 | 5.2765 | 4.4872 | 4.1308
| LOSSIEMOUTH | SP |  |  | 7.7213 | 7.7077 | 7.6923 | 7.6726 | 7.6431 | 7.6125 | 7.5714 | 7.5206 | 7.4444 | 7.3397 | 6.9549 | 5.9896 | 4.9664 | 4.7573 | 8.9117 | 8.8991 | 8.8843 | 8.8656 | 8.8411 | 8.8151 | 8.7817 | 8.741 | 8.6784 | 8.5955 | 8.2746 | 7.4426 | 6.3086 | 5.5943 | 7.5359 | 7.525 | 7.5121 | 7.4948 | 7.469 | 7.4422 | 7.4052 | 7.3592 | 7.2879 | 7.1908 | 6.8355 | 5.9359 | 4.9552 | 4.7724
BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | 0.28089 | 0.27994 | 0.26633 | 0.24894 | 0.19227 | 0.13188 | 0.079501 | 0.011954 | -0.072719 | -0.1413 | -0.3074 | -0.38234 | -0.36006 | -0.4134 | 0.40783 | 0.40572 | 0.39812 | 0.3886 | 0.36168 | 0.33166 | 0.30663 | 0.2731 | 0.23466 | 0.19094 | 0.091169 | 0.044228 | 0.049421 | 0.024851 | 0.29048 | 0.28986 | 0.27743 | 0.26177 | 0.21128 | 0.15763 | 0.11172 | 0.056166 | -0.012004 | -0.072856 | -0.21657 | -0.28077 | -0.26338 | -0.30279
| LOWER OLLACH | CT |  |  | 0.30402 | 0.306 | 0.29915 | 0.27927 | 0.22265 | 0.16837 | 0.11217 | 0.049937 | -0.018269 | -0.061866 | -0.22842 | -0.33916 | -0.35637 | -0.37036 | 0.41557 | 0.41398 | 0.40884 | 0.39544 | 0.36763 | 0.34032 | 0.31376 | 0.28484 | 0.25616 | 0.23064 | 0.12218 | 0.058957 | 0.049421 | 0.038886 | 0.31216 | 0.31432 | 0.30826 | 0.29031 | 0.23992 | 0.19202 | 0.14033 | 0.085086 | 0.031804 | -0.0052877 | -0.15341 | -0.24553 | -0.25646 | -0.26566
| LOWER OLLACH | LW |  |  | 0.28089 | 0.27994 | 0.26633 | 0.24894 | 0.19227 | 0.13188 | 0.079501 | 0.011954 | -0.072719 | -0.1413 | -0.3074 | -0.38234 | -0.35915 | -0.36974 | 0.40783 | 0.40572 | 0.39812 | 0.3886 | 0.36168 | 0.33166 | 0.30663 | 0.2731 | 0.23466 | 0.19094 | 0.091169 | 0.044228 | 0.050411 | 0.046315 | 0.29048 | 0.28986 | 0.27743 | 0.26177 | 0.21128 | 0.15763 | 0.11172 | 0.056166 | -0.012004 | -0.072856 | -0.21657 | -0.28077 | -0.2629 | -0.27105
| LOWER OLLACH | ST |  |  | 0.29846 | 0.29428 | 0.29008 | 0.28424 | 0.27027 | 0.25386 | 0.24385 | 0.23464 | 0.22053 | 0.19644 | 0.1107 | -0.11275 | -0.19233 | -0.23954 | 0.41502 | 0.41256 | 0.40995 | 0.40527 | 0.39705 | 0.38739 | 0.38056 | 0.37391 | 0.36538 | 0.35089 | 0.29691 | 0.14542 | 0.10433 | 0.081078 | 0.30667 | 0.30284 | 0.29904 | 0.29371 | 0.28227 | 0.26856 | 0.25944 | 0.25111 | 0.23826 | 0.21627 | 0.13798 | -0.066448 | -0.13249 | -0.16511
| LOWER OLLACH | SP |  |  | 0.29845 | 0.29465 | 0.29103 | 0.28669 | 0.26073 | 0.23357 | 0.21381 | 0.19368 | 0.16789 | 0.13587 | 0.03802 | -0.20763 | -0.36006 | -0.4134 | 0.41476 | 0.41267 | 0.41027 | 0.40728 | 0.3952 | 0.3817 | 0.37228 | 0.36277 | 0.34883 | 0.33384 | 0.28572 | 0.1508 | 0.05581 | 0.024851 | 0.30664 | 0.30315 | 0.29986 | 0.2959 | 0.27316 | 0.24932 | 0.23096 | 0.21229 | 0.18836 | 0.15911 | 0.075095 | -0.13286 | -0.26338 | -0.30279
KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | 0.20027 | 0.19946 | 0.19848 | 0.19747 | 0.19445 | 0.19145 | 0.18807 | 0.18466 | 0.17882 | 0.17567 | 0.16305 | 0.15887 | 0.15911 | 0.15626 | 0.19571 | 0.19521 | 0.1947 | 0.19421 | 0.19275 | 0.1914 | 0.18968 | 0.18796 | 0.18517 | 0.18348 | 0.17538 | 0.16939 | 0.16966 | 0.1696 | 0.18087 | 0.18012 | 0.17922 | 0.17831 | 0.17557 | 0.17294 | 0.16987 | 0.16677 | 0.16154 | 0.15867 | 0.14658 | 0.14281 | 0.14311 | 0.14063
| LUBNAIG | CT |  |  | 0.20159 | 0.20107 | 0.20065 | 0.19954 | 0.19677 | 0.19391 | 0.18951 | 0.18509 | 0.18072 | 0.17822 | 0.16795 | 0.1612 | 0.15911 | 0.15776 | 0.19622 | 0.19576 | 0.19549 | 0.19472 | 0.19347 | 0.1921 | 0.19011 | 0.18833 | 0.18644 | 0.18503 | 0.17819 | 0.17475 | 0.17397 | 0.17349 | 0.18204 | 0.18152 | 0.18113 | 0.18005 | 0.17757 | 0.17498 | 0.17103 | 0.16725 | 0.16344 | 0.16112 | 0.15111 | 0.14495 | 0.14311 | 0.14197
| LUBNAIG | LW |  |  | 0.20027 | 0.19946 | 0.19848 | 0.19747 | 0.19445 | 0.19145 | 0.18807 | 0.18466 | 0.17882 | 0.17567 | 0.16305 | 0.15887 | 0.16008 | 0.15981 | 0.19571 | 0.19521 | 0.1947 | 0.19421 | 0.19275 | 0.1914 | 0.18968 | 0.18796 | 0.18517 | 0.18348 | 0.17538 | 0.16939 | 0.16966 | 0.1696 | 0.18087 | 0.18012 | 0.17922 | 0.17831 | 0.17557 | 0.17294 | 0.16987 | 0.16677 | 0.16154 | 0.15867 | 0.14658 | 0.14281 | 0.14385 | 0.14361
| LUBNAIG | ST |  |  | 0.2014 | 0.2012 | 0.2009 | 0.20036 | 0.2 | 0.19958 | 0.19889 | 0.19816 | 0.19717 | 0.19526 | 0.18929 | 0.17433 | 0.16814 | 0.16529 | 0.1962 | 0.19611 | 0.19593 | 0.19553 | 0.19533 | 0.19509 | 0.19464 | 0.19415 | 0.19372 | 0.19263 | 0.18919 | 0.17826 | 0.17345 | 0.1728 | 0.18188 | 0.18171 | 0.18143 | 0.1809 | 0.18057 | 0.18018 | 0.17952 | 0.17883 | 0.17795 | 0.17617 | 0.17063 | 0.15648 | 0.15098 | 0.14849
| LUBNAIG | SP |  |  | 0.20143 | 0.20125 | 0.20109 | 0.2008 | 0.1996 | 0.19888 | 0.19779 | 0.1968 | 0.19551 | 0.19389 | 0.18725 | 0.17379 | 0.16057 | 0.15626 | 0.19621 | 0.19613 | 0.19606 | 0.19587 | 0.19522 | 0.19493 | 0.19438 | 0.19392 | 0.19323 | 0.19242 | 0.18915 | 0.18241 | 0.1744 | 0.1728 | 0.18191 | 0.18175 | 0.18161 | 0.18134 | 0.18023 | 0.17959 | 0.1786 | 0.17771 | 0.17652 | 0.17504 | 0.16903 | 0.15694 | 0.14437 | 0.14063
LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | 7.7751 | 7.4486 | 7.1183 | 6.8877 | 6.4323 | 5.9496 | 5.4384 | 4.8274 | 4.1607 | 3.6075 | 2.0539 | 0.72737 | 0.084575 | -0.17633 | 8.5559 | 8.2944 | 7.9723 | 7.7534 | 7.5006 | 7.2191 | 6.9629 | 6.6786 | 6.3613 | 6.0423 | 5.1845 | 4.3651 | 4.0264 | 3.612 | 6.8994 | 6.5855 | 6.2694 | 6.0554 | 5.6215 | 5.1619 | 4.693 | 4.1338 | 3.5228 | 3.0388 | 1.6885 | 0.4346 | -0.17448 | -0.41185
| LUNANHEAD | CT |  |  | 7.8265 | 7.5382 | 7.2244 | 6.9933 | 6.5293 | 6.0538 | 5.5823 | 5.0622 | 4.5273 | 4.0195 | 2.4007 | 0.72737 | 0.084575 | -0.17633 | 8.5559 | 8.2944 | 7.9934 | 7.7802 | 7.5159 | 7.2498 | 7.0081 | 6.7512 | 6.4703 | 6.1918 | 5.4452 | 4.477 | 4.0264 | 3.612 | 6.949 | 6.6739 | 6.3753 | 6.1703 | 5.7347 | 5.2864 | 4.8403 | 4.3531 | 3.8532 | 3.3971 | 1.981 | 0.4346 | -0.17448 | -0.41185
| LUNANHEAD | LW |  |  | 7.7751 | 7.4486 | 7.1183 | 6.8877 | 6.4323 | 5.9496 | 5.4384 | 4.8274 | 4.1607 | 3.6075 | 2.0539 | 0.81823 | 0.44619 | 0.26137 | 8.565 | 8.3074 | 7.9723 | 7.7534 | 7.5006 | 7.2191 | 6.9629 | 6.6786 | 6.3613 | 6.0423 | 5.1845 | 4.3651 | 4.2699 | 4.2187 | 6.8994 | 6.5855 | 6.2694 | 6.0554 | 5.6215 | 5.1619 | 4.693 | 4.1338 | 3.5228 | 3.0388 | 1.6885 | 0.55694 | 0.19262 | 0.0088157
| LUNANHEAD | ST |  |  | 7.8838 | 7.6379 | 7.3472 | 7.1832 | 7.0526 | 6.9233 | 6.8011 | 6.6909 | 6.5574 | 6.3604 | 5.6813 | 3.9553 | 3.1762 | 2.7439 | 8.5846 | 8.3439 | 8.0585 | 7.9239 | 7.8186 | 7.7226 | 7.6221 | 7.4967 | 7.3689 | 7.2112 | 6.685 | 5.4823 | 4.9214 | 4.7565 | 7.0029 | 6.765 | 6.4842 | 6.3327 | 6.2136 | 6.0982 | 5.9916 | 5.8946 | 5.7761 | 5.6039 | 5.0236 | 3.5538 | 2.8261 | 2.4137
| LUNANHEAD | SP |  |  | 7.9297 | 7.7011 | 7.4302 | 7.2933 | 7.1439 | 7.0037 | 6.8792 | 6.7471 | 6.5756 | 6.3921 | 5.7803 | 4.151 | 3.0397 | 2.7035 | 8.5896 | 8.3517 | 8.0694 | 7.9402 | 7.8381 | 7.7489 | 7.6749 | 7.5707 | 7.4463 | 7.3189 | 6.9475 | 6.0064 | 4.9171 | 3.9781 | 7.0438 | 6.8226 | 6.5606 | 6.4327 | 6.2934 | 6.1639 | 6.0505 | 5.9305 | 5.7802 | 5.6162 | 5.0679 | 3.6682 | 2.7019 | 2.3844
PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | 0.090163 | 0.089318 | 0.088712 | 0.088033 | 0.085882 | 0.084072 | 0.081481 | 0.078708 | 0.074537 | 0.07229 | 0.063311 | 0.060849 | 0.061559 | 0.059505 | 0.090519 | 0.090011 | 0.089666 | 0.089276 | 0.088053 | 0.087064 | 0.085818 | 0.084455 | 0.082456 | 0.081259 | 0.075569 | 0.074548 | 0.074872 | 0.074236 | 0.087828 | 0.086982 | 0.086304 | 0.085544 | 0.083287 | 0.081257 | 0.078902 | 0.07638 | 0.072601 | 0.070535 | 0.062076 | 0.059873 | 0.060557 | 0.058731
| LUSSAGIVEN | CT |  |  | 0.090766 | 0.090216 | 0.089892 | 0.089513 | 0.08732 | 0.085912 | 0.083281 | 0.080344 | 0.077128 | 0.075206 | 0.067529 | 0.063097 | 0.061559 | 0.06059 | 0.090814 | 0.090446 | 0.090238 | 0.089998 | 0.088729 | 0.087971 | 0.086527 | 0.085312 | 0.083861 | 0.082761 | 0.077699 | 0.075587 | 0.075063 | 0.074733 | 0.088537 | 0.088059 | 0.087727 | 0.087329 | 0.085083 | 0.083464 | 0.080576 | 0.077883 | 0.074994 | 0.073205 | 0.065919 | 0.061905 | 0.060557 | 0.059708
| LUSSAGIVEN | LW |  |  | 0.090163 | 0.089318 | 0.088712 | 0.088033 | 0.085882 | 0.084072 | 0.081481 | 0.078708 | 0.074537 | 0.07229 | 0.063311 | 0.060849 | 0.061801 | 0.061602 | 0.090519 | 0.090011 | 0.089666 | 0.089276 | 0.088053 | 0.087064 | 0.085818 | 0.084455 | 0.082456 | 0.081259 | 0.075569 | 0.074548 | 0.074872 | 0.074804 | 0.087828 | 0.086982 | 0.086304 | 0.085544 | 0.083287 | 0.081257 | 0.078902 | 0.07638 | 0.072601 | 0.070535 | 0.062076 | 0.059873 | 0.060707 | 0.060533
| LUSSAGIVEN | ST |  |  | 0.090667 | 0.090544 | 0.090419 | 0.089928 | 0.089609 | 0.089401 | 0.089042 | 0.087981 | 0.087325 | 0.086544 | 0.083054 | 0.072063 | 0.068225 | 0.066102 | 0.090788 | 0.090719 | 0.090648 | 0.090338 | 0.090148 | 0.090032 | 0.089814 | 0.089142 | 0.088764 | 0.088313 | 0.08619 | 0.078843 | 0.077277 | 0.076554 | 0.088414 | 0.088265 | 0.088115 | 0.087665 | 0.087324 | 0.087074 | 0.086696 | 0.085734 | 0.085017 | 0.084142 | 0.080562 | 0.070052 | 0.066384 | 0.064524
| LUSSAGIVEN | SP |  |  | 0.090748 | 0.090674 | 0.090607 | 0.090536 | 0.08971 | 0.089404 | 0.088893 | 0.088356 | 0.087154 | 0.086472 | 0.08284 | 0.073043 | 0.062916 | 0.059505 | 0.090828 | 0.090785 | 0.090744 | 0.0907 | 0.090202 | 0.090039 | 0.089745 | 0.089437 | 0.088698 | 0.088313 | 0.086291 | 0.081383 | 0.075418 | 0.074236 | 0.088513 | 0.088423 | 0.088342 | 0.088254 | 0.087463 | 0.087096 | 0.086553 | 0.085982 | 0.084852 | 0.084094 | 0.080113 | 0.071157 | 0.061725 | 0.058731
LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | 8.4703 | 8.3561 | 8.1632 | 7.9183 | 7.7289 | 7.5574 | 7.4088 | 7.2495 | 7.0441 | 6.7866 | 5.8177 | 4.6182 | 3.876 | 3.4084 | 9.5745 | 9.4736 | 9.2856 | 9.0268 | 8.8428 | 8.684 | 8.5347 | 8.3757 | 8.2196 | 8.0488 | 7.3876 | 6.4868 | 6.2755 | 5.8913 | 9.0522 | 8.9448 | 8.7559 | 8.511 | 8.3247 | 8.1529 | 7.9526 | 7.6993 | 7.449 | 7.2078 | 6.4149 | 5.2984 | 4.6673 | 4.3242
| LYNDHURST | CT |  |  | 8.4768 | 8.3604 | 8.1632 | 7.9183 | 7.7289 | 7.5574 | 7.4088 | 7.2495 | 7.0837 | 6.8388 | 5.9853 | 4.6629 | 3.876 | 3.4084 | 9.5798 | 9.4762 | 9.2856 | 9.0268 | 8.8428 | 8.684 | 8.5347 | 8.3757 | 8.2243 | 8.0563 | 7.5268 | 6.7901 | 6.3348 | 5.8913 | 9.0595 | 8.9494 | 8.7559 | 8.511 | 8.3247 | 8.1529 | 7.9673 | 7.7408 | 7.5148 | 7.2606 | 6.4635 | 5.2984 | 4.6673 | 4.3242
| LYNDHURST | LW |  |  | 8.4703 | 8.3561 | 8.1642 | 7.9289 | 7.7503 | 7.5865 | 7.4337 | 7.2551 | 7.0441 | 6.7866 | 5.8177 | 4.6182 | 4.08 | 3.6588 | 9.5745 | 9.4736 | 9.2881 | 9.0381 | 8.864 | 8.7126 | 8.5541 | 8.3837 | 8.2196 | 8.0488 | 7.3876 | 6.4868 | 6.2755 | 6.0878 | 9.0522 | 8.9448 | 8.7567 | 8.522 | 8.346 | 8.1802 | 7.9526 | 7.6993 | 7.449 | 7.2078 | 6.4149 | 5.3548 | 4.8224 | 4.5195
| LYNDHURST | ST |  |  | 8.4978 | 8.4069 | 8.2413 | 8.0433 | 7.911 | 7.8029 | 7.704 | 7.602 | 7.5063 | 7.3875 | 6.9276 | 5.5699 | 4.7332 | 4.4551 | 9.5943 | 9.51 | 9.3433 | 9.1201 | 8.9792 | 8.8682 | 8.7678 | 8.6687 | 8.5783 | 8.4725 | 8.0734 | 7.1395 | 6.5176 | 6.31 | 9.0775 | 8.9916 | 8.8283 | 8.6282 | 8.497 | 8.3908 | 8.2942 | 8.1953 | 8.1033 | 7.9899 | 7.5043 | 6.2175 | 5.4695 | 5.2141
| LYNDHURST | SP |  |  | 8.5002 | 8.413 | 8.2504 | 8.0578 | 7.9319 | 7.8324 | 7.7437 | 7.6551 | 7.5738 | 7.4832 | 7.1537 | 6.343 | 5.2666 | 4.8493 | 9.596 | 9.5142 | 9.3495 | 9.1301 | 8.9935 | 8.8883 | 8.7949 | 8.705 | 8.624 | 8.5364 | 8.2238 | 7.627 | 6.8898 | 6.0815 | 9.0802 | 8.9978 | 8.8374 | 8.643 | 8.5178 | 8.4197 | 8.3327 | 8.2464 | 8.1674 | 8.0802 | 7.7614 | 6.9111 | 5.9467 | 5.5657
THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | 0.62282 | 0.62262 | 0.61384 | 1.19 | 1.1586 | 1.1235 | 1.0826 | 1.0371 | 0.99296 | 0.9646 | 0.85712 | 0.82847 | 0.84036 | 0.82635 | 0.78564 | 0.78497 | 0.78079 | 1.3188 | 1.3008 | 1.2835 | 1.2645 | 1.2451 | 1.2252 | 1.2076 | 1.1336 | 1.1144 | 1.1135 | 1.1109 | 0.62449 | 0.62417 | 0.61625 | 1.1487 | 1.1207 | 1.089 | 1.0507 | 1.0102 | 0.97064 | 0.94377 | 0.84141 | 0.81441 | 0.82456 | 0.81439
| LYNESS | CT |  |  | 0.63484 | 0.63572 | 0.62808 | 1.1987 | 1.1603 | 1.1253 | 1.0826 | 1.0371 | 0.99296 | 0.96998 | 0.8894 | 0.83579 | 0.84036 | 0.84091 | 0.78972 | 0.78918 | 0.78514 | 1.3197 | 1.3008 | 1.2835 | 1.2645 | 1.2451 | 1.2252 | 1.2112 | 1.1578 | 1.1191 | 1.1135 | 1.1109 | 0.63495 | 0.63552 | 0.62853 | 1.1557 | 1.1208 | 1.089 | 1.0507 | 1.0102 | 0.97064 | 0.94906 | 0.87248 | 0.82155 | 0.82456 | 0.82505
| LYNESS | LW |  |  | 0.62282 | 0.62262 | 0.61384 | 1.19 | 1.1586 | 1.1235 | 1.0897 | 1.0514 | 0.99597 | 0.9646 | 0.85712 | 0.82847 | 0.84493 | 0.83152 | 0.78564 | 0.78497 | 0.78079 | 1.3188 | 1.3056 | 1.2891 | 1.2732 | 1.2534 | 1.2272 | 1.2076 | 1.1336 | 1.1144 | 1.1195 | 1.1145 | 0.62449 | 0.62417 | 0.61625 | 1.1487 | 1.1207 | 1.0891 | 1.0586 | 1.0235 | 0.97338 | 0.94377 | 0.84141 | 0.81441 | 0.82885 | 0.8171
| LYNESS | ST |  |  | 0.63299 | 0.63131 | 0.6301 | 1.2159 | 1.2134 | 1.2108 | 1.2087 | 1.2016 | 1.1924 | 1.1782 | 1.1319 | 1.0109 | 0.97127 | 0.95185 | 0.78976 | 0.78884 | 0.78811 | 1.3303 | 1.3282 | 1.3262 | 1.3246 | 1.3186 | 1.3133 | 1.3052 | 1.2776 | 1.1866 | 1.1633 | 1.1519 | 0.6335 | 0.63197 | 0.63085 | 1.1719 | 1.1693 | 1.1668 | 1.1648 | 1.1577 | 1.1492 | 1.136 | 1.0928 | 0.9715 | 0.93467 | 0.9174
| LYNESS | SP |  |  | 0.63436 | 0.63356 | 0.63327 | 1.2227 | 1.2141 | 1.2057 | 1.1961 | 1.184 | 1.1709 | 1.1474 | 1.0872 | 0.96467 | 0.85868 | 0.82635 | 0.79029 | 0.78984 | 0.78945 | 1.3338 | 1.3303 | 1.3266 | 1.3224 | 1.3165 | 1.3102 | 1.2978 | 1.2681 | 1.2043 | 1.1315 | 1.1144 | 0.63471 | 0.63398 | 0.63368 | 1.1781 | 1.1704 | 1.163 | 1.1544 | 1.1434 | 1.1316 | 1.11 | 1.0554 | 0.94333 | 0.84319 | 0.81439
STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | 0.17219 | 0.17283 | 0.1722 | 0.17125 | 0.16821 | 0.16521 | 0.16193 | 0.15893 | 0.15543 | 0.15311 | 0.14451 | 0.14206 | 0.13939 | 0.13824 | 0.16961 | 0.16983 | 0.16952 | 0.16904 | 0.16783 | 0.16655 | 0.16499 | 0.16359 | 0.16189 | 0.16053 | 0.15512 | 0.15368 | 0.15296 | 0.15251 | 0.16031 | 0.16087 | 0.16029 | 0.15942 | 0.15674 | 0.15406 | 0.1511 | 0.14839 | 0.14521 | 0.14305 | 0.13492 | 0.13264 | 0.13035 | 0.12934
| MAARUIG | CT |  |  | 0.17496 | 0.17592 | 0.17596 | 0.17541 | 0.17203 | 0.16929 | 0.16632 | 0.16334 | 0.16036 | 0.15845 | 0.15311 | 0.14569 | 0.14408 | 0.14303 | 0.17062 | 0.17094 | 0.17087 | 0.17047 | 0.16891 | 0.1677 | 0.16644 | 0.16518 | 0.16387 | 0.16276 | 0.1597 | 0.15522 | 0.15463 | 0.15424 | 0.16273 | 0.16356 | 0.16358 | 0.16304 | 0.16 | 0.15754 | 0.15489 | 0.15225 | 0.14958 | 0.1478 | 0.14283 | 0.13586 | 0.13445 | 0.13353
| MAARUIG | LW |  |  | 0.17219 | 0.17283 | 0.1722 | 0.17125 | 0.16821 | 0.16521 | 0.16193 | 0.15893 | 0.15543 | 0.15311 | 0.14451 | 0.14206 | 0.14354 | 0.14337 | 0.16961 | 0.16983 | 0.16952 | 0.16904 | 0.16783 | 0.16655 | 0.16499 | 0.16359 | 0.16189 | 0.16053 | 0.15512 | 0.15368 | 0.15422 | 0.15416 | 0.16031 | 0.16087 | 0.16029 | 0.15942 | 0.15674 | 0.15406 | 0.1511 | 0.14839 | 0.14521 | 0.14305 | 0.13492 | 0.13264 | 0.13393 | 0.13378
| MAARUIG | ST |  |  | 0.174 | 0.17365 | 0.17344 | 0.17343 | 0.17304 | 0.17256 | 0.17206 | 0.1713 | 0.17087 | 0.16955 | 0.16589 | 0.15474 | 0.15019 | 0.14783 | 0.17034 | 0.17015 | 0.17007 | 0.17001 | 0.16977 | 0.16952 | 0.16927 | 0.16874 | 0.16855 | 0.16779 | 0.16577 | 0.15866 | 0.15674 | 0.15588 | 0.16191 | 0.16158 | 0.1614 | 0.16138 | 0.16101 | 0.16057 | 0.16011 | 0.15938 | 0.159 | 0.15777 | 0.15439 | 0.14384 | 0.13978 | 0.13771
| MAARUIG | SP |  |  | 0.17387 | 0.17353 | 0.17316 | 0.17291 | 0.17123 | 0.16968 | 0.16778 | 0.16575 | 0.16396 | 0.16086 | 0.15591 | 0.14621 | 0.13939 | 0.13824 | 0.1703 | 0.17016 | 0.16996 | 0.16986 | 0.16923 | 0.16865 | 0.16786 | 0.16697 | 0.16624 | 0.1648 | 0.16257 | 0.1577 | 0.15296 | 0.15251 | 0.1618 | 0.16149 | 0.16116 | 0.16093 | 0.15946 | 0.15809 | 0.15641 | 0.15459 | 0.153 | 0.15021 | 0.14576 | 0.13693 | 0.13035 | 0.12934
LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | 12.4976 | 12.3366 | 12.2169 | 12.059 | 11.7188 | 11.3728 | 10.9586 | 10.4815 | 9.8966 | 9.381 | 7.5305 | 4.668 | 2.8403 | 1.9624 | 14.7585 | 14.6191 | 14.5287 | 14.387 | 14.2677 | 14.1353 | 13.9243 | 13.6851 | 13.3996 | 13.1134 | 12.1306 | 10.6662 | 9.6211 | 8.7469 | 13.4951 | 13.3569 | 13.2568 | 13.1108 | 12.8081 | 12.5002 | 12.1286 | 11.7057 | 11.1712 | 10.7144 | 9.0303 | 6.5279 | 5.0366 | 4.3545
| MACALPINE ROAD | CT |  |  | 12.515 | 12.3586 | 12.2486 | 12.0603 | 11.7199 | 11.3767 | 10.9586 | 10.4815 | 9.9389 | 9.381 | 7.5305 | 4.668 | 2.8403 | 1.9624 | 14.7585 | 14.6191 | 14.5287 | 14.387 | 14.2677 | 14.1353 | 13.9243 | 13.6851 | 13.3996 | 13.1134 | 12.1306 | 10.6662 | 9.6211 | 8.7469 | 13.5096 | 13.375 | 13.2828 | 13.1108 | 12.8081 | 12.5002 | 12.1286 | 11.7057 | 11.2259 | 10.7232 | 9.0303 | 6.5279 | 5.0366 | 4.3545
| MACALPINE ROAD | LW |  |  | 12.4976 | 12.3366 | 12.2169 | 12.059 | 11.7188 | 11.3728 | 11.0226 | 10.5664 | 9.8966 | 9.4105 | 7.8519 | 5.7825 | 4.2426 | 3.479 | 14.764 | 14.6276 | 14.5414 | 14.4109 | 14.3008 | 14.1949 | 14.0158 | 13.767 | 13.4096 | 13.1432 | 12.2768 | 11.2882 | 10.6264 | 10.2427 | 13.4951 | 13.3569 | 13.2568 | 13.1181 | 12.8238 | 12.518 | 12.2025 | 11.7835 | 11.1712 | 10.7144 | 9.2425 | 7.4367 | 6.1986 | 5.6139
| MACALPINE ROAD | ST |  |  | 12.5657 | 12.4334 | 12.339 | 12.2057 | 12.1018 | 12.0288 | 11.9737 | 11.9009 | 11.7927 | 11.6677 | 11.2092 | 9.7332 | 8.4231 | 7.3895 | 14.7727 | 14.6435 | 14.565 | 14.4488 | 14.3662 | 14.3084 | 14.258 | 14.2049 | 14.1111 | 14.0467 | 13.7598 | 12.5692 | 11.5996 | 10.6836 | 13.5561 | 13.4416 | 13.3639 | 13.2478 | 13.1666 | 13.1014 | 13.0452 | 12.9741 | 12.871 | 12.7461 | 12.2838 | 10.8368 | 9.7139 | 8.8934
| MACALPINE ROAD | SP |  |  | 12.5861 | 12.4638 | 12.3802 | 12.2666 | 12.1504 | 12.0669 | 11.9998 | 11.9153 | 11.7683 | 11.6386 | 11.2129 | 10.1929 | 9.1988 | 8.6601 | 14.7747 | 14.6472 | 14.5708 | 14.4593 | 14.3803 | 14.3264 | 14.2807 | 14.2327 | 14.1388 | 14.0812 | 13.7532 | 12.814 | 11.4239 | 9.9217 | 13.5745 | 13.4691 | 13.4013 | 13.3022 | 13.2099 | 13.1418 | 13.0819 | 13.0082 | 12.869 | 12.7457 | 12.3378 | 11.3536 | 10.4109 | 9.99
MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | YES | 9.8197 | 9.2125 | 8.6179 | 8.0141 | 7.1988 | 6.4943 | 5.7577 | 4.8859 | 3.8569 | 2.9133 | 0.55888 | -2.1154 | -3.3137 | -3.7331 | 12.1741 | 11.6029 | 11.0514 | 10.4566 | 9.818 | 9.312 | 8.7612 | 8.1913 | 7.5542 | 6.8756 | 5.28 | 3.8991 | 3.3019 | 2.9044 | 11.5018 | 10.9267 | 10.3645 | 9.7911 | 9.0329 | 8.3798 | 7.6809 | 6.879 | 5.9322 | 5.0465 | 2.8444 | 0.44358 | -0.60975 | -0.97638
| MACDUFF | CT |  |  | 9.8526 | 9.2622 | 8.6846 | 8.069 | 7.2643 | 6.5869 | 5.7577 | 4.8859 | 3.9932 | 3.0851 | 0.56049 | -2.1154 | -3.3137 | -3.7331 | 12.1745 | 11.6062 | 11.0514 | 10.4566 | 9.818 | 9.312 | 8.7612 | 8.1913 | 7.6064 | 6.9803 | 5.336 | 3.8991 | 3.3019 | 2.9044 | 11.5281 | 10.9671 | 10.4177 | 9.8282 | 9.0754 | 8.4439 | 7.6809 | 6.879 | 6.0581 | 5.2157 | 2.8724 | 0.44358 | -0.60975 | -0.97638
| MACDUFF | LW |  |  | 9.8197 | 9.2125 | 8.6179 | 8.0141 | 7.1988 | 6.4943 | 5.7808 | 4.9468 | 3.8569 | 2.9133 | 0.55888 | -1.3673 | -2.2063 | -2.5269 | 12.1741 | 11.6029 | 11.0514 | 10.4845 | 9.8584 | 9.3532 | 8.847 | 8.2554 | 7.5542 | 6.8756 | 5.28 | 4.2328 | 3.9178 | 3.7941 | 11.5018 | 10.9267 | 10.3645 | 9.7911 | 9.0329 | 8.3798 | 7.718 | 6.9387 | 5.9322 | 5.0465 | 2.8444 | 1.0868 | 0.35229 | 0.072166
| MACDUFF | ST |  |  | 9.8854 | 9.3036 | 8.7399 | 8.1754 | 7.6727 | 7.3004 | 6.9342 | 6.5746 | 6.1734 | 5.6795 | 4.4426 | 2.4466 | 1.3734 | 0.79984 | 12.2079 | 11.6557 | 11.1213 | 10.5793 | 10.0903 | 9.7296 | 9.3758 | 9.0311 | 8.6563 | 8.2034 | 7.1722 | 5.7008 | 4.9795 | 4.5097 | 11.562 | 11.0118 | 10.4785 | 9.9424 | 9.4639 | 9.1078 | 8.7575 | 8.4137 | 8.0311 | 7.5621 | 6.3831 | 4.475 | 3.4896 | 2.9842
| MACDUFF | SP |  |  | 9.9126 | 9.3497 | 8.8073 | 8.2614 | 7.7263 | 7.3377 | 6.9471 | 6.5511 | 6.1151 | 5.6136 | 4.4092 | 2.7048 | 1.4895 | 1.1288 | 12.2169 | 11.6736 | 11.1492 | 10.6215 | 10.1255 | 9.7692 | 9.4147 | 9.0592 | 8.6681 | 8.2363 | 7.2575 | 5.9909 | 4.8423 | 4.0158 | 11.5856 | 11.0525 | 10.5384 | 10.0208 | 9.5153 | 9.148 | 8.7786 | 8.404 | 7.99 | 7.5172 | 6.3863 | 4.7786 | 3.6179 | 3.2872
CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | 1.0137 | 1.0044 | 0.98494 | 0.95542 | 0.89291 | 0.82177 | 0.73526 | 0.63602 | 0.51585 | 0.44848 | 0.15009 | 0.094727 | 0.13485 | 0.081946 | 1.692 | 1.6853 | 1.6737 | 1.6543 | 1.619 | 1.5826 | 1.5322 | 1.4795 | 1.4093 | 1.3638 | 1.1533 | 1.1098 | 1.1276 | 1.0814 | 1.5383 | 1.5317 | 1.5136 | 1.4902 | 1.4208 | 1.347 | 1.2708 | 1.1765 | 1.0666 | 1.0209 | 0.77653 | 0.71586 | 0.75884 | 0.69555
| MACHRIE | CT |  |  | 1.0212 | 1.0134 | 0.99628 | 0.95542 | 0.89291 | 0.83015 | 0.73526 | 0.63602 | 0.54492 | 0.49154 | 0.26774 | 0.11829 | 0.16806 | 0.18182 | 1.6954 | 1.6894 | 1.679 | 1.6543 | 1.619 | 1.5826 | 1.5322 | 1.4795 | 1.4304 | 1.3945 | 1.2368 | 1.1215 | 1.1347 | 1.1315 | 1.5496 | 1.5461 | 1.5313 | 1.4988 | 1.4383 | 1.3805 | 1.2811 | 1.1765 | 1.0819 | 1.0454 | 0.90059 | 0.74733 | 0.79054 | 0.80069
| MACHRIE | LW |  |  | 1.0137 | 1.0044 | 0.98494 | 0.95964 | 0.89305 | 0.82177 | 0.742 | 0.64583 | 0.51585 | 0.44848 | 0.15009 | 0.094727 | 0.13485 | 0.10656 | 1.692 | 1.6853 | 1.6737 | 1.6588 | 1.6231 | 1.5847 | 1.5398 | 1.4821 | 1.4093 | 1.3638 | 1.1533 | 1.1098 | 1.1276 | 1.1156 | 1.5383 | 1.5317 | 1.5136 | 1.4902 | 1.4208 | 1.347 | 1.2708 | 1.1901 | 1.0666 | 1.0209 | 0.77653 | 0.71586 | 0.75884 | 0.73076
| MACHRIE | ST |  |  | 1.0241 | 1.0195 | 1.0139 | 1.0025 | 0.99873 | 0.99266 | 0.98392 | 0.9729 | 0.95239 | 0.91805 | 0.8033 | 0.44906 | 0.4086 | 0.39561 | 1.6988 | 1.6955 | 1.6912 | 1.6836 | 1.6791 | 1.673 | 1.6653 | 1.6559 | 1.6416 | 1.6187 | 1.5396 | 1.2758 | 1.2406 | 1.2246 | 1.5475 | 1.5441 | 1.5408 | 1.5327 | 1.5337 | 1.5334 | 1.5313 | 1.5278 | 1.5117 | 1.4863 | 1.4052 | 1.1014 | 1.0474 | 1.0271
| MACHRIE | SP |  |  | 1.0322 | 1.0314 | 1.0317 | 1.0314 | 1.0239 | 1.0129 | 1.0018 | 0.98493 | 0.95793 | 0.92408 | 0.78845 | 0.47274 | 0.15318 | 0.081946 | 1.7025 | 1.7009 | 1.6995 | 1.6978 | 1.6926 | 1.6847 | 1.6771 | 1.6657 | 1.6474 | 1.6265 | 1.5452 | 1.3488 | 1.1289 | 1.0814 | 1.557 | 1.5584 | 1.5613 | 1.5638 | 1.5568 | 1.5485 | 1.5365 | 1.5222 | 1.5047 | 1.4774 | 1.3613 | 1.0973 | 0.77623 | 0.69555
FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | 7.3717 | 7.3623 | 7.3448 | 7.3194 | 7.2354 | 7.1452 | 7.054 | 6.9524 | 6.8397 | 6.7711 | 6.5262 | 6.3775 | 6.4324 | 6.3997 | 7.3057 | 7.2976 | 7.2866 | 7.2699 | 7.2219 | 7.1726 | 7.1198 | 7.0589 | 6.9912 | 6.9438 | 6.7778 | 6.6656 | 6.6876 | 6.621 | 7.1646 | 7.156 | 7.1372 | 7.1086 | 7.0179 | 6.9196 | 6.8253 | 6.7325 | 6.6235 | 6.5679 | 6.3873 | 6.264 | 6.3216 | 6.2539
| MALLAIG | CT |  |  | 7.3903 | 7.3853 | 7.3701 | 7.3377 | 7.2416 | 7.1574 | 7.0649 | 6.9715 | 6.8891 | 6.8337 | 6.6615 | 6.4359 | 6.4616 | 6.4665 | 7.3136 | 7.3089 | 7.2987 | 7.2771 | 7.2219 | 7.1738 | 7.1207 | 7.0661 | 7.0162 | 6.9785 | 6.8598 | 6.6969 | 6.6969 | 6.6847 | 7.1711 | 7.1704 | 7.1692 | 7.1412 | 7.0417 | 6.9564 | 6.8587 | 6.764 | 6.6766 | 6.632 | 6.4993 | 6.3224 | 6.3551 | 6.3618
| MALLAIG | LW |  |  | 7.3717 | 7.3623 | 7.3448 | 7.3194 | 7.2354 | 7.1452 | 7.054 | 6.9524 | 6.8397 | 6.7711 | 6.5262 | 6.3775 | 6.4324 | 6.4127 | 7.3057 | 7.2976 | 7.2866 | 7.2699 | 7.2236 | 7.1726 | 7.1198 | 7.0589 | 6.9912 | 6.9438 | 6.7778 | 6.6656 | 6.6876 | 6.6788 | 7.1646 | 7.156 | 7.1372 | 7.1086 | 7.0179 | 6.9196 | 6.8253 | 6.7325 | 6.6235 | 6.5679 | 6.3873 | 6.264 | 6.3216 | 6.2998
| MALLAIG | ST |  |  | 7.3904 | 7.3816 | 7.3764 | 7.3699 | 7.3559 | 7.3404 | 7.3219 | 7.3012 | 7.2798 | 7.2448 | 7.1207 | 6.792 | 6.6786 | 6.6629 | 7.3169 | 7.3111 | 7.3072 | 7.3023 | 7.2914 | 7.2804 | 7.2665 | 7.251 | 7.2351 | 7.2099 | 7.1211 | 6.8807 | 6.7871 | 6.7636 | 7.1717 | 7.1713 | 7.1718 | 7.1697 | 7.1612 | 7.154 | 7.1417 | 7.1285 | 7.1115 | 7.0787 | 6.9716 | 6.6682 | 6.4758 | 6.4512
| MALLAIG | SP |  |  | 7.3957 | 7.39 | 7.388 | 7.386 | 7.3579 | 7.3307 | 7.2998 | 7.2655 | 7.2322 | 7.1826 | 7.0489 | 6.7411 | 6.4753 | 6.3997 | 7.3194 | 7.3153 | 7.3131 | 7.3108 | 7.2934 | 7.2773 | 7.2579 | 7.2364 | 7.215 | 7.1836 | 7.0981 | 6.8914 | 6.6934 | 6.621 | 7.1734 | 7.1739 | 7.1753 | 7.1767 | 7.158 | 7.1336 | 7.1035 | 7.0712 | 7.0403 | 6.9878 | 6.8573 | 6.5621 | 6.3458 | 6.2539
KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | YES | 3.5184 | 3.4682 | 3.3988 | 3.3106 | 3.1056 | 2.8989 | 2.6884 | 2.4038 | 2.0248 | 1.743 | 1.0765 | 0.86994 | 0.97672 | 0.74342 | 4.7206 | 4.6793 | 4.6271 | 4.5596 | 4.4457 | 4.3434 | 4.2176 | 4.0681 | 3.8805 | 3.6976 | 3.2734 | 3.1502 | 3.1485 | 2.961 | -0.3665 | -0.39234 | -0.42513 | -0.46498 | -0.58927 | -0.74489 | -0.89989 | -1.1122 | -1.4316 | -1.6371 | -2.1475 | -2.3397 | -2.2544 | -2.4336
| MARNOCH | CT |  |  | 3.5518 | 3.5157 | 3.4522 | 3.3683 | 3.1757 | 3.0075 | 2.7245 | 2.4241 | 2.1496 | 1.9749 | 1.3363 | 1.0218 | 1.0063 | 0.97355 | 4.7248 | 4.6806 | 4.6273 | 4.5596 | 4.4457 | 4.3538 | 4.2176 | 4.0731 | 3.9399 | 3.8301 | 3.3974 | 3.2045 | 3.1702 | 3.1171 | -0.3665 | -0.39234 | -0.42513 | -0.46498 | -0.50518 | -0.60806 | -0.84347 | -1.1015 | -1.3367 | -1.4711 | -1.9293 | -2.2056 | -2.2246 | -2.2534
| MARNOCH | LW |  |  | 3.5184 | 3.4682 | 3.3988 | 3.3106 | 3.1056 | 2.8989 | 2.6884 | 2.4038 | 2.0248 | 1.743 | 1.0765 | 0.86994 | 0.97672 | 0.93732 | 4.7206 | 4.6793 | 4.6271 | 4.5615 | 4.4497 | 4.3434 | 4.2344 | 4.0681 | 3.8805 | 3.6976 | 3.2734 | 3.1502 | 3.1848 | 3.1704 | -0.36328 | -0.38738 | -0.4156 | -0.44866 | -0.58927 | -0.74489 | -0.89989 | -1.1122 | -1.4316 | -1.6371 | -2.1475 | -2.3397 | -2.2544 | -2.2859
| MARNOCH | ST |  |  | 3.5443 | 3.5033 | 3.4554 | 3.4023 | 3.3583 | 3.3141 | 3.2805 | 3.2399 | 3.1703 | 3.0779 | 2.7111 | 1.9149 | 1.6763 | 1.5622 | 4.7336 | 4.6979 | 4.6539 | 4.6069 | 4.5596 | 4.5281 | 4.5006 | 4.467 | 4.4212 | 4.365 | 4.1264 | 3.5578 | 3.4228 | 3.3362 | -0.36027 | -0.38107 | -0.40599 | -0.43445 | -0.46188 | -0.48354 | -0.50055 | -0.51773 | -0.54305 | -0.5965 | -0.82273 | -1.4467 | -1.6613 | -1.762
| MARNOCH | SP |  |  | 3.5652 | 3.5346 | 3.4986 | 3.4625 | 3.3978 | 3.3481 | 3.2944 | 3.233 | 3.1607 | 3.0665 | 2.6695 | 1.6693 | 1.0022 | 0.74342 | 4.736 | 4.6994 | 4.6562 | 4.6127 | 4.5669 | 4.5399 | 4.5143 | 4.4795 | 4.4318 | 4.375 | 4.1621 | 3.5728 | 3.1485 | 2.961 | -0.35965 | -0.38001 | -0.40462 | -0.42931 | -0.45571 | -0.47196 | -0.48823 | -0.50487 | -0.52978 | -0.58984 | -0.89032 | -1.6697 | -2.2179 | -2.4336
BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | 3.3271 | 3.301 | 3.27 | 3.2282 | 3.1314 | 3.0256 | 2.9207 | 2.8157 | 2.6811 | 2.6143 | 2.3059 | 2.2446 | 2.2894 | 2.2346 | 3.5453 | 3.5316 | 3.5166 | 3.4932 | 3.4507 | 3.4049 | 3.3506 | 3.2985 | 3.226 | 3.1812 | 2.9956 | 2.9622 | 2.9766 | 2.9178 | 3.2324 | 3.208 | 3.1809 | 3.1399 | 3.06 | 2.9737 | 2.8768 | 2.783 | 2.6562 | 2.5835 | 2.3012 | 2.2557 | 2.2877 | 2.252
| MARYBANK | CT |  |  | 3.344 | 3.3305 | 3.3089 | 3.2731 | 3.1874 | 3.1034 | 2.9975 | 2.8868 | 2.7777 | 2.7215 | 2.4412 | 2.3238 | 2.3308 | 2.3243 | 3.548 | 3.5368 | 3.522 | 3.4984 | 3.4608 | 3.4248 | 3.3838 | 3.3399 | 3.2926 | 3.2506 | 3.0527 | 2.9857 | 2.9797 | 2.9635 | 3.2403 | 3.2226 | 3.1981 | 3.1587 | 3.0883 | 3.0204 | 2.9408 | 2.8562 | 2.7688 | 2.7019 | 2.404 | 2.3129 | 2.3229 | 2.3207
| MARYBANK | LW |  |  | 3.3271 | 3.301 | 3.27 | 3.2282 | 3.1314 | 3.0256 | 2.9207 | 2.8157 | 2.6811 | 2.6143 | 2.3059 | 2.2446 | 2.2894 | 2.2694 | 3.5453 | 3.5316 | 3.5166 | 3.4932 | 3.4507 | 3.4049 | 3.3506 | 3.2985 | 3.226 | 3.1812 | 2.9956 | 2.9622 | 2.9766 | 2.9698 | 3.2324 | 3.208 | 3.1809 | 3.1399 | 3.06 | 2.9737 | 2.8768 | 2.783 | 2.6562 | 2.5835 | 2.3012 | 2.2557 | 2.2877 | 2.2725
| MARYBANK | ST |  |  | 3.3489 | 3.3422 | 3.3358 | 3.3251 | 3.3183 | 3.311 | 3.3006 | 3.2894 | 3.2647 | 3.2241 | 3.0803 | 2.6929 | 2.5796 | 2.5439 | 3.5557 | 3.5509 | 3.5461 | 3.5384 | 3.5325 | 3.5264 | 3.5145 | 3.5064 | 3.4908 | 3.4619 | 3.3557 | 3.1164 | 3.0546 | 3.0307 | 3.2516 | 3.2439 | 3.2364 | 3.224 | 3.215 | 3.2055 | 3.1879 | 3.175 | 3.1501 | 3.104 | 2.9369 | 2.5787 | 2.4982 | 2.4767
| MARYBANK | SP |  |  | 3.3598 | 3.3588 | 3.3583 | 3.3583 | 3.3463 | 3.3352 | 3.3224 | 3.3056 | 3.2808 | 3.245 | 3.0731 | 2.6437 | 2.3473 | 2.2346 | 3.5602 | 3.5571 | 3.5538 | 3.5511 | 3.5419 | 3.5348 | 3.5247 | 3.5107 | 3.4921 | 3.4702 | 3.3819 | 3.1443 | 2.983 | 2.9178 | 3.2606 | 3.2568 | 3.2528 | 3.2498 | 3.2353 | 3.2238 | 3.2079 | 3.1857 | 3.1571 | 3.1214 | 2.9703 | 2.5776 | 2.3314 | 2.252
LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | 7.4047 | 7.2717 | 7.1341 | 6.9517 | 6.5147 | 6.062 | 5.4877 | 4.7849 | 3.9761 | 3.3257 | 1.3785 | -0.63341 | -1.6112 | -1.9534 | 8.1898 | 8.0952 | 8.0093 | 7.8917 | 7.6761 | 7.4525 | 7.1244 | 6.7047 | 6.272 | 5.8853 | 4.7274 | 3.7173 | 3.2024 | 2.86 | 7.6182 | 7.4996 | 7.378 | 7.216 | 6.8214 | 6.4089 | 5.8842 | 5.2452 | 4.5151 | 3.9331 | 2.1367 | 0.33498 | -0.53607 | -0.84786
| MARYTON | CT |  |  | 7.459 | 7.3463 | 7.223 | 7.0493 | 6.6282 | 6.211 | 5.5988 | 4.9107 | 4.293 | 3.6974 | 1.5782 | -0.63341 | -1.6112 | -1.9534 | 8.2041 | 8.1122 | 8.0254 | 7.8979 | 7.6799 | 7.4695 | 7.1318 | 6.7409 | 6.4163 | 6.0798 | 4.8497 | 3.7173 | 3.2024 | 2.86 | 7.667 | 7.5664 | 7.458 | 7.3068 | 6.9279 | 6.5487 | 5.9865 | 5.3558 | 4.7922 | 4.2536 | 2.3457 | 0.33498 | -0.53607 | -0.84786
| MARYTON | LW |  |  | 7.4047 | 7.2717 | 7.1341 | 6.9517 | 6.5147 | 6.062 | 5.4877 | 4.7849 | 3.9761 | 3.3257 | 1.3785 | -0.17668 | -0.80479 | -1.0608 | 8.1898 | 8.0952 | 8.0093 | 7.8917 | 7.6761 | 7.4525 | 7.1244 | 6.7047 | 6.272 | 5.8853 | 4.7274 | 3.9327 | 3.6861 | 3.5846 | 7.6182 | 7.4996 | 7.378 | 7.216 | 6.8214 | 6.4089 | 5.8842 | 5.2452 | 4.5151 | 3.9331 | 2.1367 | 0.71295 | 0.16184 | -0.062789
| MARYTON | ST |  |  | 7.5068 | 7.4245 | 7.3583 | 7.2722 | 7.2096 | 7.1484 | 6.9749 | 6.7682 | 6.61 | 6.3748 | 5.5244 | 3.4998 | 2.532 | 2.0083 | 8.2372 | 8.1679 | 8.1166 | 8.0458 | 7.9949 | 7.9452 | 7.7949 | 7.6154 | 7.4929 | 7.328 | 6.7305 | 5.4044 | 4.7998 | 4.3786 | 7.7107 | 7.6373 | 7.5805 | 7.5056 | 7.454 | 7.4003 | 7.24 | 7.0481 | 6.904 | 6.6912 | 5.9258 | 3.9928 | 3.1106 | 2.6493
| MARYTON | SP |  |  | 7.5395 | 7.4722 | 7.4207 | 7.3568 | 7.2598 | 7.1765 | 6.9805 | 6.7491 | 6.5548 | 6.3274 | 5.5448 | 3.8099 | 2.497 | 2.144 | 8.2532 | 8.191 | 8.1462 | 8.0896 | 8.0265 | 7.9727 | 7.8185 | 7.6341 | 7.4926 | 7.3351 | 6.81 | 5.6749 | 4.6117 | 3.931 | 7.7404 | 7.6807 | 7.6375 | 7.5827 | 7.4987 | 7.4237 | 7.2421 | 7.0275 | 6.8524 | 6.6459 | 5.9352 | 4.3445 | 3.0892 | 2.7681
STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | 5.0338 | 4.9576 | 4.8736 | 4.7694 | 4.539 | 4.2851 | 3.9944 | 3.6796 | 3.2943 | 3.035 | 2.4694 | 2.2549 | 2.3637 | 2.1927 | 5.6927 | 5.6675 | 5.64 | 5.6061 | 5.5344 | 5.4467 | 5.3464 | 5.2331 | 5.099 | 4.9949 | 4.762 | 4.643 | 4.6698 | 4.5295 | 5.0209 | 4.9563 | 4.8846 | 4.7934 | 4.591 | 4.3665 | 4.1027 | 3.8163 | 3.4649 | 3.2217 | 2.6973 | 2.5003 | 2.5966 | 2.4502
| MAUD | CT |  |  | 5.0826 | 5.0367 | 4.9697 | 4.8887 | 4.672 | 4.4499 | 4.161 | 3.8582 | 3.5919 | 3.3526 | 2.7918 | 2.4443 | 2.3776 | 2.3237 | 5.7024 | 5.6841 | 5.6595 | 5.6312 | 5.564 | 5.4863 | 5.3864 | 5.2776 | 5.179 | 5.0828 | 4.8664 | 4.7151 | 4.6885 | 4.6482 | 5.0625 | 5.0241 | 4.9658 | 4.8934 | 4.703 | 4.5069 | 4.2487 | 3.978 | 3.7399 | 3.5136 | 2.9864 | 2.6713 | 2.6132 | 2.5664
| MAUD | LW |  |  | 5.0338 | 4.9576 | 4.8736 | 4.7694 | 4.539 | 4.2851 | 3.9944 | 3.6796 | 3.2943 | 3.035 | 2.4694 | 2.2549 | 2.3637 | 2.3344 | 5.6927 | 5.6675 | 5.64 | 5.6061 | 5.5344 | 5.4467 | 5.3464 | 5.2331 | 5.099 | 4.9949 | 4.762 | 4.643 | 4.676 | 4.6658 | 5.0209 | 4.9563 | 4.8846 | 4.7934 | 4.591 | 4.3665 | 4.1027 | 3.8163 | 3.4649 | 3.2217 | 2.6973 | 2.5003 | 2.5966 | 2.5712
| MAUD | ST |  |  | 5.0827 | 5.0412 | 4.9994 | 4.9553 | 4.9074 | 4.8393 | 4.7902 | 4.7284 | 4.6501 | 4.5361 | 4.1463 | 3.3755 | 3.077 | 2.9417 | 5.7055 | 5.69 | 5.6739 | 5.6574 | 5.6408 | 5.6101 | 5.5826 | 5.5486 | 5.5074 | 5.4478 | 5.2814 | 4.9798 | 4.8628 | 4.8014 | 5.0652 | 5.0324 | 4.9993 | 4.9634 | 4.924 | 4.8639 | 4.82 | 4.7646 | 4.6934 | 4.5887 | 4.2243 | 3.4748 | 3.2187 | 3.1073
| MAUD | SP |  |  | 5.0997 | 5.0699 | 5.038 | 5.0068 | 4.942 | 4.8726 | 4.7937 | 4.7139 | 4.6256 | 4.5168 | 4.0834 | 3.0485 | 2.4565 | 2.1927 | 5.7112 | 5.6996 | 5.6872 | 5.6746 | 5.6534 | 5.6225 | 5.5876 | 5.5495 | 5.5073 | 5.4537 | 5.2828 | 4.914 | 4.6698 | 4.5295 | 5.0801 | 5.0579 | 5.0335 | 5.0097 | 4.9559 | 4.8967 | 4.8255 | 4.7543 | 4.6731 | 4.5741 | 4.1804 | 3.2209 | 2.682 | 2.4502
MYBSTER | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | 2.226 | 2.2233 | 2.2098 | 2.186 | 2.1347 | 2.0772 | 2.0189 | 1.9506 | 1.8469 | 1.7923 | 1.5962 | 1.4954 | 1.4305 | 1.3355 | 2.1827 | 2.1764 | 2.1683 | 2.1561 | 2.1338 | 2.1087 | 2.0786 | 2.0443 | 1.9955 | 1.9619 | 1.825 | 1.7497 | 1.6866 | 1.6301 | 2.0594 | 2.049 | 2.0338 | 2.0124 | 1.9674 | 1.9168 | 1.8651 | 1.8025 | 1.7093 | 1.6576 | 1.4664 | 1.3954 | 1.3356 | 1.248
| MELVICH | CT |  |  | 2.226 | 2.2233 | 2.2198 | 2.2089 | 2.1603 | 2.1122 | 2.0342 | 1.9506 | 1.8687 | 1.8272 | 1.6754 | 1.5551 | 1.5504 | 1.5421 | 2.1854 | 2.1825 | 2.176 | 2.1608 | 2.1338 | 2.1106 | 2.0786 | 2.0443 | 2.0081 | 1.9817 | 1.8721 | 1.793 | 1.787 | 1.7786 | 2.0707 | 2.0678 | 2.0578 | 2.0347 | 1.9858 | 1.9425 | 1.875 | 1.8025 | 1.7307 | 1.691 | 1.5403 | 1.4274 | 1.4231 | 1.4159
| MELVICH | LW |  |  | 2.2328 | 2.2249 | 2.2098 | 2.186 | 2.1347 | 2.0772 | 2.0189 | 1.9518 | 1.8469 | 1.7923 | 1.5962 | 1.4954 | 1.517 | 1.5072 | 2.1827 | 2.1764 | 2.1683 | 2.1561 | 2.1342 | 2.1087 | 2.0819 | 2.0452 | 1.9955 | 1.9619 | 1.825 | 1.7497 | 1.7553 | 1.7529 | 2.0594 | 2.049 | 2.0338 | 2.0124 | 1.9674 | 1.9168 | 1.8651 | 1.803 | 1.7093 | 1.6576 | 1.4664 | 1.3954 | 1.4178 | 1.4061
| MELVICH | ST |  |  | 2.2346 | 2.2335 | 2.2321 | 2.2301 | 2.2223 | 2.22 | 2.2115 | 2.2007 | 2.1762 | 2.126 | 1.9828 | 1.6579 | 1.5027 | 1.4769 | 2.189 | 2.1869 | 2.1842 | 2.1798 | 2.1733 | 2.1687 | 2.1601 | 2.1511 | 2.1392 | 2.1201 | 2.0362 | 1.803 | 1.7009 | 1.6913 | 2.0728 | 2.0694 | 2.0655 | 2.0592 | 2.0507 | 2.0445 | 2.0332 | 2.0215 | 2.0026 | 1.9728 | 1.8498 | 1.5415 | 1.3963 | 1.3738
| MELVICH | SP |  |  | 2.2347 | 2.2338 | 2.2327 | 2.2314 | 2.2247 | 2.223 | 2.2107 | 2.1928 | 2.1694 | 2.1238 | 2.0031 | 1.7012 | 1.4305 | 1.3355 | 2.1901 | 2.1884 | 2.187 | 2.1851 | 2.1785 | 2.1733 | 2.1647 | 2.1552 | 2.1407 | 2.1234 | 2.0656 | 1.8707 | 1.6866 | 1.6301 | 2.0756 | 2.0734 | 2.0719 | 2.0699 | 2.0576 | 2.0478 | 2.0333 | 2.0171 | 1.995 | 1.9661 | 1.8624 | 1.5893 | 1.3356 | 1.248
CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | 9.378 | 9.1089 | 8.8467 | 8.5797 | 7.7911 | 6.779 | 5.6421 | 4.4719 | 3.6907 | 3.0163 | 0.55913 | -3.1457 | -5.1664 | -6.2105 | 12.9687 | 12.771 | 12.586 | 12.3667 | 11.9753 | 11.4493 | 10.9797 | 10.4539 | 10.0149 | 9.5997 | 7.9697 | 5.4639 | 3.8819 | 2.1608 | 8.134 | 7.896 | 7.6703 | 7.439 | 6.741 | 5.8341 | 4.8065 | 3.7533 | 3.0388 | 2.4145 | 0.13064 | -3.1468 | -4.8373 | -5.6554
| MENZIESHILL | CT |  |  | 9.3821 | 9.1325 | 8.8921 | 8.63 | 7.8487 | 6.8345 | 6.0593 | 5.3877 | 4.6534 | 3.8109 | 0.95326 | -3.1457 | -5.1664 | -6.2105 | 12.9687 | 12.771 | 12.586 | 12.3667 | 11.9753 | 11.4493 | 10.9797 | 10.5942 | 10.1744 | 9.6963 | 7.9697 | 5.4639 | 3.8819 | 2.1608 | 8.1362 | 7.9149 | 7.7072 | 7.4766 | 6.7825 | 5.8732 | 5.1654 | 4.5566 | 3.8912 | 3.1253 | 0.51604 | -3.1468 | -4.8373 | -5.6554
| MENZIESHILL | LW |  |  | 9.378 | 9.1089 | 8.8467 | 8.5797 | 7.7911 | 6.779 | 5.6421 | 4.4719 | 3.6907 | 3.0163 | 0.55913 | -2.5186 | -4.1444 | -5.0932 | 12.9873 | 12.8019 | 12.6326 | 12.4502 | 12.0906 | 11.5926 | 11.0136 | 10.4539 | 10.0149 | 9.5997 | 8.008 | 6.296 | 5.6115 | 5.172 | 8.134 | 7.896 | 7.6703 | 7.439 | 6.741 | 5.8341 | 4.8065 | 3.7533 | 3.0388 | 2.4145 | 0.13064 | -2.6317 | -3.9696 | -4.7042
| MENZIESHILL | ST |  |  | 9.5782 | 9.4175 | 9.2734 | 9.1255 | 9.047 | 8.8752 | 8.6729 | 8.5396 | 8.4107 | 8.2007 | 7.3507 | 4.7819 | 2.9796 | 1.602 | 13.0676 | 12.9286 | 12.8078 | 12.6777 | 12.5869 | 12.41 | 12.1971 | 12.0443 | 11.8818 | 11.6793 | 10.8647 | 8.5923 | 6.9369 | 5.1579 | 8.3147 | 8.1773 | 8.0605 | 7.9402 | 7.8746 | 7.7164 | 7.5235 | 7.3967 | 7.2723 | 7.0732 | 6.2536 | 3.7596 | 2.2357 | 1.1675
| MENZIESHILL | SP |  |  | 9.6412 | 9.5006 | 9.3753 | 9.2509 | 9.1403 | 8.9343 | 8.7128 | 8.5651 | 8.3938 | 8.1982 | 7.4574 | 5.6943 | 4.0408 | 3.378 | 13.0999 | 12.9662 | 12.8484 | 12.7292 | 12.6265 | 12.4354 | 12.2141 | 12.0529 | 11.8601 | 11.6473 | 10.838 | 8.8355 | 6.0779 | 2.8223 | 8.3729 | 8.2533 | 8.1533 | 8.0554 | 7.9627 | 7.7758 | 7.5677 | 7.4299 | 7.2681 | 7.0853 | 6.399 | 4.7357 | 3.1278 | 2.6043
KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | YES | 4.2732 | 4.24 | 4.188 | 4.13 | 3.9969 | 3.8395 | 3.657 | 3.4626 | 3.2249 | 3.0599 | 2.7474 | 2.6078 | 2.654 | 2.4944 | 5.1802 | 5.1616 | 5.132 | 5.0992 | 5.0368 | 4.9581 | 4.8593 | 4.7518 | 4.6335 | 4.5315 | 4.3664 | 4.291 | 4.2679 | 4.1423 | 1.1417 | 1.1146 | 1.0704 | 1.0219 | 0.92292 | 0.79974 | 0.64679 | 0.48133 | 0.29465 | 0.14323 | -0.10013 | -0.19968 | -0.16524 | -0.28338
| METHLICK | CT |  |  | 4.3157 | 4.2985 | 4.2648 | 4.2152 | 4.0918 | 3.9649 | 3.7862 | 3.597 | 3.4289 | 3.2848 | 2.9255 | 2.7105 | 2.654 | 2.6113 | 5.1939 | 5.1787 | 5.1545 | 5.1191 | 5.0615 | 5.0009 | 4.9187 | 4.8314 | 4.7558 | 4.662 | 4.4354 | 4.3201 | 4.2796 | 4.231 | 1.167 | 1.1475 | 1.1139 | 1.0644 | 0.97433 | 0.88038 | 0.7495 | 0.6108 | 0.4912 | 0.35371 | 0.022608 | -0.13076 | -0.16413 | -0.19038
| METHLICK | LW |  |  | 4.2732 | 4.24 | 4.188 | 4.13 | 3.9969 | 3.8395 | 3.657 | 3.4626 | 3.2249 | 3.0599 | 2.7474 | 2.6078 | 2.6699 | 2.6518 | 5.1802 | 5.1616 | 5.132 | 5.0992 | 5.0368 | 4.9581 | 4.8593 | 4.7518 | 4.6335 | 4.5315 | 4.3664 | 4.291 | 4.3133 | 4.306 | 1.1417 | 1.1146 | 1.0704 | 1.0219 | 0.92292 | 0.79974 | 0.64679 | 0.48133 | 0.29465 | 0.14323 | -0.10013 | -0.19968 | -0.15919 | -0.17161
| METHLICK | ST |  |  | 4.3174 | 4.3046 | 4.2906 | 4.2751 | 4.253 | 4.2313 | 4.2091 | 4.1831 | 4.1393 | 4.0754 | 3.8186 | 3.2963 | 3.0748 | 2.9686 | 5.2009 | 5.1928 | 5.1835 | 5.1719 | 5.1561 | 5.1411 | 5.1256 | 5.1075 | 5.0835 | 5.0478 | 4.8886 | 4.5391 | 4.4297 | 4.359 | 1.1743 | 1.1633 | 1.1509 | 1.1356 | 1.1142 | 1.0941 | 1.0737 | 1.0497 | 1.0154 | 0.96358 | 0.73377 | 0.25749 | 0.11369 | 0.046636
| METHLICK | SP |  |  | 4.3275 | 4.3188 | 4.3085 | 4.2992 | 4.2638 | 4.2258 | 4.1851 | 4.1409 | 4.0908 | 4.0296 | 3.7636 | 3.0423 | 2.676 | 2.4944 | 5.2063 | 5.2002 | 5.192 | 5.1846 | 5.1659 | 5.1445 | 5.1214 | 5.0965 | 5.0674 | 5.0355 | 4.9006 | 4.4708 | 4.2679 | 4.1423 | 1.1831 | 1.1755 | 1.1653 | 1.1564 | 1.1286 | 1.0971 | 1.0632 | 1.0268 | 0.98434 | 0.93679 | 0.73198 | 0.10023 | -0.16524 | -0.28338
SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | 6.1301 | 6.126 | 6.1199 | 6.109 | 6.0819 | 6.02 | 5.9597 | 5.8959 | 5.806 | 5.7615 | 5.5805 | 5.5562 | 5.5914 | 5.5422 | 5.8641 | 5.8607 | 5.8523 | 5.8389 | 5.8113 | 5.7833 | 5.7524 | 5.7168 | 5.6705 | 5.642 | 5.5099 | 5.4965 | 5.5046 | 5.4776 | 5.6671 | 5.6641 | 5.6496 | 5.6301 | 5.5804 | 5.5296 | 5.4789 | 5.4271 | 5.3578 | 5.328 | 5.233 | 5.1924 | 5.2213 | 5.1918
| MID YELL | CT |  |  | 6.1301 | 6.126 | 6.1199 | 6.109 | 6.1004 | 6.0461 | 5.9789 | 5.9031 | 5.8328 | 5.7969 | 5.6367 | 5.5844 | 5.6131 | 5.6179 | 5.8701 | 5.8678 | 5.8592 | 5.8414 | 5.8113 | 5.7833 | 5.7524 | 5.7186 | 5.685 | 5.6612 | 5.5402 | 5.5087 | 5.5151 | 5.5117 | 5.6853 | 5.6857 | 5.6744 | 5.6507 | 5.6023 | 5.557 | 5.5016 | 5.4389 | 5.3794 | 5.3551 | 5.2808 | 5.229 | 5.2481 | 5.2501
| MID YELL | LW |  |  | 6.1345 | 6.1322 | 6.1289 | 6.1231 | 6.0819 | 6.02 | 5.9597 | 5.8959 | 5.806 | 5.7615 | 5.5805 | 5.5562 | 5.5914 | 5.5692 | 5.8641 | 5.8607 | 5.8523 | 5.8389 | 5.8136 | 5.7839 | 5.7545 | 5.7168 | 5.6705 | 5.642 | 5.5099 | 5.4965 | 5.5087 | 5.501 | 5.6671 | 5.6641 | 5.6496 | 5.6301 | 5.5804 | 5.5296 | 5.4789 | 5.4271 | 5.3578 | 5.328 | 5.233 | 5.1924 | 5.2213 | 5.2042
| MID YELL | ST |  |  | 6.1354 | 6.1343 | 6.1336 | 6.1306 | 6.1297 | 6.1287 | 6.1276 | 6.1253 | 6.1227 | 6.1173 | 6.0769 | 5.8794 | 5.8339 | 5.8109 | 5.8727 | 5.8698 | 5.8674 | 5.8622 | 5.8581 | 5.8541 | 5.8499 | 5.8434 | 5.8347 | 5.8195 | 5.766 | 5.6128 | 5.5905 | 5.5775 | 5.6824 | 5.6797 | 5.6775 | 5.6726 | 5.6712 | 5.6689 | 5.6665 | 5.6623 | 5.6517 | 5.6343 | 5.5795 | 5.4708 | 5.4188 | 5.3975
| MID YELL | SP |  |  | 6.1361 | 6.1361 | 6.1359 | 6.1357 | 6.1361 | 6.1359 | 6.1357 | 6.1346 | 6.1264 | 6.0948 | 6.0006 | 5.7658 | 5.5953 | 5.5422 | 5.8739 | 5.8722 | 5.8707 | 5.8688 | 5.8623 | 5.8549 | 5.8468 | 5.8371 | 5.8249 | 5.8067 | 5.7534 | 5.6197 | 5.5046 | 5.4776 | 5.6857 | 5.6845 | 5.6845 | 5.6844 | 5.6724 | 5.6612 | 5.6479 | 5.6326 | 5.6156 | 5.5892 | 5.5098 | 5.3438 | 5.2389 | 5.1918
KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | 2.3701 | 2.2977 | 2.229 | 2.1505 | 1.9748 | 0.56832 | 0.30267 | 0.071437 | -0.2478 | -0.42887 | -0.7833 | -0.93714 | -0.88588 | -1.018 | 1.8686 | 1.8389 | 1.8112 | 1.778 | 1.706 | 0.50987 | 0.40502 | 0.30926 | 0.18114 | 0.10468 | -0.069144 | -0.1681 | -0.17564 | -0.29566 | 1.5226 | 1.4726 | 1.4219 | 1.3607 | 1.2278 | -0.031903 | -0.19422 | -0.35882 | -0.57296 | -0.70592 | -1.0836 | -1.3463 | -1.2918 | -1.3108
| MIDMAR | CT |  |  | 2.4044 | 2.3554 | 2.304 | 2.2424 | 2.082 | 0.71538 | 0.4951 | 0.26141 | 0.050437 | -0.14453 | -0.58348 | -0.82174 | -0.88588 | -0.93713 | 1.8801 | 1.8585 | 1.8364 | 1.8088 | 1.7411 | 0.55754 | 0.4637 | 0.36447 | 0.27175 | 0.19352 | 0.0061545 | -0.12896 | -0.17564 | -0.23438 | 1.5529 | 1.5235 | 1.4897 | 1.446 | 1.3169 | 0.071834 | -0.10061 | -0.28269 | -0.45765 | -0.56939 | -0.86928 | -1.164 | -1.2223 | -1.2665
| MIDMAR | LW |  |  | 2.3701 | 2.2977 | 2.229 | 2.1505 | 1.9748 | 0.56832 | 0.30267 | 0.071437 | -0.2478 | -0.42887 | -0.7833 | -0.93714 | -0.86222 | -0.88686 | 1.8686 | 1.8389 | 1.8112 | 1.778 | 1.706 | 0.50987 | 0.40502 | 0.30926 | 0.18114 | 0.10468 | -0.069144 | -0.1681 | -0.14046 | -0.15177 | 1.5226 | 1.4726 | 1.4219 | 1.3607 | 1.2278 | -0.031903 | -0.19422 | -0.35882 | -0.57296 | -0.70592 | -1.0836 | -1.3463 | -1.2918 | -1.3108
| MIDMAR | ST |  |  | 2.4189 | 2.3847 | 2.3676 | 2.3466 | 2.3226 | 1.0935 | 1.0636 | 1.0229 | 0.96522 | 0.88361 | 0.55943 | -0.067305 | -0.32683 | -0.46382 | 1.8878 | 1.8731 | 1.8649 | 1.855 | 1.8444 | 0.71968 | 0.70194 | 0.68 | 0.65035 | 0.61256 | 0.4688 | 0.17882 | 0.03161 | -0.06728 | 1.5635 | 1.5441 | 1.5298 | 1.514 | 1.4958 | 0.36561 | 0.33789 | 0.3047 | 0.25241 | 0.18313 | -0.056641 | -0.56686 | -0.85973 | -0.97987
| MIDMAR | SP |  |  | 2.4252 | 2.3977 | 2.3868 | 2.373 | 2.3361 | 1.0964 | 1.0426 | 0.98862 | 0.92834 | 0.86319 | 0.53809 | -0.34842 | -0.78502 | -1.018 | 1.8908 | 1.8787 | 1.8731 | 1.8664 | 1.8513 | 0.72325 | 0.69834 | 0.67271 | 0.64452 | 0.61419 | 0.47349 | 0.10608 | -0.12957 | -0.29566 | 1.5706 | 1.5559 | 1.5474 | 1.5377 | 1.5109 | 0.37433 | 0.33911 | 0.30081 | 0.25862 | 0.20406 | -0.043857 | -0.63083 | -1.0761 | -1.2792
BRIDGE OF DUN | MILL RD MONTROSE | MINIMUM HEADROOM | NO 71317 57683 | YES | 6.5295 | 6.4399 | 6.3583 | 6.2512 | 5.9571 | 5.6547 | 5.403 | 5.114 | 4.8585 | 4.6442 | 3.9559 | 2.8612 | 2.3343 | 2.1212 | 8.5071 | 8.4612 | 8.4148 | 8.3619 | 8.2114 | 8.0394 | 7.9169 | 7.7589 | 7.595 | 7.4396 | 6.9345 | 6.1629 | 5.7211 | 5.2551 | 7.1128 | 7.0322 | 6.9579 | 6.8577 | 6.5966 | 6.3244 | 6.0998 | 5.8262 | 5.5766 | 5.3621 | 4.6671 | 3.6474 | 3.1903 | 3.009
| MILL RD MONTROSE | CT |  |  | 6.5348 | 6.458 | 6.3861 | 6.3475 | 6.0734 | 5.7754 | 5.5635 | 5.3362 | 5.089 | 4.821 | 4.0314 | 2.8612 | 2.3343 | 2.1212 | 8.5071 | 8.4612 | 8.4148 | 8.3626 | 8.2114 | 8.0394 | 7.9169 | 7.7691 | 7.6095 | 7.4396 | 6.9345 | 6.1629 | 5.7211 | 5.2551 | 7.1182 | 7.0486 | 6.9815 | 6.9332 | 6.6836 | 6.4115 | 6.2175 | 5.9999 | 5.7645 | 5.5093 | 4.7529 | 3.6474 | 3.1903 | 3.009
| MILL RD MONTROSE | LW |  |  | 6.5295 | 6.4399 | 6.3583 | 6.2512 | 5.9571 | 5.6547 | 5.403 | 5.114 | 4.8585 | 4.6442 | 3.9559 | 3.1035 | 2.7462 | 2.57 | 8.5114 | 8.4677 | 8.4259 | 8.3619 | 8.2158 | 8.0549 | 7.9269 | 7.7589 | 7.595 | 7.4488 | 6.973 | 6.3427 | 6.2579 | 6.1882 | 7.1128 | 7.0322 | 6.9579 | 6.8577 | 6.5966 | 6.3244 | 6.0998 | 5.8262 | 5.5766 | 5.3621 | 4.6671 | 3.8345 | 3.5352 | 3.3886
| MILL RD MONTROSE | ST |  |  | 6.5966 | 6.5728 | 6.5501 | 6.5239 | 6.4961 | 6.4653 | 6.4287 | 6.3777 | 6.3436 | 6.2623 | 5.9659 | 5.0899 | 4.0882 | 3.6384 | 8.5404 | 8.5214 | 8.5021 | 8.4765 | 8.4479 | 8.4155 | 8.3781 | 8.3319 | 8.2869 | 8.213 | 7.9394 | 6.9836 | 6.2483 | 5.9227 | 7.1721 | 7.1493 | 7.1264 | 7.0974 | 7.0674 | 7.0337 | 6.9949 | 6.9427 | 6.9035 | 6.8213 | 6.5164 | 5.6533 | 4.8359 | 4.4161
| MILL RD MONTROSE | SP |  |  | 6.6219 | 6.6166 | 6.6049 | 6.5947 | 6.5614 | 6.5246 | 6.4887 | 6.4454 | 6.3989 | 6.3232 | 6.0879 | 5.4714 | 4.7719 | 4.2556 | 8.5506 | 8.5399 | 8.5239 | 8.5076 | 8.4785 | 8.4472 | 8.4124 | 8.3709 | 8.3211 | 8.2501 | 8.0061 | 7.3345 | 6.4042 | 5.2792 | 7.1938 | 7.1865 | 7.1732 | 7.1603 | 7.1277 | 7.0923 | 7.0562 | 7.0137 | 6.9649 | 6.8911 | 6.6572 | 6.0348 | 5.4606 | 5.0129
ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | YES | 1.5745 | 1.1934 | 0.76194 | 0.15372 | -0.98499 | -2.2577 | -3.4026 | -4.514 | -5.9901 | -7.4658 | -11.3385 | -14.6821 | -15.5281 | -15.9531 | 5.0774 | 4.787 | 4.4655 | 4.0162 | 3.2968 | 2.3056 | 1.6191 | 0.88479 | -0.0083003 | -1.3442 | -5.0624 | -8.3203 | -8.9291 | -8.7838 | 1.9718 | 1.6011 | 1.1858 | 0.58155 | -0.47811 | -1.6747 | -2.7827 | -3.8328 | -5.2301 | -6.6383 | -10.3042 | -13.5277 | -14.0902 | -14.3406
| MILNATHORT | CT |  |  | 1.6792 | 1.343 | 0.94677 | 0.39045 | -0.734 | -1.9101 | -2.9555 | -4.0533 | -5.2408 | -6.6257 | -10.6876 | -14.3875 | -15.5281 | -15.9531 | 5.0774 | 4.787 | 4.4655 | 4.0162 | 3.2968 | 2.3056 | 1.6191 | 0.88479 | 0.0063373 | -1.2108 | -4.4223 | -7.4251 | -7.6262 | -7.6802 | 2.0316 | 1.6948 | 1.2976 | 0.72977 | -0.31338 | -1.4037 | -2.3481 | -3.3377 | -4.4075 | -5.7498 | -9.6828 | -13.0568 | -14.0057 | -14.3406
| MILNATHORT | LW |  |  | 1.5745 | 1.1934 | 0.76194 | 0.15372 | -0.98499 | -2.2577 | -3.4026 | -4.514 | -5.9901 | -7.4658 | -11.3385 | -14.6821 | -14.9796 | -15.266 | 5.0903 | 4.7932 | 4.4809 | 4.0261 | 3.3032 | 2.4807 | 1.7335 | 0.9619 | -0.0083003 | -1.3442 | -5.0624 | -8.3203 | -8.4072 | -8.444 | 1.9718 | 1.6011 | 1.1858 | 0.58155 | -0.47811 | -1.6747 | -2.7827 | -3.8328 | -5.2301 | -6.6383 | -10.3042 | -13.5277 | -13.6522 | -13.8657
| MILNATHORT | ST |  |  | 1.9599 | 1.7542 | 1.5828 | 1.4422 | 1.2442 | 1.0084 | 0.78322 | 0.53048 | 0.14105 | -0.62021 | -3.167 | -10.8109 | -15.2286 | -15.0399 | 5.3348 | 5.1794 | 5.0456 | 4.9222 | 4.7526 | 4.5529 | 4.3619 | 4.1455 | 3.8348 | 3.2328 | 0.66706 | -5.5498 | -8.9291 | -8.7838 | 2.3369 | 2.1516 | 1.9919 | 1.8487 | 1.6532 | 1.4193 | 1.1899 | 0.93061 | 0.55362 | -0.17626 | -2.6516 | -9.8294 | -14.0902 | -13.9028
| MILNATHORT | SP |  |  | 2.0035 | 1.8357 | 1.6989 | 1.5823 | 1.3132 | 1.0289 | 0.74659 | 0.43372 | 0.036287 | -0.64516 | -2.5611 | -7.0252 | -10.579 | -12.0718 | 5.3573 | 5.2293 | 5.1165 | 5.0145 | 4.8355 | 4.6367 | 4.4427 | 4.2223 | 3.9294 | 3.4345 | 2.0458 | -1.4385 | -5.3142 | -6.4829 | 2.3733 | 2.2256 | 2.0979 | 1.981 | 1.7369 | 1.4733 | 1.2057 | 0.90418 | 0.52743 | -0.092638 | -1.8795 | -6.2509 | -9.5835 | -11.0212
MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | 4.1878 | 4.003 | 3.8261 | 3.5941 | 3.006 | 2.3412 | 1.6817 | 0.84198 | 0.13234 | -0.48215 | -2.4929 | -5.6769 | -7.3988 | -8.2747 | 11.2161 | 11.0911 | 10.9733 | 10.8051 | 10.4833 | 10.1139 | 9.7912 | 9.342 | 8.8923 | 8.493 | 7.192 | 5.3352 | 4.3138 | 3.4567 | 4.4406 | 4.2665 | 4.1017 | 3.8848 | 3.3374 | 2.7302 | 2.1402 | 1.3777 | 0.72372 | 0.15413 | -1.7009 | -4.512 | -5.9384 | -6.6083
| MILTON OF CRAIGIE | CT |  |  | 4.2777 | 4.119 | 3.9654 | 3.7329 | 3.148 | 2.4541 | 1.963 | 1.3954 | 0.71475 | -0.015502 | -2.3026 | -5.6769 | -7.3988 | -8.2747 | 11.2721 | 11.1457 | 11.0307 | 10.8482 | 10.5127 | 10.1209 | 9.853 | 9.5107 | 9.0797 | 8.6408 | 7.2597 | 5.3352 | 4.3138 | 3.4567 | 4.5171 | 4.3663 | 4.2226 | 4.0067 | 3.4638 | 2.8269 | 2.3839 | 1.8651 | 1.2424 | 0.57599 | -1.5096 | -4.512 | -5.9384 | -6.6083
| MILTON OF CRAIGIE | LW |  |  | 4.1878 | 4.003 | 3.8261 | 3.5941 | 3.006 | 2.3412 | 1.6817 | 0.84198 | 0.13234 | -0.48215 | -2.4929 | -5.1311 | -6.536 | -7.3143 | 11.2161 | 11.0911 | 10.9733 | 10.8051 | 10.4833 | 10.1139 | 9.7912 | 9.342 | 8.8923 | 8.493 | 7.192 | 5.651 | 5.0088 | 4.6116 | 4.4406 | 4.2665 | 4.1017 | 3.8848 | 3.3374 | 2.7302 | 2.1402 | 1.3777 | 0.72372 | 0.15413 | -1.7009 | -4.0563 | -5.2125 | -5.797
| MILTON OF CRAIGIE | ST |  |  | 4.3287 | 4.2222 | 4.13 | 3.9708 | 3.8201 | 3.647 | 3.5289 | 3.3576 | 3.1227 | 2.8393 | 1.9158 | -0.21556 | -1.738 | -2.8331 | 11.27 | 11.1747 | 11.0938 | 10.9542 | 10.8061 | 10.6315 | 10.5177 | 10.3456 | 10.1008 | 9.8528 | 9.0503 | 7.4944 | 6.4077 | 5.4595 | 4.5703 | 4.4684 | 4.3821 | 4.2334 | 4.09 | 3.9258 | 3.8159 | 3.6539 | 3.4305 | 3.1676 | 2.323 | 0.44501 | -0.84412 | -1.72
| MILTON OF CRAIGIE | SP |  |  | 4.3574 | 4.2639 | 4.1837 | 4.0504 | 3.8894 | 3.7044 | 3.5816 | 3.4135 | 3.1473 | 2.8752 | 2.037 | 0.46971 | -0.74932 | -1.3514 | 11.2829 | 11.193 | 11.1168 | 10.9902 | 10.8396 | 10.658 | 10.5422 | 10.3714 | 10.1111 | 9.8637 | 9.0847 | 7.741 | 6.3321 | 4.8302 | 4.5964 | 4.5066 | 4.4315 | 4.3062 | 4.1527 | 3.9771 | 3.8624 | 3.7029 | 3.4517 | 3.1989 | 2.4306 | 1.0602 | 0.04436 | -0.4114
STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | 8.1517 | 7.8701 | 7.5381 | 7.1854 | 6.6702 | 6.1945 | 5.7032 | 5.1559 | 4.4779 | 3.9034 | 2.4672 | 1.3479 | 0.96163 | 0.81905 | 9.0573 | 8.8451 | 8.5627 | 8.2447 | 7.888 | 7.6091 | 7.3148 | 6.9842 | 6.5857 | 6.1856 | 5.2049 | 4.6221 | 4.4146 | 4.2524 | 8.2009 | 7.9545 | 7.6574 | 7.3364 | 6.8709 | 6.444 | 6.0012 | 5.5053 | 4.8914 | 4.3601 | 3.0499 | 2.0918 | 1.757 | 1.633
| MINTLAW | CT |  |  | 8.1692 | 7.9021 | 7.5731 | 7.2004 | 6.693 | 6.2584 | 5.7169 | 5.1559 | 4.6175 | 4.1238 | 2.6102 | 1.3479 | 0.96163 | 0.81905 | 9.0573 | 8.8451 | 8.563 | 8.2447 | 7.888 | 7.6099 | 7.3148 | 6.9842 | 6.6662 | 6.3342 | 5.3251 | 4.6221 | 4.4146 | 4.2524 | 8.214 | 7.9799 | 7.684 | 7.3417 | 6.881 | 6.4896 | 6.0058 | 5.5053 | 5.0252 | 4.5758 | 3.1942 | 2.0918 | 1.757 | 1.633
| MINTLAW | LW |  |  | 8.1517 | 7.8701 | 7.5381 | 7.1854 | 6.6702 | 6.1945 | 5.7032 | 5.168 | 4.4779 | 3.9034 | 2.4672 | 1.5679 | 1.3218 | 1.1668 | 9.0623 | 8.8476 | 8.5627 | 8.2473 | 7.8918 | 7.6091 | 7.3406 | 6.9956 | 6.5857 | 6.1856 | 5.2049 | 4.7266 | 4.6352 | 4.5794 | 8.2009 | 7.9545 | 7.6574 | 7.3364 | 6.8709 | 6.444 | 6.0012 | 5.5149 | 4.8914 | 4.3601 | 3.0499 | 2.2799 | 2.069 | 1.9341
| MINTLAW | ST |  |  | 8.1969 | 7.9446 | 7.6571 | 7.3596 | 7.0703 | 6.8493 | 6.6347 | 6.4167 | 6.1791 | 5.8898 | 5.042 | 3.5641 | 3.0633 | 2.803 | 9.0879 | 8.892 | 8.626 | 8.3415 | 8.0493 | 7.8403 | 7.6377 | 7.439 | 7.2427 | 7.0281 | 6.4878 | 5.4624 | 5.1395 | 4.9314 | 8.2426 | 8.0239 | 7.7677 | 7.4974 | 7.2344 | 7.0367 | 6.8447 | 6.6503 | 6.4387 | 6.1782 | 5.4162 | 4.0519 | 3.6008 | 3.3717
| MINTLAW | SP |  |  | 8.2138 | 7.9757 | 7.7031 | 7.433 | 7.1278 | 6.8951 | 6.6649 | 6.4292 | 6.1816 | 5.9042 | 5.0513 | 3.5621 | 2.6501 | 2.3734 | 9.0906 | 8.9013 | 8.6364 | 8.3585 | 8.0676 | 7.8614 | 7.6628 | 7.4692 | 7.2808 | 7.0819 | 6.6046 | 5.6535 | 4.9085 | 4.5269 | 8.2569 | 8.0509 | 7.8083 | 7.5635 | 7.2874 | 7.0805 | 6.8757 | 6.6667 | 6.4455 | 6.1977 | 5.4457 | 4.0985 | 3.2439 | 2.9982
BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | YES | 4.1607 | 3.2209 | 2.2098 | 1.201 | 0.23445 | -0.54027 | -1.2434 | -2.0063 | -2.8082 | -3.4577 | -5.3792 | -7.7115 | -8.8268 | -9.2189 | 5.5941 | 4.6384 | 3.6047 | 2.5794 | 1.8083 | 1.2779 | 0.83344 | 0.407 | -0.11447 | -0.53697 | -1.7396 | -2.8948 | -3.5112 | -3.9596 | 4.6497 | 3.7772 | 2.8318 | 1.8853 | 0.98908 | 0.2824 | -0.35751 | -1.049 | -1.7733 | -2.357 | -4.0952 | -6.1883 | -7.196 | -7.5453
| MONTROSE NORTH | CT |  |  | 4.1954 | 3.2739 | 2.2736 | 1.2969 | 0.33049 | -0.44128 | -1.1719 | -1.8989 | -2.6107 | -3.2916 | -5.3792 | -7.7115 | -8.8268 | -9.2189 | 5.5941 | 4.6384 | 3.6047 | 2.5794 | 1.8083 | 1.2779 | 0.83344 | 0.41253 | -0.067183 | -0.4973 | -1.7396 | -2.8948 | -3.5112 | -3.9596 | 4.681 | 3.825 | 2.8894 | 1.9745 | 1.0806 | 0.37755 | -0.28797 | -0.95145 | -1.5981 | -2.2154 | -4.0952 | -6.1883 | -7.196 | -7.5453
| MONTROSE NORTH | LW |  |  | 4.1607 | 3.2209 | 2.2098 | 1.201 | 0.23445 | -0.54027 | -1.2434 | -2.0063 | -2.8082 | -3.4577 | -5.3712 | -7.0364 | -7.9035 | -8.2145 | 5.5996 | 4.6464 | 3.6172 | 2.601 | 1.8378 | 1.3115 | 0.86795 | 0.407 | -0.11447 | -0.53697 | -1.7115 | -2.5092 | -2.8601 | -2.994 | 4.6497 | 3.7772 | 2.8318 | 1.8853 | 0.98908 | 0.2824 | -0.35751 | -1.049 | -1.7733 | -2.357 | -4.0695 | -5.5573 | -6.3419 | -6.6188
| MONTROSE NORTH | ST |  |  | 4.2498 | 3.3661 | 2.4217 | 1.4921 | 0.80689 | 0.32389 | -0.09971 | -0.48356 | -0.81833 | -1.1344 | -2.0015 | -3.5762 | -4.4426 | -5.0066 | 5.6095 | 4.6642 | 3.6436 | 2.645 | 1.9164 | 1.4351 | 1.0217 | 0.64534 | 0.31898 | 0.065136 | -0.54571 | -1.1952 | -1.7909 | -2.3358 | 4.7308 | 3.9092 | 3.0245 | 2.1512 | 1.5141 | 1.0756 | 0.69146 | 0.34043 | 0.03758 | -0.24903 | -1.0313 | -2.4001 | -3.1699 | -3.6778
| MONTROSE NORTH | SP |  |  | 4.2714 | 3.3989 | 2.4666 | 1.5595 | 0.85779 | 0.36054 | -0.074496 | -0.46661 | -0.84256 | -1.1684 | -1.967 | -3.0656 | -3.9515 | -4.1529 | 5.6115 | 4.6677 | 3.6491 | 2.6553 | 1.9302 | 1.4537 | 1.0461 | 0.67623 | 0.3529 | 0.10856 | -0.45195 | -0.97832 | -1.8552 | -2.6834 | 4.7506 | 3.9394 | 3.0659 | 2.2124 | 1.5596 | 1.1074 | 0.71199 | 0.35282 | 0.013193 | -0.28332 | -1.0087 | -1.9612 | -2.7198 | -2.8917
TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | 1.1356 | 0.9886 | 0.86198 | 0.74436 | 0.56331 | 0.36938 | 0.13741 | -0.086353 | -0.39801 | -0.63693 | -1.0564 | -1.2285 | -1.1673 | -1.2874 | 1.9681 | 1.826 | 1.7209 | 1.6279 | 1.5138 | 1.3953 | 1.2507 | 1.1156 | 0.9395 | 0.78062 | 0.53256 | 0.43035 | 0.42341 | 0.3003 | 1.6288 | 1.4855 | 1.3865 | 1.3091 | 1.2453 | 1.1072 | 0.87556 | 0.65515 | 0.36636 | 0.14365 | -0.24636 | -0.40572 | -0.34873 | -0.45587
| MOSSAT | CT |  |  | 1.1782 | 1.0522 | 0.93489 | 0.83368 | 0.65783 | 0.48855 | 0.2826 | 0.055961 | -0.17476 | -0.33686 | -0.82495 | -1.1005 | -1.1673 | -1.2184 | 1.9846 | 1.8513 | 1.7469 | 1.6596 | 1.5478 | 1.4427 | 1.3194 | 1.1827 | 1.0573 | 0.9479 | 0.63098 | 0.47091 | 0.42341 | 0.36918 | 1.6288 | 1.4855 | 1.3865 | 1.3091 | 1.2453 | 1.1855 | 1.0209 | 0.78747 | 0.57372 | 0.42075 | -0.029783 | -0.2873 | -0.34873 | -0.39376
| MOSSAT | LW |  |  | 1.1356 | 0.9886 | 0.86198 | 0.74436 | 0.56331 | 0.36938 | 0.13741 | -0.086353 | -0.39801 | -0.63693 | -1.0564 | -1.2285 | -1.1545 | -1.1738 | 1.9681 | 1.826 | 1.7209 | 1.6279 | 1.5138 | 1.3953 | 1.2507 | 1.1156 | 0.9395 | 0.78062 | 0.53256 | 0.43035 | 0.45771 | 0.44909 | 1.6319 | 1.4886 | 1.3927 | 1.3163 | 1.2521 | 1.1072 | 0.87556 | 0.65515 | 0.36636 | 0.14365 | -0.24636 | -0.40572 | -0.33862 | -0.35695
| MOSSAT | ST |  |  | 1.1817 | 1.0611 | 0.97366 | 0.90753 | 0.85523 | 0.79133 | 0.73234 | 0.67035 | 0.5876 | 0.49507 | 0.17022 | -0.44335 | -0.67173 | -0.79299 | 1.9909 | 1.8635 | 1.7791 | 1.7139 | 1.6645 | 1.6102 | 1.5585 | 1.5045 | 1.4388 | 1.3711 | 1.1527 | 0.75428 | 0.6238 | 0.5374 | 1.6382 | 1.5015 | 1.4124 | 1.3468 | 1.2985 | 1.2519 | 1.204 | 1.1534 | 1.0991 | 1.0461 | 0.91556 | 0.34491 | 0.11822 | 0.0042538
| MOSSAT | SP |  |  | 1.1875 | 1.0722 | 0.98963 | 0.92967 | 0.85666 | 0.78653 | 0.70049 | 0.61735 | 0.52758 | 0.43064 | 0.12343 | -0.68862 | -1.0961 | -1.2874 | 1.9933 | 1.8689 | 1.7869 | 1.7253 | 1.6663 | 1.6116 | 1.5459 | 1.4819 | 1.4131 | 1.3448 | 1.1558 | 0.67613 | 0.43862 | 0.3003 | 1.6385 | 1.5028 | 1.4148 | 1.3511 | 1.3032 | 1.2598 | 1.2117 | 1.1624 | 1.1109 | 1.0632 | 0.85259 | 0.10069 | -0.27943 | -0.45587
THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | 2.5286 | 2.4976 | 2.124 | 1.6715 | 1.0418 | 0.31671 | -0.13006 | -0.55588 | -1.0562 | -1.3828 | -2.3364 | -2.9991 | -3.2611 | -3.3694 | 4.3966 | 4.3751 | 4.0572 | 3.6701 | 3.1722 | 2.593 | 2.2623 | 1.95 | 1.6258 | 1.3931 | 0.71667 | 0.31326 | 0.16503 | 0.044647 | 3.7539 | 3.7297 | 3.3892 | 2.9679 | 2.4512 | 1.8497 | 1.5392 | 1.27 | 1.03 | 0.75945 | -0.12347 | -0.72301 | -0.95172 | -1.0447
| MOUNT PLEASANT | CT |  |  | 2.5816 | 2.563 | 2.2031 | 1.7517 | 1.1236 | 0.4163 | -0.077759 | -0.54187 | -0.9593 | -1.2821 | -2.2232 | -2.9991 | -3.2611 | -3.3694 | 4.4132 | 4.3954 | 4.0801 | 3.6873 | 3.1853 | 2.6114 | 2.2641 | 1.95 | 1.6733 | 1.4425 | 0.77558 | 0.31326 | 0.16503 | 0.044647 | 3.7539 | 3.7297 | 3.3892 | 2.9679 | 2.4512 | 1.8497 | 1.5392 | 1.27 | 1.0401 | 0.84371 | -0.015076 | -0.72301 | -0.95172 | -1.0447
| MOUNT PLEASANT | LW |  |  | 2.5286 | 2.4976 | 2.124 | 1.6715 | 1.0418 | 0.31671 | -0.13006 | -0.55588 | -1.0562 | -1.3828 | -2.3364 | -2.8964 | -3.0229 | -3.1069 | 4.3966 | 4.3751 | 4.0572 | 3.6701 | 3.1722 | 2.593 | 2.2623 | 1.9529 | 1.6258 | 1.3931 | 0.71667 | 0.38142 | 0.33148 | 0.29759 | 3.7582 | 3.7351 | 3.3974 | 2.9813 | 2.4675 | 1.8662 | 1.5541 | 1.2766 | 1.03 | 0.75945 | -0.12347 | -0.63519 | -0.74409 | -0.8158
| MOUNT PLEASANT | ST |  |  | 2.5759 | 2.5434 | 2.1966 | 1.7774 | 1.2801 | 0.69735 | 0.39848 | 0.1359 | -0.10071 | -0.32523 | -0.99089 | -1.697 | -2.0525 | -2.2387 | 4.4172 | 4.3968 | 4.0924 | 3.7196 | 3.2762 | 2.758 | 2.485 | 2.2303 | 2.0165 | 1.8374 | 1.3144 | 0.84214 | 0.61972 | 0.46671 | 3.7639 | 3.7447 | 3.4124 | 3.0029 | 2.5025 | 1.9183 | 1.6228 | 1.3661 | 1.1503 | 0.96834 | 0.4482 | 0.13179 | 0.054419 | -0.061175
| MOUNT PLEASANT | SP |  |  | 2.5836 | 2.5549 | 2.212 | 1.7966 | 1.2729 | 0.6679 | 0.3389 | 0.050196 | -0.2072 | -0.44903 | -1.154 | -1.8681 | -2.309 | -2.4803 | 4.4207 | 4.4025 | 4.0994 | 3.7297 | 3.2787 | 2.7539 | 2.4775 | 2.2378 | 2.0268 | 1.8398 | 1.3 | 0.83152 | 0.4724 | 0.20263 | 3.7649 | 3.7469 | 3.4151 | 3.0077 | 2.5097 | 1.9279 | 1.6337 | 1.381 | 1.1664 | 0.99015 | 0.49792 | 0.24336 | -0.10682 | -0.2586
BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | YES | 9.7555 | 9.577 | 9.4066 | 9.207 | 8.6759 | 8.0944 | 7.4877 | 6.7907 | 5.8795 | 5.1713 | 3.3621 | 2.1604 | 1.9802 | 1.8282 | 11.9346 | 11.8326 | 11.7445 | 11.633 | 11.398 | 11.1321 | 10.8331 | 10.4478 | 9.9708 | 9.4877 | 8.3365 | 7.6244 | 7.4701 | 7.2895 | 10.9748 | 10.828 | 10.6782 | 10.4967 | 10.0233 | 9.5064 | 8.966 | 8.344 | 7.5317 | 6.883 | 5.2695 | 4.2635 | 4.1018 | 3.9636
| MUIR OF ORD | CT |  |  | 9.8921 | 9.7721 | 9.6433 | 9.4818 | 8.9539 | 8.4516 | 7.7998 | 7.0719 | 6.381 | 5.8711 | 3.9986 | 2.304 | 1.9802 | 1.8282 | 11.972 | 11.8882 | 11.8015 | 11.6803 | 11.4318 | 11.1909 | 10.8992 | 10.5542 | 10.2242 | 9.9134 | 8.6602 | 7.6754 | 7.4701 | 7.2895 | 11.0928 | 10.997 | 10.8812 | 10.7288 | 10.2557 | 9.8083 | 9.2336 | 8.5954 | 7.9915 | 7.5386 | 5.8484 | 4.3928 | 4.1018 | 3.9636
| MUIR OF ORD | LW |  |  | 9.7555 | 9.577 | 9.4066 | 9.207 | 8.6759 | 8.0944 | 7.4877 | 6.7907 | 5.8795 | 5.1713 | 3.3621 | 2.1604 | 2.1857 | 2.05 | 11.9346 | 11.8326 | 11.7445 | 11.633 | 11.398 | 11.1321 | 10.8331 | 10.4478 | 9.9708 | 9.4877 | 8.3365 | 7.6244 | 7.6313 | 7.5808 | 10.9748 | 10.828 | 10.6782 | 10.4967 | 10.0233 | 9.5064 | 8.966 | 8.344 | 7.5317 | 6.883 | 5.2695 | 4.2635 | 4.2916 | 4.1622
| MUIR OF ORD | ST |  |  | 9.8889 | 9.7765 | 9.7107 | 9.6461 | 9.5896 | 9.4945 | 9.3904 | 9.2325 | 9.0267 | 8.7207 | 7.6163 | 5.1515 | 4.3535 | 4.0248 | 11.9941 | 11.9278 | 11.886 | 11.8364 | 11.7917 | 11.7185 | 11.6429 | 11.5341 | 11.4048 | 11.2198 | 10.5191 | 8.8359 | 8.3467 | 8.1034 | 11.0947 | 11.0088 | 10.9531 | 10.8935 | 10.8423 | 10.7578 | 10.6693 | 10.5393 | 10.3694 | 10.1144 | 9.1877 | 7.071 | 6.3439 | 6.04
| MUIR OF ORD | SP |  |  | 9.9294 | 9.8403 | 9.7991 | 9.7654 | 9.6421 | 9.5019 | 9.3312 | 9.111 | 8.8532 | 8.5204 | 7.3748 | 4.7331 | 3.2089 | 2.6901 | 12.0089 | 11.9532 | 11.9208 | 11.8905 | 11.828 | 11.753 | 11.6573 | 11.5323 | 11.3753 | 11.1888 | 10.5568 | 8.9267 | 7.8643 | 7.3643 | 11.1306 | 11.0656 | 11.0318 | 11.0013 | 10.8926 | 10.7713 | 10.625 | 10.4415 | 10.2226 | 9.9386 | 8.9568 | 6.6326 | 5.2509 | 4.7694
BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | 4.2774 | 4.2628 | 4.2268 | 4.1893 | 4.0814 | 3.9306 | 3.7766 | 3.6092 | 3.3442 | 3.1986 | 2.8083 | 2.622 | 2.6251 | 2.4976 | 4.9545 | 4.9365 | 4.9085 | 4.8783 | 4.8196 | 4.7503 | 4.6765 | 4.5887 | 4.4485 | 4.3587 | 4.1221 | 3.9993 | 3.8971 | 3.7179 | 4.3139 | 4.3007 | 4.2592 | 4.2131 | 4.0873 | 3.9507 | 3.8116 | 3.6594 | 3.4176 | 3.2868 | 2.9319 | 2.7556 | 2.7642 | 2.6512
| MUIREND | CT |  |  | 4.3224 | 4.3172 | 4.2942 | 4.2669 | 4.1672 | 4.0414 | 3.8656 | 3.6821 | 3.5126 | 3.396 | 2.9977 | 2.7218 | 2.6887 | 2.6634 | 4.9711 | 4.9561 | 4.9304 | 4.8972 | 4.8325 | 4.7728 | 4.6976 | 4.6163 | 4.5406 | 4.4662 | 4.1976 | 4.013 | 3.9594 | 3.8914 | 4.3712 | 4.3679 | 4.34 | 4.2992 | 4.1721 | 4.0552 | 3.8943 | 3.7248 | 3.5682 | 3.4636 | 3.1054 | 2.8473 | 2.8173 | 2.7956
| MUIREND | LW |  |  | 4.2774 | 4.2628 | 4.2268 | 4.1893 | 4.0814 | 3.9306 | 3.7766 | 3.6092 | 3.3442 | 3.1986 | 2.8083 | 2.622 | 2.6901 | 2.6645 | 4.9545 | 4.9365 | 4.9085 | 4.8783 | 4.8196 | 4.7503 | 4.6765 | 4.5887 | 4.4485 | 4.3587 | 4.1221 | 3.9993 | 4.0208 | 4.0118 | 4.3139 | 4.3007 | 4.2592 | 4.2131 | 4.0873 | 3.9507 | 3.8116 | 3.6594 | 3.4176 | 3.2868 | 2.9319 | 2.7556 | 2.8161 | 2.7942
| MUIREND | ST |  |  | 4.3147 | 4.2973 | 4.2782 | 4.2682 | 4.2549 | 4.237 | 4.2175 | 4.2014 | 4.1711 | 4.108 | 3.8709 | 3.3139 | 3.1239 | 3.0432 | 4.972 | 4.9549 | 4.9343 | 4.92 | 4.9065 | 4.8858 | 4.866 | 4.8478 | 4.8215 | 4.7832 | 4.6306 | 4.2359 | 4.1135 | 4.0276 | 4.3563 | 4.3346 | 4.3098 | 4.2966 | 4.2838 | 4.2616 | 4.2397 | 4.222 | 4.1845 | 4.1266 | 3.9056 | 3.3733 | 3.2015 | 3.1313
| MUIREND | SP |  |  | 4.3163 | 4.2997 | 4.2827 | 4.2705 | 4.2323 | 4.1946 | 4.1454 | 4.0817 | 4.0159 | 3.924 | 3.6629 | 3.0012 | 2.6251 | 2.4976 | 4.974 | 4.9583 | 4.9402 | 4.9256 | 4.8995 | 4.8712 | 4.8428 | 4.8102 | 4.7751 | 4.7295 | 4.593 | 4.1848 | 3.8971 | 3.7179 | 4.3606 | 4.3409 | 4.3204 | 4.3049 | 4.2551 | 4.2051 | 4.1528 | 4.0955 | 4.0362 | 3.9518 | 3.7123 | 3.1119 | 2.7642 | 2.6512
NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | YES | 4.4183 | 4.311 | 4.1951 | 3.9719 | 3.5867 | 3.1192 | 2.6334 | 2.0724 | 1.3333 | 0.73475 | -1.1294 | -4.044 | -5.5324 | -6.0651 | 6.5148 | 6.4385 | 6.3591 | 6.1896 | 5.9993 | 5.7672 | 5.5243 | 5.2281 | 4.8563 | 4.5187 | 3.4547 | 2.0747 | 1.3479 | 0.86802 | 4.4154 | 4.3324 | 4.2404 | 4.0649 | 3.7159 | 3.2935 | 2.8543 | 2.3439 | 1.6794 | 1.1294 | -0.59054 | -3.1771 | -4.4805 | -4.9438
| NAIRN CENTRAL | CT |  |  | 4.4854 | 4.4032 | 4.3226 | 4.1544 | 3.7613 | 3.319 | 2.7798 | 2.2092 | 1.6023 | 0.96239 | -1.109 | -4.044 | -5.5324 | -6.0651 | 6.531 | 6.4614 | 6.3891 | 6.2209 | 6.0135 | 5.7839 | 5.5243 | 5.2512 | 4.9561 | 4.6247 | 3.5236 | 2.0747 | 1.3479 | 0.86802 | 4.4727 | 4.4115 | 4.3494 | 4.2177 | 3.8589 | 3.4575 | 2.9729 | 2.4632 | 1.9236 | 1.3447 | -0.54045 | -3.1771 | -4.4805 | -4.9438
| NAIRN CENTRAL | LW |  |  | 4.4183 | 4.311 | 4.1951 | 3.9719 | 3.5867 | 3.1192 | 2.6334 | 2.0724 | 1.3333 | 0.73475 | -1.1294 | -3.1166 | -4.2056 | -4.583 | 6.5148 | 6.4385 | 6.3591 | 6.1896 | 5.9993 | 5.7672 | 5.5266 | 5.2281 | 4.8563 | 4.5187 | 3.4547 | 2.5074 | 2.0977 | 1.9524 | 4.4154 | 4.3324 | 4.2404 | 4.0649 | 3.7159 | 3.2935 | 2.8543 | 2.3439 | 1.6794 | 1.1294 | -0.59054 | -2.3763 | -3.327 | -3.6542
| NAIRN CENTRAL | ST |  |  | 4.5144 | 4.418 | 4.3257 | 4.1579 | 4.1298 | 4.092 | 4.0376 | 3.9708 | 3.8835 | 3.725 | 3.1226 | 1.2278 | 0.011806 | -0.71848 | 6.5635 | 6.5004 | 6.4391 | 6.307 | 6.272 | 6.2311 | 6.1774 | 6.1175 | 6.041 | 5.9238 | 5.4756 | 4.1412 | 3.3686 | 2.8143 | 4.5034 | 4.4326 | 4.3641 | 4.2418 | 4.2124 | 4.1754 | 4.1227 | 4.0617 | 3.9844 | 3.8373 | 3.2701 | 1.4765 | 0.37593 | -0.26104
| NAIRN CENTRAL | SP |  |  | 4.5483 | 4.4682 | 4.3916 | 4.2153 | 4.1375 | 4.0527 | 3.9526 | 3.8397 | 3.7014 | 3.513 | 2.9518 | 1.6367 | 0.54717 | 0.28966 | 6.58 | 6.525 | 6.4706 | 6.3417 | 6.294 | 6.2404 | 6.1762 | 6.1043 | 6.0066 | 5.8828 | 5.4913 | 4.5142 | 3.3873 | 2.5516 | 4.5342 | 4.4783 | 4.4241 | 4.2961 | 4.2248 | 4.1482 | 4.0573 | 3.9575 | 3.8351 | 3.6647 | 3.1515 | 1.9206 | 0.87413 | 0.63973
STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | 1.9107 | 6.842 | 6.8309 | 6.8124 | 6.792 | 6.7287 | 6.6113 | 6.4633 | 6.2432 | 6.1114 | 5.7185 | 5.56 | 5.6159 | 5.5296 | 2.0936 | 7.0266 | 7.0164 | 6.9929 | 6.9572 | 6.902 | 6.8401 | 6.7609 | 6.655 | 6.5756 | 6.3341 | 6.2366 | 6.2473 | 6.1287 | 1.8696 | 6.785 | 6.7527 | 6.7126 | 6.6097 | 6.4994 | 6.3854 | 6.2466 | 6.047 | 5.9293 | 5.5713 | 5.4229 | 5.472 | 5.3999
| NEW PITSLIGO | CT |  |  | 1.9107 | 6.842 | 6.8309 | 6.8124 | 6.792 | 6.7705 | 6.6505 | 6.4757 | 6.3144 | 6.2205 | 5.8813 | 5.6505 | 5.6291 | 5.6047 | 2.0936 | 7.0266 | 7.0164 | 6.9929 | 6.9606 | 6.9124 | 6.8401 | 6.7609 | 6.687 | 6.6307 | 6.4122 | 6.2709 | 6.2473 | 6.214 | 1.8908 | 6.8192 | 6.7963 | 6.7525 | 6.6567 | 6.5645 | 6.4171 | 6.2576 | 6.1103 | 6.026 | 5.72 | 5.505 | 5.4859 | 5.4646
| NEW PITSLIGO | LW |  |  | 1.9138 | 6.8462 | 6.8369 | 6.8237 | 6.8046 | 6.7287 | 6.6113 | 6.4633 | 6.2432 | 6.1114 | 5.7185 | 5.56 | 5.6159 | 5.5894 | 2.0962 | 7.0301 | 7.019 | 6.9984 | 6.9572 | 6.902 | 6.8438 | 6.7626 | 6.655 | 6.5756 | 6.3341 | 6.2366 | 6.2561 | 6.2453 | 1.8696 | 6.785 | 6.7527 | 6.7126 | 6.6097 | 6.4994 | 6.3854 | 6.2466 | 6.047 | 5.9293 | 5.5713 | 5.4229 | 5.472 | 5.4489
| NEW PITSLIGO | ST |  |  | 1.9188 | 6.8558 | 6.8517 | 6.8453 | 6.8395 | 6.8315 | 6.8226 | 6.8129 | 6.8019 | 6.7859 | 6.6858 | 6.2256 | 6.0153 | 5.9292 | 2.1002 | 7.0378 | 7.0344 | 7.0293 | 7.0246 | 7.0173 | 7.0049 | 6.9906 | 6.9737 | 6.9463 | 6.817 | 6.5111 | 6.389 | 6.3294 | 1.8901 | 6.8214 | 6.8119 | 6.7957 | 6.7828 | 6.7651 | 6.7467 | 6.7262 | 6.6923 | 6.6438 | 6.4537 | 6.0021 | 5.8112 | 5.7385
| NEW PITSLIGO | SP |  |  | 1.9196 | 6.857 | 6.8542 | 6.8505 | 6.8461 | 6.8413 | 6.8355 | 6.828 | 6.8186 | 6.8072 | 6.6983 | 6.1349 | 5.7036 | 5.5296 | 2.1008 | 7.0386 | 7.0363 | 7.0333 | 7.0298 | 7.0259 | 7.0203 | 7.0097 | 6.9931 | 6.9656 | 6.8508 | 6.5292 | 6.2601 | 6.1287 | 1.9005 | 6.8371 | 6.835 | 6.8311 | 6.8133 | 6.7948 | 6.7745 | 6.7482 | 6.7141 | 6.6704 | 6.4652 | 5.9528 | 5.554 | 5.3999
DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | 0.22148 | 0.22345 | 0.22164 | 0.21872 | 0.20817 | 0.19669 | 0.18309 | 0.16566 | 0.14417 | 0.13173 | 0.083303 | 0.079264 | 0.072859 | 0.065178 | 0.23445 | 0.23525 | 0.23406 | 0.2322 | 0.22576 | 0.21916 | 0.21181 | 0.20313 | 0.19347 | 0.18524 | 0.1501 | 0.14794 | 0.14494 | 0.14172 | 0.21705 | 0.21939 | 0.21754 | 0.21458 | 0.20351 | 0.1922 | 0.17822 | 0.16121 | 0.14189 | 0.13014 | 0.082447 | 0.07879 | 0.073097 | 0.066387
| NEWTON | CT |  |  | 0.22566 | 0.22662 | 0.22554 | 0.2201 | 0.20817 | 0.19669 | 0.18309 | 0.16566 | 0.14866 | 0.13879 | 0.09428 | 0.085743 | 0.090483 | 0.090729 | 0.23654 | 0.23674 | 0.23594 | 0.2325 | 0.22576 | 0.21916 | 0.21181 | 0.20313 | 0.19532 | 0.18892 | 0.15552 | 0.15179 | 0.1534 | 0.15327 | 0.22244 | 0.22262 | 0.22205 | 0.21779 | 0.20555 | 0.19346 | 0.17822 | 0.16121 | 0.1459 | 0.13657 | 0.092444 | 0.084877 | 0.089064 | 0.089315
| NEWTON | LW |  |  | 0.22148 | 0.22345 | 0.22164 | 0.21872 | 0.20909 | 0.19903 | 0.18556 | 0.16905 | 0.14417 | 0.13173 | 0.083303 | 0.079264 | 0.087401 | 0.083601 | 0.23445 | 0.23525 | 0.23406 | 0.2322 | 0.22707 | 0.22159 | 0.21516 | 0.20613 | 0.19347 | 0.18524 | 0.1501 | 0.14794 | 0.15091 | 0.14948 | 0.21705 | 0.21939 | 0.21754 | 0.21458 | 0.20351 | 0.1922 | 0.17992 | 0.16466 | 0.14189 | 0.13014 | 0.082447 | 0.07879 | 0.085954 | 0.08266
| NEWTON | ST |  |  | 0.22439 | 0.22367 | 0.22329 | 0.22222 | 0.22158 | 0.22072 | 0.2191 | 0.21795 | 0.21579 | 0.20947 | 0.18847 | 0.13811 | 0.13367 | 0.13064 | 0.23611 | 0.23562 | 0.23535 | 0.23454 | 0.23386 | 0.23311 | 0.23186 | 0.23085 | 0.2294 | 0.22522 | 0.2105 | 0.17361 | 0.17037 | 0.1684 | 0.22057 | 0.21984 | 0.21943 | 0.21868 | 0.21835 | 0.21772 | 0.21641 | 0.21562 | 0.21345 | 0.20731 | 0.18608 | 0.13592 | 0.12931 | 0.12518
| NEWTON | SP |  |  | 0.22483 | 0.22422 | 0.22408 | 0.22411 | 0.22032 | 0.21703 | 0.21328 | 0.20819 | 0.20248 | 0.19367 | 0.16798 | 0.098549 | 0.072859 | 0.065178 | 0.2363 | 0.23587 | 0.23569 | 0.23562 | 0.2335 | 0.23166 | 0.22956 | 0.22664 | 0.22329 | 0.21833 | 0.20511 | 0.16055 | 0.14494 | 0.14172 | 0.22105 | 0.22042 | 0.22029 | 0.2203 | 0.21597 | 0.21217 | 0.20785 | 0.20235 | 0.19638 | 0.18708 | 0.16356 | 0.097173 | 0.073097 | 0.066387
REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | 3.3239 | 2.5935 | 1.7725 | 0.92086 | -0.15963 | -1.2384 | -2.4256 | -3.5722 | -4.9662 | -6.2958 | -9.5096 | -12.8119 | -14.2148 | -14.6565 | 4.6427 | 4.0224 | 3.3017 | 2.5659 | 1.7404 | 0.94531 | 0.03618 | -0.83497 | -1.8315 | -2.8396 | -5.1045 | -7.0044 | -7.8045 | -8.3847 | 3.8911 | 3.2517 | 2.5063 | 1.7309 | 0.74592 | -0.22652 | -1.2985 | -2.3396 | -3.6055 | -4.8357 | -7.7522 | -10.5365 | -11.779 | -12.1798
| NEWTONHILL | CT |  |  | 3.3306 | 2.6109 | 1.7803 | 0.94237 | -0.08781 | -1.0699 | -2.1687 | -3.2935 | -4.4749 | -5.8611 | -9.5096 | -12.8119 | -14.2148 | -14.6565 | 4.6427 | 4.0224 | 3.3017 | 2.5659 | 1.7404 | 0.97281 | 0.16239 | -0.65651 | -1.5153 | -2.5435 | -5.1045 | -7.0044 | -7.8045 | -8.3847 | 3.8911 | 3.2572 | 2.5135 | 1.7526 | 0.81385 | -0.072439 | -1.0756 | -2.1049 | -3.1844 | -4.4411 | -7.7169 | -10.5365 | -11.779 | -12.1798
| NEWTONHILL | LW |  |  | 3.3239 | 2.5935 | 1.7725 | 0.92086 | -0.15963 | -1.2384 | -2.4256 | -3.5722 | -4.9662 | -6.2958 | -9.4631 | -12.116 | -13.1799 | -13.4878 | 4.6565 | 4.037 | 3.3344 | 2.6063 | 1.7641 | 0.94531 | 0.03618 | -0.83497 | -1.8315 | -2.8396 | -5.0969 | -6.6122 | -7.035 | -7.1539 | 3.894 | 3.2517 | 2.5063 | 1.7309 | 0.74592 | -0.22652 | -1.2985 | -2.3396 | -3.6055 | -4.8357 | -7.7522 | -10.0073 | -10.8563 | -11.1238
| NEWTONHILL | ST |  |  | 3.4186 | 2.7434 | 1.9966 | 1.2548 | 0.49375 | -0.2 | -0.88147 | -1.5835 | -2.3139 | -3.1825 | -5.2828 | -8.3184 | -9.3091 | -9.8885 | 4.713 | 4.1336 | 3.4817 | 2.8267 | 2.1506 | 1.5421 | 0.93522 | 0.31014 | -0.33608 | -1.086 | -2.8305 | -5.1252 | -5.8485 | -6.4907 | 3.9891 | 3.3827 | 2.7006 | 2.021 | 1.3231 | 0.69563 | 0.07003 | -0.57549 | -1.2451 | -2.0387 | -3.8916 | -6.7093 | -7.5501 | -8.0256
| NEWTONHILL | SP |  |  | 3.4219 | 2.7617 | 2.0252 | 1.2925 | 0.50761 | -0.20984 | -0.92397 | -1.6626 | -2.4213 | -3.2523 | -5.1433 | -7.8224 | -9.0532 | -9.2749 | 4.7085 | 4.1378 | 3.49 | 2.8422 | 2.1568 | 1.5376 | 0.91472 | 0.27074 | -0.39256 | -1.1138 | -2.6907 | -4.8198 | -6.1844 | -7.2723 | 3.9876 | 3.4004 | 2.7279 | 2.0561 | 1.3363 | 0.68746 | 0.032666 | -0.64528 | -1.3394 | -2.1013 | -3.7774 | -6.1248 | -7.3796 | -7.5814
ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | 4.3238 | 3.594 | 3.229 | 2.9856 | 2.8335 | 2.7421 | 2.6507 | 2.5592 | 2.4678 | 2.437 | 2.4359 | 2.4348 | 2.4348 | 2.4348 | 5.2488 | 4.498 | 4.1187 | 3.8658 | 3.7076 | 3.6127 | 3.5178 | 3.4228 | 3.3278 | 3.296 | 3.2952 | 3.2945 | 3.2945 | 3.2945 | 4.7173 | 3.983 | 3.6157 | 3.3707 | 3.2175 | 3.1254 | 3.0333 | 2.9411 | 2.8489 | 2.8177 | 2.8156 | 2.8135 | 2.8135 | 2.8135
| NIGG | CT |  |  | 4.3238 | 3.594 | 3.229 | 2.9856 | 2.8335 | 2.7421 | 2.6507 | 2.5593 | 2.4679 | 2.4372 | 2.4365 | 2.4356 | 2.4356 | 2.4356 | 5.2488 | 4.498 | 4.1187 | 3.8658 | 3.7076 | 3.6127 | 3.5178 | 3.4228 | 3.3279 | 3.2961 | 3.2956 | 3.2951 | 3.295 | 3.295 | 4.7173 | 3.983 | 3.6157 | 3.3707 | 3.2175 | 3.1254 | 3.0334 | 2.9413 | 2.8491 | 2.818 | 2.8167 | 2.8151 | 2.815 | 2.815
| NIGG | LW |  |  | 4.3238 | 3.594 | 3.229 | 2.9856 | 2.8335 | 2.7421 | 2.6507 | 2.5592 | 2.4678 | 2.437 | 2.4359 | 2.4348 | 2.4348 | 2.4348 | 5.2488 | 4.498 | 4.1187 | 3.8658 | 3.7076 | 3.6127 | 3.5178 | 3.4228 | 3.3278 | 3.296 | 3.2952 | 3.2945 | 3.2945 | 3.2945 | 4.7174 | 3.983 | 3.6157 | 3.3707 | 3.2175 | 3.1254 | 3.0333 | 2.9411 | 2.8489 | 2.8177 | 2.8156 | 2.8135 | 2.8135 | 2.8135
| NIGG | ST |  |  | 4.3239 | 3.5941 | 3.2292 | 2.9859 | 2.8338 | 2.7425 | 2.6512 | 2.5599 | 2.4686 | 2.438 | 2.4374 | 2.4357 | 2.4351 | 2.4351 | 5.2489 | 4.4981 | 4.1188 | 3.8659 | 3.7079 | 3.613 | 3.5181 | 3.4232 | 3.3283 | 3.2966 | 3.2962 | 3.2951 | 3.2947 | 3.2947 | 4.7175 | 3.9832 | 3.616 | 3.3712 | 3.2181 | 3.1262 | 3.0343 | 2.9424 | 2.8504 | 2.8195 | 2.8183 | 2.8153 | 2.8142 | 2.8142
| NIGG | SP |  |  | 4.3239 | 3.5941 | 3.2292 | 2.9859 | 2.8338 | 2.7426 | 2.6513 | 2.56 | 2.4687 | 2.4382 | 2.4379 | 2.4367 | 2.4357 | 2.4356 | 5.2489 | 4.4981 | 4.1188 | 3.8659 | 3.7079 | 3.613 | 3.5182 | 3.4233 | 3.3284 | 3.2968 | 3.2965 | 3.2958 | 3.2951 | 3.295 | 4.7175 | 3.9832 | 3.616 | 3.3712 | 3.2182 | 3.1263 | 3.0345 | 2.9426 | 2.8507 | 2.8199 | 2.8193 | 2.8171 | 2.8152 | 2.815
CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | 13.6977 | 13.5899 | 13.4541 | 13.3 | 12.9188 | 12.3441 | 11.8338 | 11.3353 | 10.8676 | 10.4938 | 9.1946 | 7.7962 | 7.0106 | 6.5631 | 15.2877 | 15.2204 | 15.1329 | 15.0268 | 14.8098 | 14.3553 | 13.9469 | 13.5774 | 13.2305 | 12.937 | 12.0747 | 11.5293 | 11.1026 | 10.7511 | 14.1654 | 14.078 | 13.9678 | 13.8377 | 13.5274 | 13.0462 | 12.6127 | 12.1776 | 11.7648 | 11.428 | 10.2347 | 9.0554 | 8.4414 | 8.1111
| NINEWELLS | CT |  |  | 13.6977 | 13.6002 | 13.4649 | 13.3064 | 12.9356 | 12.3759 | 11.9158 | 11.4867 | 11.0479 | 10.6453 | 9.2423 | 7.7962 | 7.0106 | 6.5631 | 15.2877 | 15.2204 | 15.1329 | 15.0268 | 14.8098 | 14.3553 | 13.9469 | 13.5774 | 13.2305 | 12.9394 | 12.1073 | 11.5293 | 11.1026 | 10.7511 | 14.1654 | 14.0835 | 13.9726 | 13.8377 | 13.5315 | 13.0611 | 12.6731 | 12.3027 | 11.9218 | 11.5681 | 10.3064 | 9.0554 | 8.4414 | 8.1111
| NINEWELLS | LW |  |  | 13.6998 | 13.5899 | 13.4541 | 13.3 | 12.9188 | 12.3441 | 11.8338 | 11.3353 | 10.8676 | 10.4938 | 9.1946 | 8.1069 | 7.4573 | 7.0503 | 15.2979 | 15.226 | 15.1426 | 15.0464 | 14.8294 | 14.3887 | 13.9826 | 13.6201 | 13.2552 | 12.937 | 12.0747 | 11.5851 | 11.401 | 11.189 | 14.1703 | 14.078 | 13.9678 | 13.8404 | 13.5274 | 13.0462 | 12.6127 | 12.1776 | 11.7648 | 11.428 | 10.2347 | 9.2885 | 8.7916 | 8.4949
| NINEWELLS | ST |  |  | 13.7698 | 13.6982 | 13.606 | 13.4987 | 13.2959 | 12.9327 | 12.6333 | 12.3764 | 12.1117 | 11.8867 | 10.9815 | 10.0748 | 9.4232 | 8.8967 | 15.3322 | 15.2813 | 15.2204 | 15.1475 | 15.0029 | 14.6071 | 14.2291 | 13.907 | 13.5667 | 13.2767 | 12.466 | 11.9786 | 11.8263 | 11.7183 | 14.2311 | 14.1735 | 14.1023 | 14.0167 | 13.8546 | 13.5528 | 13.3024 | 13.0804 | 12.8494 | 12.6402 | 11.7378 | 10.9653 | 10.4375 | 10.0434
| NINEWELLS | SP |  |  | 13.7643 | 13.6992 | 13.6106 | 13.5113 | 13.3015 | 12.9266 | 12.6201 | 12.3572 | 12.0783 | 11.8595 | 11.0251 | 10.3733 | 9.7014 | 9.3626 | 15.3237 | 15.2764 | 15.217 | 15.1495 | 15.0042 | 14.5987 | 14.2238 | 13.898 | 13.5611 | 13.2801 | 12.5025 | 12.0991 | 11.79 | 11.5596 | 14.2232 | 14.1713 | 14.1033 | 14.0258 | 13.8592 | 13.5488 | 13.2934 | 13.0682 | 12.8244 | 12.6347 | 11.7812 | 11.2914 | 10.6637 | 10.4183
THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | 0.16084 | 0.16111 | 0.15899 | 0.15327 | 0.14643 | 0.14064 | 0.13263 | 0.1225 | 0.11434 | 0.11027 | 0.099252 | 0.081742 | 0.082842 | 0.080088 | 0.17669 | 0.17655 | 0.17556 | 0.17272 | 0.16892 | 0.16568 | 0.16206 | 0.15715 | 0.15334 | 0.15047 | 0.13762 | 0.12421 | 0.12434 | 0.12297 | 0.15522 | 0.1554 | 0.1535 | 0.14831 | 0.142 | 0.13665 | 0.12948 | 0.12031 | 0.11296 | 0.10905 | 0.099994 | 0.08446 | 0.085376 | 0.082895
| NORTH HOY | CT |  |  | 0.16123 | 0.16111 | 0.15899 | 0.15327 | 0.14643 | 0.14064 | 0.13263 | 0.1225 | 0.11434 | 0.11027 | 0.1008 | 0.088141 | 0.090715 | 0.091082 | 0.17679 | 0.17655 | 0.17556 | 0.17272 | 0.16892 | 0.16568 | 0.16206 | 0.15715 | 0.15334 | 0.15047 | 0.14135 | 0.12994 | 0.13049 | 0.12979 | 0.15555 | 0.1554 | 0.1535 | 0.14831 | 0.142 | 0.13665 | 0.12948 | 0.12031 | 0.11296 | 0.10905 | 0.099994 | 0.088644 | 0.092902 | 0.093162
| NORTH HOY | LW |  |  | 0.16084 | 0.16145 | 0.16028 | 0.1579 | 0.15204 | 0.14647 | 0.14209 | 0.13504 | 0.12305 | 0.11883 | 0.099252 | 0.081742 | 0.082842 | 0.080088 | 0.17669 | 0.17678 | 0.17617 | 0.17497 | 0.17208 | 0.16921 | 0.16636 | 0.16243 | 0.15668 | 0.15214 | 0.13762 | 0.12421 | 0.12434 | 0.12297 | 0.15522 | 0.15572 | 0.15466 | 0.15251 | 0.1472 | 0.14213 | 0.13819 | 0.13156 | 0.12061 | 0.11655 | 0.10126 | 0.08446 | 0.085376 | 0.082895
| NORTH HOY | ST |  |  | 0.16164 | 0.16159 | 0.16165 | 0.16068 | 0.16083 | 0.16039 | 0.1605 | 0.15924 | 0.15729 | 0.15403 | 0.14257 | 0.11448 | 0.098714 | 0.092684 | 0.17712 | 0.17702 | 0.17698 | 0.1764 | 0.1762 | 0.17553 | 0.17528 | 0.17524 | 0.17485 | 0.17318 | 0.16504 | 0.14407 | 0.13251 | 0.12828 | 0.15595 | 0.15589 | 0.15593 | 0.15503 | 0.1551 | 0.15458 | 0.15461 | 0.15497 | 0.15442 | 0.15203 | 0.14348 | 0.1166 | 0.10156 | 0.095832
| NORTH HOY | SP |  |  | 0.16215 | 0.16235 | 0.1628 | 0.16322 | 0.1626 | 0.16209 | 0.161 | 0.15947 | 0.15769 | 0.1544 | 0.14562 | 0.12139 | 0.10021 | 0.093107 | 0.1773 | 0.17732 | 0.17743 | 0.17752 | 0.17724 | 0.17698 | 0.17666 | 0.17619 | 0.17486 | 0.17268 | 0.16808 | 0.15379 | 0.13873 | 0.13414 | 0.15639 | 0.15656 | 0.15694 | 0.1573 | 0.15675 | 0.15629 | 0.15571 | 0.15482 | 0.15271 | 0.14919 | 0.14116 | 0.12157 | 0.10231 | 0.095662
PERSLEY | NORTHFIELD | MINIMUM HEADROOM | NJ 90728 08364 | NO | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 9.9731 | 9.9484 | 9.9228 | 9.8838 | 9.7763 | 9.6575 | 9.5061 | 9.2943 | 9.0719 | 8.7994 | 7.9051 | 6.2099 | 5.1062 | 4.1468 | 10.1382 | 10.0975 | 10.0512 | 10.0081 | 9.8293 | 9.6266 | 9.3356 | 8.9558 | 8.5497 | 8.0951 | 6.603 | 3.9028 | 2.3197 | 1.5151
| NORTHFIELD | CT |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 9.9796 | 9.9586 | 9.9357 | 9.8838 | 9.7763 | 9.6575 | 9.5061 | 9.2943 | 9.0719 | 8.7994 | 7.9065 | 6.2099 | 5.1062 | 4.1468 | 10.1626 | 10.1349 | 10.1041 | 10.0459 | 9.8538 | 9.6343 | 9.3356 | 8.9558 | 8.5556 | 8.0951 | 6.603 | 3.9028 | 2.3197 | 1.5151
| NORTHFIELD | LW |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 9.9731 | 9.9484 | 9.9228 | 9.8958 | 9.8123 | 9.7172 | 9.6115 | 9.3859 | 9.1023 | 8.8362 | 7.9051 | 6.5636 | 5.8817 | 5.4258 | 10.1382 | 10.0975 | 10.0512 | 10.0081 | 9.8293 | 9.6266 | 9.4031 | 9.0417 | 8.5497 | 8.1339 | 6.6924 | 4.5375 | 3.2781 | 2.6034
| NORTHFIELD | ST |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 9.9909 | 9.9723 | 9.9516 | 9.9181 | 9.8845 | 9.8461 | 9.8053 | 9.7561 | 9.7032 | 9.6086 | 9.2084 | 7.9429 | 6.7965 | 5.8471 | 10.1906 | 10.1697 | 10.147 | 10.1116 | 10.079 | 10.0417 | 10.0025 | 9.9546 | 9.9039 | 9.7895 | 9.3129 | 7.7489 | 6.3592 | 5.4795
| NORTHFIELD | SP |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 9.9943 | 9.9786 | 9.9603 | 9.9391 | 9.9063 | 9.8708 | 9.8297 | 9.7841 | 9.7081 | 9.6137 | 9.25 | 8.1922 | 6.6468 | 5.0552 | 10.1985 | 10.1828 | 10.1645 | 10.1437 | 10.1067 | 10.0683 | 10.0238 | 9.9757 | 9.8982 | 9.8044 | 9.4228 | 8.3137 | 7.0494 | 6.4262
BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | 2.3818 | 2.3815 | 2.354 | 2.2595 | 2.0915 | 1.9591 | 1.8195 | 1.6608 | 1.4714 | 1.3646 | 0.93253 | 0.84031 | 0.85567 | 0.78318 | 2.6714 | 2.6727 | 2.6617 | 2.5816 | 2.4579 | 2.3806 | 2.302 | 2.2301 | 2.1482 | 2.1034 | 1.9429 | 1.8804 | 1.8795 | 1.8223 | 2.5201 | 2.5189 | 2.4934 | 2.4047 | 2.2486 | 2.1268 | 1.9994 | 1.8487 | 1.6678 | 1.5629 | 1.1392 | 1.0447 | 1.0588 | 0.97856
| NOSTIE BRIDGE | CT |  |  | 2.4268 | 2.4319 | 2.4109 | 2.3081 | 2.1351 | 2.0115 | 1.8548 | 1.7053 | 1.5582 | 1.4658 | 1.0798 | 0.89698 | 0.91388 | 0.91148 | 2.6939 | 2.698 | 2.6919 | 2.6127 | 2.4906 | 2.419 | 2.3323 | 2.2516 | 2.1793 | 2.1394 | 2.0058 | 1.909 | 1.9117 | 1.8999 | 2.5593 | 2.5627 | 2.5424 | 2.445 | 2.2835 | 2.1692 | 2.0268 | 1.892 | 1.7561 | 1.6655 | 1.288 | 1.1038 | 1.1131 | 1.1076
| NOSTIE BRIDGE | LW |  |  | 2.3818 | 2.3815 | 2.354 | 2.2595 | 2.0915 | 1.9591 | 1.8195 | 1.6608 | 1.4714 | 1.3646 | 0.93253 | 0.84031 | 0.8922 | 0.8681 | 2.6714 | 2.6727 | 2.6617 | 2.5816 | 2.4579 | 2.3806 | 2.302 | 2.2301 | 2.1482 | 2.1034 | 1.9429 | 1.8804 | 1.9049 | 1.8948 | 2.5201 | 2.5189 | 2.4934 | 2.4047 | 2.2486 | 2.1268 | 1.9994 | 1.8487 | 1.6678 | 1.5629 | 1.1392 | 1.0447 | 1.0944 | 1.0726
| NOSTIE BRIDGE | ST |  |  | 2.4187 | 2.4112 | 2.4038 | 2.3351 | 2.2639 | 2.2268 | 2.177 | 2.1297 | 2.0729 | 2.0087 | 1.8016 | 1.3021 | 1.1977 | 1.1612 | 2.6884 | 2.6855 | 2.6828 | 2.6158 | 2.5365 | 2.5024 | 2.4641 | 2.4338 | 2.4033 | 2.3709 | 2.2707 | 2.0947 | 2.0315 | 2.0136 | 2.5534 | 2.5464 | 2.5393 | 2.4737 | 2.4043 | 2.3682 | 2.3214 | 2.2769 | 2.2254 | 2.1649 | 1.9681 | 1.4834 | 1.3839 | 1.3449
| NOSTIE BRIDGE | SP |  |  | 2.4248 | 2.4192 | 2.4144 | 2.3512 | 2.2559 | 2.1961 | 2.1252 | 2.0559 | 1.9722 | 1.8851 | 1.6542 | 1.2282 | 0.85567 | 0.78318 | 2.6904 | 2.688 | 2.6867 | 2.6203 | 2.5274 | 2.4819 | 2.4316 | 2.3875 | 2.3475 | 2.3026 | 2.183 | 2.0233 | 1.8795 | 1.8223 | 2.559 | 2.5538 | 2.5491 | 2.4891 | 2.399 | 2.3432 | 2.2785 | 2.2156 | 2.1398 | 2.06 | 1.8427 | 1.4245 | 1.0588 | 0.97856
TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | YES | 8.191 | 7.4222 | 6.9846 | 6.5684 | 5.3385 | 4.1893 | 3.0594 | 2.0657 | 1.4053 | 0.85369 | -1.0345 | -2.0181 | -1.7429 | -1.9378 | 12.3844 | 11.9664 | 11.7249 | 11.4878 | 10.8113 | 10.2134 | 9.7074 | 9.2174 | 8.8478 | 8.5295 | 7.1601 | 6.3125 | 6.1136 | 5.6497 | 9.8929 | 9.0662 | 8.5972 | 8.1691 | 6.7471 | 5.5477 | 4.5472 | 3.6545 | 3.0412 | 2.5115 | 0.68347 | -0.29797 | 0.032866 | -0.17893
| OBAN | CT |  |  | 8.2868 | 7.73 | 7.4488 | 7.2467 | 6.1068 | 5.1251 | 4.3949 | 3.7711 | 3.1722 | 2.5781 | 0.52503 | -1.4936 | -1.6752 | -1.8062 | 12.428 | 12.1164 | 11.9516 | 11.8234 | 11.1914 | 10.6349 | 10.2241 | 9.8713 | 9.5292 | 9.1907 | 7.8388 | 6.4427 | 6.1136 | 5.6928 | 10.0163 | 9.4688 | 9.2028 | 9.076 | 7.7909 | 6.7111 | 5.9384 | 5.3331 | 4.7035 | 4.1221 | 2.1867 | 0.20219 | 0.032866 | -0.081749
| OBAN | LW |  |  | 8.191 | 7.4222 | 6.9846 | 6.5684 | 5.3385 | 4.1893 | 3.0594 | 2.0657 | 1.4053 | 0.85369 | -1.0345 | -2.0181 | -1.7429 | -1.9378 | 12.3844 | 11.9664 | 11.7249 | 11.4878 | 10.8113 | 10.2134 | 9.7074 | 9.2174 | 8.8478 | 8.5295 | 7.1601 | 6.3125 | 6.4282 | 6.3387 | 9.8929 | 9.0662 | 8.5972 | 8.1691 | 6.7471 | 5.5477 | 4.5472 | 3.6545 | 3.0412 | 2.5115 | 0.68347 | -0.29797 | 0.034115 | -0.17893
| OBAN | ST |  |  | 8.4818 | 8.2235 | 8.0427 | 7.823 | 7.6159 | 7.4052 | 7.1868 | 6.9254 | 6.8207 | 6.5494 | 5.5345 | 2.8172 | 1.9615 | 1.6478 | 12.5467 | 12.4001 | 12.2962 | 12.1748 | 12.0542 | 11.9317 | 11.8012 | 11.6466 | 11.5728 | 11.4091 | 10.7795 | 8.7875 | 7.8929 | 7.363 | 10.1275 | 10.002 | 9.8572 | 9.6508 | 9.4562 | 9.2688 | 9.0817 | 8.8398 | 8.7773 | 8.5168 | 7.5478 | 4.9283 | 3.9775 | 3.607
| OBAN | SP |  |  | 8.6228 | 8.4588 | 8.3652 | 8.2743 | 8.0776 | 7.835 | 7.6167 | 7.3974 | 7.168 | 6.81 | 5.6432 | 2.7644 | 0.47516 | -0.18176 | 12.6218 | 12.5252 | 12.4671 | 12.4124 | 12.2972 | 12.1585 | 12.0279 | 11.8976 | 11.7615 | 11.5476 | 10.8437 | 8.9071 | 6.9478 | 5.6497 | 10.192 | 10.1076 | 10.0712 | 10.0448 | 9.9901 | 9.7684 | 9.5666 | 9.3679 | 9.1547 | 8.7748 | 7.5415 | 4.6024 | 2.3642 | 1.629
MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | 6.824 | 6.595 | 6.4538 | 6.3547 | 5.9801 | 5.6079 | 5.2338 | 4.78 | 4.3005 | 3.8861 | 2.4642 | 0.04776 | -1.4169 | -2.1962 | 8.2468 | 8.2114 | 8.1838 | 8.1426 | 8.1003 | 8.0555 | 8.0098 | 7.9572 | 7.788 | 7.5479 | 6.7049 | 5.4705 | 4.6566 | 3.9766 | 7.4775 | 7.2913 | 7.1713 | 7.0787 | 6.7595 | 6.4381 | 6.1105 | 5.6936 | 5.2524 | 4.8559 | 3.4876 | 1.4585 | 0.30057 | -0.28325
| OLD CRAIGIE ROAD | CT |  |  | 6.8569 | 6.6777 | 6.5862 | 6.4962 | 6.1343 | 5.7662 | 5.3973 | 5.0153 | 4.6083 | 4.135 | 2.5348 | 0.04776 | -1.4169 | -2.1962 | 8.2468 | 8.2114 | 8.1838 | 8.1426 | 8.1003 | 8.0555 | 8.0098 | 7.9572 | 7.8876 | 7.6393 | 6.7675 | 5.4705 | 4.6566 | 3.9766 | 7.5031 | 7.3578 | 7.2768 | 7.1805 | 6.863 | 6.5403 | 6.2169 | 5.8781 | 5.5168 | 5.0878 | 3.6205 | 1.4585 | 0.30057 | -0.28325
| OLD CRAIGIE ROAD | LW |  |  | 6.824 | 6.595 | 6.4538 | 6.3547 | 5.9801 | 5.6079 | 5.2338 | 4.78 | 4.3005 | 3.8861 | 2.4642 | 0.67549 | -0.51727 | -1.1987 | 8.25 | 8.2152 | 8.1909 | 8.1693 | 8.1413 | 8.1041 | 8.0591 | 7.9744 | 7.788 | 7.5479 | 6.7049 | 5.7875 | 5.2667 | 4.9298 | 7.4775 | 7.2913 | 7.1713 | 7.0787 | 6.7595 | 6.4381 | 6.1105 | 5.6936 | 5.2524 | 4.8559 | 3.4876 | 1.9191 | 0.99612 | 0.49418
| OLD CRAIGIE ROAD | ST |  |  | 6.9446 | 6.8501 | 6.784 | 6.7217 | 6.6626 | 6.5992 | 6.5309 | 6.4436 | 6.3942 | 6.2842 | 5.8437 | 4.292 | 3.1106 | 2.2034 | 8.2563 | 8.2264 | 8.2075 | 8.1922 | 8.1748 | 8.1537 | 8.1297 | 8.1041 | 8.0738 | 8.028 | 7.8394 | 7.1467 | 6.3487 | 5.6342 | 7.5811 | 7.5083 | 7.4537 | 7.3943 | 7.3376 | 7.2769 | 7.2106 | 7.1276 | 7.0719 | 6.9584 | 6.5104 | 4.9954 | 4.0083 | 3.3207
| OLD CRAIGIE ROAD | SP |  |  | 6.9774 | 6.9033 | 6.8543 | 6.8298 | 6.7744 | 6.7059 | 6.6411 | 6.5711 | 6.4791 | 6.3576 | 5.9187 | 4.758 | 3.5736 | 2.9985 | 8.2572 | 8.2285 | 8.2102 | 8.2013 | 8.191 | 8.1749 | 8.1576 | 8.1366 | 8.1023 | 8.0657 | 7.9191 | 7.4175 | 6.2114 | 5.0982 | 7.6082 | 7.5526 | 7.5123 | 7.4879 | 7.438 | 7.3764 | 7.3173 | 7.2515 | 7.1592 | 7.0429 | 6.6261 | 5.527 | 4.4106 | 3.9696
KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | YES | 1.6124 | 1.3398 | 1.0969 | 0.80186 | 0.38285 | -0.2064 | -0.848 | -1.5245 | -2.3084 | -3.0109 | -4.4784 | -5.5226 | -5.976 | -6.1625 | 2.9084 | 2.6854 | 2.5036 | 2.2769 | 2.0471 | 1.6296 | 1.1765 | 0.69349 | 0.15421 | -0.38676 | -1.6376 | -2.641 | -2.7146 | -2.7721 | 1.0198 | 0.78292 | 0.57075 | 0.30339 | -0.082738 | -0.63111 | -1.2229 | -1.8491 | -2.5778 | -3.234 | -4.604 | -5.5809 | -5.9956 | -6.1656
| OLDMELDRUM | CT |  |  | 1.6473 | 1.3998 | 1.1666 | 0.89115 | 0.49772 | -0.02687 | -0.62148 | -1.2598 | -1.9123 | -2.6199 | -4.3022 | -5.5226 | -5.976 | -6.1625 | 2.9084 | 2.6854 | 2.5036 | 2.2769 | 2.0631 | 1.6822 | 1.2742 | 0.81719 | 0.3231 | -0.26582 | -1.4664 | -2.4157 | -2.5898 | -2.6639 | 1.0517 | 0.83754 | 0.6349 | 0.38562 | 0.02213 | -0.46957 | -1.0245 | -1.623 | -2.2362 | -2.8964 | -4.4434 | -5.5809 | -5.9956 | -6.1656
| OLDMELDRUM | LW |  |  | 1.6124 | 1.3398 | 1.0969 | 0.80186 | 0.38285 | -0.2064 | -0.848 | -1.5245 | -2.3084 | -3.0109 | -4.4784 | -5.4116 | -5.6331 | -5.7567 | 2.9229 | 2.7031 | 2.5287 | 2.3068 | 2.0471 | 1.6296 | 1.1765 | 0.69349 | 0.15421 | -0.38676 | -1.6376 | -2.641 | -2.7146 | -2.7571 | 1.0198 | 0.78292 | 0.57075 | 0.30339 | -0.082738 | -0.63111 | -1.2229 | -1.8491 | -2.5778 | -3.234 | -4.604 | -5.5578 | -5.6987 | -5.7996
| OLDMELDRUM | ST |  |  | 1.702 | 1.4801 | 1.3078 | 1.1153 | 0.96032 | 0.68405 | 0.40256 | 0.080395 | -0.29012 | -0.76362 | -1.8593 | -3.8608 | -4.3544 | -4.6237 | 2.9503 | 2.7487 | 2.5985 | 2.4129 | 2.2585 | 1.9603 | 1.652 | 1.3005 | 0.91496 | 0.44446 | -0.67227 | -2.2975 | -2.6243 | -2.7721 | 1.101 | 0.90982 | 0.76172 | 0.58694 | 0.44178 | 0.17818 | -0.090552 | -0.39856 | -0.75286 | -1.3066 | -2.6127 | -4.6474 | -5.1353 | -5.3916
| OLDMELDRUM | SP |  |  | 1.7116 | 1.5006 | 1.3402 | 1.1586 | 0.98079 | 0.685 | 0.37913 | 0.02815 | -0.34484 | -0.79105 | -1.8062 | -3.4708 | -4.2518 | -4.5595 | 2.9512 | 2.7521 | 2.6049 | 2.4234 | 2.2716 | 1.9806 | 1.6765 | 1.3331 | 0.95542 | 0.50921 | -0.34116 | -1.6461 | -2.1388 | -2.3009 | 1.1105 | 0.92917 | 0.79197 | 0.62709 | 0.46124 | 0.18066 | -0.10979 | -0.4426 | -0.79843 | -1.226 | -2.2371 | -3.9279 | -4.6586 | -4.9193
THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | 2.9517 | 2.8532 | 2.7535 | 2.6149 | 2.4404 | 1.966 | 1.4906 | 0.94462 | 0.23499 | -0.2726 | -1.8728 | -3.5598 | -4.1805 | -4.4189 | 4.9189 | 4.8499 | 4.7742 | 4.6369 | 4.4134 | 4.1541 | 3.9266 | 3.6444 | 3.2724 | 2.9486 | 1.8926 | 0.88219 | 0.50169 | 0.1891 | 3.637 | 3.561 | 3.4614 | 3.3309 | 2.942 | 2.5087 | 2.0836 | 1.5901 | 0.95139 | 0.48785 | -1.004 | -2.5293 | -3.0676 | -3.2711
| ORMLIE | CT |  |  | 2.9517 | 2.8532 | 2.7535 | 2.6149 | 2.4404 | 2.1064 | 1.5763 | 1.0219 | 0.47346 | -0.012077 | -1.5793 | -3.5598 | -4.1805 | -4.4189 | 4.9323 | 4.8667 | 4.7847 | 4.6369 | 4.4134 | 4.1541 | 3.9266 | 3.6444 | 3.3557 | 3.0644 | 2.0813 | 0.88219 | 0.50169 | 0.1891 | 3.6916 | 3.6289 | 3.5405 | 3.4261 | 3.0243 | 2.6197 | 2.1475 | 1.6536 | 1.1649 | 0.72675 | -0.70096 | -2.5293 | -3.0676 | -3.2711
| ORMLIE | LW |  |  | 2.9707 | 2.8765 | 2.7869 | 2.6665 | 2.448 | 1.966 | 1.4906 | 0.94462 | 0.23499 | -0.2726 | -1.8728 | -3.3593 | -3.6962 | -3.9222 | 4.9189 | 4.8499 | 4.7742 | 4.6454 | 4.4376 | 4.1935 | 3.956 | 3.6562 | 3.2724 | 2.9486 | 1.8926 | 0.96579 | 0.83473 | 0.74613 | 3.637 | 3.561 | 3.4614 | 3.3309 | 2.942 | 2.5087 | 2.0836 | 1.5901 | 0.95139 | 0.48785 | -1.004 | -2.399 | -2.6839 | -2.8731
| ORMLIE | ST |  |  | 3.0156 | 2.9576 | 2.9082 | 2.8557 | 2.8032 | 2.7419 | 2.6632 | 2.5694 | 2.4557 | 2.3025 | 1.7421 | -0.028366 | -1.0308 | -1.4264 | 4.9635 | 4.914 | 4.8715 | 4.8257 | 4.7861 | 4.7372 | 4.6739 | 4.5992 | 4.4982 | 4.3322 | 3.7221 | 2.1417 | 1.3533 | 1.1697 | 3.7127 | 3.656 | 3.6076 | 3.5656 | 3.5381 | 3.4982 | 3.4421 | 3.3721 | 3.2694 | 3.0916 | 2.4318 | 0.59531 | -0.32291 | -0.68911
| ORMLIE | SP |  |  | 3.0192 | 2.9676 | 2.9243 | 2.8828 | 2.842 | 2.7949 | 2.7351 | 2.6632 | 2.572 | 2.4049 | 1.6791 | 0.039938 | -1.2467 | -1.6495 | 4.9754 | 4.9357 | 4.9028 | 4.8703 | 4.8173 | 4.7577 | 4.6875 | 4.6045 | 4.4954 | 4.3484 | 3.8748 | 2.7152 | 1.5023 | 0.72545 | 3.7425 | 3.7045 | 3.6761 | 3.6484 | 3.5707 | 3.4876 | 3.3912 | 3.2795 | 3.1428 | 2.9387 | 2.2972 | 0.77924 | -0.51396 | -0.8851
DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | 1.7367 | 1.7361 | 1.7273 | 1.714 | 1.682 | 1.6435 | 1.6117 | 1.5702 | 1.5148 | 1.4802 | 1.3389 | 1.3159 | 1.3201 | 1.2923 | 1.9087 | 1.9076 | 1.9032 | 1.8962 | 1.8814 | 1.863 | 1.8454 | 1.8267 | 1.7992 | 1.7789 | 1.691 | 1.679 | 1.6792 | 1.6669 | 1.6033 | 1.6024 | 1.5944 | 1.5821 | 1.5534 | 1.5182 | 1.4896 | 1.4513 | 1.4006 | 1.3677 | 1.2317 | 1.2103 | 1.2144 | 1.1926
| OTTER FERRY | CT |  |  | 1.7509 | 1.7526 | 1.7467 | 1.7308 | 1.6912 | 1.658 | 1.6145 | 1.5729 | 1.5318 | 1.5061 | 1.3935 | 1.3258 | 1.3266 | 1.3218 | 1.9137 | 1.912 | 1.9092 | 1.901 | 1.8814 | 1.8656 | 1.8454 | 1.8269 | 1.8078 | 1.793 | 1.7226 | 1.6827 | 1.6821 | 1.6791 | 1.6155 | 1.6166 | 1.611 | 1.596 | 1.5598 | 1.5297 | 1.4905 | 1.4533 | 1.4162 | 1.3919 | 1.2833 | 1.2192 | 1.2199 | 1.2163
| OTTER FERRY | LW |  |  | 1.7367 | 1.7361 | 1.7273 | 1.714 | 1.682 | 1.6435 | 1.6117 | 1.5702 | 1.5148 | 1.4802 | 1.3389 | 1.3159 | 1.3323 | 1.3243 | 1.9087 | 1.9076 | 1.9032 | 1.8962 | 1.882 | 1.863 | 1.8484 | 1.8267 | 1.7992 | 1.7789 | 1.691 | 1.679 | 1.6855 | 1.6822 | 1.6033 | 1.6024 | 1.5944 | 1.5821 | 1.5534 | 1.5182 | 1.4896 | 1.4513 | 1.4006 | 1.3677 | 1.2317 | 1.2103 | 1.2247 | 1.2176
| OTTER FERRY | ST |  |  | 1.7488 | 1.7466 | 1.7442 | 1.7411 | 1.7376 | 1.733 | 1.7289 | 1.7228 | 1.7118 | 1.6959 | 1.6418 | 1.4722 | 1.4351 | 1.4156 | 1.9139 | 1.9127 | 1.9113 | 1.9091 | 1.9067 | 1.9037 | 1.9012 | 1.897 | 1.8906 | 1.8817 | 1.8507 | 1.7417 | 1.725 | 1.7158 | 1.6141 | 1.612 | 1.6098 | 1.6066 | 1.6032 | 1.5988 | 1.5948 | 1.5888 | 1.5784 | 1.5634 | 1.5124 | 1.3482 | 1.315 | 1.2978
| OTTER FERRY | SP |  |  | 1.7475 | 1.7458 | 1.7441 | 1.7421 | 1.7302 | 1.7189 | 1.7063 | 1.6921 | 1.6752 | 1.6508 | 1.5841 | 1.4521 | 1.3201 | 1.2923 | 1.9128 | 1.912 | 1.9109 | 1.9097 | 1.9043 | 1.8992 | 1.8934 | 1.8866 | 1.878 | 1.8659 | 1.8315 | 1.7619 | 1.6792 | 1.6669 | 1.6127 | 1.6112 | 1.6096 | 1.6076 | 1.597 | 1.5869 | 1.5755 | 1.5626 | 1.5471 | 1.5249 | 1.4635 | 1.3414 | 1.2144 | 1.1926
GLENAGNES | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | 25.2232 | 25.1188 | 24.8948 | 24.6908 | 24.3204 | 24.0148 | 23.8136 | 23.5981 | 23.4068 | 23.1915 | 22.5175 | 21.7109 | 21.3114 | 20.9024 | 28.2417 | 28.1801 | 27.9856 | 27.8488 | 27.5762 | 27.3746 | 27.2395 | 27.0925 | 26.9413 | 26.7772 | 26.2473 | 25.6695 | 25.143 | 24.1001 | 26.2375 | 26.1481 | 25.9509 | 25.7849 | 25.4661 | 25.2036 | 25.0191 | 24.8216 | 24.6482 | 24.4678 | 23.9039 | 23.2421 | 22.9181 | 22.6198
| OVERGATE | CT |  |  | 25.2232 | 25.1201 | 24.8948 | 24.6954 | 24.3287 | 24.036 | 23.8597 | 23.6857 | 23.4985 | 23.2864 | 22.6737 | 21.8362 | 21.3748 | 20.9247 | 28.2417 | 28.1801 | 27.9856 | 27.8488 | 27.5762 | 27.3746 | 27.2395 | 27.0925 | 26.9413 | 26.7772 | 26.3143 | 25.7332 | 25.298 | 24.7443 | 26.2375 | 26.1517 | 25.9509 | 25.7898 | 25.4707 | 25.2196 | 25.0568 | 24.8966 | 24.728 | 24.5481 | 24.0285 | 23.3324 | 22.9567 | 22.6521
| OVERGATE | LW |  |  | 25.2365 | 25.1188 | 24.8983 | 24.6908 | 24.3204 | 24.0148 | 23.8136 | 23.5981 | 23.4068 | 23.1915 | 22.5175 | 21.7109 | 21.3114 | 20.9024 | 28.259 | 28.1889 | 28.016 | 27.8764 | 27.607 | 27.4062 | 27.2719 | 27.1176 | 26.9602 | 26.7848 | 26.2473 | 25.6695 | 25.4735 | 25.2793 | 26.2441 | 26.1481 | 25.9557 | 25.7849 | 25.4661 | 25.2036 | 25.0191 | 24.8216 | 24.6482 | 24.4678 | 23.9039 | 23.2421 | 22.9181 | 22.6198
| OVERGATE | ST |  |  | 25.2903 | 25.2135 | 25.035 | 24.8849 | 24.6448 | 24.4904 | 24.4 | 24.3029 | 24.2043 | 24.067 | 23.5523 | 22.3616 | 21.4991 | 21.0465 | 28.2883 | 28.2327 | 28.0811 | 27.9704 | 27.7606 | 27.6357 | 27.5523 | 27.4648 | 27.3748 | 27.2445 | 26.7855 | 25.8243 | 25.143 | 24.6591 | 26.2893 | 26.2294 | 26.0724 | 25.951 | 25.7515 | 25.6239 | 25.5468 | 25.4641 | 25.3777 | 25.2538 | 24.8172 | 23.8828 | 23.1074 | 22.7268
| OVERGATE | SP |  |  | 25.2976 | 25.227 | 25.0542 | 24.9158 | 24.6764 | 24.5256 | 24.4453 | 24.3593 | 24.2758 | 24.1567 | 23.7792 | 22.8759 | 21.8523 | 21.2988 | 28.2908 | 28.2381 | 28.0889 | 27.9832 | 27.7736 | 27.6504 | 27.5729 | 27.4902 | 27.4117 | 27.3041 | 26.9632 | 26.1824 | 25.1684 | 24.1001 | 26.2955 | 26.2408 | 26.0887 | 25.977 | 25.779 | 25.655 | 25.587 | 25.5139 | 25.4429 | 25.3395 | 25.0102 | 24.2726 | 23.4738 | 22.9459
CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | 0.15418 | 0.15387 | 0.15328 | 0.15235 | 0.1502 | 0.14791 | 0.14561 | 0.14302 | 0.13954 | 0.13677 | 0.1265 | 0.11759 | 0.11815 | 0.11806 | 0.14696 | 0.14686 | 0.1468 | 0.14628 | 0.14536 | 0.14431 | 0.14312 | 0.14179 | 0.13975 | 0.13749 | 0.13007 | 0.12341 | 0.12361 | 0.12358 | 0.1456 | 0.14542 | 0.14489 | 0.14403 | 0.1421 | 0.14004 | 0.13796 | 0.1356 | 0.13243 | 0.13025 | 0.12064 | 0.11214 | 0.11263 | 0.11255
| OVERSCAIG | CT |  |  | 0.15478 | 0.15458 | 0.1544 | 0.15345 | 0.15156 | 0.14967 | 0.14686 | 0.14438 | 0.14156 | 0.13975 | 0.13251 | 0.12448 | 0.12372 | 0.12324 | 0.1473 | 0.14705 | 0.14693 | 0.14628 | 0.14536 | 0.14446 | 0.14312 | 0.14209 | 0.14071 | 0.13903 | 0.13393 | 0.1283 | 0.12801 | 0.12784 | 0.14616 | 0.14594 | 0.14577 | 0.14491 | 0.14315 | 0.14145 | 0.13891 | 0.13671 | 0.13415 | 0.13259 | 0.1262 | 0.11865 | 0.11798 | 0.11756
| OVERSCAIG | LW |  |  | 0.15441 | 0.15387 | 0.15328 | 0.15235 | 0.1502 | 0.14791 | 0.14561 | 0.14302 | 0.13954 | 0.13677 | 0.1265 | 0.11759 | 0.11815 | 0.11806 | 0.14749 | 0.14714 | 0.14687 | 0.14637 | 0.14539 | 0.14431 | 0.14323 | 0.14179 | 0.13975 | 0.13749 | 0.13007 | 0.12341 | 0.12361 | 0.12358 | 0.14593 | 0.14542 | 0.14489 | 0.14403 | 0.1421 | 0.14004 | 0.13796 | 0.1356 | 0.13243 | 0.13025 | 0.12064 | 0.11214 | 0.11263 | 0.11255
| OVERSCAIG | ST |  |  | 0.15524 | 0.15502 | 0.15481 | 0.15445 | 0.15397 | 0.15363 | 0.15305 | 0.1524 | 0.15181 | 0.15024 | 0.14425 | 0.12924 | 0.12294 | 0.12185 | 0.14784 | 0.14773 | 0.14762 | 0.14737 | 0.14707 | 0.14691 | 0.14654 | 0.14614 | 0.14584 | 0.14498 | 0.14115 | 0.13024 | 0.12609 | 0.12569 | 0.14666 | 0.14647 | 0.14628 | 0.14593 | 0.14548 | 0.14517 | 0.14462 | 0.14402 | 0.14348 | 0.14216 | 0.13713 | 0.12286 | 0.11697 | 0.11602
| OVERSCAIG | SP |  |  | 0.15418 | 0.15399 | 0.15386 | 0.1537 | 0.15277 | 0.15209 | 0.15139 | 0.15038 | 0.14935 | 0.14801 | 0.14358 | 0.13371 | 0.12313 | 0.12081 | 0.14696 | 0.14686 | 0.1468 | 0.14671 | 0.14623 | 0.14593 | 0.14564 | 0.14511 | 0.14458 | 0.1439 | 0.14166 | 0.13513 | 0.12774 | 0.1265 | 0.1456 | 0.14543 | 0.14531 | 0.14516 | 0.14432 | 0.14371 | 0.14308 | 0.14216 | 0.14122 | 0.14 | 0.13596 | 0.12738 | 0.11744 | 0.11533
KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | NO | 4.1349 | 4.1208 | 4.1044 | 4.0837 | 4.0566 | 4.0181 | 3.9859 | 3.9439 | 3.8701 | 3.7947 | 3.6018 | 3.3165 | 3.1381 | 3.0611 | 4.9944 | 4.9754 | 4.9485 | 4.9141 | 4.8524 | 4.7519 | 4.6778 | 4.5767 | 4.4615 | 4.3744 | 4.2326 | 4.0709 | 3.9703 | 3.8856 | 4.6031 | 4.5793 | 4.5445 | 4.5009 | 4.3996 | 4.2528 | 4.1339 | 3.9838 | 3.7973 | 3.6684 | 3.4105 | 3.1418 | 2.9741 | 2.9023
| PARK | CT |  |  | 4.1349 | 4.1208 | 4.1044 | 4.0837 | 4.0566 | 4.0254 | 3.9988 | 3.9709 | 3.9406 | 3.8648 | 3.6519 | 3.3165 | 3.1381 | 3.0611 | 5.0029 | 4.9815 | 4.9556 | 4.9311 | 4.8791 | 4.8245 | 4.7595 | 4.69 | 4.6205 | 4.5092 | 4.252 | 4.0709 | 3.9703 | 3.8856 | 4.629 | 4.6098 | 4.5838 | 4.5622 | 4.4749 | 4.383 | 4.2653 | 4.1357 | 4.0052 | 3.8519 | 3.4748 | 3.1418 | 2.9741 | 2.9023
| PARK | LW |  |  | 4.1383 | 4.1268 | 4.1123 | 4.0916 | 4.0623 | 4.0181 | 3.9859 | 3.9439 | 3.8701 | 3.7947 | 3.6018 | 3.3502 | 3.2761 | 3.2357 | 4.9944 | 4.9754 | 4.9485 | 4.9141 | 4.8524 | 4.7519 | 4.6778 | 4.5767 | 4.4615 | 4.3744 | 4.2326 | 4.1053 | 4.0758 | 4.0587 | 4.6031 | 4.5793 | 4.5445 | 4.5009 | 4.3996 | 4.2528 | 4.1339 | 3.9838 | 3.7973 | 3.6684 | 3.4105 | 3.1721 | 3.1029 | 3.0656
| PARK | ST |  |  | 4.1471 | 4.1419 | 4.1357 | 4.1293 | 4.1214 | 4.1124 | 4.1032 | 4.0921 | 4.0797 | 4.0596 | 3.9686 | 3.685 | 3.5274 | 3.4691 | 5.0135 | 5.0026 | 4.9906 | 4.9827 | 4.9685 | 4.9525 | 4.9388 | 4.9224 | 4.9022 | 4.8673 | 4.6927 | 4.3566 | 4.2185 | 4.1076 | 4.6354 | 4.6226 | 4.6087 | 4.6024 | 4.5874 | 4.57 | 4.555 | 4.5368 | 4.5092 | 4.4613 | 4.2407 | 3.8061 | 3.5962 | 3.4745
| PARK | SP |  |  | 4.1496 | 4.1457 | 4.1408 | 4.135 | 4.1291 | 4.1204 | 4.1112 | 4.1004 | 4.0918 | 4.0795 | 4.0374 | 3.8233 | 3.6351 | 3.5497 | 5.0205 | 5.0124 | 5.0025 | 4.9905 | 4.9743 | 4.9498 | 4.9245 | 4.895 | 4.8746 | 4.8464 | 4.7416 | 4.3365 | 4.1411 | 3.9844 | 4.6447 | 4.6355 | 4.625 | 4.6125 | 4.5876 | 4.5545 | 4.5196 | 4.4798 | 4.4505 | 4.4075 | 4.2435 | 3.7121 | 3.474 | 3.3668
ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | YES | 1.1336 | 1.1395 | 1.1288 | 1.1125 | 1.037 | 0.9572 | 0.87132 | 0.77422 | 0.65589 | 0.56322 | 0.34687 | 0.26007 | 0.24019 | 0.17118 | 1.6308 | 1.6309 | 1.6229 | 1.6109 | 1.5717 | 1.5295 | 1.4821 | 1.4266 | 1.3618 | 1.3014 | 1.162 | 1.0961 | 1.0418 | 0.94814 | 1.4131 | 1.4157 | 1.4032 | 1.3847 | 1.3134 | 1.2376 | 1.1545 | 1.0595 | 0.94617 | 0.85069 | 0.62895 | 0.53222 | 0.52239 | 0.45699
| PEDDIESTON | CT |  |  | 1.1672 | 1.1785 | 1.176 | 1.1697 | 1.0947 | 1.0246 | 0.93511 | 0.84195 | 0.75372 | 0.69864 | 0.48146 | 0.32323 | 0.30748 | 0.28984 | 1.645 | 1.6425 | 1.6379 | 1.6319 | 1.5918 | 1.5537 | 1.5065 | 1.4564 | 1.4081 | 1.3727 | 1.2269 | 1.1161 | 1.0896 | 1.0522 | 1.4434 | 1.4512 | 1.446 | 1.4355 | 1.3632 | 1.2958 | 1.2112 | 1.1225 | 1.038 | 0.98218 | 0.75748 | 0.59378 | 0.57567 | 0.55857
| PEDDIESTON | LW |  |  | 1.1336 | 1.1395 | 1.1288 | 1.1125 | 1.037 | 0.9572 | 0.87132 | 0.77422 | 0.65589 | 0.56322 | 0.34687 | 0.26007 | 0.31232 | 0.30013 | 1.6308 | 1.6309 | 1.6229 | 1.6109 | 1.5717 | 1.5295 | 1.4821 | 1.4266 | 1.3618 | 1.3014 | 1.162 | 1.0961 | 1.1192 | 1.1133 | 1.4131 | 1.4157 | 1.4032 | 1.3847 | 1.3134 | 1.2376 | 1.1545 | 1.0595 | 0.94617 | 0.85069 | 0.62895 | 0.53222 | 0.57812 | 0.56769
| PEDDIESTON | ST |  |  | 1.1537 | 1.1485 | 1.1411 | 1.1388 | 1.137 | 1.1307 | 1.1255 | 1.1201 | 1.1009 | 1.0685 | 0.94931 | 0.67217 | 0.56893 | 0.52782 | 1.6415 | 1.6378 | 1.6322 | 1.628 | 1.6241 | 1.6176 | 1.6117 | 1.6053 | 1.5914 | 1.5698 | 1.4888 | 1.2872 | 1.2072 | 1.1586 | 1.4335 | 1.4279 | 1.4203 | 1.4162 | 1.4124 | 1.4043 | 1.3971 | 1.3896 | 1.3692 | 1.3358 | 1.2122 | 0.91534 | 0.80814 | 0.76875
| PEDDIESTON | SP |  |  | 1.1556 | 1.1519 | 1.1477 | 1.1425 | 1.1152 | 1.09 | 1.0623 | 1.0282 | 0.99652 | 0.94361 | 0.79716 | 0.45267 | 0.24019 | 0.17118 | 1.6416 | 1.6387 | 1.6348 | 1.63 | 1.6149 | 1.6006 | 1.5849 | 1.5649 | 1.5458 | 1.5153 | 1.4287 | 1.2081 | 1.0418 | 0.94814 | 1.4344 | 1.4303 | 1.4256 | 1.4197 | 1.3936 | 1.3693 | 1.3425 | 1.3092 | 1.278 | 1.2271 | 1.0855 | 0.74119 | 0.52239 | 0.45699
PETERHEAD GRANGE | PETERHEAD GRANGE 11kV | MINIMUM HEADROOM | NK 11738 46516 | NO | 9.7917 | 9.468 | 9.0855 | 8.671 | 7.9123 | 6.9574 | 5.9849 | 4.7818 | 3.4172 | 2.1646 | -1.5014 | -6.3478 | -8.7798 | -9.6066 | 11.3714 | 11.0801 | 10.7752 | 10.4444 | 10.0951 | 9.5887 | 9.1271 | 8.5881 | 7.927 | 7.0738 | 4.584 | 2.197 | 1.0637 | 0.32037 | 9.3461 | 9.0542 | 8.715 | 8.3411 | 7.6637 | 6.8029 | 5.9258 | 4.8228 | 3.5759 | 2.4159 | -0.9139 | -5.2164 | -7.337 | -8.0569
| PETERHEAD GRANGE 11kV | CT |  |  | 9.8893 | 9.5924 | 9.2294 | 8.799 | 8.0357 | 7.0851 | 6.0635 | 4.9234 | 3.7473 | 2.4535 | -1.5014 | -6.3478 | -8.7798 | -9.6066 | 11.3714 | 11.0801 | 10.7752 | 10.4444 | 10.0951 | 9.5887 | 9.1271 | 8.6026 | 7.9947 | 7.3053 | 4.7465 | 2.197 | 1.0637 | 0.32037 | 9.4289 | 9.1602 | 8.8358 | 8.4409 | 7.7542 | 6.8951 | 5.9754 | 4.9427 | 3.878 | 2.6978 | -0.9139 | -5.2164 | -7.337 | -8.0569
| PETERHEAD GRANGE 11kV | LW |  |  | 9.7917 | 9.468 | 9.0855 | 8.671 | 7.9123 | 6.9574 | 5.9849 | 4.7818 | 3.4172 | 2.1646 | -1.3922 | -4.9661 | -6.7931 | -7.3678 | 11.3915 | 11.0975 | 10.8076 | 10.487 | 10.1495 | 9.6473 | 9.1887 | 8.5881 | 7.927 | 7.0738 | 4.584 | 2.7006 | 2.0755 | 1.874 | 9.3461 | 9.0542 | 8.715 | 8.3411 | 7.6637 | 6.8029 | 5.9258 | 4.8228 | 3.5759 | 2.4159 | -0.86414 | -4.0349 | -5.618 | -6.1169
| PETERHEAD GRANGE 11kV | ST |  |  | 9.977 | 9.6963 | 9.4035 | 9.104 | 8.8162 | 8.3906 | 7.9753 | 7.5301 | 7.0842 | 6.5056 | 4.8863 | 1.6237 | -0.18783 | -1.3273 | 11.4214 | 11.1582 | 10.8944 | 10.6271 | 10.3733 | 9.9776 | 9.5982 | 9.1866 | 8.776 | 8.3025 | 7.116 | 5.1583 | 3.9782 | 3.0948 | 9.5115 | 9.2605 | 9.0027 | 8.733 | 8.4755 | 8.0892 | 7.7112 | 7.3014 | 6.8902 | 6.3538 | 4.8547 | 1.8318 | 0.21085 | -0.791
| PETERHEAD GRANGE 11kV | SP |  |  | 9.9879 | 9.7142 | 9.4313 | 9.1524 | 8.8202 | 8.3561 | 7.9006 | 7.4063 | 6.8823 | 6.2841 | 4.8052 | 2.4278 | 0.96488 | 0.64227 | 11.4244 | 11.1654 | 10.9071 | 10.6505 | 10.4069 | 10.0225 | 9.6584 | 9.2633 | 8.8659 | 8.4241 | 7.4197 | 5.8286 | 3.8946 | 2.4676 | 9.5212 | 9.2771 | 9.0286 | 8.7799 | 8.486 | 8.0681 | 7.6579 | 7.2075 | 6.7267 | 6.1779 | 4.8286 | 2.6397 | 1.2419 | 0.94539
PETERHEAD GRANGE | PHEAD NORTH ST | MINIMUM HEADROOM | NK 13470 46450 | NO | 8.7813 | 8.7149 | 8.6403 | 8.5413 | 8.2542 | 7.9391 | 7.6536 | 7.3159 | 7.046 | 6.8177 | 6.0512 | 4.6746 | 3.6649 | 2.9902 | 13.3552 | 13.3244 | 13.2881 | 13.2283 | 13.1376 | 13.0283 | 12.9472 | 12.834 | 12.6823 | 12.5457 | 12.0862 | 11.3366 | 10.7857 | 10.2879 | 10.4248 | 10.3651 | 10.2974 | 10.2062 | 9.9407 | 9.6489 | 9.3846 | 9.0751 | 8.8282 | 8.62 | 7.9339 | 6.7412 | 5.9464 | 5.4697
| PHEAD NORTH ST | CT |  |  | 8.8043 | 8.7517 | 8.6851 | 8.5955 | 8.3047 | 7.9813 | 7.7558 | 7.5127 | 7.2472 | 6.9759 | 6.1141 | 4.6746 | 3.6649 | 2.9902 | 13.3552 | 13.3244 | 13.2881 | 13.2283 | 13.1376 | 13.0283 | 12.9472 | 12.8569 | 12.7129 | 12.5654 | 12.097 | 11.3366 | 10.7857 | 10.2879 | 10.4454 | 10.3982 | 10.3376 | 10.2555 | 9.9871 | 9.6882 | 9.4797 | 9.2563 | 9.0122 | 8.7641 | 7.9887 | 6.7412 | 5.9464 | 5.4697
| PHEAD NORTH ST | LW |  |  | 8.7813 | 8.7149 | 8.6403 | 8.5413 | 8.2542 | 7.9391 | 7.6536 | 7.3159 | 7.046 | 6.8177 | 6.0512 | 4.942 | 4.1166 | 3.5056 | 13.3647 | 13.3385 | 13.3093 | 13.2576 | 13.1727 | 13.0679 | 12.9898 | 12.834 | 12.6823 | 12.5457 | 12.0862 | 11.4803 | 11.094 | 10.7737 | 10.4248 | 10.3651 | 10.2974 | 10.2062 | 9.9407 | 9.6489 | 9.3846 | 9.0751 | 8.8282 | 8.62 | 7.9339 | 6.9877 | 6.3607 | 5.9426
| PHEAD NORTH ST | ST |  |  | 8.8608 | 8.8382 | 8.8148 | 8.7869 | 8.757 | 8.7239 | 8.6884 | 8.644 | 8.6009 | 8.5202 | 8.1975 | 7.1736 | 6.1329 | 5.269 | 13.3835 | 13.3711 | 13.3571 | 13.3404 | 13.3233 | 13.3032 | 13.28 | 13.2521 | 13.2153 | 13.1635 | 12.9489 | 12.3545 | 11.6843 | 11.0763 | 10.4987 | 10.48 | 10.4602 | 10.436 | 10.4101 | 10.3811 | 10.3496 | 10.31 | 10.2711 | 10.1983 | 9.9163 | 9.041 | 8.2115 | 7.5576
| PHEAD NORTH ST | SP |  |  | 8.8679 | 8.8516 | 8.8342 | 8.8167 | 8.7778 | 8.738 | 8.6983 | 8.6556 | 8.6032 | 8.527 | 8.2662 | 7.5143 | 6.6643 | 6.0308 | 13.3852 | 13.3758 | 13.3653 | 13.3535 | 13.3416 | 13.3283 | 13.3135 | 13.2965 | 13.2754 | 13.2377 | 13.1111 | 12.5475 | 11.7774 | 10.9916 | 10.5055 | 10.4927 | 10.4786 | 10.464 | 10.4297 | 10.3945 | 10.3593 | 10.3214 | 10.2752 | 10.2066 | 9.9848 | 9.3631 | 8.7102 | 8.2383
FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | YES | 4.9594 | 4.8726 | 4.7858 | 4.7004 | 4.089 | 3.5902 | 3.1762 | 2.761 | 2.3828 | 2.1546 | 1.4281 | 1.0661 | 1.3942 | 1.2365 | 7.1126 | 6.9912 | 6.8734 | 6.7814 | 6.5431 | 6.3435 | 6.1661 | 5.956 | 5.7515 | 5.5914 | 5.053 | 4.7082 | 4.5806 | 4.0831 | 5.9858 | 5.8263 | 5.6124 | 5.443 | 4.9328 | 4.5068 | 4.1549 | 3.7987 | 3.4694 | 3.2599 | 2.5683 | 2.254 | 2.5446 | 2.418
| PINEGROVE | CT |  |  | 4.9594 | 4.8726 | 4.7871 | 4.734 | 4.5077 | 4.0418 | 3.6431 | 3.2985 | 2.9648 | 2.7328 | 2.0435 | 1.2997 | 1.4686 | 1.4982 | 7.1528 | 7.0574 | 6.9671 | 6.9026 | 6.6619 | 6.4674 | 6.2907 | 6.1196 | 5.9469 | 5.7945 | 5.3106 | 4.7535 | 4.7148 | 4.5742 | 5.9858 | 5.9107 | 5.8369 | 5.7738 | 5.2773 | 4.8819 | 4.5457 | 4.2502 | 3.9659 | 3.7603 | 3.129 | 2.4711 | 2.6197 | 2.6468
| PINEGROVE | LW |  |  | 4.9651 | 4.8756 | 4.7858 | 4.7004 | 4.089 | 3.5902 | 3.1762 | 2.761 | 2.3828 | 2.1546 | 1.4281 | 1.0661 | 1.3942 | 1.3221 | 7.1126 | 6.9912 | 6.8734 | 6.7814 | 6.5431 | 6.3435 | 6.1661 | 5.956 | 5.7515 | 5.5914 | 5.053 | 4.7082 | 4.8253 | 4.7976 | 5.9911 | 5.8263 | 5.6124 | 5.443 | 4.9328 | 4.5068 | 4.1549 | 3.7987 | 3.4694 | 3.2599 | 2.5683 | 2.254 | 2.5446 | 2.4825
| PINEGROVE | ST |  |  | 4.9704 | 4.9108 | 4.8425 | 4.794 | 4.7594 | 4.7327 | 4.6835 | 4.6216 | 4.56 | 4.4711 | 3.9796 | 2.9694 | 2.7567 | 2.7011 | 7.1614 | 7.1011 | 7.0336 | 6.9747 | 6.9182 | 6.8672 | 6.7997 | 6.7136 | 6.6376 | 6.5246 | 6.1547 | 5.438 | 5.1823 | 5.0163 | 5.9963 | 5.9455 | 5.8872 | 5.8452 | 5.8154 | 5.7676 | 5.6792 | 5.5583 | 5.4764 | 5.3286 | 4.8461 | 3.9538 | 3.7477 | 3.7013
| PINEGROVE | SP |  |  | 4.9947 | 4.9492 | 4.894 | 4.8607 | 4.8129 | 4.7702 | 4.7095 | 4.6432 | 4.5596 | 4.3247 | 3.5611 | 2.2036 | 1.4897 | 1.2365 | 7.1842 | 7.1378 | 7.0818 | 7.0416 | 6.9688 | 6.896 | 6.8125 | 6.7215 | 6.608 | 6.4587 | 6.0275 | 5.2168 | 4.5806 | 4.0831 | 6.0177 | 5.9793 | 5.9327 | 5.9043 | 5.8634 | 5.82 | 5.6887 | 5.5495 | 5.3862 | 5.1497 | 4.5085 | 3.3164 | 2.6468 | 2.418
TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | YES | 3.1326 | 3.0732 | 3.0208 | 2.9548 | 2.8137 | 4.7682 | 4.5925 | 4.4366 | 4.22 | 4.0451 | 3.3356 | 2.7269 | 2.4379 | 2.3224 | 3.8603 | 3.8079 | 3.775 | 3.7351 | 3.6213 | 5.9554 | 5.8429 | 5.7069 | 5.529 | 5.3773 | 4.9193 | 4.5651 | 4.4182 | 4.3227 | 3.1568 | 3.0931 | 3.0451 | 2.9839 | 2.7977 | 5.0494 | 4.8549 | 4.6425 | 4.3535 | 4.1292 | 3.4563 | 2.8972 | 2.6417 | 2.5405
| PITLOCHRY | CT |  |  | 3.1656 | 3.1162 | 3.0772 | 3.0355 | 2.8945 | 4.8888 | 4.7624 | 4.6147 | 4.42 | 4.2645 | 3.5953 | 2.7269 | 2.4379 | 2.3224 | 3.8771 | 3.839 | 3.8131 | 3.7819 | 3.6687 | 6.003 | 5.8886 | 5.7682 | 5.6521 | 5.5237 | 5.0645 | 4.5651 | 4.4182 | 4.3227 | 3.1751 | 3.1298 | 3.0932 | 3.0527 | 2.9237 | 5.2231 | 5.0148 | 4.805 | 4.5994 | 4.3972 | 3.701 | 2.8972 | 2.6417 | 2.5405
| PITLOCHRY | LW |  |  | 3.1326 | 3.0732 | 3.0208 | 2.9548 | 2.8137 | 4.7682 | 4.5925 | 4.4366 | 4.22 | 4.0451 | 3.3356 | 2.801 | 2.6943 | 2.6187 | 3.8603 | 3.8079 | 3.775 | 3.7351 | 3.6213 | 5.9554 | 5.8429 | 5.7069 | 5.529 | 5.3773 | 4.9193 | 4.5955 | 4.5531 | 4.5237 | 3.1568 | 3.0931 | 3.0451 | 2.9839 | 2.7977 | 5.0494 | 4.8549 | 4.6425 | 4.3535 | 4.1292 | 3.4563 | 2.9554 | 2.8618 | 2.7955
| PITLOCHRY | ST |  |  | 3.1582 | 3.1431 | 3.1284 | 3.1268 | 3.0962 | 5.1898 | 5.1544 | 5.1162 | 5.0787 | 5.0215 | 4.8143 | 4.1838 | 3.7745 | 3.6021 | 3.8896 | 3.8699 | 3.8495 | 3.8228 | 3.796 | 6.2025 | 6.1694 | 6.137 | 6.1036 | 6.0459 | 5.8254 | 5.2 | 4.9175 | 4.7972 | 3.2041 | 3.1847 | 3.1646 | 3.1416 | 3.1137 | 5.5227 | 5.4896 | 5.448 | 5.4102 | 5.3323 | 5.0357 | 4.2001 | 3.8154 | 3.6634
| PITLOCHRY | SP |  |  | 3.1831 | 3.182 | 3.1765 | 3.1599 | 3.125 | 5.2155 | 5.1776 | 5.1389 | 5.0957 | 5.0387 | 4.8492 | 4.1024 | 3.492 | 3.3033 | 3.904 | 3.8911 | 3.8767 | 3.8601 | 3.8271 | 6.2313 | 6.1956 | 6.1586 | 6.1073 | 6.046 | 5.8504 | 5.3023 | 4.8352 | 4.6191 | 3.2137 | 3.2012 | 3.187 | 3.172 | 3.1407 | 5.5476 | 5.5116 | 5.4523 | 5.3785 | 5.2789 | 4.9705 | 4.1674 | 3.5841 | 3.4109
ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | YES | 1.9747 | 1.9436 | 1.8765 | 1.771 | 1.4805 | 1.2088 | 0.94063 | 0.67244 | 0.34709 | 0.19592 | -0.5791 | -0.93159 | -0.84078 | -0.99432 | 3.3234 | 3.2611 | 3.22 | 3.1747 | 3.1369 | 3.0666 | 2.9378 | 2.79 | 2.6169 | 2.4975 | 1.8369 | 1.5426 | 1.5836 | 1.4821 | 2.8753 | 2.8377 | 2.7594 | 2.6693 | 2.4459 | 2.2329 | 2.0163 | 1.7599 | 1.4648 | 1.2915 | 0.45114 | 0.095867 | 0.20249 | 0.070231
| POLLACHAR | CT |  |  | 2.0021 | 1.9436 | 1.897 | 1.833 | 1.6066 | 1.3417 | 1.064 | 0.7581 | 0.47597 | 0.35145 | -0.25255 | -0.81491 | -0.74823 | -0.74052 | 3.3234 | 3.2611 | 3.22 | 3.1747 | 3.1369 | 3.0684 | 2.9378 | 2.8015 | 2.6748 | 2.5817 | 2.0609 | 1.5874 | 1.5836 | 1.5633 | 2.9769 | 2.9455 | 2.8797 | 2.7495 | 2.5049 | 2.2871 | 2.0564 | 1.8086 | 1.5797 | 1.4437 | 0.795 | 0.18935 | 0.23188 | 0.23939
| POLLACHAR | LW |  |  | 1.9747 | 1.9623 | 1.8765 | 1.771 | 1.4805 | 1.2088 | 0.94063 | 0.67244 | 0.34709 | 0.19592 | -0.5791 | -0.93159 | -0.7796 | -0.85847 | 3.3313 | 3.2722 | 3.2358 | 3.2074 | 3.1685 | 3.0666 | 2.9424 | 2.79 | 2.6169 | 2.4975 | 1.8369 | 1.5426 | 1.5944 | 1.567 | 2.8753 | 2.8377 | 2.7594 | 2.6693 | 2.4459 | 2.2329 | 2.0163 | 1.7599 | 1.4648 | 1.2915 | 0.45114 | 0.095867 | 0.20676 | 0.14885
| POLLACHAR | ST |  |  | 2.0309 | 1.9763 | 1.951 | 1.9265 | 1.911 | 1.8987 | 1.883 | 1.8643 | 1.7999 | 1.7125 | 1.1891 | 0.30891 | 0.029832 | -0.035419 | 3.3433 | 3.2813 | 3.2516 | 3.2295 | 3.2108 | 3.197 | 3.1796 | 3.1654 | 3.1384 | 3.1201 | 2.716 | 2.0871 | 1.8744 | 1.8162 | 2.9592 | 2.8984 | 2.8631 | 2.8265 | 2.7984 | 2.7684 | 2.7359 | 2.7118 | 2.6455 | 2.5588 | 2.0337 | 1.1563 | 0.86412 | 0.79081
| POLLACHAR | SP |  |  | 2.0349 | 1.9828 | 1.9606 | 1.9472 | 1.8901 | 1.7939 | 1.684 | 1.5727 | 1.4408 | 1.2604 | 0.58935 | -0.27946 | -0.84078 | -0.99432 | 3.3451 | 3.2844 | 3.2563 | 3.24 | 3.2237 | 3.2132 | 3.1985 | 3.1877 | 3.135 | 3.0508 | 2.5959 | 2.0612 | 1.5932 | 1.4821 | 2.9634 | 2.9033 | 2.8719 | 2.8502 | 2.7608 | 2.6821 | 2.5939 | 2.5041 | 2.3826 | 2.2316 | 1.6307 | 0.82321 | 0.20249 | 0.070231
FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | 0.10085 | 0.10084 | 0.10084 | 0.10083 | 0.10083 | 0.10083 | 0.10082 | 0.10082 | 0.10082 | 0.10081 | 0.10077 | 0.10061 | 0.10032 | 0.10001 | 0.098231 | 0.098207 | 0.098179 | 0.098148 | 0.098127 | 0.098102 | 0.098075 | 0.098044 | 0.098008 | 0.097972 | 0.097821 | 0.097367 | 0.096409 | 0.094697 | 0.096948 | 0.096945 | 0.096942 | 0.096939 | 0.096937 | 0.096934 | 0.096932 | 0.09693 | 0.096928 | 0.096925 | 0.096899 | 0.096789 | 0.096591 | 0.096376
| POOR HOUSE | CT |  |  | 0.10085 | 0.10084 | 0.10084 | 0.10083 | 0.10083 | 0.10083 | 0.10082 | 0.10082 | 0.10082 | 0.10081 | 0.10077 | 0.10061 | 0.10032 | 0.10001 | 0.098234 | 0.098213 | 0.09819 | 0.098165 | 0.098143 | 0.098118 | 0.098091 | 0.09806 | 0.098026 | 0.097998 | 0.097883 | 0.097471 | 0.096736 | 0.095586 | 0.096948 | 0.096945 | 0.096942 | 0.096939 | 0.096937 | 0.096934 | 0.096932 | 0.09693 | 0.096928 | 0.096925 | 0.096899 | 0.096789 | 0.096591 | 0.096376
| POOR HOUSE | LW |  |  | 0.10085 | 0.10084 | 0.10084 | 0.10083 | 0.10083 | 0.10083 | 0.10082 | 0.10082 | 0.10082 | 0.10081 | 0.10077 | 0.10061 | 0.10032 | 0.10001 | 0.09825 | 0.098246 | 0.098244 | 0.098241 | 0.098239 | 0.098237 | 0.098235 | 0.098233 | 0.09823 | 0.098228 | 0.098205 | 0.09811 | 0.097938 | 0.097752 | 0.096948 | 0.096945 | 0.096942 | 0.096939 | 0.096937 | 0.096934 | 0.096932 | 0.09693 | 0.096928 | 0.096925 | 0.096899 | 0.096789 | 0.096591 | 0.096376
| POOR HOUSE | ST |  |  | 0.10085 | 0.10084 | 0.10084 | 0.10083 | 0.10083 | 0.10083 | 0.10082 | 0.10082 | 0.10082 | 0.10081 | 0.10077 | 0.10061 | 0.10032 | 0.10001 | 0.098234 | 0.098213 | 0.09819 | 0.098165 | 0.098143 | 0.098118 | 0.098091 | 0.09806 | 0.098026 | 0.097998 | 0.097883 | 0.097472 | 0.096738 | 0.095591 | 0.096948 | 0.096945 | 0.096942 | 0.096939 | 0.096937 | 0.096934 | 0.096932 | 0.09693 | 0.096928 | 0.096925 | 0.096899 | 0.096789 | 0.096591 | 0.096376
| POOR HOUSE | SP |  |  | 0.10085 | 0.10084 | 0.10084 | 0.10083 | 0.10083 | 0.10083 | 0.10082 | 0.10082 | 0.10082 | 0.10081 | 0.10077 | 0.10061 | 0.10032 | 0.10001 | 0.098231 | 0.098207 | 0.098179 | 0.098148 | 0.098127 | 0.098102 | 0.098075 | 0.098044 | 0.098008 | 0.097972 | 0.097821 | 0.097367 | 0.096409 | 0.094697 | 0.096948 | 0.096945 | 0.096942 | 0.096939 | 0.096937 | 0.096934 | 0.096932 | 0.09693 | 0.096928 | 0.096925 | 0.096899 | 0.096789 | 0.096591 | 0.096376
PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | 1.753 | 1.7347 | 1.7174 | 1.6796 | 1.6088 | 1.5412 | 1.4328 | 1.3207 | 1.2169 | 1.1675 | 0.98076 | 0.75689 | 0.77621 | 0.76109 | 1.9518 | 1.9375 | 1.9256 | 1.9015 | 1.8638 | 1.8263 | 1.7753 | 1.7246 | 1.6768 | 1.6397 | 1.4833 | 1.3868 | 1.4001 | 1.3883 | 1.8159 | 1.8 | 1.7828 | 1.7455 | 1.6796 | 1.6161 | 1.5173 | 1.416 | 1.3222 | 1.2727 | 1.0783 | 0.91547 | 0.93214 | 0.91871
| PORT ASKAIG | CT |  |  | 1.7573 | 1.7371 | 1.7177 | 1.6796 | 1.6088 | 1.5412 | 1.4328 | 1.3207 | 1.2169 | 1.1675 | 1.004 | 0.84718 | 0.84909 | 0.84442 | 1.9525 | 1.9375 | 1.9256 | 1.9015 | 1.8638 | 1.8263 | 1.7753 | 1.7246 | 1.6768 | 1.6397 | 1.5124 | 1.3929 | 1.4039 | 1.4026 | 1.8192 | 1.8015 | 1.7828 | 1.7455 | 1.6796 | 1.6161 | 1.5173 | 1.416 | 1.3222 | 1.2727 | 1.1086 | 0.95113 | 0.98875 | 0.99838
| PORT ASKAIG | LW |  |  | 1.753 | 1.7347 | 1.7174 | 1.6925 | 1.6251 | 1.5545 | 1.4834 | 1.4032 | 1.2661 | 1.2038 | 0.98076 | 0.75689 | 0.77621 | 0.76109 | 1.9518 | 1.9376 | 1.9277 | 1.9129 | 1.8808 | 1.8448 | 1.8094 | 1.7588 | 1.6888 | 1.6421 | 1.4833 | 1.3868 | 1.4001 | 1.3883 | 1.8159 | 1.8 | 1.7839 | 1.7604 | 1.6995 | 1.6343 | 1.5694 | 1.4913 | 1.3636 | 1.3009 | 1.0783 | 0.91547 | 0.93214 | 0.91871
| PORT ASKAIG | ST |  |  | 1.7626 | 1.752 | 1.7497 | 1.7426 | 1.7405 | 1.7401 | 1.7344 | 1.7251 | 1.6875 | 1.6375 | 1.4681 | 1.113 | 0.92182 | 0.88893 | 1.9568 | 1.9482 | 1.9464 | 1.9406 | 1.9354 | 1.9302 | 1.9224 | 1.9153 | 1.9011 | 1.8767 | 1.7956 | 1.5791 | 1.4546 | 1.4416 | 1.8248 | 1.8159 | 1.8135 | 1.806 | 1.8034 | 1.8016 | 1.7826 | 1.7689 | 1.7358 | 1.6919 | 1.5407 | 1.2074 | 1.0306 | 1.0032
| PORT ASKAIG | SP |  |  | 1.7697 | 1.7628 | 1.7649 | 1.7666 | 1.7559 | 1.7494 | 1.7372 | 1.7255 | 1.6924 | 1.6505 | 1.5119 | 1.1743 | 0.87361 | 0.77803 | 1.9581 | 1.9502 | 1.9491 | 1.9478 | 1.9423 | 1.9381 | 1.9308 | 1.9226 | 1.9066 | 1.8893 | 1.8114 | 1.6359 | 1.4451 | 1.396 | 1.8312 | 1.8256 | 1.8271 | 1.8282 | 1.8184 | 1.8124 | 1.7891 | 1.7761 | 1.7472 | 1.7123 | 1.6025 | 1.3089 | 1.0258 | 0.93817
PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | 1.4746 | 1.4539 | 1.4136 | 1.3691 | 1.2444 | 1.1105 | 0.98212 | 0.83985 | 0.68799 | 0.61601 | 0.37695 | 0.25416 | 0.32811 | 0.30641 | 2.1781 | 2.1647 | 2.1526 | 2.1401 | 2.0966 | 2.0375 | 1.9823 | 1.9133 | 1.8366 | 1.7881 | 1.6113 | 1.497 | 1.5204 | 1.5085 | 1.6958 | 1.6775 | 1.644 | 1.6056 | 1.5132 | 1.4086 | 1.3098 | 1.193 | 1.0655 | 0.99481 | 0.74602 | 0.60502 | 0.65709 | 0.6415
| PORT ELLEN | CT |  |  | 1.5104 | 1.4975 | 1.4654 | 1.4291 | 1.2927 | 1.1628 | 1.0351 | 0.91201 | 0.80006 | 0.73964 | 0.5405 | 0.33766 | 0.35394 | 0.34863 | 2.1781 | 2.1647 | 2.1526 | 2.1401 | 2.0977 | 2.0396 | 1.9841 | 1.9286 | 1.875 | 1.8337 | 1.6863 | 1.5335 | 1.5246 | 1.5085 | 1.7195 | 1.706 | 1.6766 | 1.6421 | 1.5346 | 1.4325 | 1.3338 | 1.237 | 1.1464 | 1.0871 | 0.88089 | 0.67497 | 0.68088 | 0.6761
| PORT ELLEN | LW |  |  | 1.4746 | 1.4539 | 1.4136 | 1.3691 | 1.2444 | 1.1105 | 0.98212 | 0.83985 | 0.68799 | 0.61601 | 0.37695 | 0.25416 | 0.32811 | 0.30641 | 2.1799 | 2.1667 | 2.1557 | 2.1442 | 2.0966 | 2.0375 | 1.9823 | 1.9133 | 1.8366 | 1.7881 | 1.6113 | 1.497 | 1.5204 | 1.5127 | 1.6958 | 1.6775 | 1.644 | 1.6056 | 1.5132 | 1.4086 | 1.3098 | 1.193 | 1.0655 | 0.99481 | 0.74602 | 0.60502 | 0.65709 | 0.6415
| PORT ELLEN | ST |  |  | 1.5021 | 1.4861 | 1.4652 | 1.4494 | 1.437 | 1.4277 | 1.4136 | 1.4033 | 1.3835 | 1.3462 | 1.2123 | 0.9112 | 0.77801 | 0.73331 | 2.1831 | 2.1777 | 2.1697 | 2.1629 | 2.152 | 2.147 | 2.1367 | 2.1319 | 2.1208 | 2.1063 | 2.017 | 1.7916 | 1.6959 | 1.664 | 1.7182 | 1.7051 | 1.688 | 1.673 | 1.6599 | 1.6495 | 1.6329 | 1.6208 | 1.6012 | 1.5658 | 1.4396 | 1.1358 | 1.01 | 0.97552
| PORT ELLEN | SP |  |  | 1.5113 | 1.5001 | 1.4849 | 1.4737 | 1.4388 | 1.4092 | 1.3758 | 1.3444 | 1.3074 | 1.2444 | 1.0762 | 0.71748 | 0.44282 | 0.35163 | 2.1834 | 2.1785 | 2.171 | 2.165 | 2.1553 | 2.1513 | 2.1425 | 2.1364 | 2.1164 | 2.0834 | 1.9963 | 1.7931 | 1.5897 | 1.5147 | 1.7243 | 1.7148 | 1.7017 | 1.6914 | 1.6645 | 1.6416 | 1.6141 | 1.5892 | 1.5577 | 1.5047 | 1.3642 | 1.0513 | 0.78385 | 0.71075
DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | YES | 2.9542 | 2.9183 | 2.7399 | 2.4483 | 2.122 | 1.7836 | 1.3969 | 1.0059 | 0.53968 | 0.29252 | -0.51792 | -0.70735 | -0.53604 | -0.72883 | 3.8644 | 3.8386 | 3.6744 | 3.4228 | 3.2191 | 3.0057 | 2.804 | 2.6096 | 2.3681 | 2.2233 | 1.7269 | 1.568 | 1.5538 | 1.3283 | 3.1644 | 3.1309 | 2.9563 | 2.6767 | 2.3804 | 2.0719 | 1.7714 | 1.465 | 1.103 | 0.89654 | 0.17908 | 0.0088908 | 0.14488 | 0.001714
| PORTREE | CT |  |  | 3.0638 | 3.0489 | 2.896 | 2.6089 | 2.2444 | 1.9183 | 1.6145 | 1.2734 | 0.8614 | 0.64252 | -0.079951 | -0.53668 | -0.53604 | -0.56619 | 3.9123 | 3.8973 | 3.7435 | 3.4918 | 3.2661 | 3.0595 | 2.87 | 2.7018 | 2.4873 | 2.3575 | 1.9202 | 1.6196 | 1.5739 | 1.5047 | 3.2558 | 3.2401 | 3.0859 | 2.8055 | 2.4731 | 2.1741 | 1.8972 | 1.6433 | 1.3342 | 1.1533 | 0.51133 | 0.13871 | 0.14488 | 0.12052
| PORTREE | LW |  |  | 2.9542 | 2.9183 | 2.7399 | 2.4483 | 2.122 | 1.7836 | 1.3969 | 1.0059 | 0.53968 | 0.29252 | -0.51792 | -0.70735 | -0.52137 | -0.5695 | 3.8644 | 3.8386 | 3.6744 | 3.4228 | 3.2191 | 3.0057 | 2.804 | 2.6096 | 2.3681 | 2.2233 | 1.7269 | 1.568 | 1.6291 | 1.6119 | 3.1644 | 3.1309 | 2.9563 | 2.6767 | 2.3804 | 2.0719 | 1.7714 | 1.465 | 1.103 | 0.89654 | 0.17908 | 0.0088908 | 0.1488 | 0.1132
| PORTREE | ST |  |  | 3.0448 | 3.0112 | 2.8836 | 2.6671 | 2.5912 | 2.5109 | 2.4254 | 2.348 | 2.1841 | 2.0389 | 1.5928 | 0.72055 | 0.35106 | 0.20193 | 3.9106 | 3.8897 | 3.7517 | 3.5417 | 3.4626 | 3.3828 | 3.3054 | 3.2396 | 3.1178 | 3.0118 | 2.6908 | 2.0957 | 1.8581 | 1.7446 | 3.2433 | 3.2132 | 3.0835 | 2.8704 | 2.7931 | 2.7122 | 2.6276 | 2.5515 | 2.4004 | 2.2619 | 1.8323 | 1.048 | 0.77666 | 0.68096
| PORTREE | SP |  |  | 3.0526 | 3.0213 | 2.9012 | 2.6876 | 2.5479 | 2.4098 | 2.2684 | 2.1263 | 1.9025 | 1.6853 | 1.0866 | 0.087253 | -0.52923 | -0.72883 | 3.9147 | 3.8952 | 3.7613 | 3.5534 | 3.4448 | 3.338 | 3.2352 | 3.1398 | 2.9924 | 2.8518 | 2.5145 | 1.9952 | 1.5538 | 1.3283 | 3.2503 | 3.2225 | 3.0999 | 2.891 | 2.7604 | 2.6307 | 2.5001 | 2.3696 | 2.1661 | 1.9673 | 1.4946 | 0.70057 | 0.1658 | 0.001714
MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | 3.1635 | 3.1602 | 3.1485 | 3.1307 | 3.0725 | 3.0113 | 2.8983 | 2.7712 | 2.6446 | 2.5186 | 2.1078 | 1.5447 | 1.2616 | 1.1654 | 3.3126 | 3.303 | 3.2908 | 3.2722 | 3.2482 | 3.2216 | 3.1893 | 3.1539 | 3.1172 | 3.0674 | 2.9073 | 2.7614 | 2.7345 | 2.7246 | 2.8402 | 2.8325 | 2.8239 | 2.8079 | 2.7702 | 2.7177 | 2.6279 | 2.5201 | 2.4125 | 2.3074 | 1.9692 | 1.4933 | 1.2469 | 1.1617
| PORTSOY | CT |  |  | 3.1797 | 3.176 | 3.1651 | 3.1311 | 3.0729 | 3.0117 | 2.8983 | 2.7712 | 2.6446 | 2.5186 | 2.1078 | 1.5447 | 1.2616 | 1.1654 | 3.3126 | 3.303 | 3.2908 | 3.2722 | 3.2482 | 3.2216 | 3.1893 | 3.1539 | 3.1172 | 3.0745 | 2.9476 | 2.7936 | 2.7512 | 2.7351 | 2.8402 | 2.8325 | 2.8239 | 2.8079 | 2.7745 | 2.724 | 2.6279 | 2.5201 | 2.4125 | 2.3074 | 1.9692 | 1.4933 | 1.2469 | 1.1617
| PORTSOY | LW |  |  | 3.1635 | 3.1602 | 3.1485 | 3.1307 | 3.0725 | 3.0113 | 2.945 | 2.8476 | 2.6764 | 2.5374 | 2.1143 | 1.7469 | 1.5376 | 1.4641 | 3.3139 | 3.3048 | 3.294 | 3.2796 | 3.2564 | 3.23 | 3.202 | 3.1661 | 3.1186 | 3.0674 | 2.9073 | 2.7614 | 2.7345 | 2.7246 | 2.8434 | 2.8372 | 2.831 | 2.8197 | 2.7702 | 2.7177 | 2.6616 | 2.5841 | 2.4414 | 2.3295 | 1.9929 | 1.6624 | 1.475 | 1.4079
| PORTSOY | ST |  |  | 3.1799 | 3.1765 | 3.1714 | 3.1622 | 3.1566 | 3.1455 | 3.1339 | 3.1233 | 3.1034 | 3.0693 | 2.9368 | 2.4577 | 2.2495 | 2.1325 | 3.3223 | 3.3183 | 3.3131 | 3.3063 | 3.2997 | 3.2914 | 3.2815 | 3.2706 | 3.2567 | 3.2356 | 3.1549 | 2.9375 | 2.8384 | 2.8149 | 2.8473 | 2.8449 | 2.8414 | 2.8357 | 2.8309 | 2.8242 | 2.8167 | 2.8085 | 2.7986 | 2.775 | 2.6687 | 2.3326 | 2.1332 | 2.0078
| PORTSOY | SP |  |  | 3.1876 | 3.1849 | 3.1827 | 3.1783 | 3.1632 | 3.1504 | 3.1335 | 3.1135 | 3.0821 | 3.044 | 2.9167 | 2.6139 | 2.307 | 2.2547 | 3.324 | 3.3209 | 3.3169 | 3.3123 | 3.306 | 3.2997 | 3.292 | 3.2831 | 3.2715 | 3.2559 | 3.2039 | 3.0492 | 2.8969 | 2.8679 | 2.8495 | 2.8476 | 2.8451 | 2.8419 | 2.8383 | 2.8349 | 2.822 | 2.8054 | 2.781 | 2.7498 | 2.6468 | 2.4031 | 2.201 | 2.1548
WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | 1.8591 | 1.3319 | 0.76518 | 0.088924 | -1.2365 | -2.7563 | -4.4996 | -5.884 | -6.8533 | -7.9336 | -11.5982 | -16.6589 | -18.5377 | -19.7535 | 4.7384 | 4.3429 | 3.8822 | 3.3095 | 2.4752 | 1.5216 | 0.60247 | 0.078173 | -0.49692 | -1.2353 | -3.6617 | -7.3176 | -9.1279 | -11.0316 | 2.6831 | 2.1711 | 1.6214 | 0.96457 | -0.33244 | -1.8197 | -3.4214 | -4.6916 | -5.6061 | -6.636 | -10.1196 | -14.8395 | -16.2978 | -17.2294
| QUEENS LANE NORTH | CT |  |  | 1.8591 | 1.3319 | 0.76518 | 0.088924 | -1.2365 | -2.7563 | -4.0818 | -4.9266 | -5.8646 | -7.0489 | -10.8178 | -16.3486 | -18.5377 | -19.7535 | 4.7384 | 4.3429 | 3.8822 | 3.3095 | 2.4752 | 1.5216 | 0.60247 | 0.078173 | -0.49414 | -1.2353 | -3.6304 | -7.3176 | -9.1279 | -11.0316 | 2.6831 | 2.1711 | 1.6214 | 0.96457 | -0.33244 | -1.8197 | -3.1 | -3.8891 | -4.7629 | -5.8732 | -9.3978 | -14.4752 | -16.2978 | -17.2294
| QUEENS LANE NORTH | LW |  |  | 1.9625 | 1.3621 | 0.80864 | 0.10611 | -1.1997 | -2.7167 | -4.4996 | -5.884 | -6.8533 | -7.9336 | -11.5982 | -16.6589 | -18.2565 | -19.2693 | 4.8733 | 4.4834 | 4.0816 | 3.56 | 2.787 | 1.8859 | 0.80771 | 0.10461 | -0.49692 | -1.2151 | -3.6617 | -6.9358 | -7.6721 | -8.1691 | 2.782 | 2.1967 | 1.6588 | 0.97483 | -0.30016 | -1.7437 | -3.4214 | -4.6916 | -5.6061 | -6.636 | -10.1196 | -14.8395 | -16.1251 | -16.8788
| QUEENS LANE NORTH | ST |  |  | 2.5668 | 2.4283 | 2.2702 | 2.0712 | 1.8796 | 1.7003 | 1.4974 | 1.2973 | 1.0965 | 0.71368 | -0.79203 | -5.3681 | -8.2147 | -9.7765 | 5.2286 | 5.121 | 4.9968 | 4.8414 | 4.6914 | 4.5327 | 4.3512 | 4.1658 | 3.9591 | 3.6363 | 2.3721 | -1.3238 | -3.7697 | -5.7824 | 3.3743 | 3.2413 | 3.0888 | 2.8954 | 2.7086 | 2.5344 | 2.3365 | 2.1408 | 1.9442 | 1.5715 | 0.11478 | -4.2642 | -6.8117 | -8.0469
| QUEENS LANE NORTH | SP |  |  | 2.6234 | 2.5323 | 2.4092 | 2.2698 | 2.0758 | 1.848 | 1.6227 | 1.3999 | 1.1675 | 0.83914 | -0.29162 | -3.8002 | -7.1911 | -8.319 | 5.2446 | 5.157 | 5.0432 | 4.9122 | 4.7601 | 4.5823 | 4.3909 | 4.1941 | 3.979 | 3.689 | 2.6637 | -0.53534 | -4.4656 | -8.1937 | 3.4296 | 3.343 | 3.2247 | 3.09 | 2.9023 | 2.6818 | 2.4629 | 2.2463 | 2.02 | 1.6994 | 0.60948 | -2.745 | -5.875 | -6.7796
QUOICH | QUOICH PRIMARY | MINIMUM HEADROOM | NH 11700 01900 | YES | 4.6112 | 7.3258 | 7.324 | 7.3203 | 7.3121 | 7.3038 | 7.2966 | 7.2874 | 7.2777 | 7.2714 | 7.2463 | 7.2377 | 7.2357 | 7.238 | 4.2888 | 6.7958 | 6.7945 | 6.7919 | 6.7859 | 6.779 | 6.775 | 6.7707 | 6.7663 | 6.7604 | 6.7404 | 6.7257 | 6.7192 | 6.7212 | 4.2706 | 6.7781 | 6.7762 | 6.7725 | 6.7647 | 6.7558 | 6.7485 | 6.7399 | 6.731 | 6.725 | 6.7008 | 6.6892 | 6.6864 | 6.6887
| QUOICH PRIMARY | CT |  |  | 4.6139 | 7.3269 | 7.3245 | 7.3204 | 7.3121 | 7.3038 | 7.2968 | 7.2874 | 7.279 | 7.2719 | 7.2497 | 7.2399 | 7.2437 | 7.2434 | 4.29 | 6.7966 | 6.795 | 6.7919 | 6.7859 | 6.779 | 6.775 | 6.7707 | 6.7663 | 6.7604 | 6.7436 | 6.7296 | 6.7293 | 6.7294 | 4.273 | 6.7799 | 6.7777 | 6.7738 | 6.7647 | 6.7564 | 6.7485 | 6.7399 | 6.7323 | 6.7255 | 6.7041 | 6.6946 | 6.6942 | 6.694
| QUOICH PRIMARY | LW |  |  | 4.6112 | 7.3258 | 7.324 | 7.3203 | 7.313 | 7.3042 | 7.2966 | 7.2887 | 7.2777 | 7.2714 | 7.2463 | 7.2377 | 7.2396 | 7.2388 | 4.2888 | 6.7958 | 6.7945 | 6.7919 | 6.7871 | 6.7811 | 6.7768 | 6.7722 | 6.7665 | 6.7608 | 6.7404 | 6.7257 | 6.7259 | 6.7258 | 4.2706 | 6.7781 | 6.7762 | 6.7725 | 6.7652 | 6.7558 | 6.7485 | 6.7412 | 6.731 | 6.725 | 6.7008 | 6.6892 | 6.6902 | 6.6898
| QUOICH PRIMARY | ST |  |  | 4.6147 | 7.3282 | 7.3278 | 7.3274 | 7.3267 | 7.3263 | 7.3243 | 7.3237 | 7.3222 | 7.3184 | 7.3054 | 7.2622 | 7.2357 | 7.238 | 4.291 | 6.7976 | 6.7974 | 6.7971 | 6.7966 | 6.7961 | 6.7945 | 6.7938 | 6.7925 | 6.7897 | 6.7769 | 6.7392 | 6.7192 | 6.7212 | 4.2739 | 6.7804 | 6.7801 | 6.7797 | 6.7789 | 6.7785 | 6.7765 | 6.7758 | 6.7742 | 6.7704 | 6.7573 | 6.7119 | 6.6864 | 6.6887
| QUOICH PRIMARY | SP |  |  | 4.6147 | 7.3282 | 7.3281 | 7.3277 | 7.3253 | 7.3227 | 7.3193 | 7.3162 | 7.3132 | 7.3061 | 7.2933 | 7.2595 | 7.2417 | 7.238 | 4.2911 | 6.7978 | 6.7977 | 6.7974 | 6.7961 | 6.7946 | 6.7927 | 6.791 | 6.7893 | 6.7857 | 6.7787 | 6.7562 | 6.7418 | 6.7355 | 4.274 | 6.7805 | 6.7804 | 6.7799 | 6.7775 | 6.7749 | 6.7715 | 6.7682 | 6.7647 | 6.758 | 6.7462 | 6.7143 | 6.6969 | 6.6934
FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | 1.1426 | 1.1425 | 1.1421 | 1.1412 | 1.14 | 1.1384 | 1.1365 | 1.1333 | 1.1313 | 1.1268 | 1.1162 | 1.1056 | 1.1059 | 1.1058 | 1.0666 | 1.0665 | 1.0662 | 1.0655 | 1.0647 | 1.0639 | 1.0626 | 1.0607 | 1.0596 | 1.0565 | 1.0497 | 1.0418 | 1.042 | 1.0419 | 1.0633 | 1.0633 | 1.0628 | 1.0619 | 1.0607 | 1.0589 | 1.057 | 1.0537 | 1.0515 | 1.0472 | 1.0375 | 1.0274 | 1.0278 | 1.0277
| RAHOY | CT |  |  | 1.1432 | 1.143 | 1.1427 | 1.1414 | 1.14 | 1.1389 | 1.1365 | 1.1333 | 1.1313 | 1.1276 | 1.1216 | 1.1127 | 1.1119 | 1.1114 | 1.0669 | 1.0669 | 1.0666 | 1.0655 | 1.0647 | 1.064 | 1.0626 | 1.0607 | 1.0597 | 1.0571 | 1.0538 | 1.0475 | 1.0472 | 1.047 | 1.0639 | 1.0638 | 1.0634 | 1.0625 | 1.061 | 1.0596 | 1.057 | 1.0537 | 1.0515 | 1.048 | 1.0427 | 1.0343 | 1.0336 | 1.0332
| RAHOY | LW |  |  | 1.1426 | 1.1425 | 1.1421 | 1.1412 | 1.1402 | 1.1384 | 1.1373 | 1.1351 | 1.1314 | 1.1268 | 1.1162 | 1.1056 | 1.1059 | 1.1058 | 1.0666 | 1.0665 | 1.0662 | 1.0656 | 1.065 | 1.0639 | 1.0632 | 1.0618 | 1.0596 | 1.0565 | 1.0497 | 1.0418 | 1.042 | 1.0419 | 1.0633 | 1.0633 | 1.0628 | 1.0619 | 1.0607 | 1.0589 | 1.0575 | 1.0554 | 1.0516 | 1.0472 | 1.0375 | 1.0274 | 1.0278 | 1.0277
| RAHOY | ST |  |  | 1.1431 | 1.143 | 1.1429 | 1.1427 | 1.1425 | 1.1415 | 1.1413 | 1.1409 | 1.1402 | 1.1393 | 1.135 | 1.1185 | 1.1114 | 1.1103 | 1.0669 | 1.0668 | 1.0667 | 1.0665 | 1.0664 | 1.0657 | 1.0656 | 1.0653 | 1.0648 | 1.0642 | 1.0615 | 1.05 | 1.0453 | 1.0449 | 1.064 | 1.0639 | 1.0638 | 1.0635 | 1.0633 | 1.0624 | 1.0623 | 1.0618 | 1.0611 | 1.0601 | 1.0552 | 1.0395 | 1.0328 | 1.0319
| RAHOY | SP |  |  | 1.1431 | 1.1429 | 1.1429 | 1.1428 | 1.1423 | 1.1419 | 1.1412 | 1.1404 | 1.1388 | 1.1377 | 1.1334 | 1.1236 | 1.1127 | 1.1104 | 1.0668 | 1.0668 | 1.0667 | 1.0666 | 1.0664 | 1.0661 | 1.0658 | 1.0652 | 1.0642 | 1.0636 | 1.0609 | 1.0549 | 1.0477 | 1.0464 | 1.0639 | 1.0638 | 1.0637 | 1.0636 | 1.063 | 1.0625 | 1.0618 | 1.0609 | 1.0594 | 1.0583 | 1.0538 | 1.0442 | 1.0344 | 1.0323
INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | 7.683 | 7.2403 | 6.6258 | 5.8217 | 4.9248 | 3.8859 | 2.9798 | 2.0426 | 0.97674 | -0.3643 | -4.5758 | -9.1583 | -9.3939 | -9.5199 | 10.8814 | 10.4902 | 9.9183 | 9.1933 | 8.4077 | 7.5341 | 6.8233 | 6.0947 | 5.2811 | 4.2438 | 0.98703 | -2.5162 | -2.6651 | -2.7512 | 8.1237 | 7.7604 | 7.2394 | 6.6067 | 5.9183 | 5.1568 | 4.5522 | 3.9404 | 3.2957 | 2.4381 | -1.5917 | -5.9953 | -6.2096 | -6.3239
| RAIGMORE | CT |  |  | 7.683 | 7.2403 | 6.6258 | 5.8217 | 4.9248 | 3.8859 | 2.9798 | 2.0426 | 1.0418 | -0.11369 | -3.3421 | -7.1097 | -7.5293 | -7.6745 | 10.8814 | 10.4902 | 9.9183 | 9.1933 | 8.4077 | 7.5341 | 6.8233 | 6.0947 | 5.3208 | 4.4324 | 1.9524 | -0.89301 | -1.1735 | -1.2795 | 8.1237 | 7.7604 | 7.2394 | 6.6067 | 5.9183 | 5.1568 | 4.5522 | 3.9404 | 3.296 | 2.5763 | -0.39953 | -4.0105 | -4.3987 | -4.5298
| RAIGMORE | LW |  |  | 7.7476 | 7.3126 | 6.7245 | 5.9737 | 5.1151 | 4.091 | 3.1317 | 2.0995 | 0.97674 | -0.3643 | -4.5758 | -9.1583 | -9.3939 | -9.5199 | 10.9375 | 10.5518 | 10.0012 | 9.3113 | 8.5558 | 7.7051 | 6.9533 | 6.1508 | 5.2811 | 4.2438 | 0.98703 | -2.5162 | -2.6651 | -2.7512 | 8.1708 | 7.8139 | 7.3125 | 6.7114 | 6.0525 | 5.3119 | 4.6801 | 4.0125 | 3.2957 | 2.4381 | -1.5917 | -5.9953 | -6.2096 | -6.3239
| RAIGMORE | ST |  |  | 7.9225 | 7.6361 | 7.2144 | 6.7537 | 6.2909 | 5.783 | 5.3342 | 4.8521 | 4.325 | 3.6467 | 1.076 | -4.9674 | -7.7694 | -8.1663 | 11.0897 | 10.846 | 10.4695 | 10.0358 | 9.6232 | 9.1617 | 8.7533 | 8.3415 | 7.8942 | 7.3205 | 5.2482 | 0.57705 | -1.5774 | -1.8835 | 8.2939 | 8.0415 | 7.6574 | 7.2357 | 6.8168 | 6.3604 | 5.9786 | 5.5982 | 5.1917 | 4.6968 | 2.9931 | -1.9778 | -4.6745 | -5.0507
| RAIGMORE | SP |  |  | 7.9337 | 7.6691 | 7.2678 | 6.8375 | 6.4123 | 5.9539 | 5.57 | 5.1962 | 4.7988 | 4.3156 | 2.7792 | -1.2941 | -5.2522 | -6.1685 | 11.0993 | 10.8747 | 10.516 | 10.1087 | 9.7294 | 9.3208 | 8.9832 | 8.6516 | 8.3013 | 7.8945 | 6.5909 | 3.4339 | 0.3643 | -0.36608 | 8.3007 | 8.0638 | 7.6939 | 7.2944 | 6.9026 | 6.4815 | 6.1455 | 5.8229 | 5.4838 | 5.111 | 3.9678 | 1.5746 | -2.241 | -3.1199
ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | 1.2262 | 1.2003 | 1.1663 | 1.1233 | 1.028 | 0.91597 | 0.79398 | 0.65908 | 0.45897 | 0.29003 | -0.15022 | -0.39724 | -0.53285 | -0.6124 | 2.0553 | 2.0405 | 2.0215 | 1.9964 | 1.9513 | 1.896 | 1.8336 | 1.7576 | 1.6558 | 1.55 | 1.2839 | 1.1709 | 1.1364 | 1.0784 | 1.372 | 1.3481 | 1.3171 | 1.2783 | 1.1915 | 1.0898 | 0.9793 | 0.85827 | 0.67739 | 0.52721 | 0.13271 | -0.098384 | -0.22354 | -0.29278
| REDFORD | CT |  |  | 1.3141 | 1.2997 | 1.278 | 1.2403 | 1.142 | 1.0541 | 0.91284 | 0.75706 | 0.60714 | 0.48644 | 0.018071 | -0.34591 | -0.53285 | -0.6124 | 2.1212 | 2.1084 | 2.0922 | 2.0622 | 2.0111 | 1.9667 | 1.9024 | 1.8302 | 1.7601 | 1.6897 | 1.394 | 1.2236 | 1.1364 | 1.0784 | 1.4561 | 1.442 | 1.4213 | 1.385 | 1.2955 | 1.2158 | 1.0892 | 0.9492 | 0.81439 | 0.70301 | 0.28122 | -0.054334 | -0.22354 | -0.29278
| REDFORD | LW |  |  | 1.2262 | 1.2003 | 1.1663 | 1.1233 | 1.028 | 0.91597 | 0.79398 | 0.65908 | 0.45897 | 0.29003 | -0.15022 | -0.39724 | -0.47811 | -0.52054 | 2.0553 | 2.0405 | 2.0215 | 1.9964 | 1.9513 | 1.896 | 1.8336 | 1.7576 | 1.6558 | 1.55 | 1.2839 | 1.1709 | 1.1406 | 1.1242 | 1.372 | 1.3481 | 1.3171 | 1.2783 | 1.1915 | 1.0898 | 0.9793 | 0.85827 | 0.67739 | 0.52721 | 0.13271 | -0.098384 | -0.17196 | -0.2103
| REDFORD | ST |  |  | 1.257 | 1.2465 | 1.2362 | 1.2191 | 1.2031 | 1.1829 | 1.158 | 1.1366 | 1.0992 | 1.0455 | 0.84123 | 0.31395 | 0.09538 | -0.027508 | 2.0692 | 2.0622 | 2.0552 | 2.0425 | 2.0316 | 2.0174 | 1.9995 | 1.9847 | 1.9614 | 1.9287 | 1.796 | 1.4397 | 1.3302 | 1.2554 | 1.3997 | 1.3901 | 1.3807 | 1.3657 | 1.3514 | 1.3335 | 1.3115 | 1.2922 | 1.2585 | 1.2101 | 1.0274 | 0.55792 | 0.35589 | 0.24403
| REDFORD | SP |  |  | 1.2616 | 1.2544 | 1.2477 | 1.2391 | 1.2149 | 1.1902 | 1.1653 | 1.1297 | 1.0931 | 1.0423 | 0.84778 | 0.29968 | -0.036968 | -0.15532 | 2.0708 | 2.0655 | 2.0602 | 2.0533 | 2.0397 | 2.0253 | 2.0113 | 1.9892 | 1.9667 | 1.9361 | 1.8291 | 1.4815 | 1.2599 | 1.1584 | 1.4038 | 1.3974 | 1.3914 | 1.3837 | 1.362 | 1.3397 | 1.3173 | 1.2856 | 1.2529 | 1.2074 | 1.0316 | 0.54274 | 0.23827 | 0.12983
BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | YES | 9.5115 | 9.0273 | 8.3634 | 7.6166 | 6.5229 | 5.3996 | 4.2759 | 3.2821 | 2.2005 | 1.3642 | -1.3262 | -3.0979 | -3.5827 | -3.7363 | 11.0003 | 10.64 | 10.0635 | 9.4388 | 8.8058 | 8.1238 | 7.4225 | 6.8016 | 6.0845 | 5.5059 | 3.5992 | 2.4127 | 2.0849 | 1.8498 | 10.0073 | 9.5756 | 8.9695 | 8.2947 | 7.3057 | 6.2913 | 5.2809 | 4.4053 | 3.4546 | 2.7321 | 0.39188 | -1.0546 | -1.4508 | -1.5881
| REDGORTON | CT |  |  | 9.5784 | 9.1481 | 8.5186 | 7.8208 | 6.7503 | 5.6982 | 4.6065 | 3.6745 | 2.7373 | 1.9434 | -0.83546 | -3.0979 | -3.5827 | -3.7363 | 11.0003 | 10.64 | 10.0635 | 9.4388 | 8.8058 | 8.1238 | 7.4225 | 6.9033 | 6.2691 | 5.7053 | 3.768 | 2.4127 | 2.0849 | 1.8498 | 10.0672 | 9.6841 | 9.109 | 8.4805 | 7.5151 | 6.5666 | 5.5831 | 4.7597 | 3.9349 | 3.2457 | 0.8264 | -1.0546 | -1.4508 | -1.5881
| REDGORTON | LW |  |  | 9.5115 | 9.0273 | 8.3634 | 7.6166 | 6.5229 | 5.3996 | 4.2759 | 3.2821 | 2.2005 | 1.3642 | -1.3262 | -3.0672 | -3.282 | -3.4559 | 11.0082 | 10.6508 | 10.0795 | 9.4637 | 8.8362 | 8.1532 | 7.4437 | 6.8016 | 6.0845 | 5.5059 | 3.5992 | 2.4812 | 2.3504 | 2.2691 | 10.0073 | 9.5756 | 8.9695 | 8.2947 | 7.3057 | 6.2913 | 5.2809 | 4.4053 | 3.4546 | 2.7321 | 0.39188 | -1.0211 | -1.1778 | -1.3393
| REDGORTON | ST |  |  | 9.622 | 9.2633 | 8.731 | 8.1369 | 7.5595 | 6.9408 | 6.287 | 5.7488 | 5.1798 | 4.5923 | 2.6083 | -0.012077 | -0.76029 | -1.0798 | 11.0239 | 10.6786 | 10.1207 | 9.526 | 8.9355 | 8.305 | 7.6442 | 7.1601 | 6.6538 | 6.1987 | 4.6713 | 3.4073 | 3.1323 | 2.8816 | 10.1054 | 9.7869 | 9.2993 | 8.7623 | 8.2461 | 7.693 | 7.1099 | 6.6449 | 6.1554 | 5.6507 | 3.9205 | 1.7359 | 1.0809 | 0.79755
| REDGORTON | SP |  |  | 9.6686 | 9.3396 | 8.8341 | 8.2825 | 7.6767 | 7.0288 | 6.3496 | 5.7924 | 5.1883 | 4.58 | 2.5216 | -0.19515 | -1.623 | -2.0301 | 11.0251 | 10.6825 | 10.1265 | 9.5368 | 8.9507 | 8.3256 | 7.6707 | 7.1938 | 6.6989 | 6.258 | 4.7944 | 3.6154 | 2.7229 | 2.148 | 10.1488 | 9.8577 | 9.3951 | 8.8966 | 8.3536 | 7.7732 | 7.1659 | 6.6835 | 6.1632 | 5.6384 | 3.8088 | 1.5608 | 0.33033 | -0.037988
REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | 19.1109 | 17.6719 | 16.5863 | 15.4569 | 14.5491 | 13.643 | 12.2664 | 10.6929 | 8.7964 | 6.5391 | 0.8487 | -2.3571 | -2.7667 | -2.9358 | 21.859 | 20.3914 | 19.3268 | 18.2438 | 17.471 | 16.7337 | 15.4709 | 14.0347 | 12.293 | 10.1663 | 4.8668 | 2.1202 | 1.9444 | 1.8138 | 20.9745 | 19.5855 | 18.5441 | 17.4569 | 16.6161 | 15.7868 | 14.5019 | 13.0258 | 11.2337 | 9.0949 | 3.6819 | 0.50529 | 0.00084117 | -0.19804
| REDMOSS | CT |  |  | 19.1109 | 17.6719 | 16.5863 | 15.4569 | 14.5491 | 13.643 | 12.2783 | 10.7599 | 8.9244 | 6.7417 | 1.4292 | -1.672 | -2.2192 | -2.428 | 21.859 | 20.3914 | 19.3268 | 18.2438 | 17.471 | 16.7337 | 15.4709 | 14.057 | 12.3421 | 10.2488 | 5.1799 | 2.7879 | 2.3899 | 2.0948 | 20.9745 | 19.5855 | 18.5441 | 17.4569 | 16.6161 | 15.7868 | 14.5019 | 13.0708 | 11.329 | 9.2586 | 4.236 | 1.0892 | 0.40889 | 0.16486
| REDMOSS | LW |  |  | 19.1366 | 17.7082 | 16.6195 | 15.4956 | 14.5917 | 13.6745 | 12.2664 | 10.6929 | 8.7964 | 6.5391 | 0.8487 | -2.3571 | -2.7667 | -2.9358 | 21.8741 | 20.4125 | 19.3521 | 18.276 | 17.5059 | 16.7629 | 15.4755 | 14.0347 | 12.293 | 10.1663 | 4.8668 | 2.1202 | 1.9444 | 1.8138 | 20.9925 | 19.6103 | 18.5825 | 17.5028 | 16.6659 | 15.8275 | 14.5042 | 13.0258 | 11.2337 | 9.0949 | 3.6819 | 0.50529 | 0.00084117 | -0.19804
| REDMOSS | ST |  |  | 19.2369 | 17.889 | 16.9044 | 15.9173 | 15.228 | 14.5557 | 13.3855 | 12.0609 | 10.4421 | 8.4477 | 3.4523 | -0.552 | -1.7958 | -2.0764 | 21.9139 | 20.486 | 19.4674 | 18.4499 | 17.7688 | 17.1304 | 15.9456 | 14.6049 | 12.9715 | 10.9512 | 6.1665 | 3.3044 | 2.3171 | 2.0849 | 21.0456 | 19.7076 | 18.7415 | 17.778 | 17.1187 | 16.4921 | 15.3685 | 14.0972 | 12.5142 | 10.5802 | 5.7863 | 2.2507 | 1.228 | 0.98397
| REDMOSS | SP |  |  | 19.2471 | 17.9115 | 16.9383 | 15.969 | 15.2967 | 14.6483 | 13.5221 | 12.2363 | 10.668 | 8.7639 | 4.212 | 0.979 | -0.89736 | -1.3629 | 21.9197 | 20.497 | 19.4828 | 18.4731 | 17.799 | 17.1696 | 16.0006 | 14.6737 | 13.0579 | 11.0744 | 6.4701 | 4.0993 | 3.0066 | 2.6035 | 21.053 | 19.7219 | 18.7618 | 17.8086 | 17.1589 | 16.5447 | 15.4425 | 14.1911 | 12.6568 | 10.8065 | 6.4312 | 3.546 | 1.9917 | 1.6004
CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | 2.8892 | 2.8853 | 2.8643 | 2.8301 | 2.7515 | 2.6566 | 2.562 | 2.4515 | 2.2938 | 2.1923 | 1.8532 | 1.6778 | 1.6475 | 1.5056 | 3.0007 | 2.9929 | 2.9795 | 2.9589 | 2.9094 | 2.8683 | 2.813 | 2.755 | 2.6781 | 2.6184 | 2.3441 | 2.2738 | 2.2687 | 2.2065 | 2.9068 | 2.8977 | 2.8755 | 2.8441 | 2.7766 | 2.6953 | 2.5987 | 2.486 | 2.3509 | 2.2617 | 1.8789 | 1.7768 | 1.7987 | 1.7118
| RHICONICH | CT |  |  | 2.8974 | 2.8966 | 2.895 | 2.8687 | 2.7868 | 2.7154 | 2.5877 | 2.4515 | 2.312 | 2.24 | 1.958 | 1.7827 | 1.7921 | 1.7828 | 3.0066 | 2.9996 | 2.9879 | 2.9589 | 2.9094 | 2.8683 | 2.813 | 2.755 | 2.6965 | 2.6455 | 2.4052 | 2.2939 | 2.2911 | 2.2786 | 2.9257 | 2.9197 | 2.9029 | 2.86 | 2.7766 | 2.7055 | 2.5987 | 2.486 | 2.3768 | 2.3026 | 1.9739 | 1.8167 | 1.8293 | 1.8276
| RHICONICH | LW |  |  | 2.8892 | 2.8853 | 2.8643 | 2.8301 | 2.7515 | 2.6566 | 2.562 | 2.4637 | 2.2938 | 2.1923 | 1.8532 | 1.6778 | 1.7188 | 1.6971 | 3.0007 | 2.9929 | 2.9795 | 2.9599 | 2.9258 | 2.88 | 2.8341 | 2.7711 | 2.6781 | 2.6184 | 2.3441 | 2.2738 | 2.2885 | 2.2796 | 2.9068 | 2.8977 | 2.8755 | 2.8441 | 2.777 | 2.6953 | 2.6141 | 2.5125 | 2.3509 | 2.2617 | 1.8789 | 1.7768 | 1.8122 | 1.7911
| RHICONICH | ST |  |  | 2.898 | 2.8977 | 2.8974 | 2.8964 | 2.8949 | 2.8922 | 2.8753 | 2.8515 | 2.8132 | 2.748 | 2.5528 | 2.1046 | 1.8875 | 1.8383 | 3.0103 | 3.0072 | 3.0034 | 2.9939 | 2.9838 | 2.976 | 2.9652 | 2.9464 | 2.9297 | 2.896 | 2.7836 | 2.442 | 2.3642 | 2.3386 | 2.9261 | 2.9215 | 2.9163 | 2.9039 | 2.8921 | 2.8829 | 2.8695 | 2.8468 | 2.8212 | 2.7715 | 2.609 | 2.152 | 2.0348 | 2.0012
| RHICONICH | SP |  |  | 2.8986 | 2.8985 | 2.8985 | 2.8985 | 2.8949 | 2.8765 | 2.8481 | 2.8094 | 2.7682 | 2.6989 | 2.5078 | 2.0384 | 1.6475 | 1.5056 | 3.0132 | 3.0108 | 3.0085 | 3.0056 | 2.9941 | 2.9829 | 2.9695 | 2.953 | 2.9319 | 2.895 | 2.7979 | 2.5494 | 2.2687 | 2.2065 | 2.9316 | 2.9286 | 2.9265 | 2.9237 | 2.9034 | 2.8842 | 2.8616 | 2.8344 | 2.8009 | 2.7429 | 2.5791 | 2.1882 | 1.7987 | 1.7118
DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | 9.9576 | 9.7379 | 9.1853 | 8.6845 | 6.6848 | 4.5523 | 2.4518 | 0.11524 | -0.88253 | -1.7675 | -4.8134 | -9.7329 | -12.5168 | -14.0158 | 11.9904 | 11.6812 | 11.4479 | 11.2318 | 10.4475 | 9.602 | 8.7669 | 7.8016 | 7.3204 | 6.864 | 5.292 | 1.9658 | -0.23892 | -2.6293 | 10.4706 | 9.8439 | 9.3661 | 8.9243 | 7.1628 | 5.2895 | 3.4425 | 1.3726 | 0.47226 | -0.33647 | -3.1099 | -7.4272 | -9.7524 | -10.9302
| ROSEBANK STREET | CT |  |  | 9.9576 | 9.7964 | 9.5975 | 9.3397 | 7.4485 | 5.3484 | 4.2408 | 3.2059 | 2.0713 | 0.74503 | -3.3447 | -9.7329 | -12.5168 | -14.0158 | 11.9904 | 11.7247 | 11.5184 | 11.3512 | 10.573 | 9.7036 | 9.2017 | 8.6954 | 8.1442 | 7.4951 | 5.4687 | 1.9658 | -0.23892 | -2.6293 | 10.5274 | 10.0724 | 9.7244 | 9.4914 | 7.8222 | 5.9748 | 4.9981 | 4.0751 | 3.0632 | 1.8736 | -1.7825 | -7.4272 | -9.7524 | -10.9302
| ROSEBANK STREET | LW |  |  | 9.9852 | 9.7379 | 9.1853 | 8.6845 | 6.6848 | 4.5523 | 2.4518 | 0.11524 | -0.88253 | -1.7675 | -4.8134 | -9.224 | -11.3262 | -12.6815 | 11.9949 | 11.6812 | 11.4479 | 11.2318 | 10.4475 | 9.602 | 8.7669 | 7.8016 | 7.3204 | 6.864 | 5.292 | 3.0479 | 2.1373 | 1.4962 | 10.4706 | 9.8439 | 9.3661 | 8.9243 | 7.1628 | 5.2895 | 3.4425 | 1.3726 | 0.47226 | -0.33647 | -3.1099 | -7.0396 | -8.7576 | -9.8094
| ROSEBANK STREET | ST |  |  | 10.0197 | 9.9036 | 9.8337 | 9.7799 | 9.7251 | 9.6461 | 9.5563 | 9.4529 | 9.336 | 9.1764 | 8.5259 | 5.0816 | 2.1588 | -0.14857 | 12.191 | 12.0662 | 11.9686 | 11.8618 | 11.7644 | 11.6497 | 11.5246 | 11.3617 | 11.2417 | 11.0332 | 10.2486 | 7.7187 | 5.236 | 2.5587 | 10.9188 | 10.8197 | 10.7029 | 10.5611 | 10.4446 | 10.3162 | 10.1816 | 9.9833 | 9.911 | 9.6668 | 8.73 | 5.5313 | 3.0413 | 1.1521
| ROSEBANK STREET | SP |  |  | 10.0261 | 9.9169 | 9.8534 | 9.811 | 9.7714 | 9.6995 | 9.6261 | 9.55 | 9.4514 | 9.3384 | 8.8329 | 6.2091 | 4.0315 | 2.9761 | 12.2422 | 12.1462 | 12.0685 | 12.0012 | 11.8917 | 11.7465 | 11.6117 | 11.466 | 11.2884 | 11.0494 | 10.1525 | 7.688 | 4.0287 | -0.7891 | 10.9648 | 10.8934 | 10.8527 | 10.8278 | 10.7782 | 10.603 | 10.4702 | 10.3342 | 10.1704 | 9.9279 | 9.0341 | 6.6549 | 4.6136 | 3.7545
KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | YES | 1.3887 | 1.3363 | 1.2908 | 1.2281 | 1.1603 | 1.0751 | 0.92583 | 0.74833 | 0.51954 | 0.30701 | -0.298 | -0.88663 | -0.93634 | -0.97582 | 2.6528 | 2.6128 | 2.5712 | 2.5033 | 2.416 | 2.3268 | 2.2295 | 2.1332 | 2.0051 | 1.8637 | 1.4673 | 1.0816 | 1.0446 | 0.97699 | 1.8225 | 1.7542 | 1.6852 | 1.6063 | 1.4885 | 1.3624 | 1.2373 | 1.0938 | 0.87738 | 0.68152 | 0.10969 | -0.44687 | -0.49118 | -0.5267
| ROTHES | CT |  |  | 1.3887 | 1.3363 | 1.2908 | 1.2281 | 1.1603 | 1.0968 | 0.94008 | 0.76431 | 0.56884 | 0.39416 | -0.10402 | -0.68677 | -0.81724 | -0.86766 | 2.6586 | 2.6197 | 2.5712 | 2.5033 | 2.416 | 2.3268 | 2.2295 | 2.1359 | 2.0251 | 1.9132 | 1.5983 | 1.2509 | 1.2004 | 1.1797 | 1.8225 | 1.7617 | 1.6936 | 1.6144 | 1.4966 | 1.3755 | 1.2373 | 1.1021 | 0.92722 | 0.76298 | 0.29418 | -0.25095 | -0.36801 | -0.41312
| ROTHES | LW |  |  | 1.4003 | 1.3445 | 1.3025 | 1.2447 | 1.1799 | 1.0751 | 0.92583 | 0.74833 | 0.51954 | 0.30701 | -0.298 | -0.88663 | -0.93634 | -0.97582 | 2.6528 | 2.6128 | 2.5741 | 2.5082 | 2.4221 | 2.3304 | 2.2425 | 2.1332 | 2.0051 | 1.8637 | 1.4673 | 1.0816 | 1.0646 | 1.0496 | 1.8298 | 1.7542 | 1.6852 | 1.6063 | 1.4885 | 1.3624 | 1.2413 | 1.0938 | 0.87738 | 0.68152 | 0.10969 | -0.44687 | -0.49118 | -0.5267
| ROTHES | ST |  |  | 1.4126 | 1.372 | 1.347 | 1.3082 | 1.2763 | 1.2525 | 1.2268 | 1.1983 | 1.1601 | 1.1109 | 0.74782 | -0.17989 | -0.67532 | -0.79756 | 2.6653 | 2.6291 | 2.6065 | 2.5731 | 2.551 | 2.5312 | 2.5022 | 2.4607 | 2.4021 | 2.3266 | 2.0428 | 1.3771 | 1.0446 | 0.97699 | 1.8616 | 1.8149 | 1.7828 | 1.7415 | 1.698 | 1.6565 | 1.6109 | 1.5605 | 1.4875 | 1.3922 | 1.0319 | 0.18926 | -0.27443 | -0.38691
| ROTHES | SP |  |  | 1.4144 | 1.3758 | 1.3531 | 1.3178 | 1.2883 | 1.2696 | 1.248 | 1.2243 | 1.1982 | 1.1606 | 0.87756 | 0.09545 | -0.60975 | -0.81869 | 2.6698 | 2.6361 | 2.6167 | 2.587 | 2.5573 | 2.5368 | 2.5089 | 2.4776 | 2.444 | 2.3863 | 2.2096 | 1.6939 | 1.1994 | 1.0616 | 1.8648 | 1.8216 | 1.7937 | 1.7569 | 1.7101 | 1.6698 | 1.6251 | 1.5768 | 1.5252 | 1.4449 | 1.2068 | 0.47574 | -0.1957 | -0.39224
DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | YES | 17.8642 | 17.7799 | 17.6869 | 17.5871 | 17.1681 | 16.6747 | 16.1429 | 15.4587 | 14.9466 | 14.506 | 12.992 | 10.7563 | 9.4446 | 8.9671 | 18.8321 | 18.7911 | 18.7475 | 18.698 | 18.512 | 18.2904 | 18.0561 | 17.7377 | 17.4859 | 17.2608 | 16.3845 | 15.2924 | 14.7175 | 14.3603 | 17.9312 | 17.8579 | 17.7743 | 17.6836 | 17.3121 | 16.8742 | 16.4019 | 15.7831 | 15.3127 | 14.9025 | 13.4858 | 11.5188 | 10.4667 | 10.0492
| ROTHESAY | CT |  |  | 17.9141 | 17.858 | 17.7931 | 17.7025 | 17.26 | 16.7443 | 16.3753 | 15.9429 | 15.4762 | 14.9572 | 13.2756 | 10.7563 | 9.4446 | 8.9671 | 18.849 | 18.8171 | 18.7817 | 18.7286 | 18.5255 | 18.2904 | 18.1191 | 17.9102 | 17.6833 | 17.4277 | 16.5383 | 15.2924 | 14.7175 | 14.3603 | 17.9742 | 17.9254 | 17.8659 | 17.7799 | 17.3846 | 16.9252 | 16.5954 | 16.2026 | 15.7787 | 15.3043 | 13.7609 | 11.5188 | 10.4667 | 10.0492
| ROTHESAY | LW |  |  | 17.8642 | 17.7799 | 17.6869 | 17.5871 | 17.1681 | 16.6747 | 16.1429 | 15.4587 | 14.9466 | 14.506 | 12.992 | 11.1988 | 10.3822 | 10.062 | 18.8321 | 18.7911 | 18.7475 | 18.698 | 18.512 | 18.292 | 18.0561 | 17.7377 | 17.4859 | 17.2608 | 16.3845 | 15.4401 | 15.1333 | 15.0262 | 17.9312 | 17.8579 | 17.7743 | 17.6836 | 17.3121 | 16.8742 | 16.4019 | 15.7831 | 15.3127 | 14.9025 | 13.4858 | 11.8386 | 11.1245 | 10.877
| ROTHESAY | ST |  |  | 17.9933 | 17.9571 | 17.9301 | 17.8909 | 17.8498 | 17.8042 | 17.7482 | 17.6888 | 17.6306 | 17.5056 | 17.0572 | 15.6164 | 14.6043 | 13.9827 | 18.8857 | 18.8637 | 18.8468 | 18.8214 | 18.7895 | 18.7544 | 18.7105 | 18.6643 | 18.6149 | 18.5259 | 18.1961 | 17.2096 | 16.5912 | 16.1554 | 18.0444 | 18.0132 | 17.9875 | 17.9494 | 17.9096 | 17.8658 | 17.8117 | 17.7544 | 17.6972 | 17.5775 | 17.1458 | 15.7786 | 14.8584 | 14.313
| ROTHESAY | SP |  |  | 18.0078 | 17.9802 | 17.9602 | 17.9368 | 17.8767 | 17.8122 | 17.7429 | 17.6755 | 17.5837 | 17.4619 | 17.0779 | 16.1087 | 15.3089 | 15.1187 | 18.8918 | 18.8738 | 18.8599 | 18.8432 | 18.81 | 18.7718 | 18.7276 | 18.684 | 18.6187 | 18.5337 | 18.2525 | 17.4955 | 16.6534 | 16.0287 | 18.0571 | 18.0337 | 18.0145 | 17.9916 | 17.9367 | 17.8777 | 17.8135 | 17.751 | 17.6639 | 17.5493 | 17.1865 | 16.2615 | 15.4848 | 15.3067
THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | 2.4975 | 2.4947 | 2.4873 | 2.4712 | 2.4332 | 2.3928 | 2.3531 | 2.314 | 2.2752 | 2.2583 | 2.1903 | 2.168 | 2.1859 | 2.1696 | 2.3825 | 2.3814 | 2.3757 | 2.3672 | 2.352 | 2.3335 | 2.3144 | 2.2956 | 2.2763 | 2.2643 | 2.2124 | 2.1921 | 2.1977 | 2.1876 | 2.5071 | 2.5055 | 2.4986 | 2.4861 | 2.454 | 2.4217 | 2.3908 | 2.3598 | 2.3287 | 2.3143 | 2.2671 | 2.2428 | 2.257 | 2.2486
| ROUSAY | CT |  |  | 2.4975 | 2.4947 | 2.4919 | 2.4867 | 2.4508 | 2.4148 | 2.3816 | 2.3443 | 2.311 | 2.2928 | 2.2306 | 2.1884 | 2.2041 | 2.2068 | 2.3871 | 2.385 | 2.3812 | 2.3709 | 2.3542 | 2.3377 | 2.3238 | 2.3073 | 2.2935 | 2.2801 | 2.2312 | 2.1983 | 2.2006 | 2.1978 | 2.5082 | 2.5055 | 2.5029 | 2.4979 | 2.473 | 2.4441 | 2.4158 | 2.3851 | 2.356 | 2.3425 | 2.3046 | 2.2724 | 2.2843 | 2.2832
| ROUSAY | LW |  |  | 2.4981 | 2.4965 | 2.4873 | 2.4712 | 2.4332 | 2.3928 | 2.3531 | 2.314 | 2.2752 | 2.2583 | 2.1903 | 2.168 | 2.1859 | 2.1738 | 2.3825 | 2.3814 | 2.3757 | 2.3672 | 2.352 | 2.3335 | 2.3144 | 2.2956 | 2.2763 | 2.2643 | 2.2124 | 2.1921 | 2.1977 | 2.1932 | 2.5071 | 2.5072 | 2.4986 | 2.4861 | 2.454 | 2.4217 | 2.3908 | 2.3598 | 2.3287 | 2.3143 | 2.2671 | 2.2428 | 2.257 | 2.2486
| ROUSAY | ST |  |  | 2.4999 | 2.499 | 2.4981 | 2.4964 | 2.4951 | 2.4933 | 2.4911 | 2.4889 | 2.4858 | 2.4733 | 2.4367 | 2.3348 | 2.306 | 2.2868 | 2.3877 | 2.3862 | 2.3848 | 2.3816 | 2.3803 | 2.378 | 2.3744 | 2.3721 | 2.3678 | 2.3595 | 2.3353 | 2.2574 | 2.2375 | 2.2268 | 2.5105 | 2.5096 | 2.5088 | 2.5071 | 2.5058 | 2.5041 | 2.502 | 2.4999 | 2.4972 | 2.4898 | 2.4606 | 2.387 | 2.3435 | 2.3257
| ROUSAY | SP |  |  | 2.5003 | 2.4996 | 2.4988 | 2.4979 | 2.4957 | 2.4851 | 2.4731 | 2.4576 | 2.4433 | 2.4204 | 2.372 | 2.2572 | 2.1898 | 2.1696 | 2.3884 | 2.3872 | 2.3863 | 2.3851 | 2.3784 | 2.3742 | 2.3694 | 2.3614 | 2.3548 | 2.3445 | 2.3217 | 2.253 | 2.2024 | 2.1876 | 2.5108 | 2.5101 | 2.5094 | 2.5086 | 2.5069 | 2.4975 | 2.487 | 2.4756 | 2.4639 | 2.4455 | 2.405 | 2.3179 | 2.2707 | 2.2528
CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | 11.7918 | 11.3618 | 11.0357 | 10.7451 | 9.925 | 9.0512 | 8.0782 | 7.1119 | 6.3391 | 5.5482 | 2.8216 | -1.1815 | -3.4072 | -4.6094 | 14.4004 | 14.2036 | 14.018 | 13.7975 | 13.3505 | 12.8476 | 12.3909 | 11.9069 | 11.4651 | 10.9719 | 9.1453 | 6.5188 | 5.0626 | 3.6727 | 12.3802 | 11.989 | 11.6855 | 11.4063 | 10.6595 | 9.8585 | 8.9626 | 8.0804 | 7.3638 | 6.6206 | 4.0623 | 0.48173 | -1.3644 | -2.288
| RUTHRIESTON | CT |  |  | 11.8023 | 11.4827 | 11.2551 | 11.0119 | 10.1909 | 9.2703 | 8.5004 | 7.8393 | 7.1199 | 6.2393 | 3.3729 | -1.1815 | -3.4072 | -4.6094 | 14.4004 | 14.2036 | 14.0212 | 13.7975 | 13.3505 | 12.8476 | 12.3909 | 12.0134 | 11.6035 | 11.0901 | 9.3228 | 6.5188 | 5.0626 | 3.6727 | 12.3808 | 12.0853 | 11.8651 | 11.6219 | 10.8699 | 10.0259 | 9.3117 | 8.7044 | 8.0439 | 7.2314 | 4.5917 | 0.48173 | -1.3644 | -2.288
| RUTHRIESTON | LW |  |  | 11.7918 | 11.3618 | 11.0357 | 10.7451 | 9.925 | 9.0512 | 8.0782 | 7.1119 | 6.3391 | 5.5482 | 2.8216 | -0.87364 | -2.5629 | -3.5452 | 14.4376 | 14.2144 | 14.018 | 13.8103 | 13.3947 | 12.9318 | 12.4044 | 11.9069 | 11.4651 | 10.9719 | 9.1453 | 6.8565 | 6.1311 | 5.6546 | 12.3802 | 11.989 | 11.6855 | 11.4063 | 10.6595 | 9.8585 | 8.9626 | 8.0804 | 7.3638 | 6.6206 | 4.0623 | 0.65446 | -0.67224 | -1.4031
| RUTHRIESTON | ST |  |  | 12.1443 | 12.0495 | 11.9465 | 11.8107 | 11.6682 | 11.5184 | 11.3652 | 11.2045 | 11.082 | 10.8218 | 9.8181 | 6.5336 | 4.2028 | 2.7783 | 14.6096 | 14.5432 | 14.4701 | 14.3733 | 14.2742 | 14.1653 | 14.0477 | 13.9189 | 13.795 | 13.5868 | 12.7757 | 10.1967 | 8.3603 | 6.8752 | 12.7026 | 12.6166 | 12.5225 | 12.3965 | 12.265 | 12.1256 | 11.9818 | 11.8298 | 11.7098 | 11.4611 | 10.51 | 7.4177 | 5.397 | 4.2756
| RUTHRIESTON | SP |  |  | 12.1855 | 12.1295 | 12.055 | 11.9726 | 11.8378 | 11.6811 | 11.5303 | 11.3763 | 11.2034 | 10.9659 | 10.1193 | 7.7189 | 5.1612 | 4.0921 | 14.6183 | 14.5683 | 14.5044 | 14.4315 | 14.3367 | 14.2266 | 14.1102 | 13.9861 | 13.8397 | 13.6447 | 12.931 | 10.8384 | 7.9972 | 5.3837 | 12.7374 | 12.6863 | 12.6176 | 12.5403 | 12.417 | 12.2733 | 12.1332 | 11.9895 | 11.8264 | 11.6044 | 10.8239 | 8.6176 | 6.2717 | 5.4299
FORT WILLIAM | SALEN | MINIMUM HEADROOM | NM 69002 65519 | YES | 2.4238 | 2.3553 | 2.2966 | 2.2471 | 2.1375 | 2.0195 | 1.8956 | 1.7483 | 1.5696 | 1.4794 | 1.1362 | 1.0353 | 1.1118 | 1.0847 | 2.7072 | 2.6697 | 2.6382 | 2.6053 | 2.5482 | 2.4878 | 2.433 | 2.3657 | 2.2819 | 2.224 | 1.9761 | 1.8955 | 1.9204 | 1.8977 | 2.5303 | 2.4719 | 2.4198 | 2.373 | 2.265 | 2.1512 | 2.0284 | 1.8867 | 1.7368 | 1.6513 | 1.3087 | 1.2122 | 1.2716 | 1.2499
| SALEN | CT |  |  | 2.4349 | 2.3729 | 2.3176 | 2.2583 | 2.1415 | 2.0195 | 1.9024 | 1.7852 | 1.6681 | 1.5867 | 1.3021 | 1.0946 | 1.1262 | 1.126 | 2.7096 | 2.6741 | 2.6424 | 2.6053 | 2.5482 | 2.4878 | 2.433 | 2.3745 | 2.3188 | 2.2659 | 2.0566 | 1.9201 | 1.9214 | 1.9064 | 2.5413 | 2.489 | 2.4409 | 2.3864 | 2.2741 | 2.1541 | 2.0399 | 1.9249 | 1.8179 | 1.7407 | 1.4536 | 1.2631 | 1.2877 | 1.2878
| SALEN | LW |  |  | 2.4238 | 2.3553 | 2.2966 | 2.2471 | 2.1375 | 2.0212 | 1.8956 | 1.7483 | 1.5696 | 1.4794 | 1.1362 | 1.0353 | 1.1118 | 1.0847 | 2.7072 | 2.6697 | 2.6382 | 2.6115 | 2.5588 | 2.5045 | 2.4427 | 2.3657 | 2.2819 | 2.224 | 1.9761 | 1.8955 | 1.9204 | 1.9107 | 2.5303 | 2.4719 | 2.4198 | 2.373 | 2.265 | 2.1512 | 2.0284 | 1.8867 | 1.7368 | 1.6513 | 1.3087 | 1.2122 | 1.2716 | 1.2499
| SALEN | ST |  |  | 2.4407 | 2.39 | 2.3546 | 2.3294 | 2.32 | 2.3089 | 2.2887 | 2.2684 | 2.2436 | 2.1949 | 2.0335 | 1.6212 | 1.5106 | 1.4746 | 2.7157 | 2.6875 | 2.6672 | 2.6515 | 2.643 | 2.6339 | 2.6179 | 2.6025 | 2.5859 | 2.5534 | 2.4433 | 2.137 | 2.0569 | 2.0258 | 2.5475 | 2.5058 | 2.4761 | 2.4539 | 2.4446 | 2.434 | 2.4148 | 2.3955 | 2.3713 | 2.3227 | 2.1622 | 1.7514 | 1.6319 | 1.591
| SALEN | SP |  |  | 2.4509 | 2.4058 | 2.3765 | 2.3625 | 2.3467 | 2.3282 | 2.306 | 2.2823 | 2.2441 | 2.197 | 2.0297 | 1.5972 | 1.2527 | 1.1217 | 2.7198 | 2.6941 | 2.6764 | 2.6669 | 2.6577 | 2.6472 | 2.6338 | 2.6197 | 2.594 | 2.566 | 2.4729 | 2.2076 | 1.9762 | 1.8977 | 2.5565 | 2.5198 | 2.4957 | 2.4838 | 2.4693 | 2.4526 | 2.4319 | 2.4085 | 2.3706 | 2.324 | 2.1585 | 1.7333 | 1.3954 | 1.2881
TAYNUILT | SALEN 2 | MINIMUM HEADROOM | NM 57252 42849 | YES | 0.027418 | 0.022238 | 0.0085744 | -0.021712 | -0.057632 | -0.088476 | -0.13408 | -0.20797 | -0.28961 | -0.33587 | -0.49521 | -0.56737 | -0.55111 | -0.60505 | 0.95412 | 0.94743 | 0.93274 | 0.90609 | 0.86701 | 0.82604 | 0.77985 | 0.72581 | 0.6494 | 0.59716 | 0.35927 | 0.31566 | 0.31516 | 0.27416 | 0.4489 | 0.43763 | 0.42474 | 0.39637 | 0.35873 | 0.32968 | 0.28547 | 0.23619 | 0.16713 | 0.097658 | -0.11167 | -0.29407 | -0.3505 | -0.39356
| SALEN 2 | CT |  |  | 0.027418 | 0.022238 | 0.0085744 | -0.021712 | -0.057632 | -0.088476 | -0.13408 | -0.20797 | -0.28037 | -0.31696 | -0.4448 | -0.52678 | -0.47567 | -0.45874 | 0.9585 | 0.95411 | 0.93772 | 0.90609 | 0.86701 | 0.82604 | 0.77985 | 0.72923 | 0.68126 | 0.63746 | 0.44703 | 0.33842 | 0.34525 | 0.34008 | 0.4489 | 0.44066 | 0.4274 | 0.39648 | 0.35873 | 0.33074 | 0.28821 | 0.24263 | 0.18502 | 0.1365 | -0.028834 | -0.19225 | -0.20024 | -0.2042
| SALEN 2 | LW |  |  | 0.031593 | 0.023582 | 0.012607 | -0.0069774 | -0.038687 | -0.078256 | -0.13323 | -0.19737 | -0.28961 | -0.33587 | -0.49521 | -0.56737 | -0.53507 | -0.55941 | 0.95412 | 0.94743 | 0.93274 | 0.91318 | 0.8757 | 0.82992 | 0.78363 | 0.72581 | 0.6494 | 0.59716 | 0.35927 | 0.31566 | 0.33074 | 0.32164 | 0.45962 | 0.43763 | 0.42474 | 0.39637 | 0.37081 | 0.32968 | 0.28547 | 0.23619 | 0.16713 | 0.097658 | -0.11167 | -0.29407 | -0.28964 | -0.291
| SALEN 2 | ST |  |  | 0.037897 | 0.035414 | 0.032796 | 0.027339 | 0.020847 | 0.018963 | 0.0094514 | 0.0020685 | -0.011176 | -0.036523 | -0.11812 | -0.32013 | -0.36211 | -0.35589 | 0.96541 | 0.9611 | 0.95622 | 0.94925 | 0.93981 | 0.93317 | 0.91973 | 0.91281 | 0.89479 | 0.86861 | 0.76779 | 0.46608 | 0.42006 | 0.40352 | 0.47002 | 0.46514 | 0.45972 | 0.45293 | 0.43281 | 0.42414 | 0.40102 | 0.37795 | 0.35022 | 0.30291 | 0.15597 | -0.20979 | -0.3505 | -0.35966
| SALEN 2 | SP |  |  | 0.040821 | 0.040313 | 0.040046 | 0.039174 | 0.029029 | 0.023317 | 0.011297 | -0.0019746 | -0.018557 | -0.045738 | -0.11579 | -0.36498 | -0.55111 | -0.60505 | 0.96702 | 0.96455 | 0.96148 | 0.95748 | 0.9467 | 0.93491 | 0.91956 | 0.90418 | 0.88047 | 0.85302 | 0.7699 | 0.53578 | 0.31516 | 0.27416 | 0.47054 | 0.46677 | 0.46246 | 0.45715 | 0.43665 | 0.42748 | 0.40468 | 0.38122 | 0.35521 | 0.31246 | 0.21738 | -0.067161 | -0.33034 | -0.39356
THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | 0.32679 | 0.33399 | 0.90541 | 0.87725 | 0.7982 | 0.72874 | 0.6545 | 0.57404 | 0.47787 | 0.42177 | 0.19073 | 0.10415 | 0.12932 | 0.10154 | 0.62578 | 0.62486 | 1.1592 | 1.1439 | 1.1069 | 1.0748 | 1.0373 | 0.99373 | 0.94237 | 0.90432 | 0.72883 | 0.66127 | 0.67171 | 0.66365 | 0.37567 | 0.38112 | 0.90892 | 0.88306 | 0.8118 | 0.74938 | 0.68177 | 0.6077 | 0.51935 | 0.46581 | 0.24301 | 0.15928 | 0.18678 | 0.16206
| SANDAY | CT |  |  | 0.36908 | 0.37869 | 0.95346 | 0.91249 | 0.83093 | 0.76239 | 0.68713 | 0.60768 | 0.53 | 0.48042 | 0.29953 | 0.1726 | 0.20105 | 0.20741 | 0.64072 | 0.64061 | 1.1751 | 1.1508 | 1.1104 | 1.0764 | 1.0404 | 1.0031 | 0.9647 | 0.93166 | 0.79701 | 0.70033 | 0.70428 | 0.70084 | 0.41263 | 0.42019 | 0.95068 | 0.91244 | 0.83836 | 0.77618 | 0.7082 | 0.63665 | 0.5662 | 0.51907 | 0.34497 | 0.22309 | 0.2432 | 0.24728
| SANDAY | LW |  |  | 0.32679 | 0.33399 | 0.90541 | 0.87725 | 0.7982 | 0.72874 | 0.6545 | 0.57404 | 0.47787 | 0.42177 | 0.19073 | 0.10415 | 0.13808 | 0.11511 | 0.62578 | 0.62486 | 1.1592 | 1.1439 | 1.1069 | 1.0748 | 1.0373 | 0.99373 | 0.94237 | 0.90432 | 0.72883 | 0.66127 | 0.67171 | 0.66365 | 0.37567 | 0.38112 | 0.90892 | 0.88306 | 0.8118 | 0.74938 | 0.68177 | 0.6077 | 0.51935 | 0.46581 | 0.24301 | 0.15928 | 0.18678 | 0.16873
| SANDAY | ST |  |  | 0.35875 | 0.35363 | 0.93827 | 0.93203 | 0.92531 | 0.91776 | 0.90663 | 0.89602 | 0.87937 | 0.84828 | 0.74081 | 0.43917 | 0.31263 | 0.2902 | 0.63944 | 0.63638 | 1.1778 | 1.1727 | 1.1669 | 1.1612 | 1.1528 | 1.1433 | 1.1315 | 1.1112 | 1.0356 | 0.80709 | 0.72173 | 0.7128 | 0.40415 | 0.39941 | 0.93935 | 0.93321 | 0.92651 | 0.91919 | 0.90838 | 0.89771 | 0.88173 | 0.8523 | 0.75014 | 0.45028 | 0.37804 | 0.35721
| SANDAY | SP |  |  | 0.36093 | 0.35563 | 0.94253 | 0.93755 | 0.90535 | 0.87751 | 0.84205 | 0.8061 | 0.76269 | 0.7027 | 0.58185 | 0.32686 | 0.12932 | 0.10154 | 0.64124 | 0.63837 | 1.1812 | 1.1775 | 1.1635 | 1.1518 | 1.1355 | 1.1196 | 1.0972 | 1.0689 | 1.0043 | 0.85451 | 0.69095 | 0.66679 | 0.40633 | 0.4015 | 0.94358 | 0.9388 | 0.91007 | 0.88536 | 0.85349 | 0.82135 | 0.78169 | 0.72758 | 0.61678 | 0.38002 | 0.18768 | 0.16206
DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | YES | 4.1997 | 4.1917 | 4.1574 | 4.1091 | 3.9529 | 3.7825 | 3.6069 | 3.385 | 3.1156 | 2.9463 | 2.2474 | 1.8724 | 1.7968 | 1.753 | 5.4744 | 5.4639 | 5.4428 | 5.4028 | 5.3187 | 5.2339 | 5.1368 | 5.0306 | 4.8755 | 4.7633 | 4.2816 | 4.0343 | 3.9716 | 3.921 | 4.6425 | 4.6335 | 4.6012 | 4.5557 | 4.4035 | 4.236 | 4.0634 | 3.846 | 3.583 | 3.4157 | 2.7299 | 2.3639 | 2.2798 | 2.2433
| SANDBANK | CT |  |  | 4.2331 | 4.2293 | 4.1991 | 4.1285 | 3.9669 | 3.8065 | 3.6073 | 3.4053 | 3.2096 | 3.0598 | 2.5014 | 1.8724 | 1.7968 | 1.753 | 5.4831 | 5.4736 | 5.4515 | 5.4028 | 5.3187 | 5.2339 | 5.1368 | 5.0364 | 4.9269 | 4.8304 | 4.4579 | 4.0343 | 3.9716 | 3.921 | 4.6709 | 4.6656 | 4.6363 | 4.5685 | 4.4204 | 4.2678 | 4.0723 | 3.8737 | 3.6811 | 3.5335 | 2.9859 | 2.3639 | 2.2798 | 2.2433
| SANDBANK | LW |  |  | 4.1997 | 4.1917 | 4.1574 | 4.1091 | 3.9529 | 3.7825 | 3.6069 | 3.385 | 3.1156 | 2.9463 | 2.2474 | 1.9037 | 1.8803 | 1.8091 | 5.4744 | 5.4639 | 5.4428 | 5.4133 | 5.3384 | 5.2544 | 5.1644 | 5.0306 | 4.8755 | 4.7633 | 4.2816 | 4.0551 | 4.0437 | 4.0127 | 4.6425 | 4.6335 | 4.6012 | 4.5557 | 4.4035 | 4.236 | 4.0634 | 3.846 | 3.583 | 3.4157 | 2.7299 | 2.3891 | 2.3656 | 2.3001
| SANDBANK | ST |  |  | 4.2358 | 4.2253 | 4.2162 | 4.1973 | 4.1908 | 4.1779 | 4.1603 | 4.1429 | 4.1075 | 4.0367 | 3.7846 | 2.9722 | 2.7519 | 2.6661 | 5.4925 | 5.4851 | 5.4782 | 5.4622 | 5.4524 | 5.4385 | 5.4212 | 5.4033 | 5.3762 | 5.3274 | 5.1493 | 4.5383 | 4.3873 | 4.3248 | 4.6755 | 4.6655 | 4.6567 | 4.6378 | 4.6303 | 4.6166 | 4.5985 | 4.5803 | 4.5458 | 4.4777 | 4.2321 | 3.4306 | 3.201 | 3.1116
| SANDBANK | SP |  |  | 4.2469 | 4.2431 | 4.2398 | 4.2357 | 4.2028 | 4.1718 | 4.1318 | 4.09 | 4.0271 | 3.9379 | 3.6588 | 3.0457 | 2.3884 | 2.2691 | 5.4965 | 5.4925 | 5.4875 | 5.4815 | 5.4647 | 5.4482 | 5.4259 | 5.4032 | 5.3636 | 5.3134 | 5.1487 | 4.7585 | 4.2602 | 4.1249 | 4.6852 | 4.6814 | 4.6776 | 4.6729 | 4.643 | 4.6147 | 4.5777 | 4.536 | 4.4731 | 4.3848 | 4.1087 | 3.505 | 2.8597 | 2.7384
SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | 3.2129 | 3.1754 | 3.1024 | 3.0102 | 2.7904 | 2.5569 | 2.2966 | 1.9679 | 1.6833 | 1.5516 | 1.0613 | 1.0377 | 1.1842 | 1.0874 | 3.5081 | 3.4821 | 3.4381 | 3.3786 | 3.2568 | 3.1241 | 2.9788 | 2.8144 | 2.6658 | 2.5677 | 2.2104 | 2.1781 | 2.2034 | 2.075 | 3.1016 | 3.0518 | 2.9672 | 2.8538 | 2.6124 | 2.3516 | 2.0705 | 1.7727 | 1.509 | 1.3678 | 0.86675 | 0.84038 | 0.96921 | 0.88389
| SANDWICK | CT |  |  | 3.2767 | 3.2618 | 3.2065 | 3.1022 | 2.8632 | 2.6347 | 2.4582 | 2.2306 | 1.992 | 1.8825 | 1.3489 | 1.1859 | 1.3468 | 1.3911 | 3.5213 | 3.5012 | 3.4569 | 3.3808 | 3.2649 | 3.1533 | 3.0601 | 2.9483 | 2.8457 | 2.7724 | 2.3476 | 2.2232 | 2.2621 | 2.2449 | 3.1388 | 3.1045 | 3.0246 | 2.8843 | 2.6553 | 2.4356 | 2.2501 | 2.0283 | 1.8252 | 1.7052 | 1.1299 | 0.97287 | 1.1141 | 1.1534
| SANDWICK | LW |  |  | 3.2129 | 3.1754 | 3.1024 | 3.0102 | 2.7904 | 2.5569 | 2.2966 | 1.9679 | 1.6833 | 1.5516 | 1.0613 | 1.0377 | 1.1842 | 1.1015 | 3.5081 | 3.4821 | 3.4381 | 3.3786 | 3.2568 | 3.1241 | 2.9788 | 2.8144 | 2.6658 | 2.5677 | 2.2104 | 2.1781 | 2.2317 | 2.2008 | 3.1016 | 3.0518 | 2.9672 | 2.8538 | 2.6124 | 2.3516 | 2.0705 | 1.7727 | 1.509 | 1.3678 | 0.86675 | 0.84038 | 0.96921 | 0.89719
| SANDWICK | ST |  |  | 3.2748 | 3.2628 | 3.2516 | 3.2275 | 3.2178 | 3.2049 | 3.1913 | 3.1753 | 3.142 | 3.0838 | 2.9031 | 2.2442 | 2.1705 | 2.1311 | 3.5358 | 3.5278 | 3.5194 | 3.4995 | 3.4909 | 3.4802 | 3.4664 | 3.4477 | 3.4188 | 3.3669 | 3.1735 | 2.6248 | 2.5657 | 2.5177 | 3.1628 | 3.1472 | 3.1309 | 3.0949 | 3.0808 | 3.0631 | 3.0422 | 3.0193 | 2.977 | 2.8976 | 2.6189 | 1.9037 | 1.8364 | 1.8022
| SANDWICK | SP |  |  | 3.2903 | 3.2864 | 3.2859 | 3.2848 | 3.2425 | 3.2029 | 3.1587 | 3.109 | 3.0515 | 2.9624 | 2.6697 | 1.8951 | 1.2633 | 1.0874 | 3.5399 | 3.5371 | 3.5347 | 3.53 | 3.5069 | 3.4844 | 3.453 | 3.4146 | 3.3743 | 3.3198 | 3.1424 | 2.6252 | 2.2034 | 2.075 | 3.1703 | 3.1648 | 3.1614 | 3.1557 | 3.1107 | 3.0677 | 3.0158 | 2.9535 | 2.8848 | 2.7862 | 2.464 | 1.6345 | 1.0383 | 0.88389
SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | -0.52851 | -0.61172 | -0.72161 | -0.85548 | -1.1582 | -1.4802 | -1.7794 | -2.1059 | -2.4494 | -2.6236 | -3.1349 | -3.155 | -2.9143 | -3.031 | 1.3786 | 1.3303 | 1.2697 | 1.18 | 1.0146 | 0.85906 | 0.68707 | 0.48314 | 0.31118 | 0.19609 | -0.19255 | -0.2978 | -0.22244 | -0.42941 | 0.53678 | 0.46111 | 0.35439 | 0.2208 | -0.078432 | -0.39425 | -0.68362 | -0.98447 | -1.2949 | -1.4581 | -1.9399 | -1.9703 | -1.7586 | -1.86
| SCALLOWAY | CT |  |  | -0.47173 | -0.5261 | -0.61861 | -0.76629 | -1.0758 | -1.366 | -1.5777 | -1.8353 | -2.0974 | -2.2429 | -2.8102 | -3.0061 | -2.7251 | -2.6616 | 1.3879 | 1.3465 | 1.283 | 1.18 | 1.0146 | 0.85906 | 0.75315 | 0.61428 | 0.48137 | 0.38902 | -0.03109 | -0.2561 | -0.21526 | -0.24921 | 0.56973 | 0.51143 | 0.40801 | 0.23312 | -0.075504 | -0.36251 | -0.53315 | -0.76515 | -0.97363 | -1.1073 | -1.645 | -1.8359 | -1.5898 | -1.5186
| SCALLOWAY | LW |  |  | -0.52851 | -0.61172 | -0.72161 | -0.85548 | -1.1582 | -1.4802 | -1.7794 | -2.1059 | -2.4494 | -2.6236 | -3.1349 | -3.155 | -2.9143 | -3.031 | 1.3786 | 1.3303 | 1.2697 | 1.1914 | 1.0348 | 0.86074 | 0.68707 | 0.48314 | 0.31118 | 0.19609 | -0.19255 | -0.2978 | -0.22244 | -0.25911 | 0.53678 | 0.46111 | 0.35439 | 0.2208 | -0.078432 | -0.39425 | -0.68362 | -0.98447 | -1.2949 | -1.4581 | -1.9399 | -1.9703 | -1.7586 | -1.86
| SCALLOWAY | ST |  |  | -0.45466 | -0.4735 | -0.48849 | -0.5263 | -0.54195 | -0.56052 | -0.57944 | -0.60865 | -0.65461 | -0.73214 | -0.9657 | -1.4752 | -1.6021 | -1.6435 | 1.4118 | 1.3965 | 1.3852 | 1.3564 | 1.3431 | 1.3265 | 1.3095 | 1.2836 | 1.2479 | 1.1856 | 0.97197 | 0.31859 | 0.20065 | 0.12844 | 0.59414 | 0.58249 | 0.57413 | 0.53437 | 0.53193 | 0.52751 | 0.52081 | 0.49172 | 0.45067 | 0.38527 | 0.17637 | -0.46904 | -0.58974 | -0.62524
| SCALLOWAY | SP |  |  | -0.42982 | -0.43536 | -0.43547 | -0.43596 | -0.47754 | -0.5196 | -0.56345 | -0.61623 | -0.68208 | -0.78321 | -1.1482 | -1.9088 | -2.6036 | -2.8495 | 1.421 | 1.4138 | 1.4102 | 1.4058 | 1.3853 | 1.3611 | 1.3341 | 1.2975 | 1.2486 | 1.1826 | 0.94672 | 0.34451 | -0.21259 | -0.42941 | 0.62446 | 0.62832 | 0.63485 | 0.62966 | 0.59676 | 0.56273 | 0.52701 | 0.48397 | 0.43258 | 0.35704 | 0.089953 | -0.80914 | -1.4791 | -1.6991
TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | 0.044552 | 0.044306 | 0.043498 | 0.04134 | 0.036933 | 0.033745 | 0.027934 | 0.023687 | 0.018046 | 0.0089883 | 0.0051482 | 0.0044421 | 0.0034723 | 0.0015427 | 0.059601 | 0.059351 | 0.058918 | 0.057632 | 0.055198 | 0.05354 | 0.050126 | 0.047719 | 0.044751 | 0.038154 | 0.035996 | 0.035613 | 0.034975 | 0.034288 | 0.045532 | 0.045499 | 0.044591 | 0.042523 | 0.037835 | 0.034178 | 0.028472 | 0.024054 | 0.018426 | 0.010426 | 0.0061792 | 0.0055326 | 0.0046308 | 0.0029365
| SCAMMADALE | CT |  |  | 0.046241 | 0.045881 | 0.04537 | 0.042769 | 0.038287 | 0.035227 | 0.030435 | 0.025658 | 0.02179 | 0.019375 | 0.0072573 | 0.0055351 | 0.0076191 | 0.0080202 | 0.060451 | 0.060147 | 0.059869 | 0.058368 | 0.055897 | 0.054304 | 0.051674 | 0.049047 | 0.047257 | 0.045769 | 0.037302 | 0.036408 | 0.03705 | 0.037157 | 0.047629 | 0.047526 | 0.047012 | 0.044547 | 0.039775 | 0.036262 | 0.03112 | 0.025986 | 0.022016 | 0.019738 | 0.0085367 | 0.0065733 | 0.0083999 | 0.0087514
| SCAMMADALE | LW |  |  | 0.044552 | 0.044306 | 0.043498 | 0.04134 | 0.036933 | 0.033745 | 0.027934 | 0.023687 | 0.018046 | 0.0089883 | 0.0051482 | 0.0044421 | 0.0068279 | 0.0054275 | 0.059601 | 0.059351 | 0.058918 | 0.057632 | 0.055198 | 0.05354 | 0.050126 | 0.047719 | 0.044751 | 0.038154 | 0.035996 | 0.035613 | 0.036465 | 0.03596 | 0.045532 | 0.045499 | 0.044591 | 0.042523 | 0.037835 | 0.034178 | 0.028472 | 0.024054 | 0.018426 | 0.010426 | 0.0061792 | 0.0055326 | 0.0077402 | 0.0063963
| SCAMMADALE | ST |  |  | 0.046372 | 0.046285 | 0.045716 | 0.045107 | 0.045161 | 0.044185 | 0.04398 | 0.043987 | 0.043031 | 0.041495 | 0.034891 | 0.021502 | 0.020134 | 0.019164 | 0.060621 | 0.06057 | 0.060197 | 0.059799 | 0.059788 | 0.059125 | 0.058982 | 0.058936 | 0.058318 | 0.057394 | 0.053184 | 0.043611 | 0.042732 | 0.042191 | 0.047508 | 0.047394 | 0.046902 | 0.046413 | 0.046488 | 0.045688 | 0.045475 | 0.045512 | 0.044616 | 0.043082 | 0.036944 | 0.023839 | 0.021881 | 0.020594
| SCAMMADALE | SP |  |  | 0.046373 | 0.046268 | 0.046264 | 0.045649 | 0.043717 | 0.042733 | 0.041425 | 0.038719 | 0.037342 | 0.034018 | 0.027979 | 0.0077861 | 0.0034723 | 0.0015427 | 0.060616 | 0.060552 | 0.060539 | 0.060124 | 0.059011 | 0.058501 | 0.057801 | 0.056205 | 0.055474 | 0.053581 | 0.050165 | 0.037317 | 0.034975 | 0.034288 | 0.047503 | 0.047359 | 0.047335 | 0.046814 | 0.044803 | 0.0436 | 0.042078 | 0.039393 | 0.037792 | 0.034341 | 0.027898 | 0.0087131 | 0.0046308 | 0.0029365
ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | YES | 9.7623 | 9.6598 | 9.5745 | 9.4686 | 9.1994 | 8.8925 | 8.558 | 8.2025 | 7.7104 | 7.3098 | 5.8315 | 3.6931 | 2.6668 | 2.3248 | 10.8248 | 10.7503 | 10.6865 | 10.5972 | 10.4475 | 10.2903 | 10.1071 | 9.9035 | 9.6386 | 9.4084 | 8.5152 | 7.4561 | 6.9441 | 6.6131 | 9.8332 | 9.7406 | 9.6585 | 9.5544 | 9.3269 | 9.0619 | 8.7664 | 8.4466 | 8.0176 | 7.6556 | 6.2962 | 4.4742 | 3.6379 | 3.3619
| SCONE | CT |  |  | 9.7906 | 9.6998 | 9.628 | 9.523 | 9.261 | 8.9854 | 8.6449 | 8.2782 | 7.8844 | 7.4397 | 5.8315 | 3.6931 | 2.6668 | 2.3248 | 10.8272 | 10.7544 | 10.69 | 10.5972 | 10.4475 | 10.2903 | 10.1123 | 9.9245 | 9.724 | 9.4846 | 8.5626 | 7.4561 | 6.9441 | 6.6131 | 9.848 | 9.7638 | 9.6882 | 9.5745 | 9.3456 | 9.1059 | 8.8219 | 8.5194 | 8.1964 | 7.8127 | 6.3203 | 4.4742 | 3.6379 | 3.3619
| SCONE | LW |  |  | 9.7623 | 9.6598 | 9.5745 | 9.4686 | 9.1994 | 8.8925 | 8.558 | 8.2025 | 7.7104 | 7.3098 | 5.8784 | 4.3441 | 3.5678 | 3.3147 | 10.8248 | 10.7503 | 10.6865 | 10.6056 | 10.4623 | 10.2942 | 10.1071 | 9.9035 | 9.6386 | 9.4084 | 8.5152 | 7.7427 | 7.4619 | 7.3692 | 9.8332 | 9.7406 | 9.6585 | 9.5544 | 9.3269 | 9.0619 | 8.7664 | 8.4466 | 8.0176 | 7.6556 | 6.2962 | 4.9837 | 4.3608 | 4.1585
| SCONE | ST |  |  | 9.8344 | 9.7589 | 9.6977 | 9.6264 | 9.5672 | 9.4992 | 9.4286 | 9.3472 | 9.2622 | 9.1256 | 8.608 | 7.0479 | 6.3064 | 5.8737 | 10.8614 | 10.8039 | 10.7592 | 10.7032 | 10.6585 | 10.6077 | 10.554 | 10.4923 | 10.4241 | 10.3249 | 9.9485 | 8.7792 | 8.2795 | 7.9271 | 9.8967 | 9.8327 | 9.7804 | 9.7149 | 9.6608 | 9.5981 | 9.5318 | 9.4548 | 9.3721 | 9.2392 | 8.7276 | 7.1624 | 6.521 | 6.1861
| SCONE | SP |  |  | 9.8479 | 9.7823 | 9.7275 | 9.6634 | 9.579 | 9.4878 | 9.3919 | 9.2851 | 9.1644 | 9.0103 | 8.5478 | 7.4389 | 6.6309 | 6.4866 | 10.8666 | 10.8144 | 10.7716 | 10.7231 | 10.6712 | 10.6137 | 10.5528 | 10.4835 | 10.4007 | 10.2986 | 9.9775 | 9.148 | 8.2534 | 7.693 | 9.9069 | 9.8517 | 9.804 | 9.7493 | 9.6794 | 9.6023 | 9.5201 | 9.4266 | 9.3158 | 9.1797 | 8.7631 | 7.701 | 6.8285 | 6.6949
THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | 0.76199 | 0.76708 | 0.75953 | 0.74932 | 0.71663 | 0.68823 | 0.65812 | 0.62565 | 0.58525 | 0.56848 | 0.5064 | 0.48933 | 0.49101 | 0.47945 | 0.84828 | 0.84919 | 0.84511 | 0.84074 | 0.82729 | 0.81655 | 0.80262 | 0.78525 | 0.76407 | 0.75242 | 0.70444 | 0.68826 | 0.69242 | 0.68369 | 0.68566 | 0.68798 | 0.68166 | 0.67278 | 0.64804 | 0.62487 | 0.60209 | 0.57894 | 0.5497 | 0.53404 | 0.48405 | 0.45433 | 0.46603 | 0.45337
| SHAPINSAY | CT |  |  | 0.78337 | 0.78916 | 0.78272 | 0.76487 | 0.73278 | 0.70344 | 0.67299 | 0.63756 | 0.60384 | 0.58526 | 0.5346 | 0.50581 | 0.52365 | 0.52736 | 0.85839 | 0.85976 | 0.85569 | 0.84547 | 0.83247 | 0.81931 | 0.80602 | 0.79056 | 0.77517 | 0.76067 | 0.72178 | 0.6978 | 0.70071 | 0.69886 | 0.7001 | 0.70359 | 0.69938 | 0.68907 | 0.66496 | 0.64306 | 0.61883 | 0.59169 | 0.56556 | 0.55198 | 0.5146 | 0.4812 | 0.48746 | 0.48708
| SHAPINSAY | LW |  |  | 0.76199 | 0.76708 | 0.75953 | 0.74932 | 0.71663 | 0.68823 | 0.65812 | 0.62565 | 0.58525 | 0.56848 | 0.5064 | 0.48933 | 0.50627 | 0.49405 | 0.84828 | 0.84919 | 0.84511 | 0.84074 | 0.82729 | 0.81655 | 0.80262 | 0.78525 | 0.76407 | 0.75242 | 0.70444 | 0.68826 | 0.69328 | 0.68912 | 0.68566 | 0.68798 | 0.68166 | 0.67278 | 0.64804 | 0.62487 | 0.60209 | 0.57894 | 0.5497 | 0.53404 | 0.48405 | 0.45433 | 0.46603 | 0.45892
| SHAPINSAY | ST |  |  | 0.77421 | 0.77293 | 0.7717 | 0.77007 | 0.76888 | 0.76675 | 0.76394 | 0.76316 | 0.75753 | 0.74873 | 0.71355 | 0.64636 | 0.61931 | 0.60916 | 0.85268 | 0.85202 | 0.85111 | 0.84969 | 0.84767 | 0.84519 | 0.8421 | 0.84023 | 0.83578 | 0.83056 | 0.80499 | 0.75056 | 0.72799 | 0.72097 | 0.69644 | 0.69472 | 0.69302 | 0.69176 | 0.69056 | 0.68833 | 0.68571 | 0.68377 | 0.67873 | 0.66995 | 0.64023 | 0.57709 | 0.54673 | 0.53509
| SHAPINSAY | SP |  |  | 0.77279 | 0.77136 | 0.77104 | 0.77026 | 0.75825 | 0.74723 | 0.73371 | 0.71992 | 0.70237 | 0.67968 | 0.63299 | 0.52707 | 0.49101 | 0.47945 | 0.85083 | 0.85006 | 0.84964 | 0.84883 | 0.84435 | 0.83998 | 0.83405 | 0.82848 | 0.81887 | 0.80944 | 0.78624 | 0.71991 | 0.69242 | 0.68369 | 0.69615 | 0.69428 | 0.69319 | 0.6916 | 0.68152 | 0.67231 | 0.66179 | 0.65048 | 0.63871 | 0.62114 | 0.58513 | 0.50608 | 0.46625 | 0.45337
BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | 0.47503 | 4.0144 | 4.0023 | 3.9856 | 3.935 | 3.8802 | 3.8273 | 3.7695 | 3.6848 | 3.6454 | 3.5019 | 3.4675 | 3.4824 | 3.4262 | 0.63696 | 3.9058 | 3.9046 | 3.9007 | 3.8965 | 3.8932 | 3.8893 | 3.886 | 3.8596 | 3.8474 | 3.8014 | 3.7802 | 3.79 | 3.7722 | 0.39595 | 3.664 | 3.662 | 3.6554 | 3.6482 | 3.5964 | 3.5454 | 3.4886 | 3.4047 | 3.3602 | 3.1882 | 3.1567 | 3.1704 | 3.1211
| SHIELDAIG | CT |  |  | 0.49559 | 4.0379 | 4.0307 | 4.0119 | 3.9607 | 3.9143 | 3.8427 | 3.7695 | 3.7014 | 3.6717 | 3.561 | 3.4904 | 3.5031 | 3.5013 | 0.63696 | 3.9058 | 3.9046 | 3.9007 | 3.8965 | 3.8932 | 3.8893 | 3.8863 | 3.8645 | 3.8554 | 3.8215 | 3.7946 | 3.7997 | 3.7994 | 0.39595 | 3.664 | 3.662 | 3.6554 | 3.6482 | 3.6235 | 3.5562 | 3.4887 | 3.4248 | 3.3923 | 3.2511 | 3.1776 | 3.1887 | 3.1872
| SHIELDAIG | LW |  |  | 0.47503 | 4.0144 | 4.0023 | 3.9856 | 3.935 | 3.8802 | 3.8273 | 3.7714 | 3.6848 | 3.6454 | 3.5019 | 3.4675 | 3.4996 | 3.4831 | 0.63722 | 3.9062 | 3.9051 | 3.903 | 3.901 | 3.8966 | 3.8926 | 3.886 | 3.8596 | 3.8474 | 3.8014 | 3.7802 | 3.79 | 3.7856 | 0.39634 | 3.6646 | 3.6627 | 3.6591 | 3.6496 | 3.5964 | 3.5454 | 3.4886 | 3.4047 | 3.3602 | 3.1882 | 3.1567 | 3.1849 | 3.1704
| SHIELDAIG | ST |  |  | 0.49071 | 4.0279 | 4.0255 | 4.0226 | 4.0212 | 4.0194 | 4.0169 | 4.0147 | 4.0009 | 3.981 | 3.9151 | 3.7245 | 3.685 | 3.6658 | 0.63805 | 3.9075 | 3.907 | 3.906 | 3.9042 | 3.9031 | 3.9018 | 3.9002 | 3.8969 | 3.8936 | 3.8797 | 3.8279 | 3.8255 | 3.8247 | 0.39777 | 3.6669 | 3.666 | 3.6643 | 3.6614 | 3.6595 | 3.6574 | 3.6546 | 3.6491 | 3.6435 | 3.6071 | 3.4143 | 3.3646 | 3.3406
| SHIELDAIG | SP |  |  | 0.49427 | 4.0329 | 4.0322 | 4.0316 | 4.018 | 4.0057 | 3.9912 | 3.9743 | 3.9555 | 3.9257 | 3.8319 | 3.6332 | 3.4824 | 3.4262 | 0.63841 | 3.9081 | 3.9074 | 3.9069 | 3.9062 | 3.9056 | 3.9046 | 3.9027 | 3.9003 | 3.8969 | 3.8879 | 3.8428 | 3.7927 | 3.7722 | 0.39839 | 3.6679 | 3.6668 | 3.6659 | 3.6647 | 3.6638 | 3.6621 | 3.659 | 3.655 | 3.6355 | 3.5425 | 3.3376 | 3.1704 | 3.1211
SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | 2.4688 | 2.4651 | 2.46 | 2.4538 | 2.4271 | 2.3816 | 2.3371 | 2.29 | 2.2067 | 2.1673 | 2.0071 | 1.9694 | 1.9933 | 1.9449 | 2.5188 | 2.5155 | 2.5094 | 2.4991 | 2.4789 | 2.4616 | 2.4385 | 2.4125 | 2.3726 | 2.349 | 2.2439 | 2.2205 | 2.2287 | 2.1999 | 2.4072 | 2.4029 | 2.3917 | 2.3781 | 2.3427 | 2.3055 | 2.2687 | 2.2298 | 2.1661 | 2.1304 | 1.9846 | 1.9492 | 1.9702 | 1.9284
| SHIN | CT |  |  | 2.4709 | 2.468 | 2.4639 | 2.4575 | 2.4437 | 2.4084 | 2.3558 | 2.298 | 2.2361 | 2.2031 | 2.0599 | 1.9963 | 2.006 | 2.0048 | 2.5219 | 2.5181 | 2.5126 | 2.4991 | 2.4789 | 2.4616 | 2.4385 | 2.4133 | 2.3877 | 2.3676 | 2.2703 | 2.2316 | 2.2325 | 2.2281 | 2.4214 | 2.421 | 2.4147 | 2.4025 | 2.37 | 2.3394 | 2.2924 | 2.2424 | 2.1921 | 2.1622 | 2.033 | 1.9736 | 1.9822 | 1.9812
| SHIN | LW |  |  | 2.4688 | 2.4651 | 2.46 | 2.4538 | 2.4271 | 2.3816 | 2.3371 | 2.29 | 2.2067 | 2.1673 | 2.0071 | 1.9694 | 1.9933 | 1.9791 | 2.5188 | 2.5155 | 2.5094 | 2.5022 | 2.4832 | 2.4621 | 2.443 | 2.4125 | 2.3726 | 2.349 | 2.2439 | 2.2205 | 2.2292 | 2.2239 | 2.4072 | 2.4029 | 2.3917 | 2.3781 | 2.3427 | 2.3055 | 2.2687 | 2.2298 | 2.1661 | 2.1304 | 1.9846 | 1.9492 | 1.9702 | 1.9579
| SHIN | ST |  |  | 2.473 | 2.4712 | 2.4694 | 2.4668 | 2.4641 | 2.4611 | 2.457 | 2.4522 | 2.4468 | 2.4381 | 2.3785 | 2.2135 | 2.1601 | 2.138 | 2.523 | 2.5216 | 2.5196 | 2.5151 | 2.5126 | 2.51 | 2.5039 | 2.4974 | 2.492 | 2.4802 | 2.4359 | 2.3179 | 2.2891 | 2.277 | 2.4187 | 2.4159 | 2.4132 | 2.4096 | 2.4068 | 2.4033 | 2.3988 | 2.394 | 2.3847 | 2.3697 | 2.3211 | 2.1583 | 2.1172 | 2.0979
| SHIN | SP |  |  | 2.473 | 2.4717 | 2.4702 | 2.4685 | 2.4652 | 2.4616 | 2.4575 | 2.4533 | 2.4455 | 2.4215 | 2.3455 | 2.1448 | 1.9968 | 1.9449 | 2.523 | 2.5222 | 2.5215 | 2.5199 | 2.5158 | 2.5108 | 2.505 | 2.4998 | 2.4889 | 2.4759 | 2.4369 | 2.3196 | 2.2287 | 2.1999 | 2.4208 | 2.4192 | 2.418 | 2.4168 | 2.4074 | 2.3983 | 2.3883 | 2.3773 | 2.3648 | 2.3459 | 2.2824 | 2.1129 | 1.9745 | 1.9284
FORT WILLIAM | SHONA BEAG | MINIMUM HEADROOM | NM 67173 74363 | YES | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793
| SHONA BEAG | CT |  |  | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793
| SHONA BEAG | LW |  |  | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793
| SHONA BEAG | ST |  |  | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793
| SHONA BEAG | SP |  |  | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093509 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.093652 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793 | 0.091793
KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | YES | 16.0639 | 15.6713 | 15.3597 | 14.9869 | 14.4276 | 13.6912 | 12.8981 | 12.223 | 11.3756 | 10.6524 | 8.6614 | 5.8258 | 4.2879 | 3.7464 | 18.8319 | 18.4537 | 18.2047 | 17.9055 | 17.6165 | 17.1309 | 16.609 | 16.1921 | 15.6894 | 15.2144 | 13.9765 | 12.5356 | 11.7185 | 11.0869 | 15.8904 | 15.5066 | 15.1953 | 14.8171 | 14.2769 | 13.5484 | 12.7637 | 12.1152 | 11.3096 | 10.6029 | 8.6851 | 6.2243 | 4.9308 | 4.4798
| SKENE | CT |  |  | 16.088 | 15.7155 | 15.4077 | 15.0614 | 14.5706 | 14.0138 | 13.3745 | 12.7435 | 12.094 | 11.2733 | 8.679 | 5.8258 | 4.2879 | 3.7464 | 18.8319 | 18.4537 | 18.2047 | 17.9055 | 17.6224 | 17.2798 | 16.9031 | 16.555 | 16.1986 | 15.6739 | 13.9884 | 12.5356 | 11.7185 | 11.0869 | 15.8943 | 15.5273 | 15.2124 | 14.8571 | 14.3888 | 13.8598 | 13.259 | 12.6811 | 12.0881 | 11.2939 | 8.7431 | 6.2243 | 4.9308 | 4.4798
| SKENE | LW |  |  | 16.0639 | 15.6713 | 15.3597 | 14.9869 | 14.4276 | 13.6912 | 12.8981 | 12.223 | 11.3756 | 10.6524 | 8.6614 | 6.4906 | 5.394 | 5.037 | 18.8577 | 18.4819 | 18.2235 | 17.9244 | 17.6165 | 17.1309 | 16.609 | 16.1921 | 15.6894 | 15.2144 | 13.9765 | 12.8747 | 12.4775 | 12.3465 | 15.8904 | 15.5066 | 15.1953 | 14.8171 | 14.2769 | 13.5484 | 12.7637 | 12.1152 | 11.3096 | 10.6029 | 8.6851 | 6.7371 | 5.8193 | 5.5231
| SKENE | ST |  |  | 16.2546 | 15.9458 | 15.7628 | 15.5784 | 15.4894 | 15.3885 | 15.2783 | 15.1585 | 15.0118 | 14.7521 | 13.869 | 11.2897 | 10.0498 | 9.3181 | 18.9027 | 18.5658 | 18.3804 | 18.1886 | 18.1127 | 18.0306 | 17.9239 | 17.7803 | 17.628 | 17.4078 | 16.6941 | 14.8117 | 13.9732 | 13.2719 | 16.0766 | 15.7866 | 15.6106 | 15.4304 | 15.3379 | 15.2335 | 15.1193 | 14.995 | 14.845 | 14.5788 | 13.6488 | 10.9839 | 9.8954 | 9.2826
| SKENE | SP |  |  | 16.2418 | 15.9449 | 15.7691 | 15.5832 | 15.4492 | 15.2991 | 15.136 | 14.9469 | 14.7785 | 14.5654 | 13.9476 | 11.8128 | 10.5897 | 10.3247 | 18.8988 | 18.5669 | 18.3852 | 18.1984 | 18.1269 | 18.0477 | 17.9643 | 17.8446 | 17.7132 | 17.5524 | 17.0701 | 15.2011 | 13.7831 | 12.6785 | 16.0585 | 15.7811 | 15.6121 | 15.4312 | 15.2999 | 15.149 | 14.986 | 14.7948 | 14.6272 | 14.4205 | 13.8091 | 11.567 | 10.3186 | 10.0802
BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | 4.691 | 4.7006 | 4.663 | 4.6111 | 4.4676 | 4.3076 | 4.1201 | 3.9193 | 3.6846 | 3.5486 | 2.9812 | 2.8994 | 2.8573 | 2.7934 | 5.2458 | 5.2445 | 5.2225 | 5.1928 | 5.1239 | 5.0417 | 4.9507 | 4.8473 | 4.7304 | 4.6467 | 4.2665 | 4.2117 | 4.1567 | 4.0829 | 4.6149 | 4.6224 | 4.588 | 4.5404 | 4.4121 | 4.2644 | 4.0945 | 3.9148 | 3.7034 | 3.5868 | 3.063 | 2.9895 | 2.9547 | 2.8984
| SKULAMUS | CT |  |  | 4.7607 | 4.7714 | 4.7445 | 4.6781 | 4.5237 | 4.3748 | 4.2108 | 4.0168 | 3.8262 | 3.7097 | 3.2367 | 2.9684 | 3.009 | 3.0083 | 5.273 | 5.2719 | 5.2535 | 5.2132 | 5.1358 | 5.0593 | 4.9759 | 4.8853 | 4.7962 | 4.7254 | 4.4096 | 4.228 | 4.2265 | 4.199 | 4.6755 | 4.6838 | 4.6585 | 4.5966 | 4.4576 | 4.3243 | 4.1779 | 4.0024 | 3.8308 | 3.7313 | 3.3025 | 3.0518 | 3.0878 | 3.0872
| SKULAMUS | LW |  |  | 4.691 | 4.7006 | 4.663 | 4.6111 | 4.4676 | 4.3076 | 4.1201 | 3.9193 | 3.6846 | 3.5486 | 2.9812 | 2.8994 | 2.9904 | 2.9484 | 5.2458 | 5.2445 | 5.2225 | 5.1928 | 5.1239 | 5.0417 | 4.9507 | 4.8473 | 4.7304 | 4.6467 | 4.2665 | 4.2117 | 4.2448 | 4.2293 | 4.6149 | 4.6224 | 4.588 | 4.5404 | 4.4121 | 4.2644 | 4.0945 | 3.9148 | 3.7034 | 3.5868 | 3.063 | 2.9895 | 3.0696 | 3.0329
| SKULAMUS | ST |  |  | 4.7463 | 4.7324 | 4.7197 | 4.7067 | 4.6953 | 4.6692 | 4.6409 | 4.6099 | 4.5591 | 4.4832 | 4.2265 | 3.6244 | 3.525 | 3.4634 | 5.272 | 5.263 | 5.2541 | 5.2432 | 5.232 | 5.2133 | 5.1932 | 5.1695 | 5.1359 | 5.0879 | 4.9201 | 4.4757 | 4.4073 | 4.3614 | 4.6644 | 4.6519 | 4.6404 | 4.6279 | 4.6167 | 4.5936 | 4.5682 | 4.5403 | 4.4947 | 4.4259 | 4.1903 | 3.6063 | 3.526 | 3.4854
| SKULAMUS | SP |  |  | 4.7469 | 4.7331 | 4.7217 | 4.7105 | 4.6528 | 4.5839 | 4.5121 | 4.4289 | 4.3368 | 4.1911 | 3.8641 | 3.2919 | 2.8573 | 2.7934 | 5.2717 | 5.2632 | 5.2547 | 5.2463 | 5.2182 | 5.182 | 5.1452 | 5.1012 | 5.0496 | 4.9801 | 4.8115 | 4.4892 | 4.1567 | 4.0829 | 4.6648 | 4.6526 | 4.6422 | 4.6321 | 4.581 | 4.5204 | 4.4573 | 4.3839 | 4.302 | 4.1805 | 3.8976 | 3.3751 | 2.9547 | 2.8984
WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | 3.0154 | 2.3679 | 2.063 | 1.6872 | 9.7309 | 9.0178 | 8.2361 | 7.5007 | 6.7104 | 5.9402 | 3.6785 | 0.50318 | -1.0086 | -1.5536 | 5.5381 | 5.1277 | 4.9067 | 4.6357 | 12.5401 | 12.1333 | 11.682 | 11.2681 | 10.818 | 10.3462 | 8.9625 | 6.9373 | 5.7758 | 4.6599 | 3.1421 | 2.5468 | 2.268 | 1.9246 | 9.5707 | 8.9186 | 8.2081 | 7.5348 | 6.8121 | 6.1121 | 4.0608 | 1.1507 | -0.24715 | -0.7432
| SPRINGHILL | CT |  |  | 3.0756 | 2.5632 | 2.3044 | 1.9753 | 10.0388 | 9.3427 | 8.6734 | 8.0334 | 7.3554 | 6.525 | 3.9004 | 0.50318 | -1.0086 | -1.5536 | 5.5416 | 5.175 | 4.9551 | 4.6818 | 12.5776 | 12.1736 | 11.786 | 11.4179 | 11.027 | 10.5287 | 8.9625 | 6.9373 | 5.7758 | 4.6599 | 3.1998 | 2.7328 | 2.4986 | 2.2013 | 9.8675 | 9.2288 | 8.6157 | 8.0272 | 7.4032 | 6.6428 | 4.2592 | 1.1507 | -0.24715 | -0.7432
| SPRINGHILL | LW |  |  | 3.0154 | 2.3679 | 2.063 | 1.6872 | 9.7309 | 9.0178 | 8.2361 | 7.5007 | 6.7104 | 5.9402 | 3.6785 | 1.069 | -0.017721 | -0.40047 | 5.5381 | 5.1277 | 4.9067 | 4.6357 | 12.5401 | 12.1333 | 11.682 | 11.2681 | 10.818 | 10.3462 | 8.9956 | 7.5642 | 7.1087 | 6.9435 | 3.1421 | 2.5468 | 2.268 | 1.9246 | 9.5707 | 8.9186 | 8.2081 | 7.5348 | 6.8121 | 6.1121 | 4.0608 | 1.6917 | 0.69133 | 0.34808
| SPRINGHILL | ST |  |  | 3.3215 | 2.9959 | 2.7936 | 2.5452 | 11.0742 | 10.8649 | 10.6516 | 10.4835 | 10.3231 | 10.0407 | 9.0265 | 6.1637 | 4.6147 | 3.9029 | 5.6845 | 5.4194 | 5.2593 | 5.0722 | 13.2187 | 13.0763 | 12.9248 | 12.7869 | 12.6428 | 12.4236 | 11.649 | 9.4971 | 8.1038 | 6.9305 | 3.4283 | 3.1346 | 2.949 | 2.7209 | 10.8208 | 10.6348 | 10.4442 | 10.2964 | 10.1564 | 9.904 | 9.0036 | 6.4299 | 4.9987 | 4.3435
| SPRINGHILL | SP |  |  | 3.3933 | 3.1057 | 2.9335 | 2.7511 | 11.3019 | 11.094 | 10.8886 | 10.6792 | 10.4524 | 10.1731 | 9.3267 | 7.0024 | 5.3352 | 4.8572 | 5.7193 | 5.471 | 5.3225 | 5.1649 | 13.3203 | 13.1782 | 13.0283 | 12.8712 | 12.6977 | 12.4805 | 11.7988 | 9.8289 | 7.6362 | 5.2621 | 3.4949 | 3.237 | 3.08 | 2.9141 | 11.034 | 10.8497 | 10.6663 | 10.4802 | 10.2794 | 10.0278 | 9.2751 | 7.2026 | 5.696 | 5.2663
BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | YES | 6.3485 | 6.2948 | 6.2414 | 6.1726 | 5.9884 | 5.7487 | 5.5035 | 5.2179 | 4.9074 | 4.6876 | 4.0959 | 3.8816 | 3.982 | 3.9086 | 6.5193 | 6.4893 | 6.4581 | 6.4156 | 6.3254 | 6.1961 | 6.062 | 5.8954 | 5.7248 | 5.5738 | 5.1564 | 4.9962 | 4.9912 | 4.835 | 3.1879 | 3.1794 | 3.1707 | 3.1599 | 3.1412 | 3.1048 | 3.0646 | 2.9675 | 2.7593 | 2.6446 | 2.3676 | 2.2701 | 2.3671 | 2.2697
| ST CYRUS | CT |  |  | 6.361 | 6.3251 | 6.2834 | 6.2313 | 6.0536 | 5.8451 | 5.6035 | 5.3494 | 5.1064 | 4.9314 | 4.3595 | 4.017 | 4.0009 | 3.9684 | 6.5195 | 6.4944 | 6.4652 | 6.4237 | 6.3331 | 6.2181 | 6.0926 | 5.9553 | 5.8201 | 5.6976 | 5.2761 | 5.0328 | 4.9912 | 4.9296 | 3.1901 | 3.1836 | 3.1762 | 3.1664 | 3.1471 | 3.1128 | 3.0742 | 3.0318 | 2.8763 | 2.779 | 2.5425 | 2.3736 | 2.3808 | 2.3626
| ST CYRUS | LW |  |  | 6.3485 | 6.2948 | 6.2414 | 6.1726 | 5.9884 | 5.7487 | 5.5035 | 5.2179 | 4.9074 | 4.6876 | 4.0959 | 3.8816 | 3.982 | 3.9503 | 6.5193 | 6.4893 | 6.4581 | 6.4156 | 6.3254 | 6.1961 | 6.062 | 5.8954 | 5.7248 | 5.5738 | 5.1564 | 4.9962 | 5.0255 | 5.0112 | 3.1879 | 3.1794 | 3.1707 | 3.1599 | 3.1412 | 3.1048 | 3.0646 | 2.9675 | 2.7593 | 2.6446 | 2.3676 | 2.2701 | 2.3671 | 2.3446
| ST CYRUS | ST |  |  | 6.3662 | 6.3385 | 6.309 | 6.2796 | 6.2567 | 6.2061 | 6.1526 | 6.0947 | 6.0112 | 5.8942 | 5.553 | 4.8176 | 4.5906 | 4.486 | 6.5301 | 6.513 | 6.4943 | 6.4734 | 6.4555 | 6.4129 | 6.3668 | 6.317 | 6.2527 | 6.1663 | 5.9231 | 5.3741 | 5.2195 | 5.1206 | 3.1919 | 3.1871 | 3.182 | 3.1762 | 3.1704 | 3.1492 | 3.125 | 3.0985 | 3.0669 | 3.0276 | 2.9464 | 2.839 | 2.8097 | 2.7965
| ST CYRUS | SP |  |  | 6.3848 | 6.3693 | 6.353 | 6.3353 | 6.3021 | 6.2437 | 6.183 | 6.1153 | 6.0423 | 5.9385 | 5.5697 | 4.7732 | 4.1528 | 3.9086 | 6.5365 | 6.5247 | 6.5118 | 6.4974 | 6.4763 | 6.4326 | 6.3856 | 6.3316 | 6.2726 | 6.1945 | 5.9699 | 5.4795 | 5.0455 | 4.835 | 3.1926 | 3.1885 | 3.1842 | 3.1797 | 3.1734 | 3.1521 | 3.1278 | 3.1006 | 3.0699 | 3.0322 | 2.9543 | 2.7654 | 2.4493 | 2.2697
ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 09165377 | NO | 29.2679 | 29.2559 | 29.2344 | 29.2061 | 29.1521 | 29.0889 | 29.0202 | 28.9222 | 28.7965 | 28.669 | 28.3818 | 28.0347 | 27.8577 | 27.7938 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 32.0307 | 32.0235 | 32.0142 | 32.0002 | 31.9884 | 31.9773 | 31.9649 | 31.9463 | 31.8395 | 31.7091 | 31.4308 | 31.1333 | 30.984 | 30.9306
| ST FERGUS GAS TERM | CT |  |  | 29.2778 | 29.2666 | 29.2471 | 29.2168 | 29.1647 | 29.1115 | 29.0225 | 28.9222 | 28.8242 | 28.723 | 28.3955 | 28.0347 | 27.8577 | 27.7938 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 32.0307 | 32.0235 | 32.0142 | 32.0002 | 31.9884 | 31.9773 | 31.9649 | 31.9503 | 31.8714 | 31.7741 | 31.455 | 31.1333 | 30.984 | 30.9306
| ST FERGUS GAS TERM | LW |  |  | 29.2679 | 29.2559 | 29.2344 | 29.2061 | 29.1521 | 29.0889 | 29.0202 | 28.9293 | 28.7965 | 28.669 | 28.3818 | 28.1206 | 27.9957 | 27.9461 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 32.0327 | 32.0275 | 32.0198 | 32.0091 | 32.0005 | 31.9889 | 31.9742 | 31.9463 | 31.8395 | 31.7091 | 31.4308 | 31.1991 | 31.0948 | 31.0537
| ST FERGUS GAS TERM | ST |  |  | 29.2832 | 29.2743 | 29.2642 | 29.2519 | 29.2458 | 29.2334 | 29.2249 | 29.2131 | 29.1959 | 29.1651 | 29.0433 | 28.708 | 28.5543 | 28.4615 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 32.0351 | 32.0318 | 32.0276 | 32.0216 | 32.018 | 32.0106 | 32.0063 | 31.9998 | 31.9929 | 31.9812 | 31.9291 | 31.7046 | 31.5692 | 31.4907
| ST FERGUS GAS TERM | SP |  |  | 29.2873 | 29.2798 | 29.2726 | 29.2643 | 29.2522 | 29.2394 | 29.2232 | 29.2008 | 29.1781 | 29.1487 | 29.0396 | 28.7216 | 28.5371 | 28.4826 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 32.036 | 32.0328 | 32.0294 | 32.0253 | 32.0224 | 32.0185 | 32.0136 | 32.0051 | 31.9968 | 31.9884 | 31.9571 | 31.7357 | 31.5527 | 31.5054
ST FILLANS | ST FILLANS P S | MINIMUM HEADROOM | NN 69422464 | YES | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | CT |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | LW |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | ST |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | SP |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | 15.6486 | 15.0108 | 14.5066 | 14.1402 | 12.9522 | 11.7642 | 10.2665 | 8.6151 | 7.9218 | 7.2315 | 4.833 | 1.4275 | -0.33692 | -1.5718 | 15.6219 | 15.5789 | 15.5284 | 15.4627 | 15.1417 | 14.5755 | 13.989 | 13.3178 | 12.9529 | 12.551 | 11.1103 | 8.4518 | 6.6531 | 4.5785 | 15.1944 | 14.4718 | 13.9259 | 13.5707 | 12.2098 | 10.9399 | 9.6307 | 8.2328 | 7.7026 | 7.2174 | 5.3835 | 2.3235 | 0.94387 | -0.013409
| ST MACHAR | CT |  |  | 15.7278 | 15.2797 | 14.9926 | 14.8037 | 13.653 | 12.4199 | 11.6991 | 10.9921 | 10.1407 | 9.1891 | 6.2794 | 1.7166 | -0.33692 | -1.5718 | 15.6219 | 15.5789 | 15.5284 | 15.4627 | 15.3895 | 14.8084 | 14.375 | 13.9558 | 13.4946 | 12.9666 | 11.3157 | 8.4518 | 6.6531 | 4.5785 | 15.3187 | 14.8339 | 14.566 | 14.4651 | 13.1788 | 11.807 | 11.0821 | 10.466 | 9.7856 | 9.0398 | 6.691 | 2.6435 | 0.94387 | -0.013409
| ST MACHAR | LW |  |  | 15.6486 | 15.0108 | 14.5066 | 14.1402 | 12.9522 | 11.7642 | 10.2665 | 8.6151 | 7.9218 | 7.2315 | 4.833 | 1.4275 | 0.12916 | -0.91239 | 15.64 | 15.6058 | 15.5683 | 15.5215 | 15.1417 | 14.5755 | 13.989 | 13.3178 | 12.9529 | 12.551 | 11.1103 | 9.0254 | 8.4415 | 7.9521 | 15.1944 | 14.4718 | 13.9259 | 13.5707 | 12.2098 | 10.9399 | 9.6307 | 8.2328 | 7.7026 | 7.2174 | 5.3835 | 2.3235 | 1.2974 | 0.50953
| ST MACHAR | ST |  |  | 16.0937 | 15.976 | 15.8485 | 15.654 | 15.4553 | 15.2585 | 15.0545 | 14.7919 | 14.6687 | 14.3922 | 13.4221 | 10.47 | 8.2349 | 6.6285 | 15.6537 | 15.6288 | 15.6011 | 15.5671 | 15.5334 | 15.4953 | 15.4519 | 15.3988 | 15.3429 | 15.2603 | 14.8077 | 12.3877 | 10.2685 | 8.0593 | 15.7119 | 15.6049 | 15.4915 | 15.3159 | 15.129 | 14.9528 | 14.776 | 14.5314 | 14.4732 | 14.2728 | 13.6391 | 11.2642 | 9.1972 | 7.6994
| ST MACHAR | SP |  |  | 16.1815 | 16.12 | 16.0357 | 15.944 | 15.7723 | 15.5692 | 15.3966 | 15.2318 | 15.0319 | 14.7738 | 13.8705 | 11.4445 | 9.2654 | 8.1988 | 15.6544 | 15.6313 | 15.6037 | 15.573 | 15.541 | 15.5043 | 15.4632 | 15.4181 | 15.3586 | 15.2874 | 14.8255 | 12.3561 | 9.0787 | 4.9278 | 15.8191 | 15.7788 | 15.718 | 15.6555 | 15.4898 | 15.2936 | 15.1457 | 15.0086 | 14.8562 | 14.6493 | 13.9408 | 12.1156 | 10.2138 | 9.3023
THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | 1.9899 | 1.9685 | 1.9118 | 1.8518 | 2.2068 | 1.9697 | 1.7406 | 1.4858 | 1.2123 | 1.0491 | 0.49424 | 0.3962 | 0.45458 | 0.33903 | 2.4497 | 2.451 | 2.4297 | 2.3977 | 3.1492 | 3.0599 | 2.9744 | 2.8903 | 2.8092 | 2.7737 | 2.5281 | 2.3814 | 2.4183 | 2.3613 | 2.0711 | 2.0631 | 1.9929 | 1.8953 | 2.4973 | 2.2484 | 2.0082 | 1.7352 | 1.4828 | 1.3359 | 0.83804 | 0.74737 | 0.81014 | 0.7031
| ST MARYS | CT |  |  | 2.0405 | 2.0156 | 1.9849 | 1.9312 | 2.2739 | 2.1518 | 1.9509 | 1.7248 | 1.5176 | 1.388 | 0.80276 | 0.57964 | 0.64494 | 0.6488 | 2.4624 | 2.4585 | 2.4529 | 2.4357 | 3.2009 | 3.1217 | 3.0502 | 2.968 | 2.8923 | 2.8603 | 2.6668 | 2.5221 | 2.5274 | 2.5003 | 2.1784 | 2.1796 | 2.1285 | 2.0102 | 2.613 | 2.3985 | 2.2025 | 1.9781 | 1.7622 | 1.6424 | 1.1217 | 0.91931 | 0.98982 | 0.99759
| ST MARYS | LW |  |  | 1.9899 | 1.9685 | 1.9118 | 1.8518 | 2.2068 | 1.9697 | 1.7406 | 1.4858 | 1.2123 | 1.0491 | 0.49424 | 0.3962 | 0.52128 | 0.46077 | 2.4497 | 2.451 | 2.4297 | 2.3977 | 3.1492 | 3.0599 | 2.9744 | 2.8903 | 2.8092 | 2.7737 | 2.5281 | 2.3814 | 2.4183 | 2.404 | 2.0711 | 2.0631 | 1.9929 | 1.8953 | 2.4973 | 2.2484 | 2.0082 | 1.7352 | 1.4828 | 1.3359 | 0.83804 | 0.74737 | 0.86763 | 0.8091
| ST MARYS | ST |  |  | 2.0432 | 2.025 | 2.0094 | 1.9959 | 2.4581 | 2.4215 | 2.3932 | 2.3531 | 2.3014 | 2.228 | 1.9834 | 1.4158 | 1.1537 | 1.0741 | 2.4645 | 2.4627 | 2.4623 | 2.4603 | 3.301 | 3.2982 | 3.2952 | 3.2904 | 3.2781 | 3.2552 | 3.1842 | 2.8009 | 2.6239 | 2.5788 | 2.1594 | 2.1381 | 2.1194 | 2.0981 | 2.924 | 2.8994 | 2.8647 | 2.8417 | 2.7992 | 2.7212 | 2.4387 | 1.765 | 1.604 | 1.5237
| ST MARYS | SP |  |  | 2.0461 | 2.0288 | 2.0175 | 2.004 | 2.4399 | 2.3827 | 2.335 | 2.2689 | 2.1996 | 2.0489 | 1.7181 | 0.89147 | 0.45458 | 0.33903 | 2.4662 | 2.4649 | 2.4655 | 2.466 | 3.2908 | 3.2617 | 3.2314 | 3.1967 | 3.1604 | 3.106 | 2.9916 | 2.7438 | 2.4566 | 2.3613 | 2.1745 | 2.1558 | 2.1459 | 2.1328 | 2.893 | 2.8121 | 2.7285 | 2.6295 | 2.5204 | 2.3742 | 2.0439 | 1.2068 | 0.81014 | 0.7031
WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | 17.1003 | 16.9187 | 16.7775 | 16.6867 | 16.3369 | 15.963 | 15.5639 | 15.1701 | 15.007 | 14.8454 | 14.2085 | 13.279 | 12.6978 | 12.2081 | 17.9805 | 17.9083 | 17.8258 | 17.7533 | 17.5708 | 17.3596 | 17.2073 | 17.091 | 16.9596 | 16.8132 | 16.349 | 15.349 | 14.4026 | 11.6691 | 16.6371 | 16.4771 | 16.34 | 16.2369 | 15.9153 | 15.5663 | 15.1895 | 14.8374 | 14.6749 | 14.5084 | 13.9198 | 13.0963 | 12.6606 | 12.3045
| ST NICHOLAS | CT |  |  | 17.1003 | 16.9523 | 16.8572 | 16.8025 | 16.4607 | 16.0655 | 15.8302 | 15.6533 | 15.453 | 15.2117 | 14.4816 | 13.322 | 12.6978 | 12.2081 | 17.9805 | 17.9083 | 17.8258 | 17.7533 | 17.5708 | 17.3596 | 17.2073 | 17.091 | 16.9596 | 16.8132 | 16.349 | 15.349 | 14.4026 | 13.0853 | 16.6371 | 16.4967 | 16.3949 | 16.3158 | 15.9948 | 15.6229 | 15.3872 | 15.2259 | 15.0428 | 14.8225 | 14.1621 | 13.1437 | 12.6606 | 12.3045
| ST NICHOLAS | LW |  |  | 17.1031 | 16.9187 | 16.7775 | 16.6867 | 16.3369 | 15.963 | 15.5639 | 15.1701 | 15.007 | 14.8454 | 14.2085 | 13.279 | 12.7837 | 12.3311 | 17.9914 | 17.9353 | 17.8571 | 17.796 | 17.6344 | 17.4562 | 17.2658 | 17.0921 | 17.0001 | 16.9047 | 16.5645 | 16.041 | 15.7825 | 15.5385 | 16.6466 | 16.4771 | 16.34 | 16.2369 | 15.9153 | 15.5663 | 15.1895 | 14.8374 | 14.6749 | 14.5084 | 13.9198 | 13.0963 | 12.7284 | 12.4049
| ST NICHOLAS | ST |  |  | 17.2277 | 17.1732 | 17.1171 | 17.0767 | 17.0406 | 17.0035 | 16.9634 | 16.9103 | 16.8969 | 16.8451 | 16.6446 | 15.8587 | 15.1119 | 14.4618 | 18.0081 | 17.9841 | 17.9589 | 17.9295 | 17.8881 | 17.8431 | 17.7923 | 17.7338 | 17.6849 | 17.6199 | 17.3689 | 16.5401 | 15.52 | 14.1305 | 16.7673 | 16.7199 | 16.6705 | 16.6299 | 16.5927 | 16.5538 | 16.5112 | 16.4588 | 16.438 | 16.3814 | 16.1656 | 15.4452 | 14.8382 | 14.3379
| ST NICHOLAS | SP |  |  | 17.2327 | 17.2001 | 17.1667 | 17.1517 | 17.1158 | 17.0709 | 17.0347 | 17.0021 | 16.9708 | 16.9203 | 16.726 | 16.0973 | 15.3961 | 14.9234 | 18.0092 | 17.9868 | 17.963 | 17.9449 | 17.8988 | 17.844 | 17.7867 | 17.7268 | 17.6596 | 17.5722 | 17.234 | 16.2477 | 14.4835 | 11.6691 | 16.7887 | 16.7552 | 16.717 | 16.693 | 16.6576 | 16.6137 | 16.5756 | 16.5417 | 16.5071 | 16.4549 | 16.2606 | 15.6773 | 15.0955 | 14.7456
ARDMORE | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | 0.14342 | 0.15651 | 0.14381 | 0.12585 | 0.065567 | 0.010288 | -0.044361 | -0.10603 | -0.18461 | -0.22615 | -0.37719 | -0.42526 | -0.47195 | -0.48088 | 0.56845 | 0.55885 | 0.55131 | 0.54451 | 0.52684 | 0.50035 | 0.46957 | 0.44077 | 0.40721 | 0.3789 | 0.26751 | 0.22672 | 0.20889 | 0.19499 | 0.35387 | 0.35804 | 0.34694 | 0.3327 | 0.29044 | 0.25043 | 0.20116 | 0.15251 | 0.097347 | 0.058977 | -0.092776 | -0.14201 | -0.16438 | -0.17151
| STOCKINISH | CT |  |  | 0.18636 | 0.19662 | 0.18766 | 0.1559 | 0.087193 | 0.028742 | -0.038074 | -0.10603 | -0.17101 | -0.20434 | -0.31671 | -0.4159 | -0.38581 | -0.37899 | 0.56957 | 0.55971 | 0.55248 | 0.54451 | 0.52684 | 0.50035 | 0.46957 | 0.44077 | 0.41164 | 0.38997 | 0.30931 | 0.22974 | 0.23489 | 0.23167 | 0.38061 | 0.38253 | 0.37328 | 0.34509 | 0.2935 | 0.25043 | 0.20116 | 0.15251 | 0.10459 | 0.074962 | -0.035616 | -0.13673 | -0.11489 | -0.10898
| STOCKINISH | LW |  |  | 0.14342 | 0.15651 | 0.14381 | 0.12585 | 0.065567 | 0.010288 | -0.044361 | -0.10546 | -0.18461 | -0.22615 | -0.37719 | -0.42526 | -0.39137 | -0.41226 | 0.56845 | 0.55885 | 0.55131 | 0.54478 | 0.52847 | 0.50522 | 0.48006 | 0.4462 | 0.40721 | 0.3789 | 0.26751 | 0.22672 | 0.23809 | 0.23112 | 0.35387 | 0.35804 | 0.34694 | 0.3327 | 0.29044 | 0.25156 | 0.21109 | 0.15933 | 0.097347 | 0.058977 | -0.092776 | -0.14201 | -0.11974 | -0.13415
| STOCKINISH | ST |  |  | 0.17462 | 0.16386 | 0.15952 | 0.15611 | 0.15426 | 0.15042 | 0.14608 | 0.14069 | 0.1292 | 0.1078 | 0.038453 | -0.15656 | -0.20263 | -0.22111 | 0.58228 | 0.56335 | 0.55783 | 0.55397 | 0.54954 | 0.54569 | 0.54144 | 0.52629 | 0.51089 | 0.50295 | 0.46514 | 0.32511 | 0.29295 | 0.28106 | 0.37431 | 0.36372 | 0.35908 | 0.35388 | 0.35001 | 0.34536 | 0.34044 | 0.3331 | 0.32343 | 0.30434 | 0.24189 | 0.041933 | 0.0053491 | -0.0049613
| STOCKINISH | SP |  |  | 0.17298 | 0.16058 | 0.15603 | 0.15203 | 0.12091 | 0.092722 | 0.060856 | 0.025636 | -0.015237 | -0.068731 | -0.17036 | -0.35277 | -0.47195 | -0.48088 | 0.58216 | 0.56329 | 0.55825 | 0.55442 | 0.54936 | 0.54085 | 0.528 | 0.51317 | 0.49302 | 0.47081 | 0.41766 | 0.31694 | 0.20889 | 0.19499 | 0.37338 | 0.36208 | 0.35735 | 0.35347 | 0.33222 | 0.31289 | 0.29118 | 0.26724 | 0.23624 | 0.19845 | 0.11763 | -0.030965 | -0.16438 | -0.17151
PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | 0.33078 | 0.3305 | 0.32993 | 0.32909 | 0.32561 | 0.32364 | 0.32064 | 0.31726 | 0.3115 | 0.30866 | 0.29721 | 0.29416 | 0.29275 | 0.28965 | 0.31627 | 0.31604 | 0.31571 | 0.31522 | 0.31323 | 0.31221 | 0.31075 | 0.30909 | 0.30627 | 0.30479 | 0.29773 | 0.29648 | 0.29619 | 0.29503 | 0.31203 | 0.31186 | 0.31123 | 0.31033 | 0.30674 | 0.30439 | 0.30152 | 0.29842 | 0.29319 | 0.29058 | 0.27983 | 0.2771 | 0.27591 | 0.27319
| STONEFIELD | CT |  |  | 0.33212 | 0.33241 | 0.33228 | 0.33179 | 0.32833 | 0.32597 | 0.32273 | 0.31887 | 0.31483 | 0.31212 | 0.30164 | 0.29651 | 0.29435 | 0.29298 | 0.31688 | 0.31698 | 0.31686 | 0.31655 | 0.31456 | 0.31328 | 0.31155 | 0.30975 | 0.30805 | 0.30649 | 0.29958 | 0.2976 | 0.29687 | 0.29637 | 0.31374 | 0.31381 | 0.31369 | 0.31345 | 0.31 | 0.30737 | 0.3037 | 0.29986 | 0.29626 | 0.29373 | 0.28379 | 0.27923 | 0.27735 | 0.27614
| STONEFIELD | LW |  |  | 0.33078 | 0.3305 | 0.32993 | 0.32909 | 0.32561 | 0.32364 | 0.32064 | 0.31726 | 0.3115 | 0.30866 | 0.29721 | 0.29416 | 0.2956 | 0.29534 | 0.31627 | 0.31604 | 0.31571 | 0.31522 | 0.31323 | 0.31221 | 0.31075 | 0.30909 | 0.30627 | 0.30479 | 0.29773 | 0.29648 | 0.29697 | 0.29688 | 0.31203 | 0.31186 | 0.31123 | 0.31033 | 0.30674 | 0.30439 | 0.30152 | 0.29842 | 0.29319 | 0.29058 | 0.27983 | 0.2771 | 0.27836 | 0.27813
| STONEFIELD | ST |  |  | 0.33191 | 0.33176 | 0.33138 | 0.3313 | 0.33104 | 0.33058 | 0.33034 | 0.32877 | 0.32818 | 0.32687 | 0.32149 | 0.30869 | 0.30381 | 0.30079 | 0.31684 | 0.31676 | 0.31652 | 0.31645 | 0.31629 | 0.316 | 0.31587 | 0.31484 | 0.31452 | 0.31375 | 0.31047 | 0.30208 | 0.30001 | 0.29898 | 0.31338 | 0.3132 | 0.31285 | 0.31278 | 0.31252 | 0.31206 | 0.31178 | 0.31044 | 0.30974 | 0.30836 | 0.30302 | 0.29061 | 0.28561 | 0.28297
| STONEFIELD | SP |  |  | 0.33185 | 0.33164 | 0.33148 | 0.33102 | 0.32985 | 0.32894 | 0.32773 | 0.32632 | 0.32509 | 0.32215 | 0.31603 | 0.30349 | 0.29275 | 0.28965 | 0.31681 | 0.3167 | 0.31662 | 0.31633 | 0.31571 | 0.31525 | 0.31461 | 0.31384 | 0.31329 | 0.31163 | 0.30892 | 0.30271 | 0.29619 | 0.29503 | 0.31331 | 0.31306 | 0.31287 | 0.31244 | 0.31111 | 0.31002 | 0.30865 | 0.30712 | 0.30587 | 0.30296 | 0.29751 | 0.28601 | 0.27591 | 0.27319
FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | YES | 18.5768 | 17.7881 | 16.8765 | 15.9325 | 14.6543 | 13.5556 | 12.4486 | 11.3341 | 10.1882 | 9.2493 | 6.6597 | 3.37 | 1.7551 | 1.1963 | 20.9459 | 20.2773 | 19.4797 | 18.6843 | 17.7584 | 17.0215 | 16.2911 | 15.577 | 14.8646 | 14.2413 | 12.5819 | 10.7676 | 9.8345 | 9.1012 | 20.0491 | 19.3257 | 18.4834 | 17.6087 | 16.4296 | 15.4179 | 14.3919 | 13.3591 | 12.2984 | 11.4177 | 8.9976 | 6.0412 | 4.6193 | 4.1301
| STONEHAVEN | CT |  |  | 18.6085 | 17.8511 | 16.9462 | 16.0354 | 14.8052 | 13.8231 | 12.8612 | 11.9077 | 10.9739 | 9.9239 | 6.788 | 3.37 | 1.7551 | 1.1963 | 20.9459 | 20.2773 | 19.4797 | 18.6843 | 17.7584 | 17.0949 | 16.4707 | 15.8692 | 15.2959 | 14.6215 | 12.6372 | 10.7676 | 9.8345 | 9.1012 | 20.0721 | 19.3758 | 18.5365 | 17.6892 | 16.5539 | 15.6554 | 14.7737 | 13.8992 | 13.0442 | 12.0667 | 9.1455 | 6.0412 | 4.6193 | 4.1301
| STONEHAVEN | LW |  |  | 18.5768 | 17.7881 | 16.8765 | 15.9325 | 14.6543 | 13.5556 | 12.4486 | 11.3341 | 10.1882 | 9.2493 | 6.6597 | 4.075 | 2.9707 | 2.5892 | 20.9566 | 20.2823 | 19.4983 | 18.7033 | 17.7606 | 17.0215 | 16.2911 | 15.577 | 14.8646 | 14.2413 | 12.5819 | 11.1903 | 10.7739 | 10.6296 | 20.0491 | 19.3257 | 18.4834 | 17.6087 | 16.4296 | 15.4179 | 14.3919 | 13.3591 | 12.2984 | 11.4177 | 8.9976 | 6.6266 | 5.6588 | 5.3249
| STONEHAVEN | ST |  |  | 18.7564 | 18.0667 | 17.2763 | 16.5093 | 15.7506 | 15.286 | 14.8796 | 14.5141 | 14.1733 | 13.7593 | 12.4275 | 9.4838 | 8.0435 | 7.3142 | 21.0479 | 20.4322 | 19.7149 | 18.9734 | 18.1044 | 17.6219 | 17.1989 | 16.8284 | 16.5083 | 16.1978 | 15.3265 | 13.357 | 12.2867 | 11.4625 | 20.2141 | 19.5844 | 18.8555 | 18.1476 | 17.4402 | 17.0095 | 16.628 | 16.2827 | 15.9606 | 15.5676 | 14.2928 | 11.5776 | 10.2352 | 9.5461
| STONEHAVEN | SP |  |  | 18.7741 | 18.1006 | 17.3245 | 16.5736 | 15.7766 | 15.2845 | 14.8364 | 14.4244 | 14.0518 | 13.6845 | 12.579 | 10.246 | 8.6184 | 8.2248 | 21.0529 | 20.4459 | 19.7349 | 18.9971 | 18.1229 | 17.6382 | 17.2104 | 16.8351 | 16.515 | 16.2312 | 15.4687 | 13.7822 | 12.0898 | 10.6584 | 20.2294 | 19.6148 | 18.8989 | 18.2066 | 17.4657 | 17.0119 | 16.5934 | 16.2066 | 15.8562 | 15.512 | 14.4743 | 12.2608 | 10.7911 | 10.4269
STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 67734109 | NO | 2.0796 | 2.0795 | 2.0795 | 2.0794 | 2.0794 | 2.0793 | 2.0792 | 2.079 | 2.0789 | 2.0787 | 2.0732 | 2.0616 | 2.0617 | 2.0616 | 1.9265 | 1.9263 | 1.9261 | 1.9256 | 1.9252 | 1.9247 | 1.9241 | 1.9233 | 1.9223 | 1.9212 | 1.9176 | 1.9149 | 1.915 | 1.9149 | 1.7258 | 1.7254 | 1.7249 | 1.7242 | 1.7235 | 1.7227 | 1.7218 | 1.7207 | 1.7194 | 1.7176 | 1.7118 | 1.7064 | 1.7064 | 1.7064
| STONEYHILL | CT |  |  | 2.0796 | 2.0796 | 2.0795 | 2.0795 | 2.0794 | 2.0793 | 2.0792 | 2.079 | 2.0789 | 2.0788 | 2.0783 | 2.0703 | 2.0699 | 2.0698 | 1.9266 | 1.9264 | 1.9262 | 1.9258 | 1.9254 | 1.9248 | 1.9242 | 1.9233 | 1.9225 | 1.9217 | 1.9191 | 1.9169 | 1.9166 | 1.9165 | 1.7258 | 1.7254 | 1.7249 | 1.7242 | 1.7236 | 1.7227 | 1.7219 | 1.721 | 1.72 | 1.7187 | 1.7147 | 1.7105 | 1.7104 | 1.7104
| STONEYHILL | LW |  |  | 2.0796 | 2.0795 | 2.0795 | 2.0794 | 2.0794 | 2.0793 | 2.0792 | 2.0791 | 2.0789 | 2.0787 | 2.0732 | 2.0616 | 2.0617 | 2.0616 | 1.9265 | 1.9263 | 1.9261 | 1.9256 | 1.9252 | 1.9247 | 1.9241 | 1.9234 | 1.9223 | 1.9212 | 1.9176 | 1.9149 | 1.915 | 1.9149 | 1.7259 | 1.7254 | 1.7249 | 1.7242 | 1.7235 | 1.7228 | 1.7218 | 1.7207 | 1.7194 | 1.7176 | 1.7118 | 1.7064 | 1.7064 | 1.7064
| STONEYHILL | ST |  |  | 2.0796 | 2.0796 | 2.0796 | 2.0795 | 2.0795 | 2.0795 | 2.0794 | 2.0794 | 2.0793 | 2.0793 | 2.079 | 2.0721 | 2.0657 | 2.0654 | 1.9267 | 1.9266 | 1.9265 | 1.9264 | 1.9262 | 1.926 | 1.9258 | 1.9256 | 1.9251 | 1.9247 | 1.9228 | 1.918 | 1.9163 | 1.916 | 1.7262 | 1.726 | 1.7258 | 1.7255 | 1.7252 | 1.7249 | 1.7245 | 1.724 | 1.7234 | 1.7226 | 1.7194 | 1.711 | 1.7081 | 1.7081
| STONEYHILL | SP |  |  | 2.0796 | 2.0796 | 2.0796 | 2.0796 | 2.0795 | 2.0795 | 2.0795 | 2.0794 | 2.0794 | 2.0793 | 2.0791 | 2.0784 | 2.0706 | 2.0691 | 1.9267 | 1.9267 | 1.9266 | 1.9265 | 1.9264 | 1.9262 | 1.926 | 1.9257 | 1.9254 | 1.9251 | 1.9238 | 1.9198 | 1.9167 | 1.9161 | 1.7262 | 1.726 | 1.7259 | 1.7257 | 1.7255 | 1.7253 | 1.725 | 1.7246 | 1.7243 | 1.7238 | 1.722 | 1.7159 | 1.7107 | 1.7101
PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | 13.7892 | 12.7991 | 11.673 | 10.5439 | 9.6579 | 8.8184 | 7.9481 | 7.1741 | 6.5868 | 6.0963 | 4.6793 | 3.5904 | 3.1217 | 2.9429 | 9.6621 | 8.6181 | 7.4198 | 6.1998 | 5.3889 | 4.6372 | 3.9052 | 3.3178 | 2.7523 | 2.2318 | 0.77201 | -0.2003 | -0.3324 | -0.39186 | 9.9632 | 9.0905 | 8.0751 | 6.9303 | 6.1296 | 5.3652 | 4.6243 | 3.9717 | 3.3509 | 2.7433 | 0.97499 | -0.409 | -0.47911 | -0.55647
| STONEYWOOD T1&T2 | CT |  |  | 13.8063 | 12.8288 | 11.7165 | 10.5866 | 9.6972 | 8.8478 | 8.0605 | 7.3978 | 6.8179 | 6.3076 | 4.9147 | 3.6101 | 3.1217 | 2.9429 | 9.6621 | 8.6181 | 7.4198 | 6.1998 | 5.3889 | 4.6372 | 3.9052 | 3.3286 | 2.8012 | 2.3194 | 1.0889 | 0.27402 | 0.20001 | 0.17329 | 9.9753 | 9.1128 | 8.0751 | 6.9303 | 6.1296 | 5.3652 | 4.6293 | 4.0111 | 3.4434 | 2.8887 | 1.4438 | 0.2672 | 0.13301 | 0.093459
| STONEYWOOD T1&T2 | LW |  |  | 13.7892 | 12.7991 | 11.673 | 10.5439 | 9.6579 | 8.8184 | 7.9481 | 7.1741 | 6.5868 | 6.0963 | 4.6793 | 3.5904 | 3.2639 | 3.1425 | 9.6817 | 8.6363 | 7.4409 | 6.2229 | 5.4112 | 4.6646 | 3.9129 | 3.3178 | 2.7523 | 2.2318 | 0.77201 | -0.2003 | -0.23733 | -0.25258 | 9.9632 | 9.0905 | 8.0945 | 6.9545 | 6.1521 | 5.3957 | 4.6243 | 3.9717 | 3.3509 | 2.7433 | 0.97499 | -0.409 | -0.47891 | -0.50374
| STONEYWOOD T1&T2 | ST |  |  | 13.8755 | 12.9276 | 11.8527 | 10.7793 | 10.0902 | 9.4814 | 8.8551 | 8.3604 | 7.9638 | 7.6165 | 6.6845 | 5.4709 | 4.8045 | 4.5185 | 9.7313 | 8.7288 | 7.5801 | 6.4236 | 5.6952 | 5.0458 | 4.3826 | 3.8812 | 3.4264 | 3.0145 | 1.8394 | 0.32598 | -0.3324 | -0.39186 | 10.0388 | 9.2043 | 8.2355 | 7.1383 | 6.4441 | 5.8291 | 5.2011 | 4.7231 | 4.3115 | 3.9542 | 2.6213 | 0.47657 | -0.47911 | -0.55647
| STONEYWOOD T1&T2 | SP |  |  | 13.8819 | 12.9384 | 11.8673 | 10.8007 | 10.103 | 9.4885 | 8.8618 | 8.3667 | 7.9649 | 7.6361 | 6.8099 | 5.9804 | 5.2943 | 5.1296 | 9.7353 | 8.7385 | 7.5952 | 6.447 | 5.7282 | 5.0917 | 4.4508 | 3.9701 | 3.5457 | 3.1873 | 2.2359 | 1.1394 | 0.13681 | -0.12023 | 10.0446 | 9.2142 | 8.248 | 7.1572 | 6.4662 | 5.8569 | 5.2408 | 4.774 | 4.3777 | 4.0544 | 3.1883 | 1.6432 | 0.19604 | -0.15451
PERSLEY | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | 5.2004 | 4.6987 | 4.1267 | 3.5467 | 3.1569 | 2.7994 | 2.4485 | 2.1628 | 1.905 | 1.6764 | 0.99907 | 0.37553 | 0.23804 | 0.14742 | 7.6018 | 7.0945 | 6.5125 | 5.921 | 5.5299 | 5.1698 | 4.8191 | 4.5445 | 4.2817 | 4.0459 | 3.3933 | 2.9847 | 2.9368 | 2.9077 | 5.9625 | 5.4768 | 4.92 | 4.3476 | 3.9472 | 3.565 | 3.1946 | 2.8683 | 2.5579 | 2.2541 | 1.3699 | 0.67795 | 0.6429 | 0.60422
| STONEYWOOD T3 | CT |  |  | 5.2004 | 4.6987 | 4.1267 | 3.5467 | 3.1569 | 2.7994 | 2.4485 | 2.1653 | 1.922 | 1.7079 | 1.1195 | 0.48275 | 0.23804 | 0.14742 | 7.6018 | 7.0945 | 6.5125 | 5.921 | 5.5299 | 5.1698 | 4.8191 | 4.547 | 4.2993 | 4.079 | 3.5189 | 3.1717 | 3.1383 | 3.1243 | 5.9625 | 5.4768 | 4.92 | 4.3476 | 3.9472 | 3.565 | 3.1971 | 2.888 | 2.6042 | 2.3268 | 1.6044 | 1.0161 | 0.94896 | 0.92918
| STONEYWOOD T3 | LW |  |  | 5.2082 | 4.7061 | 4.1356 | 3.5572 | 3.1681 | 2.813 | 2.4545 | 2.1628 | 1.905 | 1.6764 | 0.99907 | 0.37553 | 0.29602 | 0.23253 | 7.61 | 7.1023 | 6.5217 | 5.9314 | 5.5401 | 5.1827 | 4.8244 | 4.5445 | 4.2817 | 4.0459 | 3.3933 | 2.9847 | 2.9532 | 2.9406 | 5.9751 | 5.4875 | 4.9316 | 4.3597 | 3.9585 | 3.5803 | 3.1946 | 2.8683 | 2.5579 | 2.2541 | 1.3699 | 0.67795 | 0.643 | 0.63058
| STONEYWOOD T3 | ST |  |  | 5.2284 | 4.7434 | 4.1914 | 3.6386 | 3.2858 | 2.9734 | 2.6523 | 2.4014 | 2.1902 | 2.006 | 1.4966 | 0.84178 | 0.34379 | 0.30281 | 7.6305 | 7.1405 | 6.5767 | 5.991 | 5.6234 | 5.2976 | 4.9689 | 4.7286 | 4.513 | 4.3316 | 3.8404 | 3.2105 | 2.9368 | 2.9077 | 6.0139 | 5.5585 | 5.0379 | 4.5111 | 4.1758 | 3.8745 | 3.5611 | 3.3113 | 3.0852 | 2.863 | 2.1931 | 1.1207 | 0.6429 | 0.60422
| STONEYWOOD T3 | SP |  |  | 5.2302 | 4.7474 | 4.1977 | 3.6483 | 3.2993 | 2.992 | 2.6795 | 2.4367 | 2.2368 | 2.0734 | 1.6519 | 1.2048 | 0.69388 | 0.51123 | 7.6323 | 7.1445 | 6.5812 | 5.9981 | 5.6331 | 5.3111 | 4.9886 | 4.7541 | 4.5465 | 4.3799 | 3.9544 | 3.5455 | 3.1319 | 3.0199 | 6.0168 | 5.5654 | 5.0487 | 4.5278 | 4.1989 | 3.9064 | 3.6087 | 3.3734 | 3.1691 | 2.9852 | 2.4766 | 1.7041 | 0.98047 | 0.8052
CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | 0.30189 | 0.29528 | 0.28715 | 0.27065 | 0.23657 | 0.15812 | 0.076602 | -0.014398 | -0.12606 | -0.19021 | -0.448 | -0.49758 | -0.46921 | -0.52414 | 0.6429 | 0.63853 | 0.63216 | 0.62226 | 0.60775 | 0.59363 | 0.57733 | 0.53742 | 0.47943 | 0.44007 | 0.26169 | 0.22555 | 0.23633 | 0.19816 | 0.44885 | 0.44719 | 0.44468 | 0.44126 | 0.42831 | 0.35819 | 0.28471 | 0.19988 | 0.084821 | 0.020908 | -0.23313 | -0.28474 | -0.2562 | -0.3173
| STRACHUR | CT |  |  | 0.3037 | 0.2976 | 0.28715 | 0.27065 | 0.24333 | 0.19088 | 0.10304 | 0.01705 | -0.063919 | -0.11798 | -0.32582 | -0.45691 | -0.43493 | -0.4322 | 0.64308 | 0.63853 | 0.63216 | 0.62226 | 0.60775 | 0.59363 | 0.57733 | 0.54974 | 0.51036 | 0.47711 | 0.3338 | 0.23998 | 0.24261 | 0.23623 | 0.44949 | 0.4476 | 0.44502 | 0.44126 | 0.43554 | 0.3846 | 0.30616 | 0.22926 | 0.1533 | 0.099869 | -0.10433 | -0.23826 | -0.22129 | -0.22169
| STRACHUR | LW |  |  | 0.30189 | 0.29811 | 0.28913 | 0.27738 | 0.23657 | 0.15812 | 0.076602 | -0.014398 | -0.12606 | -0.19021 | -0.448 | -0.49758 | -0.45917 | -0.47704 | 0.6429 | 0.6394 | 0.63388 | 0.62668 | 0.61254 | 0.59681 | 0.58127 | 0.53742 | 0.47943 | 0.44007 | 0.26169 | 0.22555 | 0.23921 | 0.23234 | 0.44885 | 0.44719 | 0.44468 | 0.44174 | 0.42831 | 0.35819 | 0.28471 | 0.19988 | 0.084821 | 0.020908 | -0.23313 | -0.28474 | -0.24314 | -0.26107
| STRACHUR | ST |  |  | 0.30284 | 0.29528 | 0.28794 | 0.2797 | 0.27537 | 0.26936 | 0.26334 | 0.25873 | 0.25248 | 0.2343 | 0.12511 | -0.16235 | -0.22394 | -0.24497 | 0.64395 | 0.63971 | 0.63551 | 0.63043 | 0.62695 | 0.62244 | 0.61801 | 0.61401 | 0.6093 | 0.60216 | 0.57665 | 0.36403 | 0.32159 | 0.30572 | 0.4493 | 0.44719 | 0.44511 | 0.44276 | 0.44096 | 0.43878 | 0.43666 | 0.43488 | 0.43291 | 0.42542 | 0.32189 | 0.042052 | -0.015884 | -0.034493
| STRACHUR | SP |  |  | 0.30602 | 0.30005 | 0.29466 | 0.28887 | 0.27891 | 0.26906 | 0.25861 | 0.24551 | 0.21278 | 0.16507 | 0.040628 | -0.25541 | -0.46921 | -0.52414 | 0.64521 | 0.64169 | 0.6383 | 0.63454 | 0.62917 | 0.62379 | 0.61804 | 0.6123 | 0.60626 | 0.59772 | 0.5591 | 0.38539 | 0.23633 | 0.19816 | 0.44973 | 0.44787 | 0.44604 | 0.44411 | 0.44139 | 0.43866 | 0.4358 | 0.43311 | 0.40965 | 0.36646 | 0.25276 | -0.040626 | -0.2562 | -0.3173
TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | NO | 1.8848 | 1.8723 | 1.8562 | 1.8375 | 1.804 | 1.759 | 1.7044 | 1.6499 | 1.558 | 1.4804 | 1.3176 | 1.2572 | 1.2557 | 1.2141 | 2.1342 | 2.1274 | 2.1182 | 2.1074 | 2.0907 | 2.0673 | 2.0402 | 2.0139 | 1.9713 | 1.9239 | 1.8354 | 1.8097 | 1.8047 | 1.7694 | 2.0164 | 2.0042 | 1.9885 | 1.9702 | 1.9378 | 1.8944 | 1.8469 | 1.8 | 1.7215 | 1.6493 | 1.5036 | 1.4543 | 1.4548 | 1.4197
| STRATHDON | CT |  |  | 1.8932 | 1.8863 | 1.8712 | 1.8572 | 1.8167 | 1.7787 | 1.7259 | 1.6579 | 1.5937 | 1.5497 | 1.3813 | 1.2854 | 1.2557 | 1.2371 | 2.1368 | 2.1321 | 2.1217 | 2.1126 | 2.0907 | 2.071 | 2.0477 | 2.0207 | 1.9944 | 1.9698 | 1.8649 | 1.82 | 1.8047 | 1.7904 | 2.0245 | 2.0177 | 2.003 | 1.9892 | 1.95 | 1.9135 | 1.8643 | 1.8088 | 1.7558 | 1.7162 | 1.5589 | 1.4779 | 1.4548 | 1.4403
| STRATHDON | LW |  |  | 1.8848 | 1.8723 | 1.8562 | 1.8375 | 1.804 | 1.759 | 1.7044 | 1.6499 | 1.558 | 1.4804 | 1.3176 | 1.2572 | 1.2731 | 1.2691 | 2.1342 | 2.1274 | 2.1182 | 2.1074 | 2.0911 | 2.0673 | 2.0402 | 2.0139 | 1.9713 | 1.9239 | 1.8354 | 1.8097 | 1.8155 | 1.814 | 2.0164 | 2.0042 | 1.9885 | 1.9702 | 1.9378 | 1.8944 | 1.8469 | 1.8 | 1.7215 | 1.6493 | 1.5036 | 1.4543 | 1.4667 | 1.4636
| STRATHDON | ST |  |  | 1.8956 | 1.8919 | 1.8869 | 1.881 | 1.873 | 1.8588 | 1.8495 | 1.8372 | 1.8172 | 1.7936 | 1.7028 | 1.4723 | 1.3825 | 1.342 | 2.139 | 2.1368 | 2.1337 | 2.1299 | 2.1251 | 2.1158 | 2.1101 | 2.1024 | 2.0908 | 2.0776 | 2.023 | 1.8811 | 1.8462 | 1.8258 | 2.0269 | 2.0232 | 2.0184 | 2.0126 | 2.005 | 1.9916 | 1.9827 | 1.9709 | 1.9514 | 1.9285 | 1.8401 | 1.6243 | 1.5526 | 1.5212
| STRATHDON | SP |  |  | 1.8981 | 1.8955 | 1.8922 | 1.8881 | 1.8788 | 1.8668 | 1.8531 | 1.8365 | 1.822 | 1.7997 | 1.7167 | 1.4583 | 1.2807 | 1.2141 | 2.1405 | 2.1388 | 2.1367 | 2.1339 | 2.1291 | 2.1224 | 2.1143 | 2.1042 | 2.0958 | 2.0825 | 2.0414 | 1.901 | 1.8066 | 1.7694 | 2.0294 | 2.0267 | 2.0236 | 2.0195 | 2.0106 | 1.9994 | 1.9862 | 1.9703 | 1.9563 | 1.9346 | 1.8566 | 1.6264 | 1.4717 | 1.4197
STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | 10.0978 | 9.9225 | 9.7163 | 9.4897 | 9.1432 | 8.8414 | 8.5436 | 8.2059 | 7.8135 | 7.52 | 6.91 | 6.6385 | 6.7276 | 6.5671 | 10.9795 | 10.842 | 10.6614 | 10.4742 | 10.2782 | 10.1061 | 9.9353 | 9.7297 | 9.5145 | 9.3071 | 8.9302 | 8.7666 | 8.7964 | 8.6402 | 10.6041 | 10.4344 | 10.2363 | 10.0206 | 9.6988 | 9.4253 | 9.1557 | 8.8541 | 8.505 | 8.2455 | 7.696 | 7.4481 | 7.527 | 7.3961
| STRICHEN | CT |  |  | 10.148 | 10.005 | 9.82 | 9.6264 | 9.3075 | 9.0587 | 8.733 | 8.3948 | 8.0776 | 7.861 | 7.2647 | 6.8661 | 6.7731 | 6.708 | 10.9911 | 10.8437 | 10.6614 | 10.4742 | 10.2782 | 10.162 | 9.9886 | 9.8091 | 9.6442 | 9.4936 | 9.0807 | 8.8553 | 8.8017 | 8.7484 | 10.6473 | 10.5059 | 10.3265 | 10.1399 | 9.8424 | 9.6154 | 9.3212 | 9.0176 | 8.733 | 8.5393 | 8.009 | 7.6547 | 7.5761 | 7.5204
| STRICHEN | LW |  |  | 10.0978 | 9.9225 | 9.7163 | 9.4897 | 9.1432 | 8.8414 | 8.5436 | 8.2059 | 7.8135 | 7.52 | 6.91 | 6.6385 | 6.7276 | 6.6941 | 10.9795 | 10.842 | 10.6719 | 10.4867 | 10.2798 | 10.1061 | 9.9353 | 9.7297 | 9.5145 | 9.3071 | 8.9302 | 8.7666 | 8.7964 | 8.7835 | 10.6041 | 10.4344 | 10.2363 | 10.0206 | 9.6988 | 9.4253 | 9.1557 | 8.8541 | 8.505 | 8.2455 | 7.696 | 7.4481 | 7.527 | 7.4973
| STRICHEN | ST |  |  | 10.1433 | 10.0036 | 9.8388 | 9.6688 | 9.4884 | 9.3675 | 9.2723 | 9.1756 | 9.0672 | 8.9424 | 8.5145 | 7.7491 | 7.4172 | 7.2546 | 10.9998 | 10.8654 | 10.6947 | 10.5218 | 10.3422 | 10.2404 | 10.1539 | 10.0765 | 10.0077 | 9.9433 | 9.7237 | 9.2104 | 9.0309 | 8.9395 | 10.6436 | 10.5049 | 10.3427 | 10.1764 | 10.0007 | 9.8869 | 9.7948 | 9.7028 | 9.6019 | 9.4876 | 9.1024 | 8.4469 | 8.1358 | 7.9941
| STRICHEN | SP |  |  | 10.1593 | 10.0303 | 9.8776 | 9.7235 | 9.532 | 9.4089 | 9.2988 | 9.1806 | 9.0761 | 8.9606 | 8.4971 | 7.4936 | 6.8637 | 6.5671 | 11.0044 | 10.8665 | 10.6974 | 10.5274 | 10.3496 | 10.2522 | 10.1676 | 10.0906 | 10.0259 | 9.9691 | 9.7718 | 9.1677 | 8.8149 | 8.6402 | 10.6579 | 10.5288 | 10.3775 | 10.2248 | 10.0395 | 9.9234 | 9.8187 | 9.7088 | 9.6119 | 9.5063 | 9.09 | 8.2131 | 7.6563 | 7.3961
THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | YES | 4.589 | 4.1166 | 3.6585 | 3.1802 | 2.4335 | 1.6901 | 0.94114 | 0.2253 | -0.47562 | -1.0265 | -2.2543 | -2.6577 | -2.3756 | -2.5426 | 6.7484 | 6.2641 | 5.8685 | 5.4865 | 5.0379 | 4.6055 | 4.1518 | 3.7729 | 3.4091 | 3.0018 | 2.141 | 1.6225 | 1.6774 | 1.651 | 5.8983 | 5.507 | 5.1405 | 4.7581 | 4.1883 | 3.5158 | 2.8308 | 2.1734 | 1.5292 | 1.0048 | -0.15898 | -0.55298 | -0.30566 | -0.44148
| STROMNESS | CT |  |  | 4.7493 | 4.2911 | 3.8589 | 3.31 | 2.5304 | 1.7881 | 1.1369 | 0.48104 | -0.13589 | -0.57132 | -1.7921 | -2.4522 | -2.2524 | -2.2085 | 6.7484 | 6.2641 | 5.9126 | 5.5413 | 5.0872 | 4.6581 | 4.22 | 3.8516 | 3.5127 | 3.1619 | 2.3722 | 1.8467 | 1.8458 | 1.8532 | 5.998 | 5.6145 | 5.2572 | 4.8021 | 4.2029 | 3.5928 | 2.9951 | 2.3978 | 1.8349 | 1.4237 | 0.2617 | -0.36689 | -0.19367 | -0.15482
| STROMNESS | LW |  |  | 4.589 | 4.1166 | 3.6585 | 3.1802 | 2.4335 | 1.6901 | 0.94114 | 0.2253 | -0.47562 | -1.0265 | -2.2543 | -2.6577 | -2.3756 | -2.5071 | 6.7544 | 6.2829 | 5.8685 | 5.4865 | 5.0379 | 4.6055 | 4.1518 | 3.7729 | 3.4091 | 3.0018 | 2.141 | 1.6225 | 1.6774 | 1.651 | 5.8983 | 5.507 | 5.1405 | 4.7581 | 4.1883 | 3.5158 | 2.8308 | 2.1734 | 1.5292 | 1.0048 | -0.15898 | -0.55298 | -0.30566 | -0.42081
| STROMNESS | ST |  |  | 4.7434 | 4.2799 | 3.9418 | 3.6044 | 3.3256 | 3.0197 | 2.7209 | 2.515 | 2.2551 | 1.8962 | 1.0055 | -0.25095 | -0.66787 | -0.81449 | 6.7688 | 6.3056 | 5.9621 | 5.6402 | 5.3488 | 5.0393 | 4.7334 | 4.5007 | 4.2465 | 3.9232 | 3.2238 | 2.3764 | 2.0513 | 1.9707 | 6.0061 | 5.6267 | 5.3482 | 5.0677 | 4.837 | 4.5827 | 4.3324 | 4.1596 | 3.9464 | 3.6332 | 2.7922 | 1.5891 | 1.1965 | 1.0665
| STROMNESS | SP |  |  | 4.7619 | 4.3093 | 3.988 | 3.6924 | 3.3103 | 2.923 | 2.5361 | 2.2121 | 1.855 | 1.383 | 0.33528 | -1.3839 | -2.2331 | -2.5426 | 6.7685 | 6.3073 | 5.9654 | 5.6477 | 5.3592 | 5.0216 | 4.6991 | 4.4471 | 4.1828 | 3.8488 | 3.1785 | 2.3778 | 1.8591 | 1.7081 | 6.0187 | 5.6488 | 5.3839 | 5.141 | 4.8429 | 4.5377 | 4.2338 | 3.957 | 3.6252 | 3.1896 | 2.2252 | 0.63237 | -0.16351 | -0.44148
THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | 0.7456 | 0.75078 | 0.74561 | 0.73646 | 0.70875 | 0.68293 | 0.65404 | 0.62368 | 0.5833 | 0.55717 | 0.47445 | 0.44273 | 0.43635 | 0.41868 | 0.85363 | 0.85508 | 0.85266 | 0.84802 | 0.83472 | 0.82196 | 0.8081 | 0.79242 | 0.7748 | 0.75881 | 0.70243 | 0.67933 | 0.6776 | 0.66378 | 0.7208 | 0.7234 | 0.72048 | 0.71515 | 0.69957 | 0.68509 | 0.66678 | 0.64662 | 0.62165 | 0.60143 | 0.5364 | 0.51102 | 0.50668 | 0.49572
| STRONSAY | CT |  |  | 0.76334 | 0.76898 | 0.7661 | 0.75237 | 0.71825 | 0.69118 | 0.65954 | 0.62399 | 0.58742 | 0.56931 | 0.49938 | 0.45129 | 0.45341 | 0.45089 | 0.86002 | 0.86154 | 0.85972 | 0.85166 | 0.83472 | 0.82196 | 0.8081 | 0.79242 | 0.7748 | 0.76396 | 0.7154 | 0.6819 | 0.67908 | 0.67415 | 0.73119 | 0.73439 | 0.73319 | 0.72476 | 0.70343 | 0.68755 | 0.66883 | 0.64799 | 0.62522 | 0.61203 | 0.55641 | 0.51807 | 0.51451 | 0.51125
| STRONSAY | LW |  |  | 0.7456 | 0.75078 | 0.74561 | 0.73646 | 0.70875 | 0.68293 | 0.65404 | 0.62368 | 0.5833 | 0.55717 | 0.47445 | 0.44273 | 0.45612 | 0.44747 | 0.85363 | 0.85508 | 0.85266 | 0.84802 | 0.8361 | 0.82474 | 0.81026 | 0.79409 | 0.77516 | 0.75881 | 0.70243 | 0.67933 | 0.68352 | 0.68026 | 0.7208 | 0.7234 | 0.72048 | 0.71515 | 0.69957 | 0.68509 | 0.66678 | 0.64662 | 0.62165 | 0.60143 | 0.5364 | 0.51102 | 0.51772 | 0.51399
| STRONSAY | ST |  |  | 0.75815 | 0.75666 | 0.75567 | 0.75429 | 0.75213 | 0.75059 | 0.74506 | 0.74205 | 0.73683 | 0.72402 | 0.6851 | 0.5794 | 0.54199 | 0.52519 | 0.85857 | 0.85773 | 0.85709 | 0.8557 | 0.8536 | 0.85243 | 0.84809 | 0.84513 | 0.8424 | 0.83481 | 0.81069 | 0.73211 | 0.70971 | 0.6988 | 0.72804 | 0.72707 | 0.72634 | 0.7252 | 0.72271 | 0.7213 | 0.71614 | 0.71284 | 0.70939 | 0.70005 | 0.67173 | 0.58668 | 0.55969 | 0.54859
| STRONSAY | SP |  |  | 0.75768 | 0.75563 | 0.75475 | 0.75376 | 0.7418 | 0.7308 | 0.71873 | 0.70424 | 0.68816 | 0.6637 | 0.61319 | 0.50329 | 0.43635 | 0.41868 | 0.85839 | 0.85735 | 0.85681 | 0.85619 | 0.85141 | 0.84692 | 0.84213 | 0.83563 | 0.82782 | 0.81613 | 0.7909 | 0.72898 | 0.6776 | 0.66378 | 0.72763 | 0.72625 | 0.72551 | 0.72471 | 0.7177 | 0.71114 | 0.7041 | 0.69507 | 0.68465 | 0.66904 | 0.63613 | 0.55979 | 0.50668 | 0.49572
FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | 2.0668 | 2.0613 | 2.055 | 2.0476 | 2.0248 | 1.9829 | 1.9347 | 1.8835 | 1.8107 | 1.7749 | 1.6518 | 1.6253 | 1.646 | 1.6066 | 2.259 | 2.2534 | 2.2461 | 2.2359 | 2.2166 | 2.1965 | 2.1738 | 2.1475 | 2.1129 | 2.0891 | 1.9941 | 1.9753 | 1.9771 | 1.9543 | 2.091 | 2.0845 | 2.072 | 2.055 | 2.0162 | 1.9764 | 1.9339 | 1.8873 | 1.8238 | 1.788 | 1.6522 | 1.625 | 1.6419 | 1.61
| STRONTIAN | CT |  |  | 2.0689 | 2.0641 | 2.0581 | 2.0485 | 2.0263 | 2.006 | 1.953 | 1.8936 | 1.8357 | 1.8061 | 1.7046 | 1.6452 | 1.6633 | 1.6652 | 2.2646 | 2.2599 | 2.2526 | 2.2387 | 2.2187 | 2.2004 | 2.1772 | 2.1527 | 2.1273 | 2.1079 | 2.0282 | 1.9825 | 1.9841 | 1.9797 | 2.105 | 2.1008 | 2.0902 | 2.0687 | 2.0301 | 1.9949 | 1.9478 | 1.8983 | 1.8496 | 1.8206 | 1.708 | 1.6431 | 1.6545 | 1.6554
| STRONTIAN | LW |  |  | 2.0668 | 2.0613 | 2.055 | 2.0476 | 2.0248 | 1.9829 | 1.9347 | 1.8835 | 1.8107 | 1.7749 | 1.6518 | 1.6253 | 1.6518 | 1.6362 | 2.259 | 2.2534 | 2.2461 | 2.2359 | 2.2166 | 2.1965 | 2.1738 | 2.1475 | 2.1129 | 2.0891 | 1.9941 | 1.9753 | 1.9836 | 1.9788 | 2.091 | 2.0845 | 2.072 | 2.055 | 2.0162 | 1.9764 | 1.9339 | 1.8873 | 1.8238 | 1.788 | 1.6522 | 1.625 | 1.6452 | 1.6338
| STRONTIAN | ST |  |  | 2.0708 | 2.0669 | 2.0628 | 2.0583 | 2.0558 | 2.0529 | 2.0492 | 2.0453 | 2.0383 | 2.0278 | 1.9882 | 1.8315 | 1.7964 | 1.785 | 2.2645 | 2.261 | 2.2568 | 2.2514 | 2.2487 | 2.2458 | 2.2417 | 2.2377 | 2.2298 | 2.216 | 2.1746 | 2.0609 | 2.0347 | 2.0237 | 2.1026 | 2.0977 | 2.0922 | 2.0852 | 2.0822 | 2.0785 | 2.0733 | 2.0684 | 2.0568 | 2.0362 | 1.9745 | 1.8187 | 1.778 | 1.7632
| STRONTIAN | SP |  |  | 2.0712 | 2.0676 | 2.064 | 2.06 | 2.0565 | 2.0529 | 2.0489 | 2.0443 | 2.0372 | 2.0185 | 1.9396 | 1.765 | 1.646 | 1.6066 | 2.2663 | 2.2633 | 2.2601 | 2.2565 | 2.2506 | 2.2448 | 2.2389 | 2.231 | 2.2196 | 2.2053 | 2.166 | 2.0634 | 1.9771 | 1.9543 | 2.1057 | 2.1019 | 2.0983 | 2.0942 | 2.0829 | 2.0723 | 2.0611 | 2.0471 | 2.0285 | 2.0034 | 1.9333 | 1.7661 | 1.6419 | 1.61
SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | 2.8021 | 2.7846 | 2.748 | 2.7076 | 2.6181 | 2.5255 | 2.4228 | 2.318 | 2.1981 | 2.1232 | 1.8704 | 1.6557 | 1.4097 | 1.2267 | 3.1294 | 3.1187 | 3.1 | 3.0819 | 3.0428 | 3.0032 | 2.9545 | 2.9041 | 2.8479 | 2.7934 | 2.5919 | 2.3557 | 2.0829 | 1.9528 | 2.7784 | 2.7645 | 2.735 | 2.6891 | 2.6126 | 2.5387 | 2.4604 | 2.3711 | 2.2776 | 2.192 | 1.9544 | 1.7488 | 1.4536 | 1.2717
| SUMBURGH | CT |  |  | 2.8127 | 2.7985 | 2.7614 | 2.7076 | 2.6181 | 2.5309 | 2.438 | 2.3221 | 2.224 | 2.1587 | 1.9617 | 1.7719 | 1.7946 | 1.794 | 3.1327 | 3.1232 | 3.1042 | 3.0819 | 3.0428 | 3.0041 | 2.9595 | 2.9064 | 2.8633 | 2.82 | 2.6567 | 2.4837 | 2.4666 | 2.4553 | 2.7845 | 2.7719 | 2.7401 | 2.6891 | 2.6126 | 2.5387 | 2.4659 | 2.3711 | 2.2901 | 2.2376 | 2.039 | 1.8586 | 1.8764 | 1.875
| SUMBURGH | LW |  |  | 2.8021 | 2.7846 | 2.748 | 2.7109 | 2.6201 | 2.5255 | 2.4228 | 2.318 | 2.1981 | 2.1232 | 1.8704 | 1.6557 | 1.6901 | 1.6619 | 3.1294 | 3.1187 | 3.1 | 3.0842 | 3.0447 | 3.0032 | 2.9545 | 2.9041 | 2.8479 | 2.7934 | 2.5919 | 2.3828 | 2.3823 | 2.3752 | 2.7784 | 2.7645 | 2.735 | 2.7025 | 2.6253 | 2.5451 | 2.4604 | 2.3742 | 2.2776 | 2.192 | 1.9544 | 1.7488 | 1.778 | 1.7532
| SUMBURGH | ST |  |  | 2.8352 | 2.8201 | 2.8178 | 2.7973 | 2.7973 | 2.7865 | 2.7701 | 2.7529 | 2.7135 | 2.6527 | 2.4326 | 1.9175 | 1.6461 | 1.6135 | 3.1497 | 3.137 | 3.1355 | 3.1233 | 3.1222 | 3.1137 | 3.1048 | 3.0956 | 3.0638 | 3.0151 | 2.8286 | 2.3557 | 2.1065 | 2.0865 | 2.8009 | 2.7912 | 2.7901 | 2.774 | 2.7758 | 2.7715 | 2.7671 | 2.7603 | 2.7233 | 2.6662 | 2.4583 | 1.8843 | 1.5648 | 1.5318
| SUMBURGH | SP |  |  | 2.8441 | 2.8336 | 2.8366 | 2.8394 | 2.8199 | 2.809 | 2.7852 | 2.759 | 2.7169 | 2.6644 | 2.4443 | 1.9117 | 1.4097 | 1.2267 | 3.153 | 3.1422 | 3.1427 | 3.1431 | 3.1323 | 3.1282 | 3.1167 | 3.1042 | 3.0777 | 3.0422 | 2.8926 | 2.4978 | 2.0829 | 1.9528 | 2.8095 | 2.8041 | 2.8079 | 2.8117 | 2.8009 | 2.796 | 2.7847 | 2.7673 | 2.728 | 2.6794 | 2.4759 | 1.9793 | 1.4536 | 1.2717
ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | YES | 8.0784 | 7.8981 | 7.7258 | 7.6004 | 7.2497 | 6.8943 | 6.4984 | 6.0803 | 5.5755 | 5.2569 | 4.2143 | 3.512 | 3.658 | 3.3029 | 10.0771 | 9.8793 | 9.6312 | 9.4319 | 9.2743 | 9.1236 | 8.9475 | 8.7011 | 8.4217 | 8.2029 | 7.5168 | 6.9839 | 6.9666 | 6.5435 | 9.1646 | 8.9412 | 8.7206 | 8.5525 | 8.1413 | 7.7506 | 7.3789 | 6.9537 | 6.453 | 6.1036 | 5.0453 | 4.4025 | 4.563 | 4.2609
| TAIN | CT |  |  | 8.1786 | 8.0565 | 7.9354 | 7.8858 | 7.5192 | 7.1816 | 6.8218 | 6.3848 | 5.9385 | 5.6736 | 4.8847 | 3.9425 | 3.8876 | 3.8328 | 10.0771 | 9.8793 | 9.6312 | 9.4319 | 9.2743 | 9.1236 | 8.9945 | 8.7943 | 8.5529 | 8.3748 | 7.8403 | 7.1993 | 7.0999 | 6.978 | 9.2797 | 9.1224 | 8.9374 | 8.7454 | 8.4625 | 8.0717 | 7.6571 | 7.2203 | 6.793 | 6.5151 | 5.6517 | 4.8019 | 4.7593 | 4.7121
| TAIN | LW |  |  | 8.0784 | 7.8981 | 7.7258 | 7.6004 | 7.2497 | 6.8943 | 6.4984 | 6.0803 | 5.5755 | 5.2569 | 4.2143 | 3.512 | 3.658 | 3.6276 | 10.0884 | 9.8976 | 9.6511 | 9.4679 | 9.3203 | 9.1621 | 8.9475 | 8.7011 | 8.4217 | 8.2029 | 7.5168 | 6.9839 | 7.0562 | 7.0337 | 9.1646 | 8.9412 | 8.7206 | 8.5525 | 8.1413 | 7.7506 | 7.3789 | 6.9537 | 6.453 | 6.1036 | 5.0453 | 4.4025 | 4.6012 | 4.5483
| TAIN | ST |  |  | 8.1811 | 8.0442 | 7.8778 | 7.7632 | 7.6494 | 7.5653 | 7.4808 | 7.3869 | 7.2854 | 7.133 | 6.5259 | 4.8075 | 3.9487 | 3.8336 | 10.1126 | 9.9381 | 9.713 | 9.5547 | 9.4403 | 9.3368 | 9.2437 | 9.1433 | 9.0436 | 8.9321 | 8.5793 | 7.793 | 7.3727 | 7.2329 | 9.2915 | 9.1239 | 8.9192 | 8.7739 | 8.6417 | 8.546 | 8.4526 | 8.3514 | 8.2402 | 8.0693 | 7.4974 | 6.1664 | 5.6067 | 5.4605
| TAIN | SP |  |  | 8.2248 | 8.1157 | 7.9748 | 7.8817 | 7.736 | 7.5857 | 7.4491 | 7.2955 | 7.1293 | 6.9279 | 6.3332 | 4.8738 | 3.6894 | 3.3029 | 10.1141 | 9.9427 | 9.7201 | 9.567 | 9.4586 | 9.362 | 9.2785 | 9.1918 | 9.0963 | 9.0113 | 8.6893 | 7.8283 | 6.9666 | 6.5435 | 9.3412 | 9.205 | 9.0296 | 8.9067 | 8.7362 | 8.5639 | 8.4082 | 8.2415 | 8.0647 | 7.8389 | 7.167 | 5.6756 | 4.563 | 4.2609
ARDMORE | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | YES | 2.2974 | 2.3233 | 2.2782 | 2.2265 | 2.0487 | 1.886 | 1.7361 | 1.5769 | 1.4144 | 1.3274 | 1.0093 | 0.9102 | 0.79846 | 0.77959 | 2.6387 | 2.6359 | 2.596 | 2.5629 | 2.4896 | 2.4183 | 2.3514 | 2.2701 | 2.1864 | 2.1293 | 1.9088 | 1.8254 | 1.7963 | 1.7621 | 2.4638 | 2.4731 | 2.4347 | 2.3993 | 2.2632 | 2.116 | 1.9796 | 1.8292 | 1.676 | 1.593 | 1.2954 | 1.2091 | 1.1065 | 1.0914
| TARBERT | CT |  |  | 2.4039 | 2.4174 | 2.3845 | 2.3309 | 2.183 | 2.0294 | 1.8823 | 1.7257 | 1.5824 | 1.5132 | 1.2942 | 1.0121 | 1.0291 | 1.0204 | 2.6777 | 2.6506 | 2.6108 | 2.5824 | 2.527 | 2.4521 | 2.3847 | 2.3149 | 2.2494 | 2.203 | 2.0599 | 1.8624 | 1.8579 | 1.8444 | 2.5308 | 2.5313 | 2.5066 | 2.4743 | 2.3786 | 2.2376 | 2.102 | 1.9589 | 1.8272 | 1.758 | 1.5521 | 1.3029 | 1.3221 | 1.3156
| TARBERT | LW |  |  | 2.2974 | 2.3233 | 2.2782 | 2.2265 | 2.0487 | 1.886 | 1.7361 | 1.5769 | 1.4144 | 1.3274 | 1.0093 | 0.9102 | 1.0022 | 0.96995 | 2.6387 | 2.6359 | 2.596 | 2.5629 | 2.4896 | 2.4183 | 2.3514 | 2.2701 | 2.1864 | 2.1293 | 1.9088 | 1.8254 | 1.8564 | 1.8456 | 2.4638 | 2.4731 | 2.4347 | 2.3993 | 2.2632 | 2.116 | 1.9796 | 1.8292 | 1.676 | 1.593 | 1.2954 | 1.2091 | 1.2943 | 1.2643
| TARBERT | ST |  |  | 2.3703 | 2.3483 | 2.3193 | 2.3011 | 2.29 | 2.2707 | 2.253 | 2.2359 | 2.2095 | 2.1604 | 2.01 | 1.5797 | 1.4087 | 1.341 | 2.6725 | 2.6502 | 2.6189 | 2.5997 | 2.5883 | 2.5723 | 2.5584 | 2.5427 | 2.5232 | 2.4906 | 2.3937 | 2.0896 | 1.9838 | 1.9528 | 2.5137 | 2.4932 | 2.4655 | 2.4499 | 2.4383 | 2.4207 | 2.4046 | 2.3889 | 2.3663 | 2.3272 | 2.208 | 1.8377 | 1.6804 | 1.6285
| TARBERT | SP |  |  | 2.3677 | 2.3414 | 2.3114 | 2.2918 | 2.199 | 2.1072 | 2.0054 | 1.9 | 1.7939 | 1.636 | 1.4014 | 0.97467 | 0.79846 | 0.77959 | 2.6714 | 2.647 | 2.6152 | 2.5963 | 2.5536 | 2.5137 | 2.4696 | 2.4232 | 2.3737 | 2.3042 | 2.1897 | 1.9684 | 1.7963 | 1.7621 | 2.5109 | 2.4867 | 2.4576 | 2.439 | 2.3806 | 2.3135 | 2.2209 | 2.1255 | 2.0275 | 1.8838 | 1.6655 | 1.2775 | 1.1065 | 1.0914
PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | 0.15652 | 0.15453 | 0.15267 | 0.15024 | 0.14453 | 0.13813 | 0.13203 | 0.12513 | 0.11579 | 0.11077 | 0.090577 | 0.085657 | 0.08585 | 0.083147 | 0.15007 | 0.14891 | 0.14793 | 0.14671 | 0.14403 | 0.14098 | 0.1382 | 0.13482 | 0.13032 | 0.1276 | 0.11415 | 0.1122 | 0.11078 | 0.10756 | 0.14742 | 0.14539 | 0.14353 | 0.14132 | 0.13616 | 0.13037 | 0.12489 | 0.11861 | 0.11014 | 0.10552 | 0.086479 | 0.082116 | 0.082344 | 0.080046
| TARBERT JURA | CT |  |  | 0.15718 | 0.15658 | 0.15526 | 0.15381 | 0.14861 | 0.1432 | 0.13618 | 0.12889 | 0.12175 | 0.11762 | 0.099772 | 0.089609 | 0.08585 | 0.083373 | 0.15026 | 0.14986 | 0.149 | 0.14806 | 0.145 | 0.14249 | 0.13944 | 0.13632 | 0.13322 | 0.13077 | 0.1182 | 0.11289 | 0.11078 | 0.10856 | 0.14845 | 0.14786 | 0.1466 | 0.14518 | 0.13971 | 0.13477 | 0.1285 | 0.12201 | 0.11574 | 0.11178 | 0.094797 | 0.085628 | 0.082344 | 0.080185
| TARBERT JURA | LW |  |  | 0.15652 | 0.15453 | 0.15267 | 0.15024 | 0.14453 | 0.13813 | 0.13203 | 0.12513 | 0.11579 | 0.11077 | 0.090577 | 0.085657 | 0.087797 | 0.087135 | 0.15007 | 0.14891 | 0.14793 | 0.14671 | 0.14403 | 0.14098 | 0.1382 | 0.13482 | 0.13032 | 0.1276 | 0.11415 | 0.1122 | 0.11286 | 0.11256 | 0.14742 | 0.14539 | 0.14353 | 0.14132 | 0.13616 | 0.13037 | 0.12489 | 0.11861 | 0.11014 | 0.10552 | 0.086479 | 0.082116 | 0.084001 | 0.083433
| TARBERT JURA | ST |  |  | 0.15768 | 0.15742 | 0.15666 | 0.15613 | 0.15524 | 0.15416 | 0.15355 | 0.15204 | 0.15004 | 0.14772 | 0.13882 | 0.11317 | 0.10362 | 0.09826 | 0.15065 | 0.15049 | 0.14999 | 0.14964 | 0.14908 | 0.14839 | 0.148 | 0.14703 | 0.1458 | 0.14444 | 0.13925 | 0.12188 | 0.11723 | 0.11372 | 0.1488 | 0.14849 | 0.14777 | 0.14724 | 0.14635 | 0.1453 | 0.14464 | 0.14321 | 0.14118 | 0.13884 | 0.13063 | 0.10598 | 0.097551 | 0.092921
| TARBERT JURA | SP |  |  | 0.15801 | 0.15768 | 0.15753 | 0.15678 | 0.15574 | 0.15434 | 0.15344 | 0.1519 | 0.14989 | 0.14774 | 0.13752 | 0.1151 | 0.091602 | 0.083147 | 0.15084 | 0.15061 | 0.1505 | 0.14998 | 0.14937 | 0.14851 | 0.14799 | 0.14705 | 0.14581 | 0.14463 | 0.1398 | 0.12807 | 0.11274 | 0.10756 | 0.14913 | 0.1488 | 0.14863 | 0.14796 | 0.14685 | 0.14545 | 0.14445 | 0.1429 | 0.14095 | 0.13891 | 0.12971 | 0.10934 | 0.087479 | 0.080046
PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | YES | 2.1664 | 2.0995 | 2.0711 | 2.056 | 1.9723 | 1.9123 | 1.8778 | 1.8437 | 1.8057 | 1.7811 | 1.7078 | 1.6435 | 1.6597 | 1.5999 | 3.044 | 3.0018 | 2.9779 | 2.961 | 2.9097 | 2.8708 | 2.8434 | 2.799 | 2.7499 | 2.7051 | 2.5439 | 2.4343 | 2.435 | 2.3507 | 2.7131 | 2.7047 | 2.6715 | 2.6457 | 2.5126 | 2.417 | 2.3589 | 2.2961 | 2.2295 | 2.1832 | 2.0265 | 1.9563 | 1.9553 | 1.8845
| TARBERT LOCH FYNE | CT |  |  | 2.175 | 2.1264 | 2.1103 | 2.1147 | 2.0398 | 1.9969 | 1.9552 | 1.9228 | 1.8893 | 1.8601 | 1.7794 | 1.7202 | 1.7548 | 1.7584 | 3.0524 | 3.0215 | 3.0044 | 2.994 | 2.9428 | 2.9077 | 2.8763 | 2.8398 | 2.8024 | 2.7606 | 2.6152 | 2.482 | 2.4726 | 2.4531 | 2.7137 | 2.7066 | 2.702 | 2.7003 | 2.6607 | 2.586 | 2.5153 | 2.4556 | 2.3958 | 2.3455 | 2.1869 | 2.0436 | 2.0607 | 2.0637
| TARBERT LOCH FYNE | LW |  |  | 2.1664 | 2.0995 | 2.0711 | 2.056 | 1.9723 | 1.9123 | 1.8778 | 1.8437 | 1.8057 | 1.7811 | 1.7078 | 1.6435 | 1.698 | 1.6844 | 3.044 | 3.0018 | 2.9779 | 2.961 | 2.9097 | 2.8708 | 2.8434 | 2.799 | 2.7499 | 2.7051 | 2.5439 | 2.4343 | 2.452 | 2.446 | 2.7131 | 2.7047 | 2.6715 | 2.6457 | 2.5126 | 2.417 | 2.3589 | 2.2961 | 2.2295 | 2.1832 | 2.0265 | 1.9563 | 2.0053 | 1.9932
| TARBERT LOCH FYNE | ST |  |  | 2.1824 | 2.1588 | 2.1348 | 2.1161 | 2.0951 | 2.0845 | 2.0684 | 2.052 | 2.0491 | 2.0354 | 1.9856 | 1.878 | 1.8757 | 1.8729 | 3.0555 | 3.0364 | 3.0166 | 2.9977 | 2.9779 | 2.9635 | 2.9458 | 2.9276 | 2.9156 | 2.8938 | 2.8147 | 2.604 | 2.5449 | 2.5132 | 2.7141 | 2.7088 | 2.7035 | 2.6998 | 2.696 | 2.6943 | 2.6919 | 2.67 | 2.6626 | 2.6347 | 2.5331 | 2.2719 | 2.2236 | 2.2059
| TARBERT LOCH FYNE | SP |  |  | 2.1979 | 2.183 | 2.1672 | 2.1574 | 2.1332 | 2.1163 | 2.0971 | 2.078 | 2.0595 | 2.028 | 1.9534 | 1.7772 | 1.6597 | 1.5999 | 3.0648 | 3.0498 | 3.0341 | 3.0221 | 3.0025 | 2.9861 | 2.9686 | 2.9513 | 2.9305 | 2.902 | 2.8222 | 2.6153 | 2.435 | 2.3507 | 2.7156 | 2.711 | 2.7064 | 2.7036 | 2.6997 | 2.6974 | 2.695 | 2.6925 | 2.677 | 2.6214 | 2.4806 | 2.1608 | 1.9553 | 1.8845
TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | YES | 1.1279 | 1.13 | 1.129 | 1.1223 | 1.0975 | 1.0711 | 1.0473 | 0.95299 | 0.83682 | 0.7789 | 0.55583 | 0.51322 | 0.51705 | 0.46259 | 1.6272 | 1.6283 | 1.621 | 1.6095 | 1.5701 | 1.5287 | 1.4893 | 1.439 | 1.3809 | 1.3436 | 1.171 | 1.1278 | 1.1191 | 1.0666 | 1.3418 | 1.3478 | 1.3464 | 1.3396 | 1.2995 | 1.242 | 1.177 | 1.0925 | 0.99413 | 0.93011 | 0.64904 | 0.59228 | 0.60868 | 0.56463
| TAYNUILT | CT |  |  | 1.1311 | 1.1328 | 1.13 | 1.1223 | 1.0975 | 1.0733 | 1.0473 | 1.0068 | 0.91729 | 0.86781 | 0.67858 | 0.57329 | 0.59585 | 0.59486 | 1.6416 | 1.6433 | 1.6381 | 1.6247 | 1.5848 | 1.5462 | 1.5038 | 1.4595 | 1.4167 | 1.384 | 1.2399 | 1.1507 | 1.1441 | 1.1273 | 1.354 | 1.3595 | 1.3578 | 1.3504 | 1.3126 | 1.2725 | 1.2032 | 1.1306 | 1.061 | 1.0075 | 0.76873 | 0.64753 | 0.656 | 0.65281
| TAYNUILT | LW |  |  | 1.1279 | 1.1321 | 1.1306 | 1.1252 | 1.0989 | 1.0711 | 1.0473 | 0.95299 | 0.83682 | 0.7789 | 0.55583 | 0.51322 | 0.57622 | 0.55896 | 1.6272 | 1.6283 | 1.621 | 1.6095 | 1.5701 | 1.5287 | 1.4893 | 1.439 | 1.3809 | 1.3436 | 1.171 | 1.1278 | 1.1453 | 1.1404 | 1.3418 | 1.349 | 1.3465 | 1.3396 | 1.2995 | 1.242 | 1.177 | 1.0925 | 0.99413 | 0.93011 | 0.64904 | 0.59228 | 0.63431 | 0.62309
| TAYNUILT | ST |  |  | 1.1313 | 1.13 | 1.129 | 1.1292 | 1.1318 | 1.1331 | 1.1332 | 1.1339 | 1.1313 | 1.1223 | 1.0841 | 0.91728 | 0.85703 | 0.83828 | 1.6383 | 1.6349 | 1.6317 | 1.629 | 1.6267 | 1.6227 | 1.6169 | 1.6121 | 1.6027 | 1.5847 | 1.5147 | 1.2762 | 1.2261 | 1.2021 | 1.3497 | 1.3478 | 1.3464 | 1.3476 | 1.3511 | 1.3529 | 1.3534 | 1.355 | 1.3514 | 1.3334 | 1.2212 | 0.90202 | 0.84573 | 0.82944
| TAYNUILT | SP |  |  | 1.1349 | 1.135 | 1.1361 | 1.1367 | 1.1318 | 1.127 | 1.1216 | 1.1147 | 1.1076 | 1.0929 | 1.0061 | 0.70141 | 0.51705 | 0.46259 | 1.6415 | 1.6388 | 1.6372 | 1.6347 | 1.6217 | 1.6085 | 1.5947 | 1.5785 | 1.5609 | 1.5338 | 1.4624 | 1.2786 | 1.1191 | 1.0666 | 1.3539 | 1.3535 | 1.3545 | 1.3551 | 1.345 | 1.3354 | 1.3248 | 1.3124 | 1.2916 | 1.2474 | 1.1328 | 0.83283 | 0.60868 | 0.56463
BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | YES | 3.9142 | 3.7993 | 3.698 | 3.5728 | 2.6499 | 1.6206 | 0.55873 | -0.60601 | -1.191 | -1.7681 | -3.6608 | -6.4481 | -7.7086 | -8.62 | 5.1777 | 5.0795 | 4.9697 | 4.8329 | 4.2913 | 3.7109 | 3.0992 | 2.4037 | 1.9781 | 1.5243 | -0.016383 | -2.5272 | -4.098 | -5.773 | 3.2063 | 2.7281 | 2.4027 | 2.1861 | 1.0493 | -0.13946 | -1.3793 | -2.761 | -3.4566 | -4.1391 | -6.4297 | -9.6008 | -11.1474 | -12.0281
| THIMBLEROW | CT |  |  | 3.9142 | 3.7993 | 3.698 | 3.5728 | 2.9824 | 1.9444 | 1.3575 | 0.82238 | 0.20761 | -0.56395 | -2.8252 | -6.3002 | -7.7086 | -8.5771 | 5.1777 | 5.0795 | 4.985 | 4.8613 | 4.3518 | 3.7258 | 3.3187 | 2.9151 | 2.4684 | 1.9185 | 0.23287 | -2.5272 | -4.098 | -5.773 | 3.2443 | 2.8947 | 2.7162 | 2.6032 | 1.4969 | 0.26685 | -0.4438 | -1.1036 | -1.8469 | -2.7474 | -5.4341 | -9.5459 | -11.1474 | -12.0281
| THIMBLEROW | LW |  |  | 3.9813 | 3.9094 | 3.7734 | 3.6254 | 2.6499 | 1.6206 | 0.55873 | -0.60601 | -1.191 | -1.7681 | -3.6608 | -6.4481 | -7.6648 | -8.62 | 5.2087 | 5.1369 | 4.9697 | 4.8329 | 4.2913 | 3.7109 | 3.0992 | 2.4037 | 1.9781 | 1.5243 | -0.016383 | -2.0891 | -2.8202 | -3.4165 | 3.2063 | 2.7281 | 2.4027 | 2.1861 | 1.0493 | -0.13946 | -1.3793 | -2.761 | -3.4566 | -4.1391 | -6.4297 | -9.6008 | -10.8058 | -11.6773
| THIMBLEROW | ST |  |  | 4.0164 | 3.9806 | 3.9354 | 3.8788 | 3.8356 | 3.7573 | 3.6855 | 3.5579 | 3.4351 | 3.2038 | 2.1459 | -0.66515 | -2.4534 | -3.3106 | 5.2564 | 5.2216 | 5.1782 | 5.1215 | 5.0646 | 4.9792 | 4.8974 | 4.7714 | 4.6456 | 4.4409 | 3.2876 | -0.32413 | -2.5066 | -2.9885 | 3.5946 | 3.4977 | 3.3912 | 3.2452 | 3.1172 | 2.994 | 2.8768 | 2.7087 | 2.6529 | 2.4234 | 1.1996 | -3.5102 | -6.1806 | -6.7883
| THIMBLEROW | SP |  |  | 4.0328 | 4.0102 | 3.9824 | 3.9399 | 3.9053 | 3.8322 | 3.7823 | 3.7149 | 3.594 | 3.449 | 2.7762 | 0.63559 | -1.7941 | -2.8688 | 5.259 | 5.2291 | 5.1933 | 5.1445 | 5.0947 | 5.0141 | 4.9479 | 4.8668 | 4.7396 | 4.5598 | 3.7453 | 1.3818 | -1.7495 | -5.0835 | 3.6468 | 3.6163 | 3.5801 | 3.5296 | 3.4397 | 3.2645 | 3.135 | 3.0013 | 2.8347 | 2.5799 | 1.7467 | -1.3186 | -5.2005 | -6.5699
TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | 0.0052859 | 0.12179 | 0.1205 | 0.11836 | 0.1151 | 0.10952 | 0.1045 | 0.097899 | 0.08777 | 0.080861 | 0.056393 | 0.050544 | 0.051651 | 0.045049 | 0.018418 | 0.12656 | 0.12585 | 0.1246 | 0.12289 | 0.11991 | 0.11775 | 0.11437 | 0.10969 | 0.10567 | 0.089129 | 0.086869 | 0.08759 | 0.085265 | 0.0079722 | 0.11541 | 0.11397 | 0.1118 | 0.10804 | 0.10257 | 0.098086 | 0.092041 | 0.082907 | 0.076453 | 0.05328 | 0.04809 | 0.049164 | 0.043334
| TIRORAN BRIDGE | CT |  |  | 0.0062966 | 0.12354 | 0.1221 | 0.12102 | 0.1166 | 0.1126 | 0.10676 | 0.099194 | 0.091416 | 0.086362 | 0.06721 | 0.055409 | 0.051651 | 0.049329 | 0.018867 | 0.12736 | 0.12644 | 0.12576 | 0.12323 | 0.12097 | 0.11787 | 0.11474 | 0.11131 | 0.10835 | 0.095209 | 0.089002 | 0.087721 | 0.08693 | 0.009288 | 0.11762 | 0.11633 | 0.1153 | 0.11076 | 0.10656 | 0.099999 | 0.093146 | 0.086178 | 0.081453 | 0.063255 | 0.052458 | 0.049164 | 0.047129
| TIRORAN BRIDGE | LW |  |  | 0.0052859 | 0.12179 | 0.1205 | 0.11836 | 0.1151 | 0.10952 | 0.1045 | 0.097899 | 0.08777 | 0.080861 | 0.056393 | 0.050544 | 0.05266 | 0.052153 | 0.018418 | 0.12656 | 0.12585 | 0.1246 | 0.12289 | 0.11991 | 0.11775 | 0.11437 | 0.10969 | 0.10567 | 0.089129 | 0.086869 | 0.08759 | 0.087417 | 0.0079722 | 0.11541 | 0.11397 | 0.1118 | 0.10804 | 0.10257 | 0.098086 | 0.092041 | 0.082907 | 0.076453 | 0.05328 | 0.04809 | 0.049944 | 0.0495
| TIRORAN BRIDGE | ST |  |  | 0.0063006 | 0.12402 | 0.1235 | 0.12273 | 0.12147 | 0.12077 | 0.12003 | 0.11784 | 0.11592 | 0.11325 | 0.10343 | 0.075486 | 0.06673 | 0.0615 | 0.018949 | 0.12779 | 0.12748 | 0.12701 | 0.12624 | 0.12583 | 0.1254 | 0.12403 | 0.12292 | 0.12136 | 0.11536 | 0.09639 | 0.092706 | 0.090924 | 0.0091771 | 0.11784 | 0.11732 | 0.11658 | 0.11539 | 0.11465 | 0.11387 | 0.11188 | 0.10987 | 0.10713 | 0.097437 | 0.070392 | 0.061937 | 0.057696
| TIRORAN BRIDGE | SP |  |  | 0.0065162 | 0.12437 | 0.12391 | 0.12378 | 0.12277 | 0.12178 | 0.1211 | 0.11906 | 0.11755 | 0.1149 | 0.10497 | 0.080713 | 0.053814 | 0.045049 | 0.019056 | 0.12797 | 0.12768 | 0.12761 | 0.12704 | 0.12648 | 0.12612 | 0.12489 | 0.12402 | 0.12243 | 0.11696 | 0.10496 | 0.088275 | 0.085265 | 0.0094323 | 0.11825 | 0.11782 | 0.11767 | 0.1166 | 0.11555 | 0.11474 | 0.1128 | 0.11125 | 0.10868 | 0.098228 | 0.076153 | 0.051022 | 0.043334
BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | 1.5071 | 1.4992 | 1.4835 | 1.465 | 1.4209 | 1.3611 | 1.2912 | 1.2119 | 1.1079 | 1.0018 | 0.83312 | 0.77726 | 0.77963 | 0.72982 | 1.5953 | 1.5918 | 1.587 | 1.5818 | 1.5699 | 1.5475 | 1.524 | 1.4951 | 1.4415 | 1.367 | 1.2704 | 1.241 | 1.2229 | 1.1902 | 1.3993 | 1.3964 | 1.3921 | 1.3874 | 1.3821 | 1.3657 | 1.3109 | 1.2445 | 1.1581 | 1.0585 | 0.91748 | 0.87231 | 0.87169 | 0.83093
| TOMATIN | CT |  |  | 1.5214 | 1.5181 | 1.5054 | 1.4886 | 1.4453 | 1.3954 | 1.3209 | 1.2329 | 1.1452 | 1.0832 | 0.88116 | 0.80267 | 0.79367 | 0.78467 | 1.5953 | 1.5918 | 1.587 | 1.5818 | 1.5743 | 1.5547 | 1.5297 | 1.4997 | 1.4645 | 1.4278 | 1.2902 | 1.2482 | 1.2393 | 1.2271 | 1.3993 | 1.3964 | 1.3921 | 1.3874 | 1.3821 | 1.3657 | 1.3377 | 1.2661 | 1.1956 | 1.1449 | 0.95937 | 0.89463 | 0.88674 | 0.87918
| TOMATIN | LW |  |  | 1.5071 | 1.4992 | 1.4835 | 1.465 | 1.4209 | 1.3611 | 1.2912 | 1.2119 | 1.1079 | 1.0018 | 0.83312 | 0.77726 | 0.79616 | 0.78798 | 1.5967 | 1.5934 | 1.5895 | 1.5838 | 1.5699 | 1.5475 | 1.524 | 1.4951 | 1.4415 | 1.367 | 1.2704 | 1.241 | 1.2472 | 1.2444 | 1.4007 | 1.3979 | 1.3946 | 1.3907 | 1.3855 | 1.3672 | 1.3109 | 1.2445 | 1.1581 | 1.0585 | 0.91748 | 0.87231 | 0.88769 | 0.88123
| TOMATIN | ST |  |  | 1.5251 | 1.5187 | 1.5147 | 1.509 | 1.505 | 1.487 | 1.4634 | 1.4266 | 1.3808 | 1.3291 | 1.1846 | 0.98723 | 0.92277 | 0.89468 | 1.6065 | 1.5976 | 1.596 | 1.5936 | 1.5915 | 1.5841 | 1.5733 | 1.5493 | 1.5313 | 1.5108 | 1.4423 | 1.3127 | 1.2807 | 1.262 | 1.4076 | 1.4014 | 1.4 | 1.3979 | 1.3962 | 1.3864 | 1.3717 | 1.3444 | 1.3192 | 1.2918 | 1.2164 | 1.045 | 0.99156 | 0.96846
| TOMATIN | SP |  |  | 1.5254 | 1.5206 | 1.5172 | 1.5139 | 1.5015 | 1.4781 | 1.4447 | 1.4006 | 1.3505 | 1.2939 | 1.1476 | 0.89802 | 0.77963 | 0.72982 | 1.6068 | 1.598 | 1.5963 | 1.5948 | 1.593 | 1.5862 | 1.5757 | 1.5601 | 1.5357 | 1.5169 | 1.4518 | 1.2929 | 1.2229 | 1.1902 | 1.4075 | 1.4017 | 1.4002 | 1.3989 | 1.3973 | 1.3882 | 1.3732 | 1.3511 | 1.3219 | 1.2955 | 1.214 | 0.97745 | 0.87169 | 0.83093
LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | 0.1099 | 0.10982 | 0.10959 | 0.10933 | 0.10894 | 0.1084 | 0.10799 | 0.1073 | 0.1066 | 0.10615 | 0.10442 | 0.10271 | 0.10283 | 0.10281 | 0.10517 | 0.10513 | 0.10499 | 0.10483 | 0.10467 | 0.1044 | 0.10423 | 0.10383 | 0.10349 | 0.1032 | 0.1017 | 0.10037 | 0.10041 | 0.1004 | 0.10444 | 0.10437 | 0.10415 | 0.10391 | 0.10356 | 0.10307 | 0.1027 | 0.10206 | 0.10143 | 0.10101 | 0.099371 | 0.097707 | 0.097808 | 0.097791
| TORBOLL | CT |  |  | 0.11011 | 0.11012 | 0.10995 | 0.10975 | 0.10939 | 0.1089 | 0.10842 | 0.10777 | 0.10716 | 0.10679 | 0.10535 | 0.10416 | 0.10399 | 0.10389 | 0.10524 | 0.10524 | 0.10511 | 0.10496 | 0.10482 | 0.10457 | 0.10437 | 0.10406 | 0.10376 | 0.10354 | 0.10255 | 0.10142 | 0.10136 | 0.10132 | 0.10462 | 0.10463 | 0.10446 | 0.10427 | 0.10395 | 0.10351 | 0.10308 | 0.10249 | 0.10193 | 0.10159 | 0.10022 | 0.099079 | 0.098933 | 0.098841
| TORBOLL | LW |  |  | 0.1099 | 0.10982 | 0.10959 | 0.10933 | 0.10894 | 0.1084 | 0.10799 | 0.1073 | 0.1066 | 0.10615 | 0.10442 | 0.10271 | 0.10283 | 0.10281 | 0.10517 | 0.10513 | 0.10499 | 0.10483 | 0.10467 | 0.1044 | 0.10423 | 0.10383 | 0.10349 | 0.1032 | 0.1017 | 0.10037 | 0.10041 | 0.1004 | 0.10444 | 0.10437 | 0.10415 | 0.10391 | 0.10356 | 0.10307 | 0.1027 | 0.10206 | 0.10143 | 0.10101 | 0.099371 | 0.097707 | 0.097808 | 0.097791
| TORBOLL | ST |  |  | 0.11006 | 0.11003 | 0.10999 | 0.10997 | 0.10982 | 0.10976 | 0.10958 | 0.10952 | 0.1094 | 0.10909 | 0.10827 | 0.10534 | 0.10408 | 0.10384 | 0.10523 | 0.10522 | 0.1052 | 0.10518 | 0.10509 | 0.10506 | 0.10493 | 0.1049 | 0.10484 | 0.10465 | 0.10405 | 0.10193 | 0.10111 | 0.10103 | 0.10458 | 0.10455 | 0.10452 | 0.1045 | 0.10436 | 0.1043 | 0.10413 | 0.10407 | 0.10396 | 0.10367 | 0.10291 | 0.10013 | 0.098951 | 0.098748
| TORBOLL | SP |  |  | 0.11007 | 0.11004 | 0.11001 | 0.10999 | 0.10986 | 0.10959 | 0.10946 | 0.10932 | 0.10905 | 0.10884 | 0.10799 | 0.10553 | 0.10406 | 0.10357 | 0.10524 | 0.10522 | 0.10521 | 0.10519 | 0.10514 | 0.10498 | 0.10492 | 0.10487 | 0.1047 | 0.10462 | 0.10421 | 0.10275 | 0.10141 | 0.10115 | 0.10459 | 0.10456 | 0.10454 | 0.10451 | 0.1044 | 0.10415 | 0.10403 | 0.10391 | 0.10365 | 0.10347 | 0.1027 | 0.1004 | 0.098998 | 0.098551
KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | YES | 12.3368 | 11.3322 | 10.1733 | 8.9561 | 7.4692 | 5.7016 | 3.8286 | 1.968 | -0.06688 | -2.0295 | -5.7606 | -8.3804 | -9.3571 | -9.7202 | 13.8223 | 12.8616 | 11.7515 | 10.5774 | 9.2828 | 7.6926 | 6.0503 | 4.3429 | 2.5891 | 0.72859 | -2.6444 | -4.2238 | -4.6829 | -5.0158 | 12.6421 | 11.6862 | 10.5696 | 9.3733 | 7.9669 | 6.3346 | 4.5915 | 2.8699 | 0.9876 | -0.83541 | -4.2721 | -6.7112 | -7.6027 | -7.9341
| TORRYBURN | CT |  |  | 12.3368 | 11.3322 | 10.1733 | 8.9561 | 7.6389 | 5.9808 | 4.2665 | 2.457 | 0.61909 | -1.4033 | -5.7596 | -8.3804 | -9.3571 | -9.7202 | 13.826 | 12.8688 | 11.7566 | 10.5908 | 9.3 | 7.7067 | 6.1094 | 4.4246 | 2.7121 | 0.84613 | -2.6273 | -4.2238 | -4.6829 | -5.0158 | 12.6792 | 11.7429 | 10.639 | 9.4699 | 8.1134 | 6.5873 | 5.0093 | 3.3472 | 1.6562 | -0.23422 | -4.2709 | -6.7112 | -7.6027 | -7.9341
| TORRYBURN | LW |  |  | 12.3553 | 11.3547 | 10.2042 | 8.9899 | 7.4692 | 5.7016 | 3.8286 | 1.968 | -0.06688 | -2.0295 | -5.7606 | -7.8905 | -8.5311 | -8.7549 | 13.8223 | 12.8616 | 11.7515 | 10.5774 | 9.2828 | 7.6926 | 6.0503 | 4.3429 | 2.5891 | 0.72859 | -2.6444 | -4.2193 | -4.3739 | -4.4361 | 12.6421 | 11.6862 | 10.5696 | 9.3733 | 7.9669 | 6.3346 | 4.5915 | 2.8699 | 0.9876 | -0.83541 | -4.2721 | -6.2658 | -6.8488 | -7.0523
| TORRYBURN | ST |  |  | 12.3911 | 11.4198 | 10.3019 | 9.1232 | 7.8886 | 6.4705 | 5.071 | 3.5848 | 2.0898 | 0.46088 | -2.67 | -4.8961 | -5.7562 | -6.3179 | 13.8892 | 12.9658 | 11.9068 | 10.811 | 9.4819 | 7.9563 | 6.4432 | 4.8416 | 3.2089 | 1.4235 | -1.867 | -3.6097 | -3.9299 | -4.1862 | 12.7674 | 11.8744 | 10.8486 | 9.7855 | 8.6733 | 7.3206 | 5.9739 | 4.5432 | 3.0937 | 1.4951 | -1.6119 | -3.8375 | -4.5808 | -4.9298
| TORRYBURN | SP |  |  | 12.3903 | 11.4234 | 10.3109 | 9.1337 | 7.9007 | 6.4851 | 5.0885 | 3.6049 | 2.1187 | 0.51975 | -2.3957 | -4.8694 | -5.6748 | -5.9623 | 13.8803 | 12.9608 | 11.9066 | 10.8131 | 9.4901 | 7.9663 | 6.4551 | 4.8438 | 3.2103 | 1.444 | -1.7498 | -3.4309 | -3.8746 | -4.2367 | 12.7565 | 11.8699 | 10.853 | 9.7938 | 8.6644 | 7.3282 | 5.9755 | 4.5394 | 3.101 | 1.533 | -1.4211 | -3.4847 | -4.2371 | -4.4948
LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | 0.18163 | 1.3536 | 1.3403 | 1.3239 | 1.2821 | 1.2387 | 1.1866 | 1.1333 | 1.0499 | 1.0063 | 0.84388 | 0.7923 | 0.81509 | 0.76609 | 0.35132 | 1.4369 | 1.4301 | 1.4216 | 1.403 | 1.3838 | 1.3575 | 1.3303 | 1.2897 | 1.2639 | 1.1519 | 1.12 | 1.1276 | 1.1042 | 0.31323 | 1.3959 | 1.3837 | 1.3687 | 1.3312 | 1.2924 | 1.2448 | 1.1962 | 1.1204 | 1.0797 | 0.92549 | 0.87713 | 0.89551 | 0.8556
| TRESSADY | CT |  |  | 0.19328 | 1.3697 | 1.361 | 1.3457 | 1.3022 | 1.2644 | 1.2055 | 1.1399 | 1.0785 | 1.044 | 0.90717 | 0.82975 | 0.82928 | 0.82407 | 0.35495 | 1.4415 | 1.4359 | 1.4268 | 1.4041 | 1.3853 | 1.36 | 1.3307 | 1.3026 | 1.2819 | 1.1839 | 1.1353 | 1.1318 | 1.1262 | 0.32329 | 1.4096 | 1.4014 | 1.3871 | 1.3472 | 1.3128 | 1.2604 | 1.2015 | 1.1463 | 1.114 | 0.98324 | 0.90931 | 0.90744 | 0.90276
| TRESSADY | LW |  |  | 0.18163 | 1.3536 | 1.3403 | 1.3239 | 1.2821 | 1.2387 | 1.1866 | 1.1333 | 1.0499 | 1.0063 | 0.84388 | 0.7923 | 0.81509 | 0.80422 | 0.35132 | 1.4369 | 1.4301 | 1.4216 | 1.403 | 1.3838 | 1.3575 | 1.3303 | 1.2897 | 1.2639 | 1.1519 | 1.12 | 1.1276 | 1.124 | 0.31323 | 1.3959 | 1.3837 | 1.3687 | 1.3312 | 1.2924 | 1.2448 | 1.1962 | 1.1204 | 1.0797 | 0.92549 | 0.87713 | 0.89551 | 0.88694
| TRESSADY | ST |  |  | 0.19231 | 1.3687 | 1.3651 | 1.3584 | 1.3535 | 1.3486 | 1.3388 | 1.3312 | 1.3185 | 1.2944 | 1.219 | 1.0325 | 0.95654 | 0.93223 | 0.35625 | 1.4442 | 1.442 | 1.4377 | 1.4343 | 1.431 | 1.4238 | 1.4185 | 1.4115 | 1.3964 | 1.3483 | 1.2173 | 1.1738 | 1.1615 | 0.32285 | 1.4095 | 1.4061 | 1.3998 | 1.3952 | 1.3905 | 1.381 | 1.3737 | 1.362 | 1.3395 | 1.2673 | 1.084 | 1.014 | 0.99282
| TRESSADY | SP |  |  | 0.19593 | 1.3749 | 1.3738 | 1.3723 | 1.364 | 1.3557 | 1.3457 | 1.3352 | 1.3191 | 1.2947 | 1.2084 | 1.0052 | 0.82704 | 0.76609 | 0.3576 | 1.4468 | 1.4457 | 1.4443 | 1.4403 | 1.4361 | 1.4308 | 1.4255 | 1.4162 | 1.4024 | 1.3601 | 1.247 | 1.1334 | 1.1042 | 0.32604 | 1.4151 | 1.414 | 1.4124 | 1.4049 | 1.3974 | 1.3883 | 1.3787 | 1.3637 | 1.3411 | 1.2629 | 1.076 | 0.90765 | 0.8556
SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | 4.5934 | 4.5883 | 4.5441 | 4.485 | 4.3405 | 4.1872 | 4.0429 | 3.8886 | 3.7026 | 3.6061 | 3.3066 | 3.1632 | 3.2463 | 3.186 | 5.2934 | 5.2888 | 5.2701 | 5.244 | 5.1834 | 5.1181 | 5.0578 | 4.9934 | 4.8659 | 4.7649 | 4.3824 | 4.3425 | 4.3566 | 4.2804 | 4.6498 | 4.6383 | 4.5986 | 4.5455 | 4.4192 | 4.2801 | 4.1524 | 4.0181 | 3.8474 | 3.7583 | 3.3166 | 3.2632 | 3.3448 | 3.2573
| TUMBLIN | CT |  |  | 4.6351 | 4.6345 | 4.5924 | 4.5046 | 4.3513 | 4.2075 | 4.0705 | 3.8886 | 3.7227 | 3.666 | 3.4454 | 3.2777 | 3.3341 | 3.3415 | 5.3081 | 5.3048 | 5.2854 | 5.2481 | 5.1857 | 5.1231 | 5.0666 | 4.9934 | 4.9023 | 4.8282 | 4.4633 | 4.373 | 4.3977 | 4.3884 | 4.6914 | 4.6871 | 4.6528 | 4.5885 | 4.46 | 4.3279 | 4.1968 | 4.0393 | 3.8932 | 3.8231 | 3.4471 | 3.3237 | 3.4104 | 3.4332
| TUMBLIN | LW |  |  | 4.5934 | 4.5883 | 4.5441 | 4.485 | 4.3405 | 4.1872 | 4.0429 | 3.8905 | 3.7026 | 3.6061 | 3.3066 | 3.1632 | 3.2463 | 3.2018 | 5.2934 | 5.2888 | 5.2701 | 5.244 | 5.1834 | 5.1181 | 5.0578 | 4.994 | 4.8659 | 4.7649 | 4.3824 | 4.3425 | 4.3767 | 4.3559 | 4.6498 | 4.6383 | 4.5986 | 4.5455 | 4.4192 | 4.2801 | 4.1524 | 4.0181 | 3.8474 | 3.7583 | 3.3166 | 3.2632 | 3.3448 | 3.2957
| TUMBLIN | ST |  |  | 4.6319 | 4.628 | 4.6252 | 4.6114 | 4.6078 | 4.5979 | 4.5867 | 4.564 | 4.5312 | 4.478 | 4.3056 | 3.9573 | 3.807 | 3.7528 | 5.3099 | 5.3072 | 5.3045 | 5.2973 | 5.2964 | 5.2945 | 5.2921 | 5.2855 | 5.2741 | 5.2541 | 5.1153 | 4.6578 | 4.6118 | 4.5795 | 4.6912 | 4.6833 | 4.6753 | 4.6616 | 4.6548 | 4.6454 | 4.6346 | 4.6127 | 4.5827 | 4.5342 | 4.3757 | 3.9845 | 3.9133 | 3.8658
| TUMBLIN | SP |  |  | 4.643 | 4.644 | 4.6463 | 4.6428 | 4.6054 | 4.5703 | 4.5307 | 4.4749 | 4.4241 | 4.3479 | 4.1202 | 3.6224 | 3.3102 | 3.186 | 5.3142 | 5.3134 | 5.3138 | 5.314 | 5.3012 | 5.2894 | 5.2758 | 5.2554 | 5.236 | 5.2061 | 5.1029 | 4.6579 | 4.3566 | 4.2804 | 4.6979 | 4.693 | 4.6901 | 4.6866 | 4.6533 | 4.622 | 4.5867 | 4.536 | 4.4905 | 4.4225 | 4.2187 | 3.7676 | 3.3567 | 3.2573
TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | 2.307 | 2.3036 | 2.2998 | 2.2935 | 2.2842 | 2.2741 | 2.2542 | 2.2138 | 2.1758 | 2.1561 | 2.0529 | 2.0312 | 2.0416 | 2.0258 | 2.2456 | 2.2421 | 2.2379 | 2.2314 | 2.2217 | 2.2112 | 2.2022 | 2.1918 | 2.1779 | 2.1618 | 2.1013 | 2.0828 | 2.0821 | 2.0804 | 2.1325 | 2.1291 | 2.1222 | 2.1128 | 2.0902 | 2.0652 | 2.0406 | 2.0046 | 1.9706 | 1.9518 | 1.886 | 1.8607 | 1.8719 | 1.8589
| TUMMEL BRIDGE | CT |  |  | 2.307 | 2.3036 | 2.2998 | 2.2935 | 2.2842 | 2.2741 | 2.2542 | 2.2138 | 2.1758 | 2.1586 | 2.0742 | 2.0397 | 2.0416 | 2.0388 | 2.2456 | 2.2421 | 2.2379 | 2.2314 | 2.2217 | 2.2112 | 2.2022 | 2.1919 | 2.1807 | 2.1693 | 2.113 | 2.0979 | 2.0981 | 2.0957 | 2.1384 | 2.136 | 2.1307 | 2.1199 | 2.0962 | 2.0737 | 2.0406 | 2.0046 | 1.9706 | 1.9548 | 1.8986 | 1.8673 | 1.872 | 1.8705
| TUMMEL BRIDGE | LW |  |  | 2.3075 | 2.3045 | 2.3009 | 2.2953 | 2.287 | 2.2765 | 2.2555 | 2.228 | 2.1792 | 2.1561 | 2.0529 | 2.0312 | 2.0422 | 2.0342 | 2.2459 | 2.2425 | 2.2384 | 2.2323 | 2.2234 | 2.2124 | 2.2029 | 2.1918 | 2.1779 | 2.1618 | 2.1013 | 2.0828 | 2.0821 | 2.0804 | 2.1325 | 2.1291 | 2.1222 | 2.1128 | 2.0902 | 2.0652 | 2.0418 | 2.017 | 1.9732 | 1.9518 | 1.886 | 1.8607 | 1.8719 | 1.8633
| TUMMEL BRIDGE | ST |  |  | 2.3099 | 2.3086 | 2.3072 | 2.3052 | 2.303 | 2.3006 | 2.2973 | 2.2941 | 2.2904 | 2.284 | 2.2609 | 2.1624 | 2.1328 | 2.1142 | 2.2488 | 2.2473 | 2.2457 | 2.2435 | 2.2411 | 2.2384 | 2.2349 | 2.2313 | 2.227 | 2.2199 | 2.1941 | 2.1257 | 2.0985 | 2.0886 | 2.1385 | 2.1371 | 2.1357 | 2.1333 | 2.1319 | 2.1305 | 2.1276 | 2.1256 | 2.1189 | 2.1079 | 2.0726 | 1.9959 | 1.9622 | 1.9452
| TUMMEL BRIDGE | SP |  |  | 2.3109 | 2.31 | 2.3089 | 2.3077 | 2.3063 | 2.3047 | 2.3025 | 2.3002 | 2.2977 | 2.2932 | 2.2775 | 2.1532 | 2.0591 | 2.0258 | 2.2496 | 2.2485 | 2.2472 | 2.2458 | 2.244 | 2.242 | 2.2395 | 2.2368 | 2.2338 | 2.2289 | 2.2144 | 2.1524 | 2.1028 | 2.0891 | 2.1415 | 2.1409 | 2.1405 | 2.1401 | 2.136 | 2.132 | 2.1272 | 2.1215 | 2.1151 | 2.1039 | 2.0626 | 1.9628 | 1.8915 | 1.8589
MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | YES | 0.054182 | -0.1323 | -0.34059 | -0.59559 | -1.0763 | -1.9358 | -2.902 | -4.0095 | -5.416 | -6.8124 | -9.7211 | -11.7767 | -12.5498 | -12.8411 | 2.158 | 1.9795 | 1.7934 | 1.5784 | 1.3326 | 0.68203 | -0.057934 | -0.88085 | -1.8647 | -3.0084 | -5.2071 | -6.6247 | -6.7302 | -6.7846 | 1.8642 | 1.6688 | 1.4578 | 1.205 | 0.85513 | 0.084009 | -0.75939 | -1.6651 | -2.764 | -3.9429 | -6.3654 | -8.1054 | -8.6047 | -8.8718
| TURRIFF | CT |  |  | 0.1494 | -0.019022 | -0.21966 | -0.48842 | -0.96019 | -1.7673 | -2.8438 | -3.9982 | -5.2179 | -6.4922 | -9.4635 | -11.7767 | -12.5498 | -12.8411 | 2.158 | 1.9795 | 1.7934 | 1.5784 | 1.3326 | 0.68203 | -0.057934 | -0.88085 | -1.8305 | -2.9293 | -4.9961 | -6.3922 | -6.5925 | -6.678 | 1.8839 | 1.6852 | 1.4746 | 1.2206 | 0.87915 | 0.13794 | -0.73227 | -1.6506 | -2.6771 | -3.8058 | -6.0767 | -7.9253 | -8.6047 | -8.8718
| TURRIFF | LW |  |  | 0.054182 | -0.1323 | -0.34059 | -0.59559 | -1.0763 | -1.9358 | -2.902 | -4.0095 | -5.416 | -6.8124 | -9.7211 | -11.5289 | -11.9517 | -12.1458 | 2.1722 | 1.9982 | 1.8222 | 1.6191 | 1.3869 | 0.73015 | -0.014184 | -0.87086 | -1.8647 | -3.0084 | -5.2071 | -6.6247 | -6.7302 | -6.7846 | 1.8642 | 1.6688 | 1.4578 | 1.205 | 0.85513 | 0.084009 | -0.75939 | -1.6651 | -2.764 | -3.9429 | -6.3654 | -8.1054 | -8.3372 | -8.4466
| TURRIFF | ST |  |  | 0.15081 | -0.033888 | -0.19818 | -0.37213 | -0.54311 | -1.0866 | -1.7265 | -2.3898 | -3.1656 | -4.119 | -6.1143 | -8.5554 | -9.4725 | -9.9543 | 2.2007 | 2.0495 | 1.8971 | 1.7382 | 1.5784 | 1.0124 | 0.3331 | -0.39884 | -1.2231 | -2.2064 | -4.0496 | -5.8094 | -6.3069 | -6.4413 | 1.9419 | 1.7839 | 1.626 | 1.4626 | 1.2935 | 0.7393 | 0.073143 | -0.63776 | -1.4356 | -2.4036 | -4.3743 | -6.4756 | -7.2409 | -7.4905
| TURRIFF | SP |  |  | 0.16654 | -0.007724 | -0.15958 | -0.31457 | -0.53599 | -1.1003 | -1.7887 | -2.5016 | -3.3356 | -4.3168 | -6.2645 | -8.5919 | -9.7842 | -10.156 | 2.2033 | 2.056 | 1.9087 | 1.7585 | 1.6063 | 1.0529 | 0.38462 | -0.33401 | -1.1488 | -2.1068 | -3.7801 | -5.1798 | -5.9337 | -6.1342 | 1.9483 | 1.7972 | 1.6491 | 1.4961 | 1.3201 | 0.76826 | 0.10339 | -0.60378 | -1.3932 | -2.3313 | -4.1058 | -5.8712 | -6.9058 | -7.1921
RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | 2.211 | 2.2007 | 2.1908 | 2.1588 | 2.1269 | 2.0709 | 2.0117 | 1.9515 | 1.8926 | 1.828 | 1.6799 | 1.5232 | 1.363 | 1.2735 | 2.3173 | 2.3144 | 2.3104 | 2.3005 | 2.2863 | 2.2575 | 2.2199 | 2.1817 | 2.1433 | 2.0807 | 1.9573 | 1.8153 | 1.6635 | 1.6147 | 2.2036 | 2.2032 | 2.2027 | 2.2012 | 2.1999 | 2.1673 | 2.1123 | 2.0565 | 2.001 | 1.9228 | 1.761 | 1.5832 | 1.4269 | 1.3426
| TYNDRUM | CT |  |  | 2.211 | 2.204 | 2.1949 | 2.1588 | 2.1269 | 2.0709 | 2.0117 | 1.9515 | 1.8926 | 1.8493 | 1.7213 | 1.5651 | 1.5661 | 1.5634 | 2.3173 | 2.3146 | 2.3104 | 2.3005 | 2.2863 | 2.2575 | 2.2199 | 2.1817 | 2.1433 | 2.1068 | 1.998 | 1.8582 | 1.8569 | 1.8558 | 2.2036 | 2.2032 | 2.2027 | 2.2012 | 2.1999 | 2.1673 | 2.1123 | 2.0565 | 2.001 | 1.9534 | 1.812 | 1.6331 | 1.6311 | 1.6285
| TYNDRUM | LW |  |  | 2.2322 | 2.2007 | 2.1908 | 2.1782 | 2.128 | 2.0746 | 2.0218 | 1.967 | 1.8997 | 1.828 | 1.6799 | 1.5232 | 1.5327 | 1.5285 | 2.319 | 2.3144 | 2.3107 | 2.306 | 2.2938 | 2.2605 | 2.2239 | 2.1857 | 2.1433 | 2.0807 | 1.9573 | 1.8153 | 1.8188 | 1.8172 | 2.2044 | 2.2036 | 2.2033 | 2.2028 | 2.2014 | 2.1704 | 2.119 | 2.0653 | 2.0032 | 1.9228 | 1.761 | 1.5832 | 1.5914 | 1.5878
| TYNDRUM | ST |  |  | 2.2394 | 2.2372 | 2.2352 | 2.232 | 2.2067 | 2.204 | 2.1777 | 2.1504 | 2.1186 | 2.0589 | 1.9222 | 1.5755 | 1.3706 | 1.3622 | 2.3209 | 2.3203 | 2.3198 | 2.3173 | 2.3139 | 2.3121 | 2.3086 | 2.2923 | 2.2639 | 2.2093 | 2.0872 | 1.8163 | 1.6635 | 1.6611 | 2.2044 | 2.2044 | 2.2043 | 2.204 | 2.2034 | 2.2032 | 2.2026 | 2.2016 | 2.1916 | 2.1228 | 1.9673 | 1.6255 | 1.4301 | 1.4229
| TYNDRUM | SP |  |  | 2.2414 | 2.2405 | 2.2397 | 2.2386 | 2.2117 | 2.2075 | 2.1799 | 2.1519 | 2.1224 | 2.0892 | 1.9772 | 1.6937 | 1.363 | 1.2735 | 2.3216 | 2.3216 | 2.3215 | 2.321 | 2.3181 | 2.3166 | 2.3128 | 2.2971 | 2.2702 | 2.2415 | 2.1526 | 1.9228 | 1.6765 | 1.6147 | 2.2045 | 2.2045 | 2.2046 | 2.2045 | 2.204 | 2.204 | 2.2033 | 2.2027 | 2.1981 | 2.1611 | 2.0428 | 1.7422 | 1.4269 | 1.3426
DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | 1.6075 | 1.6092 | 1.5839 | 1.5517 | 1.4512 | 1.3402 | 1.2339 | 1.1006 | 0.9242 | 0.82343 | 0.40688 | 0.31316 | 0.25404 | 0.17376 | 1.6974 | 1.6946 | 1.6802 | 1.6623 | 1.6206 | 1.5732 | 1.5241 | 1.4564 | 1.3682 | 1.307 | 1.0287 | 0.97299 | 0.93341 | 0.88453 | 1.4748 | 1.4769 | 1.4523 | 1.4211 | 1.3351 | 1.2401 | 1.1445 | 1.0214 | 0.86064 | 0.76594 | 0.36727 | 0.28013 | 0.2282 | 0.15701
| UIG | CT |  |  | 1.6582 | 1.6658 | 1.6508 | 1.6084 | 1.5093 | 1.4225 | 1.2865 | 1.143 | 1.0096 | 0.92885 | 0.62025 | 0.38345 | 0.37207 | 0.3544 | 1.7169 | 1.7166 | 1.7056 | 1.6782 | 1.6262 | 1.5807 | 1.5241 | 1.4639 | 1.4045 | 1.3552 | 1.1508 | 0.99941 | 0.98888 | 0.97278 | 1.5251 | 1.5333 | 1.5193 | 1.4792 | 1.3827 | 1.2983 | 1.1861 | 1.0573 | 0.9374 | 0.86152 | 0.56693 | 0.34335 | 0.33328 | 0.31789
| UIG | LW |  |  | 1.6075 | 1.6092 | 1.5839 | 1.5517 | 1.4512 | 1.3402 | 1.2339 | 1.1006 | 0.9242 | 0.82343 | 0.40688 | 0.31316 | 0.36484 | 0.3421 | 1.6974 | 1.6946 | 1.6802 | 1.6623 | 1.6206 | 1.5732 | 1.5274 | 1.4564 | 1.3682 | 1.307 | 1.0287 | 0.97299 | 0.99107 | 0.98261 | 1.4748 | 1.4769 | 1.4523 | 1.4211 | 1.3351 | 1.2401 | 1.1445 | 1.0214 | 0.86064 | 0.76594 | 0.36727 | 0.28013 | 0.32535 | 0.30551
| UIG | ST |  |  | 1.6467 | 1.6371 | 1.6276 | 1.6161 | 1.6056 | 1.5912 | 1.5722 | 1.5528 | 1.5273 | 1.4789 | 1.3003 | 0.81342 | 0.6538 | 0.58626 | 1.7159 | 1.7102 | 1.7041 | 1.6946 | 1.6865 | 1.676 | 1.6624 | 1.6471 | 1.6307 | 1.5997 | 1.4876 | 1.1559 | 1.0771 | 1.0451 | 1.5138 | 1.5049 | 1.4959 | 1.4846 | 1.474 | 1.4594 | 1.4405 | 1.421 | 1.3955 | 1.3477 | 1.1814 | 0.72237 | 0.57756 | 0.51846
| UIG | SP |  |  | 1.6489 | 1.6397 | 1.6325 | 1.6241 | 1.5872 | 1.5501 | 1.4997 | 1.4423 | 1.3799 | 1.2884 | 1.0756 | 0.62307 | 0.25404 | 0.17376 | 1.7173 | 1.7123 | 1.7075 | 1.7013 | 1.684 | 1.6656 | 1.6451 | 1.6196 | 1.5897 | 1.5475 | 1.4415 | 1.1888 | 0.93341 | 0.88453 | 1.5157 | 1.5071 | 1.5002 | 1.4917 | 1.4552 | 1.4187 | 1.378 | 1.3305 | 1.2764 | 1.1934 | 0.9994 | 0.58119 | 0.2282 | 0.15701
GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | YES | 0.68908 | 0.67592 | 0.66546 | 0.64003 | 0.58528 | 0.39986 | 0.22172 | 0.059436 | -0.072141 | -0.13532 | -0.35686 | -0.45556 | -0.34552 | -0.4493 | 1.0319 | 1.0201 | 1.0112 | 0.99056 | 0.97154 | 0.95597 | 0.89868 | 0.81435 | 0.74156 | 0.69055 | 0.53152 | 0.43642 | 0.44348 | 0.32765 | 0.75558 | 0.74278 | 0.73262 | 0.70798 | 0.64301 | 0.47488 | 0.30817 | 0.14724 | 0.015533 | -0.054807 | -0.2624 | -0.33018 | -0.23129 | -0.31925
| ULLAPOOL | CT |  |  | 0.68908 | 0.67592 | 0.66546 | 0.64003 | 0.61296 | 0.52729 | 0.3792 | 0.2573 | 0.14256 | 0.08548 | -0.096497 | -0.36053 | -0.32789 | -0.32984 | 1.0319 | 1.0201 | 1.0112 | 0.99056 | 0.97154 | 0.95597 | 0.93821 | 0.88049 | 0.82209 | 0.77761 | 0.64749 | 0.46951 | 0.46463 | 0.43695 | 0.75558 | 0.74278 | 0.73262 | 0.70798 | 0.68307 | 0.5809 | 0.44137 | 0.32402 | 0.21337 | 0.14944 | -0.028306 | -0.23957 | -0.21335 | -0.21381
| ULLAPOOL | LW |  |  | 0.69715 | 0.679 | 0.66965 | 0.65261 | 0.58528 | 0.39986 | 0.22172 | 0.059436 | -0.072141 | -0.13532 | -0.35686 | -0.45556 | -0.34552 | -0.37299 | 1.0385 | 1.0231 | 1.0152 | 1.0015 | 0.98409 | 0.96496 | 0.89868 | 0.81435 | 0.74156 | 0.69055 | 0.53152 | 0.43642 | 0.47941 | 0.46729 | 0.7634 | 0.74582 | 0.73675 | 0.72027 | 0.64301 | 0.47488 | 0.30817 | 0.14724 | 0.015533 | -0.054807 | -0.2624 | -0.33018 | -0.22951 | -0.25078
| ULLAPOOL | ST |  |  | 0.70158 | 0.69179 | 0.68572 | 0.67808 | 0.66056 | 0.64761 | 0.62367 | 0.61042 | 0.59664 | 0.57291 | 0.49658 | 0.20435 | 0.029515 | -0.0050586 | 1.0415 | 1.0323 | 1.0267 | 1.0199 | 1.0079 | 0.99943 | 0.98238 | 0.97218 | 0.96149 | 0.94291 | 0.88343 | 0.62228 | 0.50559 | 0.49175 | 0.76768 | 0.75817 | 0.75227 | 0.74482 | 0.72914 | 0.71783 | 0.69587 | 0.68328 | 0.67013 | 0.64726 | 0.57357 | 0.29293 | 0.1534 | 0.12156
| ULLAPOOL | SP |  |  | 0.70117 | 0.69205 | 0.68656 | 0.6806 | 0.6641 | 0.6522 | 0.6299 | 0.61855 | 0.6053 | 0.58508 | 0.39417 | -0.04666 | -0.33575 | -0.4493 | 1.0411 | 1.0324 | 1.0273 | 1.0217 | 1.0107 | 1.0031 | 0.98738 | 0.97872 | 0.96833 | 0.95232 | 0.90984 | 0.66642 | 0.44348 | 0.32765 | 0.76725 | 0.75838 | 0.75305 | 0.74724 | 0.73257 | 0.72232 | 0.70199 | 0.69127 | 0.67862 | 0.64665 | 0.44728 | 0.028475 | -0.23129 | -0.31925
SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | 3.0369 | 3.039 | 3.0148 | 2.9604 | 2.9002 | 2.8468 | 2.7894 | 2.6881 | 2.5979 | 2.5715 | 2.4908 | 2.4294 | 2.4743 | 2.4118 | 3.3896 | 3.389 | 3.3795 | 3.3614 | 3.3301 | 3.3015 | 3.2625 | 3.2205 | 3.1822 | 3.165 | 3.0897 | 3.0466 | 3.0667 | 3.0513 | 2.9132 | 2.9149 | 2.8936 | 2.8457 | 2.7927 | 2.7427 | 2.6732 | 2.5839 | 2.5043 | 2.4804 | 2.3937 | 2.3177 | 2.3571 | 2.3045
| UNST | CT |  |  | 3.0417 | 3.039 | 3.0148 | 2.9604 | 2.9002 | 2.8468 | 2.7894 | 2.6881 | 2.5979 | 2.5715 | 2.4908 | 2.4758 | 2.5345 | 2.549 | 3.3963 | 3.3947 | 3.3838 | 3.3614 | 3.3301 | 3.3015 | 3.2625 | 3.2205 | 3.1822 | 3.165 | 3.1075 | 3.073 | 3.1059 | 3.1166 | 2.9173 | 2.9149 | 2.8936 | 2.8457 | 2.7927 | 2.7427 | 2.6732 | 2.5839 | 2.5043 | 2.4804 | 2.4065 | 2.3673 | 2.4142 | 2.4269
| UNST | LW |  |  | 3.0369 | 3.0418 | 3.0265 | 3.0019 | 2.9431 | 2.8856 | 2.8094 | 2.7388 | 2.6326 | 2.6001 | 2.4947 | 2.4294 | 2.4743 | 2.4439 | 3.3896 | 3.389 | 3.3795 | 3.3657 | 3.3351 | 3.3048 | 3.2678 | 3.2359 | 3.1894 | 3.1676 | 3.0897 | 3.0466 | 3.0667 | 3.0516 | 2.9132 | 2.9174 | 2.9039 | 2.8822 | 2.8233 | 2.7588 | 2.691 | 2.6284 | 2.5344 | 2.505 | 2.3937 | 2.3177 | 2.3571 | 2.3305
| UNST | ST |  |  | 3.045 | 3.0459 | 3.0478 | 3.0401 | 3.0486 | 3.0559 | 3.0635 | 3.0725 | 3.0675 | 3.0566 | 3.01 | 2.8421 | 2.7515 | 2.7304 | 3.3979 | 3.3965 | 3.3954 | 3.391 | 3.3914 | 3.3906 | 3.3895 | 3.3887 | 3.3749 | 3.3629 | 3.3174 | 3.2303 | 3.1884 | 3.1805 | 2.9203 | 2.9211 | 2.9227 | 2.9159 | 2.9233 | 2.9295 | 2.9361 | 2.9439 | 2.9393 | 2.9225 | 2.8525 | 2.6638 | 2.5796 | 2.5611
| UNST | SP |  |  | 3.052 | 3.056 | 3.062 | 3.0683 | 3.063 | 3.0593 | 3.0535 | 3.0456 | 3.0304 | 2.9969 | 2.8858 | 2.6499 | 2.4751 | 2.4118 | 3.4001 | 3.3999 | 3.4002 | 3.4005 | 3.394 | 3.3881 | 3.381 | 3.3727 | 3.3551 | 3.3381 | 3.2867 | 3.1593 | 3.0761 | 3.0513 | 2.9265 | 2.9299 | 2.9352 | 2.9406 | 2.936 | 2.9326 | 2.9275 | 2.9146 | 2.8894 | 2.8562 | 2.7577 | 2.5215 | 2.3605 | 2.3045
SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | 5.6407 | 5.6292 | 5.5622 | 5.4695 | 5.2418 | 5.0087 | 4.7847 | 4.5589 | 4.2886 | 4.1786 | 3.7174 | 3.6867 | 3.8026 | 3.6377 | 6.3998 | 6.3869 | 6.3562 | 6.3161 | 6.2299 | 6.1322 | 6.0399 | 5.9405 | 5.8209 | 5.7411 | 5.4374 | 5.3854 | 5.4279 | 5.3267 | 5.5077 | 5.4859 | 5.4148 | 5.3116 | 5.0776 | 4.8382 | 4.588 | 4.3084 | 3.9918 | 3.7739 | 3.242 | 3.2184 | 3.3574 | 3.1996
| VOE | CT |  |  | 5.7011 | 5.6962 | 5.6319 | 5.4957 | 5.2791 | 5.074 | 4.865 | 4.5999 | 4.3616 | 4.2854 | 3.9062 | 3.8087 | 3.9831 | 4.0337 | 6.4233 | 6.4158 | 6.3892 | 6.3413 | 6.2583 | 6.1707 | 6.0806 | 5.9732 | 5.8729 | 5.8148 | 5.526 | 5.4638 | 5.5253 | 5.5254 | 5.5571 | 5.5414 | 5.4686 | 5.3124 | 5.0778 | 4.8633 | 4.6376 | 4.3613 | 4.108 | 3.9801 | 3.3995 | 3.3267 | 3.5241 | 3.5702
| VOE | LW |  |  | 5.6407 | 5.6292 | 5.5622 | 5.4695 | 5.2418 | 5.0087 | 4.7847 | 4.5589 | 4.2886 | 4.1786 | 3.7174 | 3.6867 | 3.8244 | 3.7344 | 6.3998 | 6.3869 | 6.3562 | 6.3161 | 6.2299 | 6.1322 | 6.0399 | 5.9405 | 5.8209 | 5.7411 | 5.4374 | 5.3854 | 5.4305 | 5.4042 | 5.5077 | 5.4859 | 5.4148 | 5.3116 | 5.0776 | 4.8382 | 4.588 | 4.3084 | 3.9918 | 3.7739 | 3.242 | 3.2184 | 3.3583 | 3.2638
| VOE | ST |  |  | 5.6942 | 5.6877 | 5.6815 | 5.6551 | 5.6582 | 5.6571 | 5.6559 | 5.6485 | 5.6189 | 5.5608 | 5.3514 | 4.8476 | 4.7019 | 4.6313 | 6.4272 | 6.4198 | 6.4123 | 6.3995 | 6.392 | 6.3819 | 6.3705 | 6.3469 | 6.322 | 6.2819 | 6.1469 | 5.8552 | 5.7538 | 5.7276 | 5.5655 | 5.5529 | 5.5405 | 5.5042 | 5.4955 | 5.4803 | 5.4639 | 5.4418 | 5.3937 | 5.308 | 5.0132 | 4.2848 | 4.223 | 4.1855
| VOE | SP |  |  | 5.7148 | 5.7172 | 5.7246 | 5.7312 | 5.6898 | 5.6529 | 5.6101 | 5.553 | 5.4891 | 5.3857 | 5.0503 | 4.347 | 3.8026 | 3.6377 | 6.4322 | 6.4279 | 6.4247 | 6.4206 | 6.3989 | 6.3783 | 6.3551 | 6.3175 | 6.2846 | 6.2357 | 6.0862 | 5.7336 | 5.4279 | 5.3267 | 5.5807 | 5.5776 | 5.5779 | 5.5773 | 5.5294 | 5.4856 | 5.4336 | 5.3636 | 5.2798 | 5.1557 | 4.7824 | 3.8537 | 3.3574 | 3.1996
GLENAGNES | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | 17.6079 | 17.5059 | 17.3184 | 17.1672 | 16.5141 | 15.8274 | 15.1478 | 14.4068 | 14.0637 | 13.755 | 12.7248 | 11.1314 | 10.1162 | 9.4647 | 19.216 | 19.1126 | 19.0207 | 18.9435 | 18.6871 | 18.4017 | 18.1608 | 17.8892 | 17.6753 | 17.3666 | 16.3772 | 15.241 | 14.6717 | 13.5366 | 17.591 | 17.4516 | 17.3362 | 17.2376 | 16.6976 | 16.0841 | 15.4786 | 14.8179 | 14.4996 | 14.2052 | 13.2282 | 11.7576 | 10.8879 | 10.3469
| WALTON | CT |  |  | 17.6079 | 17.5079 | 17.4176 | 17.3281 | 16.746 | 16.0313 | 15.6472 | 15.2976 | 14.9129 | 14.4711 | 13.131 | 11.1314 | 10.1162 | 9.4647 | 19.216 | 19.1126 | 19.0285 | 18.953 | 18.6944 | 18.4017 | 18.2286 | 18.0599 | 17.8786 | 17.5854 | 16.7273 | 15.576 | 14.6717 | 13.5622 | 17.591 | 17.465 | 17.3726 | 17.288 | 16.8899 | 16.249 | 15.9017 | 15.5774 | 15.2212 | 14.8141 | 13.5732 | 11.7576 | 10.8879 | 10.3469
| WALTON | LW |  |  | 17.6273 | 17.5059 | 17.3184 | 17.1672 | 16.5141 | 15.8274 | 15.1478 | 14.4068 | 14.0637 | 13.755 | 12.7248 | 11.2512 | 10.4217 | 9.77 | 19.2275 | 19.1139 | 19.0207 | 18.9435 | 18.6871 | 18.4094 | 18.1608 | 17.8892 | 17.6753 | 17.3666 | 16.3772 | 15.241 | 14.9154 | 14.6254 | 17.6032 | 17.4516 | 17.3362 | 17.2376 | 16.6976 | 16.0841 | 15.4786 | 14.8179 | 14.4996 | 14.2052 | 13.2282 | 11.8825 | 11.2013 | 10.6687
| WALTON | ST |  |  | 17.686 | 17.6442 | 17.5789 | 17.5285 | 17.4668 | 17.3836 | 17.3285 | 17.2609 | 17.1896 | 17.0835 | 16.647 | 15.5319 | 14.3224 | 13.2789 | 19.287 | 19.2372 | 19.1729 | 19.1226 | 19.0434 | 18.9515 | 18.8876 | 18.8131 | 18.755 | 18.6587 | 18.112 | 16.4797 | 15.4918 | 15.0303 | 17.6968 | 17.651 | 17.5866 | 17.5329 | 17.464 | 17.3782 | 17.3203 | 17.2496 | 17.2053 | 17.1079 | 16.7099 | 15.1602 | 13.9917 | 13.4523
| WALTON | SP |  |  | 17.6888 | 17.6533 | 17.5985 | 17.5548 | 17.4968 | 17.4181 | 17.3695 | 17.3158 | 17.2621 | 17.1797 | 16.8718 | 15.9439 | 15.0471 | 14.4778 | 19.2996 | 19.2582 | 19.2053 | 19.1655 | 19.09 | 18.9941 | 18.9331 | 18.8675 | 18.8015 | 18.7023 | 18.3399 | 17.2219 | 15.737 | 13.5366 | 17.7135 | 17.6787 | 17.6272 | 17.5867 | 17.5285 | 17.4514 | 17.4038 | 17.3513 | 17.2992 | 17.2199 | 16.9075 | 16.0412 | 14.592 | 13.9365
INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | 15.7628 | 15.511 | 15.2327 | 14.8997 | 14.497 | 14.0218 | 13.5853 | 12.7667 | 11.8947 | 10.6615 | 6.7182 | 2.0585 | 0.20593 | -0.31988 | 19.8711 | 19.6689 | 19.4311 | 19.1776 | 18.8724 | 18.5182 | 18.2223 | 17.8737 | 17.426 | 16.4719 | 13.4194 | 9.8178 | 8.2862 | 7.8899 | 17.7953 | 17.5612 | 17.2992 | 16.9926 | 16.6222 | 16.1176 | 15.618 | 15.0589 | 14.566 | 13.4901 | 9.6966 | 5.2143 | 3.4408 | 2.9502
| WATERLOO PLACE | CT |  |  | 15.7628 | 15.511 | 15.2327 | 14.8997 | 14.497 | 14.0218 | 13.5853 | 12.7667 | 11.9141 | 10.8592 | 7.8586 | 4.0484 | 3.4417 | 3.1998 | 19.8711 | 19.6689 | 19.4311 | 19.1776 | 18.8724 | 18.5182 | 18.2223 | 17.8737 | 17.426 | 16.6116 | 14.2962 | 11.3659 | 10.9115 | 10.7324 | 17.7953 | 17.5612 | 17.2992 | 16.9926 | 16.6222 | 16.1176 | 15.7238 | 15.3114 | 14.69 | 13.6764 | 10.7929 | 7.1332 | 6.5663 | 6.3503
| WATERLOO PLACE | LW |  |  | 15.8177 | 15.576 | 15.3197 | 15.023 | 14.6445 | 14.196 | 13.7506 | 12.8849 | 11.8947 | 10.6615 | 6.7182 | 2.0585 | 1.7093 | 1.5001 | 19.9123 | 19.7181 | 19.497 | 19.2711 | 18.9843 | 18.6507 | 18.328 | 17.9651 | 17.4269 | 16.4719 | 13.4194 | 9.8178 | 9.5592 | 9.4109 | 17.8462 | 17.6214 | 17.3796 | 17.1065 | 16.6822 | 16.1333 | 15.618 | 15.0589 | 14.566 | 13.4901 | 9.6966 | 5.2143 | 4.8933 | 4.7082
| WATERLOO PLACE | ST |  |  | 15.9502 | 15.806 | 15.6579 | 15.5405 | 15.3934 | 15.2343 | 15.0357 | 14.8199 | 14.5231 | 14.1046 | 11.3281 | 3.6299 | 0.20593 | -0.31988 | 20.009 | 19.8855 | 19.7428 | 19.6473 | 19.5274 | 19.403 | 19.2513 | 19.0872 | 18.8694 | 18.5594 | 16.9083 | 10.9299 | 8.2862 | 7.8899 | 17.9674 | 17.8317 | 17.6887 | 17.5794 | 17.4421 | 17.2949 | 17.1115 | 16.9126 | 16.6407 | 16.2558 | 14.1316 | 6.7253 | 3.4408 | 2.9502
| WATERLOO PLACE | SP |  |  | 15.9585 | 15.8279 | 15.6982 | 15.5938 | 15.4805 | 15.3517 | 15.2198 | 15.0537 | 14.8303 | 14.5475 | 13.2713 | 7.7263 | 2.903 | 1.4243 | 20.0149 | 19.9012 | 19.772 | 19.6855 | 19.5904 | 19.4878 | 19.3853 | 19.2568 | 19.0922 | 18.8806 | 18.1191 | 14.1167 | 10.3729 | 9.2187 | 17.975 | 17.8518 | 17.7259 | 17.6284 | 17.5222 | 17.4028 | 17.2809 | 17.1274 | 16.9227 | 16.6625 | 15.7259 | 10.6769 | 6.0445 | 4.6362
LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | 14.3159 | 14.2296 | 14.1252 | 14.0625 | 13.8002 | 13.5007 | 13.1645 | 12.7088 | 12.1366 | 11.6358 | 9.8188 | 6.946 | 5.1634 | 4.2665 | 14.4575 | 14.405 | 14.3429 | 14.2731 | 14.1241 | 13.9641 | 13.7814 | 13.5537 | 13.284 | 12.9892 | 11.9472 | 10.4645 | 9.5181 | 8.7348 | 14.5285 | 14.4565 | 14.3691 | 14.3069 | 14.0825 | 13.8236 | 13.4922 | 13.0913 | 12.5745 | 12.104 | 10.4732 | 7.9472 | 6.4646 | 5.7705
| WEST KIRKTON | CT |  |  | 14.3521 | 14.2782 | 14.1871 | 14.104 | 13.8385 | 13.5445 | 13.1645 | 12.7088 | 12.2263 | 11.681 | 9.8188 | 6.946 | 5.1634 | 4.2665 | 14.4676 | 14.4156 | 14.3512 | 14.2731 | 14.1241 | 13.9641 | 13.7814 | 13.5537 | 13.3134 | 13.0245 | 11.976 | 10.4645 | 9.5181 | 8.7348 | 14.5582 | 14.496 | 14.4173 | 14.3247 | 14.0861 | 13.8246 | 13.4922 | 13.0913 | 12.6686 | 12.179 | 10.4732 | 7.9472 | 6.4646 | 5.7705
| WEST KIRKTON | LW |  |  | 14.3159 | 14.2296 | 14.1252 | 14.0625 | 13.8002 | 13.5007 | 13.1969 | 12.7562 | 12.1366 | 11.6358 | 9.9436 | 7.8465 | 6.3938 | 5.6479 | 14.4575 | 14.405 | 14.3429 | 14.2989 | 14.1752 | 14.0299 | 13.8775 | 13.6168 | 13.284 | 12.9892 | 11.9472 | 10.8981 | 10.3082 | 9.9544 | 14.5285 | 14.4565 | 14.3691 | 14.3069 | 14.0825 | 13.8236 | 13.5506 | 13.1383 | 12.5745 | 12.104 | 10.4887 | 8.6625 | 7.5327 | 6.9708
| WEST KIRKTON | ST |  |  | 14.3853 | 14.3221 | 14.2543 | 14.215 | 14.1576 | 14.0891 | 14.0395 | 13.9711 | 13.8876 | 13.7517 | 13.24 | 11.4935 | 10.0968 | 9.0721 | 14.4859 | 14.4445 | 14.3995 | 14.3616 | 14.3136 | 14.2566 | 14.2086 | 14.1482 | 14.0742 | 13.9634 | 13.5388 | 12.1816 | 11.2306 | 10.4022 | 14.5886 | 14.5388 | 14.4853 | 14.4425 | 14.3895 | 14.3254 | 14.273 | 14.206 | 14.1237 | 13.9876 | 13.4704 | 11.753 | 10.5791 | 9.8008
| WEST KIRKTON | SP |  |  | 14.4072 | 14.3507 | 14.2888 | 14.2673 | 14.1986 | 14.1228 | 14.0627 | 13.9821 | 13.8649 | 13.7315 | 13.2833 | 12.0949 | 10.8387 | 10.2412 | 14.4978 | 14.4608 | 14.4194 | 14.3979 | 14.3512 | 14.2977 | 14.2521 | 14.1922 | 14.0972 | 13.9873 | 13.605 | 12.5421 | 11.1091 | 9.7824 | 14.6104 | 14.5666 | 14.5185 | 14.4963 | 14.4381 | 14.3729 | 14.3169 | 14.2443 | 14.1312 | 14.0031 | 13.5726 | 12.4231 | 11.2224 | 10.7638
KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | 0.089383 | 0.087621 | 0.082097 | 0.074137 | 0.053751 | 0.03217 | 0.0097094 | -0.014343 | -0.050627 | -0.066736 | -0.1278 | -0.13658 | -0.13168 | -0.14858 | 0.089436 | 0.088046 | 0.085393 | 0.081272 | 0.072516 | 0.063002 | 0.052351 | 0.03965 | 0.01998 | 0.0097072 | -0.032007 | -0.036305 | -0.039698 | -0.051967 | 0.081949 | 0.080207 | 0.075201 | 0.067928 | 0.049702 | 0.030523 | 0.01025 | -0.01197 | -0.045266 | -0.06036 | -0.11974 | -0.12764 | -0.12315 | -0.13796
| WESTER DRUMMOND | CT |  |  | 0.098235 | 0.09822 | 0.093777 | 0.08573 | 0.064602 | 0.046425 | 0.02077 | -0.0046605 | -0.029643 | -0.04242 | -0.098741 | -0.1249 | -0.12314 | -0.12474 | 0.092601 | 0.091902 | 0.088696 | 0.083903 | 0.073859 | 0.065857 | 0.054529 | 0.044207 | 0.033272 | 0.024474 | -0.016834 | -0.032853 | -0.034416 | -0.038759 | 0.089701 | 0.089652 | 0.085137 | 0.077613 | 0.058768 | 0.042484 | 0.019488 | -0.0028131 | -0.025124 | -0.037508 | -0.092722 | -0.117 | -0.11542 | -0.1168
| WESTER DRUMMOND | LW |  |  | 0.089383 | 0.087621 | 0.082097 | 0.074137 | 0.053751 | 0.03217 | 0.0097094 | -0.014343 | -0.050627 | -0.066736 | -0.1278 | -0.13658 | -0.12658 | -0.13144 | 0.089436 | 0.088046 | 0.085393 | 0.081272 | 0.072516 | 0.063002 | 0.052351 | 0.03965 | 0.01998 | 0.0097072 | -0.032007 | -0.036305 | -0.032646 | -0.034461 | 0.081949 | 0.080207 | 0.075201 | 0.067928 | 0.049702 | 0.030523 | 0.01025 | -0.01197 | -0.045266 | -0.06036 | -0.11974 | -0.12764 | -0.11885 | -0.12308
| WESTER DRUMMOND | ST |  |  | 0.09592 | 0.094787 | 0.093393 | 0.091113 | 0.089803 | 0.087945 | 0.084884 | 0.080967 | 0.0771 | 0.069151 | 0.038067 | -0.043097 | -0.061168 | -0.070998 | 0.091988 | 0.091357 | 0.090451 | 0.088659 | 0.087413 | 0.086011 | 0.083766 | 0.080637 | 0.078558 | 0.074034 | 0.05437 | -0.0026679 | -0.012018 | -0.019378 | 0.087731 | 0.086703 | 0.085398 | 0.083192 | 0.081777 | 0.079946 | 0.076988 | 0.073127 | 0.069598 | 0.062229 | 0.032861 | -0.045286 | -0.061202 | -0.069788
| WESTER DRUMMOND | SP |  |  | 0.098222 | 0.097117 | 0.096702 | 0.095669 | 0.089885 | 0.083423 | 0.07673 | 0.06999 | 0.061321 | 0.050499 | 0.012536 | -0.069276 | -0.13168 | -0.14858 | 0.093481 | 0.092761 | 0.092373 | 0.09145 | 0.088915 | 0.085656 | 0.082417 | 0.079299 | 0.074565 | 0.069784 | 0.049858 | 0.0028467 | -0.039698 | -0.051967 | 0.089932 | 0.088901 | 0.088503 | 0.087483 | 0.082326 | 0.076448 | 0.070401 | 0.064356 | 0.056421 | 0.046741 | 0.012152 | -0.063219 | -0.12315 | -0.13796
CARRADALE | WESTPARK FERGUS | MINIMUM HEADROOM | NR 66116 20950 | YES | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578
| WESTPARK FERGUS | CT |  |  | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578
| WESTPARK FERGUS | LW |  |  | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578
| WESTPARK FERGUS | ST |  |  | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578
| WESTPARK FERGUS | SP |  |  | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.8886 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.2402 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578 | 3.4578
THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | 3.8078 | 3.8098 | 3.804 | 3.7921 | 3.7604 | 3.7364 | 3.7088 | 3.6823 | 3.6488 | 3.6251 | 3.5705 | 3.5227 | 3.5294 | 3.5243 | 3.8601 | 3.8597 | 3.8569 | 3.8494 | 3.8342 | 3.8236 | 3.8096 | 3.7961 | 3.7781 | 3.7612 | 3.7236 | 3.6822 | 3.6841 | 3.6817 | 3.5081 | 3.5099 | 3.5041 | 3.4937 | 3.4665 | 3.4439 | 3.4198 | 3.3964 | 3.3679 | 3.3501 | 3.3054 | 3.288 | 3.3 | 3.2905
| WESTRAY | CT |  |  | 3.8217 | 3.824 | 3.8192 | 3.7985 | 3.7719 | 3.7492 | 3.7254 | 3.6987 | 3.666 | 3.6542 | 3.5964 | 3.5723 | 3.5863 | 3.5849 | 3.8654 | 3.8651 | 3.8623 | 3.8494 | 3.8371 | 3.8266 | 3.8158 | 3.8036 | 3.7857 | 3.7782 | 3.737 | 3.7185 | 3.7214 | 3.7185 | 3.5198 | 3.5217 | 3.5166 | 3.4999 | 3.4757 | 3.4546 | 3.4329 | 3.4085 | 3.3813 | 3.3707 | 3.3274 | 3.3062 | 3.3229 | 3.3274
| WESTRAY | LW |  |  | 3.8078 | 3.8098 | 3.804 | 3.7921 | 3.7604 | 3.7364 | 3.7088 | 3.6823 | 3.6488 | 3.6251 | 3.5705 | 3.5227 | 3.5294 | 3.5243 | 3.8601 | 3.8597 | 3.8569 | 3.8502 | 3.8342 | 3.8236 | 3.8096 | 3.7961 | 3.7781 | 3.7612 | 3.7236 | 3.6822 | 3.6841 | 3.6817 | 3.5081 | 3.5099 | 3.5041 | 3.4937 | 3.4665 | 3.4439 | 3.4198 | 3.3964 | 3.3679 | 3.3501 | 3.3054 | 3.288 | 3.3 | 3.2905
| WESTRAY | ST |  |  | 3.8178 | 3.8161 | 3.8148 | 3.8123 | 3.8118 | 3.8075 | 3.8014 | 3.8003 | 3.796 | 3.7879 | 3.7535 | 3.6343 | 3.5802 | 3.5681 | 3.8643 | 3.8632 | 3.8623 | 3.8604 | 3.8596 | 3.8561 | 3.8511 | 3.8497 | 3.8466 | 3.8416 | 3.818 | 3.7491 | 3.7099 | 3.7025 | 3.5171 | 3.5155 | 3.5143 | 3.5121 | 3.5117 | 3.5088 | 3.5048 | 3.5038 | 3.5001 | 3.4928 | 3.4644 | 3.4006 | 3.3856 | 3.3791
| WESTRAY | SP |  |  | 3.8207 | 3.8193 | 3.8185 | 3.8178 | 3.8078 | 3.7993 | 3.7861 | 3.776 | 3.7589 | 3.742 | 3.7068 | 3.6044 | 3.5651 | 3.5545 | 3.8664 | 3.8655 | 3.8647 | 3.8641 | 3.8596 | 3.8559 | 3.849 | 3.8447 | 3.8348 | 3.8274 | 3.8099 | 3.7457 | 3.715 | 3.7028 | 3.5191 | 3.5178 | 3.5173 | 3.5166 | 3.5079 | 3.5004 | 3.4897 | 3.4805 | 3.4672 | 3.4518 | 3.4203 | 3.3372 | 3.3031 | 3.2938
TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | 2.9737 | 2.8213 | 2.6317 | 2.4127 | 1.9582 | 1.4367 | 0.89527 | 0.35243 | -0.281 | -0.6941 | -1.6779 | -1.9917 | -1.7736 | -2.0272 | 4.5889 | 4.497 | 4.3834 | 4.2514 | 4.0323 | 3.7664 | 3.4661 | 3.1598 | 2.8054 | 2.5099 | 1.8384 | 1.6048 | 1.6512 | 1.3302 | 3.8772 | 3.7423 | 3.5756 | 3.3797 | 2.9637 | 2.488 | 1.9982 | 1.5056 | 0.92454 | 0.53345 | -0.39317 | -0.69191 | -0.50085 | -0.71641
| WHITEHOUSE | CT |  |  | 3.0543 | 2.9563 | 2.794 | 2.6102 | 2.1822 | 1.7535 | 1.2678 | 0.75179 | 0.28216 | -0.083323 | -1.1273 | -1.7056 | -1.7026 | -1.7479 | 4.608 | 4.535 | 4.4213 | 4.2944 | 4.0846 | 3.8655 | 3.6305 | 3.3687 | 3.1293 | 2.8621 | 2.0872 | 1.7041 | 1.6512 | 1.5602 | 3.9498 | 3.8643 | 3.7205 | 3.5514 | 3.1649 | 2.7752 | 2.3304 | 1.8587 | 1.4289 | 1.1003 | 0.10529 | -0.43284 | -0.43168 | -0.4716
| WHITEHOUSE | LW |  |  | 2.9737 | 2.8213 | 2.6317 | 2.4127 | 1.9582 | 1.4367 | 0.89527 | 0.35243 | -0.281 | -0.6941 | -1.6779 | -1.9917 | -1.7736 | -1.8512 | 4.5889 | 4.497 | 4.3834 | 4.2514 | 4.0323 | 3.7664 | 3.4661 | 3.1598 | 2.8054 | 2.5099 | 1.8384 | 1.6048 | 1.675 | 1.6454 | 3.8772 | 3.7423 | 3.5756 | 3.3797 | 2.9637 | 2.488 | 1.9982 | 1.5056 | 0.92454 | 0.53345 | -0.39317 | -0.69191 | -0.50085 | -0.5691
| WHITEHOUSE | ST |  |  | 3.0704 | 2.9968 | 2.9102 | 2.8206 | 2.7473 | 2.6555 | 2.567 | 2.4556 | 2.3112 | 2.0924 | 1.4108 | 0.028367 | -0.42368 | -0.64787 | 4.6357 | 4.5839 | 4.5212 | 4.4554 | 4.395 | 4.3196 | 4.2476 | 4.1597 | 4.057 | 3.9066 | 3.4261 | 2.383 | 2.1184 | 1.9504 | 3.9635 | 3.8996 | 3.8254 | 3.7471 | 3.68 | 3.5959 | 3.5138 | 3.4087 | 3.2741 | 3.0698 | 2.4273 | 1.1049 | 0.6951 | 0.49505
| WHITEHOUSE | SP |  |  | 3.1077 | 3.054 | 2.9906 | 2.929 | 2.8194 | 2.6877 | 2.5614 | 2.4107 | 2.2507 | 2.0346 | 1.2818 | -0.45521 | -1.5717 | -2.0272 | 4.6509 | 4.6077 | 4.5552 | 4.5024 | 4.4319 | 4.3408 | 4.2555 | 4.1514 | 4.0419 | 3.9059 | 3.48 | 2.3958 | 1.6687 | 1.3302 | 3.9979 | 3.9524 | 3.8994 | 3.8468 | 3.7463 | 3.626 | 3.5103 | 3.3712 | 3.2227 | 3.0238 | 2.3363 | 0.72214 | -0.3114 | -0.71641
PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | 7.4915 | 7.2534 | 6.9771 | 6.6684 | 6.2117 | 5.6777 | 5.0113 | 4.3378 | 3.519 | 2.7661 | -0.029208 | -3.953 | -5.6209 | -6.1104 | 8.326 | 8.1676 | 7.9835 | 7.7696 | 7.4967 | 7.2014 | 6.8371 | 6.4445 | 5.9818 | 5.5004 | 3.7614 | 1.6377 | 0.71344 | 0.08076 | 7.3975 | 7.2131 | 6.9922 | 6.738 | 6.3543 | 5.9085 | 5.3275 | 4.7459 | 4.0384 | 3.3824 | 0.97155 | -2.3045 | -3.7069 | -4.1235
| WHITESTRIPES | CT |  |  | 7.4915 | 7.2534 | 6.9771 | 6.6684 | 6.2117 | 5.7141 | 5.1077 | 4.4742 | 3.8 | 2.9858 | -0.029208 | -3.953 | -5.6209 | -6.1104 | 8.326 | 8.1676 | 7.9835 | 7.7696 | 7.4967 | 7.2014 | 6.8629 | 6.5173 | 6.1496 | 5.6884 | 3.7891 | 1.6377 | 0.71344 | 0.08076 | 7.3975 | 7.2131 | 6.9922 | 6.738 | 6.3543 | 5.9352 | 5.4188 | 4.8835 | 4.314 | 3.6117 | 0.97155 | -2.3045 | -3.7069 | -4.1235
| WHITESTRIPES | LW |  |  | 7.5391 | 7.3091 | 7.0611 | 6.7693 | 6.2645 | 5.6777 | 5.0113 | 4.3378 | 3.519 | 2.7661 | 0.080046 | -3.0367 | -4.4277 | -4.8552 | 8.3656 | 8.2137 | 8.0529 | 7.8596 | 7.5746 | 7.234 | 6.8371 | 6.4445 | 5.9818 | 5.5004 | 3.7614 | 2.1116 | 1.5445 | 1.3856 | 7.4445 | 7.2672 | 7.0735 | 6.837 | 6.4109 | 5.9085 | 5.3275 | 4.7459 | 4.0384 | 3.3824 | 1.0762 | -1.4737 | -2.6786 | -3.0409
| WHITESTRIPES | ST |  |  | 7.6194 | 7.4368 | 7.2508 | 7.053 | 6.8739 | 6.6805 | 6.4858 | 6.264 | 6.0228 | 5.6919 | 4.4729 | 1.1102 | 0.030451 | -0.53051 | 8.4157 | 8.3003 | 8.1812 | 8.0508 | 7.9255 | 7.7907 | 7.6529 | 7.4955 | 7.3228 | 7.0901 | 6.2245 | 3.7919 | 2.9691 | 2.2998 | 7.5213 | 7.3917 | 7.2584 | 7.1131 | 6.985 | 6.8457 | 6.7035 | 6.539 | 6.3588 | 6.0937 | 5.1043 | 2.2747 | 1.3659 | 0.88922
| WHITESTRIPES | SP |  |  | 7.6185 | 7.4487 | 7.2748 | 7.0955 | 6.8997 | 6.6868 | 6.467 | 6.2176 | 5.9431 | 5.6356 | 4.5739 | 2.0104 | 0.47456 | 0.32299 | 8.4058 | 8.2965 | 8.1824 | 8.063 | 7.9321 | 7.7879 | 7.638 | 7.4669 | 7.2757 | 7.0599 | 6.303 | 4.3451 | 2.6468 | 1.4661 | 7.518 | 7.4001 | 7.2779 | 7.1503 | 7.0082 | 6.8518 | 6.6876 | 6.4987 | 6.2887 | 6.0496 | 5.2243 | 3.1653 | 1.7462 | 1.6121
CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | 7.1165 | 7.1102 | 7.0888 | 7.0581 | 6.9551 | 6.8571 | 6.7016 | 6.5381 | 6.3824 | 6.2626 | 5.7924 | 5.6396 | 5.7038 | 5.6133 | 7.3856 | 7.3793 | 7.367 | 7.3422 | 7.2856 | 7.2312 | 7.1549 | 7.0746 | 6.992 | 6.9133 | 6.5879 | 6.4751 | 6.4935 | 6.4411 | 6.7124 | 6.7059 | 6.6861 | 6.6547 | 6.56 | 6.4699 | 6.3298 | 6.1825 | 6.0405 | 5.9265 | 5.4729 | 5.3243 | 5.3806 | 5.3053
| WHITING BAY | CT |  |  | 7.1368 | 7.134 | 7.1142 | 7.0581 | 6.9551 | 6.8571 | 6.7016 | 6.5381 | 6.388 | 6.2983 | 5.9563 | 5.6626 | 5.7197 | 5.7336 | 7.3944 | 7.39 | 7.3775 | 7.3422 | 7.2856 | 7.2312 | 7.1549 | 7.0746 | 6.9997 | 6.9408 | 6.7047 | 6.4842 | 6.4935 | 6.4864 | 6.73 | 6.7265 | 6.7079 | 6.6547 | 6.56 | 6.4699 | 6.3298 | 6.1825 | 6.0469 | 5.9616 | 5.6321 | 5.3453 | 5.3946 | 5.4068
| WHITING BAY | LW |  |  | 7.1165 | 7.1102 | 7.0888 | 7.0585 | 6.9649 | 6.8623 | 6.7562 | 6.604 | 6.3824 | 6.2626 | 5.7924 | 5.6396 | 5.7038 | 5.6638 | 7.3856 | 7.3793 | 7.367 | 7.3497 | 7.305 | 7.2543 | 7.2002 | 7.1097 | 6.992 | 6.9133 | 6.5879 | 6.4751 | 6.5006 | 6.4852 | 6.7124 | 6.7059 | 6.6861 | 6.6582 | 6.5743 | 6.4818 | 6.3856 | 6.2433 | 6.0405 | 5.9265 | 5.4729 | 5.3243 | 5.3806 | 5.3456
| WHITING BAY | ST |  |  | 7.1314 | 7.1263 | 7.1201 | 7.1041 | 7.0982 | 7.0897 | 7.0786 | 7.0636 | 7.0329 | 6.9774 | 6.7881 | 6.2661 | 6.1098 | 6.0797 | 7.3943 | 7.3908 | 7.3861 | 7.3746 | 7.3669 | 7.3575 | 7.3464 | 7.3321 | 7.3114 | 7.2752 | 7.1482 | 6.7629 | 6.6465 | 6.6209 | 6.7259 | 6.7212 | 6.7152 | 6.6997 | 6.6932 | 6.6841 | 6.6726 | 6.6571 | 6.628 | 6.5754 | 6.3948 | 5.8853 | 5.7356 | 5.7093
| WHITING BAY | SP |  |  | 7.1448 | 7.1458 | 7.1476 | 7.1466 | 7.1315 | 7.1152 | 7.0978 | 7.0744 | 7.0325 | 6.973 | 6.7454 | 6.2453 | 5.7374 | 5.6133 | 7.4004 | 7.3997 | 7.3988 | 7.3956 | 7.3869 | 7.3768 | 7.3663 | 7.3523 | 7.3247 | 7.2892 | 7.1585 | 6.8625 | 6.5173 | 6.4411 | 6.738 | 6.7387 | 6.74 | 6.7384 | 6.7247 | 6.7097 | 6.6937 | 6.6721 | 6.6323 | 6.577 | 6.3665 | 5.9014 | 5.4161 | 5.3053
MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | YES | 14.5994 | 14.3517 | 14.044 | 13.8959 | 13.5945 | 13.3261 | 13.059 | 12.8555 | 12.6621 | 12.5275 | 12.1802 | 11.9186 | 11.4617 | 11.3177 | 15.3155 | 15.0885 | 14.8094 | 14.6777 | 14.4065 | 14.1686 | 13.9284 | 13.7524 | 13.5879 | 13.4684 | 13.1378 | 12.7653 | 12.3749 | 12.0067 | 14.3173 | 14.0828 | 13.7935 | 13.6542 | 13.3654 | 13.1093 | 12.8538 | 12.6656 | 12.4887 | 12.3618 | 12.0317 | 11.8894 | 11.8207 | 11.7547
| WICK | CT |  |  | 14.6074 | 14.3576 | 14.0468 | 13.8988 | 13.5946 | 13.328 | 13.0595 | 12.8555 | 12.6621 | 12.5275 | 12.1933 | 12.0223 | 11.9566 | 11.9318 | 15.316 | 15.0885 | 14.8094 | 14.6777 | 14.4065 | 14.1686 | 13.9284 | 13.7524 | 13.5879 | 13.4684 | 13.1627 | 12.8663 | 12.8103 | 12.6021 | 14.3244 | 14.0879 | 13.7953 | 13.6566 | 13.3654 | 13.1099 | 12.8538 | 12.6656 | 12.4887 | 12.3618 | 12.0431 | 11.9021 | 11.8792 | 11.8654
| WICK | LW |  |  | 14.5994 | 14.3517 | 14.044 | 13.8959 | 13.5945 | 13.3261 | 13.059 | 12.8557 | 12.6643 | 12.5281 | 12.1802 | 11.9186 | 11.886 | 11.8614 | 15.3155 | 15.0913 | 14.8172 | 14.6878 | 14.422 | 14.186 | 13.9501 | 13.7783 | 13.6197 | 13.5046 | 13.1378 | 12.7735 | 12.7492 | 12.7322 | 14.3173 | 14.0828 | 13.7935 | 13.6542 | 13.3666 | 13.1093 | 12.8546 | 12.6669 | 12.4919 | 12.3635 | 12.0317 | 11.8894 | 11.8802 | 11.8679
| WICK | ST |  |  | 14.6135 | 14.364 | 14.0603 | 13.9278 | 13.6596 | 13.4292 | 13.1859 | 13.0057 | 12.8412 | 12.7181 | 12.3893 | 11.9458 | 11.4617 | 11.3177 | 15.3224 | 15.0975 | 14.8248 | 14.7047 | 14.4576 | 14.2453 | 14.0218 | 13.8616 | 13.7171 | 13.606 | 13.3057 | 12.7653 | 12.3749 | 12.2661 | 14.331 | 14.0951 | 13.8099 | 13.686 | 13.4287 | 13.2077 | 12.9753 | 12.8096 | 12.6602 | 12.5443 | 12.2309 | 11.96 | 11.8207 | 11.7547
| WICK | SP |  |  | 14.6144 | 14.3674 | 14.0621 | 13.9288 | 13.6577 | 13.4234 | 13.1766 | 12.992 | 12.8249 | 12.7039 | 12.4072 | 12.1845 | 11.7329 | 11.4578 | 15.3232 | 15.1004 | 14.8261 | 14.7058 | 14.4585 | 14.2444 | 14.0197 | 13.8576 | 13.7117 | 13.5996 | 13.3018 | 13.0155 | 12.5665 | 12.0067 | 14.3318 | 14.0987 | 13.8116 | 13.6871 | 13.4278 | 13.2036 | 12.9686 | 12.7992 | 12.6479 | 12.5348 | 12.2528 | 12.0413 | 11.8848 | 11.8089
WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | 10.7698 | 10.3175 | 10.1198 | 9.9714 | 9.4735 | 9.0351 | 8.595 | 8.0661 | 7.5807 | 7.0797 | 5.388 | 2.9808 | 1.5334 | 0.59115 | 12.614 | 12.4835 | 12.3226 | 12.1056 | 11.8363 | 11.527 | 11.2379 | 10.8974 | 10.4486 | 9.8718 | 8.0007 | 5.6858 | 5.3072 | 4.0712 | 10.7771 | 10.388 | 10.2102 | 10.0734 | 9.6288 | 9.2353 | 8.8383 | 8.3538 | 7.9038 | 7.4342 | 5.3971 | 2.3689 | 1.7977 | 1.4245
| WOODHILL | CT |  |  | 10.8256 | 10.5073 | 10.4189 | 10.3251 | 9.8408 | 9.3513 | 8.9519 | 8.5336 | 8.0761 | 7.5389 | 5.8567 | 3.0675 | 1.5334 | 0.59115 | 12.614 | 12.4835 | 12.3226 | 12.1056 | 11.8363 | 11.527 | 11.2379 | 10.912 | 10.5422 | 10.0744 | 8.7142 | 6.7582 | 6.2388 | 5.1879 | 10.8244 | 10.5521 | 10.4699 | 10.3782 | 9.9433 | 9.503 | 9.1421 | 8.7593 | 8.3397 | 7.8449 | 6.3103 | 3.517 | 2.6303 | 1.9613
| WOODHILL | LW |  |  | 10.7698 | 10.3175 | 10.1198 | 9.9714 | 9.4735 | 9.0351 | 8.595 | 8.0661 | 7.5807 | 7.0797 | 5.388 | 2.9808 | 1.8051 | 0.96106 | 12.635 | 12.5257 | 12.3498 | 12.1526 | 11.9012 | 11.6034 | 11.2764 | 10.8974 | 10.4486 | 9.8718 | 8.0007 | 5.6858 | 5.3072 | 4.9794 | 10.7771 | 10.388 | 10.2102 | 10.0734 | 9.6288 | 9.2353 | 8.8383 | 8.3538 | 7.9038 | 7.4342 | 5.3971 | 2.3689 | 1.7977 | 1.4245
| WOODHILL | ST |  |  | 11.0137 | 10.8808 | 10.7859 | 10.6508 | 10.5032 | 10.3502 | 10.2026 | 10.0486 | 9.9499 | 9.7491 | 8.975 | 6.3232 | 4.129 | 3.6496 | 12.6951 | 12.6322 | 12.5875 | 12.5375 | 12.4752 | 12.3504 | 12.2085 | 12.0357 | 11.8411 | 11.5288 | 10.3228 | 7.1341 | 5.4433 | 5.069 | 10.995 | 10.8882 | 10.804 | 10.6828 | 10.5508 | 10.4139 | 10.2801 | 10.1389 | 10.0443 | 9.8551 | 8.8762 | 4.925 | 2.8265 | 2.3704
| WOODHILL | SP |  |  | 11.0714 | 10.9798 | 10.9203 | 10.8548 | 10.747 | 10.6095 | 10.4912 | 10.3665 | 10.2229 | 10.0263 | 9.3295 | 7.4043 | 5.3513 | 4.3493 | 12.6981 | 12.6413 | 12.6057 | 12.5609 | 12.5186 | 12.4494 | 12.3525 | 12.2241 | 12.0799 | 11.8873 | 11.132 | 8.8195 | 6.3544 | 4.0712 | 11.0458 | 10.9758 | 10.9232 | 10.8642 | 10.7686 | 10.6468 | 10.5411 | 10.4279 | 10.2957 | 10.1156 | 9.4869 | 6.9654 | 3.9931 | 3.0959

## Primary Headroom Gen
Grid Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Generation Headroom Winter MVA | [13 empty] | Generation Headroom Summer MVA | [13 empty] | Generation Headroom Spring/Autumn MVA
[5 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050
FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | 0.10851 | -0.0087476 | -0.13823 | -0.29846 | -0.45416 | -0.60841 | -0.7583 | -0.90403 | -1.0287 | -1.1055 | -1.2266 | -1.4262 | -1.607 | -1.7898 | 0.11933 | 0.025682 | -0.073587 | -0.19936 | -0.32272 | -0.44752 | -0.57136 | -0.69247 | -0.79829 | -0.86895 | -0.98322 | -1.168 | -1.326 | -1.4851 | 0.096085 | -0.021665 | -0.15474 | -0.31874 | -0.47827 | -0.63697 | -0.79141 | -0.94182 | -1.0712 | -1.1526 | -1.2821 | -1.4912 | -1.6721 | -1.8601
| ABERCHALDER | CT |  |  | 0.10851 | -0.0087476 | -0.13823 | -0.29846 | -0.45416 | -0.60841 | -0.7583 | -0.90403 | -1.0287 | -1.1055 | -1.2266 | -1.4262 | -1.607 | -1.7898 | 0.11933 | 0.025682 | -0.073587 | -0.19936 | -0.32272 | -0.44752 | -0.57136 | -0.69247 | -0.79829 | -0.86895 | -0.98322 | -1.168 | -1.326 | -1.4851 | 0.096085 | -0.021665 | -0.15474 | -0.31874 | -0.47827 | -0.63697 | -0.79141 | -0.94182 | -1.0712 | -1.1526 | -1.2821 | -1.4912 | -1.6721 | -1.8601
| ABERCHALDER | LW |  |  | 0.22103 | 0.21213 | 0.19303 | 0.18365 | 0.17155 | 0.15768 | 0.14268 | 0.12666 | 0.1121 | 0.096924 | 0.049286 | -0.035869 | -0.11383 | -0.19776 | 0.20671 | 0.19624 | 0.1885 | 0.17925 | 0.16885 | 0.15747 | 0.14519 | 0.13214 | 0.12025 | 0.10786 | 0.069007 | -0.00032121 | -0.063904 | -0.13225 | 0.20471 | 0.19262 | 0.18299 | 0.17158 | 0.15874 | 0.14467 | 0.12948 | 0.11331 | 0.098595 | 0.083265 | 0.03515 | -0.050804 | -0.12954 | -0.21427
| ABERCHALDER | ST |  |  | 0.22445 | 0.21854 | 0.21262 | 0.19413 | 0.18688 | 0.17973 | 0.16964 | 0.15976 | 0.15027 | 0.14087 | 0.10899 | 0.063491 | 0.02208 | -0.014313 | 0.20895 | 0.20537 | 0.19671 | 0.18961 | 0.18264 | 0.1758 | 0.16756 | 0.15953 | 0.15183 | 0.14407 | 0.11792 | 0.08058 | 0.046522 | 0.016477 | 0.20827 | 0.19964 | 0.19319 | 0.18435 | 0.17568 | 0.1672 | 0.15696 | 0.14699 | 0.13741 | 0.12785 | 0.095539 | 0.049492 | 0.0075503 | -0.029355
| ABERCHALDER | SP |  |  | 0.22053 | 0.21262 | 0.19417 | 0.18671 | 0.17551 | 0.16281 | 0.15027 | 0.13791 | 0.12569 | 0.11364 | 0.078392 | 0.0091151 | -0.048836 | -0.10379 | 0.2065 | 0.19694 | 0.19004 | 0.18311 | 0.17281 | 0.16263 | 0.15258 | 0.14266 | 0.13285 | 0.12314 | 0.09472 | 0.038971 | -0.0077097 | -0.051964 | 0.20423 | 0.1934 | 0.18475 | 0.17606 | 0.16317 | 0.15043 | 0.13785 | 0.12544 | 0.11318 | 0.10106 | 0.065601 | -0.004082 | -0.06246 | -0.11782
TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | YES | 9.9476 | 9.9464 | 9.9141 | 9.8809 | 9.6727 | 9.4436 | 9.202 | 8.9488 | 7.6948 | 7.6159 | 7.4488 | 6.3628 | 5.2913 | 4.6893 | 8.6585 | 8.6465 | 8.6121 | 8.5546 | 7.2588 | 7.0154 | 6.7529 | 6.468 | 6.0975 | 5.9664 | 5.648 | 4.5249 | 3.5191 | 2.9334 | 7.3248 | 7.3235 | 7.2977 | 7.2711 | 7.0696 | 6.8485 | 6.6153 | 6.3706 | 5.9971 | 5.8452 | 5.4754 | 4.2691 | 3.1368 | 2.4722
| ABERFELDY | CT |  |  | 9.9476 | 9.9464 | 9.9141 | 9.8809 | 9.6727 | 9.4436 | 9.202 | 8.9488 | 7.6948 | 7.6159 | 7.4488 | 6.3628 | 5.2913 | 4.6893 | 8.6585 | 8.6465 | 8.6121 | 8.5546 | 7.2588 | 7.0154 | 6.7529 | 6.468 | 6.0975 | 5.9664 | 5.648 | 4.5249 | 3.5191 | 2.9334 | 7.3248 | 7.3235 | 7.2977 | 7.2711 | 7.0696 | 6.8485 | 6.6153 | 6.3706 | 5.9971 | 5.8452 | 5.4754 | 4.2691 | 3.1368 | 2.4722
| ABERFELDY | LW |  |  | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.9494 | 9.7404 | 9.7404 | 8.6649 | 8.6573 | 8.6453 | 8.6152 | 8.5817 | 8.5489 | 8.5218 | 8.5031 | 8.4848 | 8.4651 | 7.3046 | 7.164 | 6.842 | 6.7018 | 7.3265 | 7.3265 | 7.3265 | 7.3265 | 7.3265 | 7.3265 | 7.3265 | 7.3265 | 7.3265 | 7.3265 | 7.2457 | 7.0707 | 6.6681 | 6.4937
| ABERFELDY | ST |  |  | 9.9491 | 9.9489 | 9.9487 | 9.9484 | 9.9463 | 9.9438 | 9.9409 | 9.9376 | 9.9339 | 9.9327 | 9.929 | 9.9229 | 9.7864 | 9.7683 | 8.6643 | 8.6575 | 8.6484 | 8.6313 | 8.6063 | 8.5764 | 8.5395 | 8.5087 | 8.4856 | 8.4626 | 7.298 | 7.1404 | 6.8688 | 6.7018 | 7.3262 | 7.326 | 7.3258 | 7.3255 | 7.3235 | 7.321 | 7.3181 | 7.3147 | 7.3111 | 7.3099 | 7.2425 | 7.0479 | 6.7168 | 6.5134
| ABERFELDY | SP |  |  | 9.9488 | 9.9485 | 9.9481 | 9.9478 | 9.9477 | 9.9477 | 9.9476 | 9.9475 | 9.9475 | 9.947 | 9.9453 | 9.944 | 9.9357 | 9.9175 | 8.6704 | 8.6692 | 8.6678 | 8.6663 | 8.6598 | 8.6521 | 8.6408 | 8.6297 | 8.6154 | 8.6004 | 8.557 | 8.5036 | 8.4588 | 7.3201 | 7.3259 | 7.3256 | 7.3253 | 7.3249 | 7.3249 | 7.3248 | 7.3247 | 7.3247 | 7.3246 | 7.3241 | 7.3224 | 7.3211 | 7.3128 | 7.2728
STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | 4.2062 | 4.2054 | 4.2046 | 4.2033 | 4.1991 | 4.1942 | 4.1883 | 4.1817 | 4.1741 | 4.1698 | 4.1555 | 4.1222 | 4.0385 | 3.8279 | 4.4771 | 4.4763 | 4.4755 | 4.4742 | 4.4701 | 4.4623 | 4.4508 | 4.4182 | 4.3853 | 4.3535 | 4.2576 | 4.0919 | 3.9033 | 3.6653 | 4.1238 | 4.122 | 4.1197 | 4.115 | 4.1072 | 4.0986 | 4.0892 | 4.0666 | 4.0434 | 4.0221 | 3.9574 | 3.8424 | 3.7051 | 3.5175
| ABERFOYLE | CT |  |  | 4.2062 | 4.2054 | 4.2046 | 4.2033 | 4.1991 | 4.1942 | 4.1883 | 4.1817 | 4.1741 | 4.1698 | 4.1555 | 4.1222 | 4.0385 | 3.8279 | 4.4771 | 4.4763 | 4.4755 | 4.4742 | 4.4701 | 4.4623 | 4.4508 | 4.4182 | 4.3853 | 4.3535 | 4.2576 | 4.0919 | 3.9033 | 3.6653 | 4.1238 | 4.122 | 4.1197 | 4.115 | 4.1072 | 4.0986 | 4.0892 | 4.0666 | 4.0434 | 4.0221 | 3.9574 | 3.8424 | 3.7051 | 3.5175
| ABERFOYLE | LW |  |  | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.2073 | 4.4783 | 4.4783 | 4.4783 | 4.4783 | 4.4783 | 4.4737 | 4.4672 | 4.4609 | 4.4548 | 4.4481 | 4.4283 | 4.3965 | 4.3645 | 4.3328 | 4.125 | 4.1241 | 4.1226 | 4.1189 | 4.1147 | 4.1106 | 4.1067 | 4.1028 | 4.099 | 4.0948 | 4.0827 | 4.063 | 4.0433 | 4.0237
| ABERFOYLE | ST |  |  | 4.2072 | 4.207 | 4.2069 | 4.2068 | 4.2056 | 4.2042 | 4.2025 | 4.2007 | 4.1986 | 4.1979 | 4.1958 | 4.1923 | 4.1742 | 4.164 | 4.4781 | 4.478 | 4.4778 | 4.4777 | 4.4765 | 4.4751 | 4.4679 | 4.4539 | 4.4398 | 4.421 | 4.3661 | 4.2777 | 4.1755 | 4.0816 | 4.1251 | 4.1244 | 4.1234 | 4.1217 | 4.1184 | 4.1145 | 4.1052 | 4.0959 | 4.0864 | 4.0745 | 4.0399 | 3.984 | 3.914 | 3.8521
| ABERFOYLE | SP |  |  | 4.207 | 4.2069 | 4.2067 | 4.2066 | 4.2065 | 4.2065 | 4.2065 | 4.2064 | 4.2064 | 4.2062 | 4.2054 | 4.2048 | 4.2008 | 4.1921 | 4.478 | 4.4778 | 4.4776 | 4.4775 | 4.4775 | 4.4774 | 4.4774 | 4.4774 | 4.4773 | 4.4749 | 4.4536 | 4.4209 | 4.3868 | 4.3495 | 4.1256 | 4.1253 | 4.1251 | 4.1248 | 4.1242 | 4.1234 | 4.121 | 4.1186 | 4.1156 | 4.111 | 4.0975 | 4.0771 | 4.0545 | 4.0282
KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | YES | 9.6912 | 9.6903 | 9.6891 | 9.6874 | 9.1139 | 8.5258 | 7.9179 | 4.9099 | 3.9736 | 3.7863 | 3.25 | 2.0308 | 1.0894 | 0.74995 | 9.3676 | 9.3646 | 9.3603 | 9.3499 | 8.7616 | 8.1624 | 7.5435 | 4.8042 | 3.8678 | 3.6806 | 3.1443 | 1.925 | 0.98364 | 0.64419 | 8.1619 | 8.1594 | 8.1559 | 8.1487 | 7.5635 | 6.9673 | 4.5307 | 3.8798 | 2.9434 | 2.7562 | 2.2199 | 1.0007 | 0.05925 | -0.28019
| ABERLOUR | CT |  |  | 9.6912 | 9.6903 | 9.6891 | 9.6874 | 9.4863 | 9.2697 | 9.0405 | 8.7982 | 8.4577 | 8.375 | 8.1932 | 4.6135 | 3.8746 | 3.5943 | 9.3676 | 9.3646 | 9.3603 | 9.351 | 9.142 | 8.9175 | 8.6806 | 8.4095 | 8.0408 | 7.9275 | 7.6551 | 4.5077 | 3.7688 | 3.4886 | 8.1619 | 8.1594 | 8.1559 | 8.1487 | 7.9418 | 7.7194 | 7.4846 | 7.2213 | 6.8601 | 4.9944 | 4.8207 | 3.5833 | 2.8445 | 2.5642
| ABERLOUR | LW |  |  | 9.6922 | 9.692 | 9.6916 | 9.6907 | 9.1139 | 8.5258 | 7.9179 | 4.9099 | 3.9736 | 3.7863 | 3.25 | 2.0308 | 1.0894 | 0.74995 | 9.3684 | 9.3656 | 9.3611 | 9.3499 | 8.7616 | 8.1624 | 7.5435 | 4.8042 | 3.8678 | 3.6806 | 3.1443 | 1.925 | 0.98364 | 0.64419 | 8.1627 | 8.1606 | 8.1572 | 8.1487 | 7.5635 | 6.9673 | 4.5307 | 3.8798 | 2.9434 | 2.7562 | 2.2199 | 1.0007 | 0.05925 | -0.28019
| ABERLOUR | ST |  |  | 9.6921 | 9.6918 | 9.6916 | 9.6911 | 9.551 | 9.4011 | 9.2575 | 9.095 | 8.8345 | 8.769 | 8.6055 | 7.9783 | 4.7474 | 4.4575 | 9.3694 | 9.3679 | 9.3659 | 9.3622 | 9.2177 | 9.0625 | 8.9043 | 8.7274 | 8.4528 | 8.3671 | 8.145 | 7.4287 | 4.6416 | 4.3517 | 8.1634 | 8.1622 | 8.1607 | 8.1579 | 8.0145 | 7.8608 | 7.7065 | 7.5335 | 7.2626 | 7.1824 | 7.0038 | 4.6073 | 3.7172 | 3.4274
| ABERLOUR | SP |  |  | 9.6919 | 9.6917 | 9.6914 | 9.6911 | 9.675 | 9.6595 | 9.6431 | 9.625 | 9.5953 | 9.5631 | 9.4487 | 9.3383 | 7.9483 | 7.4988 | 9.3705 | 9.37 | 9.3696 | 9.3691 | 9.3517 | 9.3347 | 9.3131 | 9.2897 | 9.2532 | 9.2131 | 9.0758 | 8.9297 | 7.5062 | 7.025 | 8.1642 | 8.1638 | 8.1633 | 8.1629 | 8.1459 | 8.1292 | 8.1091 | 8.087 | 8.0524 | 8.0144 | 7.8833 | 7.7468 | 4.5672 | 4.1205
ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | 2.2864 | 2.2162 | 2.1487 | 2.0676 | 1.9732 | 1.8435 | 1.6911 | 1.5294 | 1.3368 | 1.173 | 0.68354 | -0.13727 | -1.9719 | -2.7 | 2.2301 | 2.1995 | 2.1699 | 2.1342 | 2.0805 | 2.027 | 1.9735 | 1.9194 | 1.8451 | 1.7071 | 0.95242 | -0.084737 | -2.0395 | -2.6832 | 2.2484 | 2.1868 | 2.1274 | 2.0395 | 1.865 | 1.7034 | 1.5442 | 1.3736 | 1.1663 | 0.98106 | 0.35261 | -0.68479 | -2.7405 | -3.4293
| ABERNETHY | CT |  |  | 2.2864 | 2.2162 | 2.1487 | 2.0676 | 1.9732 | 1.8435 | 1.6911 | 1.5294 | 1.3368 | 1.173 | 0.68354 | -0.059584 | -1.8269 | -2.7 | 2.2301 | 2.1995 | 2.1699 | 2.1342 | 2.0805 | 2.027 | 1.9735 | 1.9194 | 1.8451 | 1.7071 | 1.1569 | 0.32446 | -1.5409 | -2.5367 | 2.2484 | 2.1868 | 2.1274 | 2.0395 | 1.865 | 1.7034 | 1.5442 | 1.3736 | 1.1663 | 0.98106 | 0.41415 | -0.43342 | -2.4046 | -3.4293
| ABERNETHY | LW |  |  | 2.3501 | 2.3442 | 2.3386 | 2.3321 | 2.3009 | 2.1413 | 1.9767 | 1.8102 | 1.5964 | 1.417 | 0.75619 | -0.13727 | -1.9719 | -2.5333 | 2.2579 | 2.2553 | 2.2528 | 2.2497 | 2.2151 | 2.1792 | 2.1416 | 2.1013 | 1.9317 | 1.7241 | 0.95242 | -0.084737 | -2.0395 | -2.6832 | 2.3044 | 2.2993 | 2.2944 | 2.2887 | 2.146 | 1.958 | 1.7694 | 1.5792 | 1.3356 | 1.1262 | 0.35261 | -0.68479 | -2.7405 | -3.3991
| ABERNETHY | ST |  |  | 2.3522 | 2.3483 | 2.3444 | 2.3392 | 2.2734 | 2.2034 | 2.1257 | 1.9858 | 1.7763 | 1.629 | 1.1374 | 0.31185 | -1.0622 | -2.1009 | 2.2588 | 2.2571 | 2.2553 | 2.2529 | 2.187 | 2.1171 | 2.0496 | 1.9731 | 1.852 | 1.8195 | 1.4434 | 0.5158 | -0.93783 | -2.1503 | 2.3063 | 2.3029 | 2.2994 | 2.2949 | 2.2195 | 2.0918 | 1.9639 | 1.8124 | 1.5861 | 1.4167 | 0.8478 | -0.081821 | -1.5827 | -2.7854
| ABERNETHY | SP |  |  | 2.3496 | 2.3443 | 2.3391 | 2.3338 | 2.3246 | 2.3155 | 2.3064 | 2.2972 | 2.287 | 2.2765 | 2.0655 | 1.7853 | 1.421 | 1.1539 | 2.2603 | 2.2553 | 2.253 | 2.2507 | 2.2457 | 2.24 | 2.2337 | 2.2274 | 2.2195 | 2.2106 | 2.1793 | 2.1378 | 1.7746 | 1.4831 | 2.304 | 2.2993 | 2.2947 | 2.2901 | 2.2818 | 2.2736 | 2.2654 | 2.2298 | 2.1817 | 2.1209 | 1.8755 | 1.5548 | 1.156 | 0.85647
TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | 21.6791 | 21.6668 | 21.6406 | 21.5927 | 21.3313 | 21.0107 | 20.6922 | 20.3754 | 20.1278 | 20.0884 | 19.7792 | 19.4388 | 12.4659 | 10.5268 | 18.1974 | 18.1856 | 18.1615 | 18.1166 | 17.8677 | 17.5635 | 17.2612 | 17.187 | 17.0679 | 16.9736 | 13.2303 | 11.0134 | 7.4253 | 5.3745 | 17.6055 | 17.603 | 17.5889 | 17.5734 | 17.5477 | 17.5167 | 17.4819 | 17.4434 | 17.3999 | 17.3694 | 13.1018 | 10.905 | 7.2893 | 5.1231
| ABOYNE | CT |  |  | 21.6791 | 21.6668 | 21.6406 | 21.5927 | 21.4026 | 21.2306 | 21.0567 | 20.8084 | 20.4874 | 20.1058 | 19.7792 | 19.4388 | 12.9676 | 10.5268 | 18.1974 | 18.1856 | 18.1615 | 18.1166 | 17.9364 | 17.7734 | 17.6084 | 17.3727 | 17.0679 | 16.9736 | 16.8281 | 12.03 | 8.2137 | 5.3745 | 17.6055 | 17.603 | 17.5889 | 17.5734 | 17.5477 | 17.5167 | 17.4819 | 17.4434 | 17.3999 | 17.3694 | 17.2913 | 11.836 | 7.9892 | 5.1231
| ABOYNE | LW |  |  | 21.6886 | 21.6833 | 21.6749 | 21.6539 | 21.3313 | 21.0107 | 20.6922 | 20.3754 | 20.1278 | 20.0884 | 19.9404 | 19.8801 | 12.4659 | 11.2917 | 18.2066 | 18.2016 | 18.1936 | 18.1738 | 17.8677 | 17.5635 | 17.2612 | 17.187 | 17.1529 | 17.1272 | 13.2303 | 11.0134 | 7.4253 | 6.0193 | 17.6092 | 17.6092 | 17.6092 | 17.6092 | 17.6079 | 17.6053 | 17.6013 | 17.5956 | 17.5848 | 17.5825 | 13.1018 | 10.905 | 7.2893 | 5.8773
| ABOYNE | ST |  |  | 21.6875 | 21.6824 | 21.6758 | 21.6637 | 21.527 | 21.3931 | 21.229 | 21.0332 | 20.772 | 20.4426 | 20.0233 | 19.8415 | 19.6997 | 12.6791 | 18.2056 | 18.2007 | 18.1944 | 18.1829 | 18.0528 | 17.9255 | 17.7693 | 17.583 | 17.3346 | 17.1504 | 17.0697 | 12.8183 | 10.4601 | 7.7243 | 17.6082 | 17.6075 | 17.6069 | 17.6062 | 17.5995 | 17.5914 | 17.5819 | 17.5707 | 17.5568 | 17.5525 | 17.5382 | 12.6929 | 10.3471 | 7.5905
| ABOYNE | SP |  |  | 21.6908 | 21.6891 | 21.6873 | 21.6854 | 21.6507 | 21.6109 | 21.5423 | 21.4746 | 21.3853 | 21.2667 | 20.7899 | 20.176 | 20.0394 | 19.9205 | 18.2086 | 18.207 | 18.2052 | 18.2033 | 18.1704 | 18.1327 | 18.0676 | 18.0034 | 17.9186 | 17.8061 | 17.3535 | 17.1676 | 17.076 | 16.9745 | 17.6109 | 17.6091 | 17.6072 | 17.6051 | 17.6037 | 17.6034 | 17.6032 | 17.6029 | 17.6025 | 17.6007 | 17.5939 | 17.5877 | 17.5277 | 17.4559
GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | 0.45968 | 0.45944 | 0.45917 | 0.45888 | 0.45775 | 0.45641 | 0.45491 | 0.45309 | 0.45106 | 0.44997 | 0.44613 | 0.43729 | 0.024679 | -0.0035949 | 0.7158 | 0.71488 | 0.71357 | 0.71039 | 0.70661 | 0.70291 | 0.69906 | 0.68804 | 0.67697 | 0.66587 | 0.63096 | 0.57177 | 0.14679 | 0.071736 | 0.06758 | 0.067349 | 0.067075 | 0.06678 | 0.065654 | 0.064317 | 0.062812 | 0.060991 | 0.05897 | 0.057875 | 0.054033 | 0.045191 | -0.35043 | -0.3787
| ACHILTIBUIE | CT |  |  | 0.45968 | 0.45944 | 0.45917 | 0.45888 | 0.45775 | 0.45641 | 0.45491 | 0.45309 | 0.45106 | 0.44997 | 0.44613 | 0.43729 | 0.024679 | -0.0035949 | 0.7158 | 0.71488 | 0.71357 | 0.7108 | 0.70703 | 0.7031 | 0.69906 | 0.68804 | 0.67697 | 0.66587 | 0.63096 | 0.57177 | 0.14679 | 0.071736 | 0.06758 | 0.067349 | 0.067075 | 0.06678 | 0.065654 | 0.064317 | 0.062812 | 0.060991 | 0.05897 | 0.057875 | 0.054033 | 0.045191 | -0.35043 | -0.3787
| ACHILTIBUIE | LW |  |  | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.061963 | 0.061963 | 0.716 | 0.71515 | 0.71379 | 0.71039 | 0.70661 | 0.70291 | 0.69929 | 0.69575 | 0.69229 | 0.68855 | 0.67737 | 0.6583 | 0.27342 | 0.25564 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | -0.31314 | -0.31314
| ACHILTIBUIE | ST |  |  | 0.45993 | 0.45992 | 0.45991 | 0.4599 | 0.45981 | 0.45971 | 0.45958 | 0.45944 | 0.45929 | 0.45924 | 0.45909 | 0.45882 | 0.2585 | 0.25774 | 0.71634 | 0.71591 | 0.71534 | 0.71426 | 0.71272 | 0.71089 | 0.7038 | 0.69684 | 0.69004 | 0.68355 | 0.66365 | 0.63112 | 0.41878 | 0.38822 | 0.067833 | 0.067823 | 0.067812 | 0.067802 | 0.067717 | 0.067612 | 0.067486 | 0.067349 | 0.067191 | 0.067149 | 0.066991 | 0.066728 | -0.1251 | -0.12586
| ACHILTIBUIE | SP |  |  | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.45994 | 0.71676 | 0.7167 | 0.71664 | 0.71656 | 0.71615 | 0.71567 | 0.71333 | 0.711 | 0.708 | 0.70545 | 0.69811 | 0.68669 | 0.67569 | 0.66481 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844 | 0.067844
BROADFORD | ACHINTEE | MINIMUM HEADROOM | NG 93973 41406 | YES | 1.0379 | 1.0379 | 0.92177 | 0.80819 | 0.58156 | 0.32189 | 0.051402 | -0.2291 | -0.56905 | -0.75843 | -1.1067 | -2.0561 | -2.7644 | -3.2438 | 1.025 | 1.0249 | 0.91555 | 0.80705 | 0.58563 | 0.33275 | 0.069278 | -0.20415 | -0.5368 | -0.71868 | -1.0539 | -1.9821 | -2.6721 | -3.1339 | 1.0262 | 1.0261 | 0.91067 | 0.79593 | 0.56789 | 0.307 | 0.035275 | -0.24656 | -0.58789 | -0.77869 | -1.1296 | -2.0833 | -2.7955 | -3.2787
| ACHINTEE | CT |  |  | 1.0379 | 1.0379 | 0.92177 | 0.80819 | 0.58156 | 0.32189 | 0.051402 | -0.2291 | -0.56905 | -0.75843 | -1.1067 | -2.0561 | -2.7644 | -3.2438 | 1.025 | 1.0249 | 0.91555 | 0.80705 | 0.58563 | 0.33275 | 0.069278 | -0.20415 | -0.5368 | -0.71868 | -1.0539 | -1.9821 | -2.6721 | -3.1339 | 1.0262 | 1.0261 | 0.91067 | 0.79593 | 0.56789 | 0.307 | 0.035275 | -0.24656 | -0.58789 | -0.77869 | -1.1296 | -2.0833 | -2.7955 | -3.2787
| ACHINTEE | LW |  |  | 1.038 | 1.038 | 0.98498 | 0.93459 | 0.88441 | 0.83402 | 0.78363 | 0.73303 | 0.68263 | 0.63185 | 0.52974 | 0.3573 | 0.18123 | 0.00083578 | 1.025 | 1.0249 | 0.97583 | 0.92759 | 0.87953 | 0.83127 | 0.78302 | 0.73457 | 0.68633 | 0.63787 | 0.54025 | 0.37543 | 0.20716 | 0.034783 | 1.0262 | 1.0261 | 0.97349 | 0.92341 | 0.87293 | 0.82188 | 0.77084 | 0.71957 | 0.66853 | 0.61726 | 0.5141 | 0.3399 | 0.16203 | -0.020188
| ACHINTEE | ST |  |  | 1.038 | 1.038 | 1.0158 | 0.96819 | 0.87403 | 0.77559 | 0.68042 | 0.57689 | 0.43059 | 0.37373 | 0.21458 | -0.18409 | -0.68904 | -0.9785 | 1.025 | 1.025 | 0.99193 | 0.95983 | 0.86714 | 0.77016 | 0.6762 | 0.5739 | 0.42884 | 0.37333 | 0.21836 | -0.17273 | -0.6699 | -0.95137 | 1.0263 | 1.0262 | 0.99018 | 0.9568 | 0.86285 | 0.7644 | 0.6687 | 0.56465 | 0.41783 | 0.36049 | 0.2 | -0.20045 | -0.70721 | -0.9985
| ACHINTEE | SP |  |  | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.0249 | 1.0248 | 1.0246 | 1.0244 | 1.0242 | 1.0239 | 1.0234 | 1.0231 | 1.0231 | 1.0263 | 1.0263 | 1.0263 | 1.0263 | 1.0262 | 1.0262 | 1.026 | 1.0259 | 1.0258 | 1.0258 | 1.0258 | 1.0258 | 1.0258 | 1.0258
BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | 0.57291 | 0.57286 | 0.55898 | 0.54506 | 0.32922 | 0.11195 | -0.11268 | -0.35362 | -0.7002 | -0.75987 | -0.93079 | -1.3194 | -1.6498 | -1.7736 | 0.54394 | 0.54375 | 0.53526 | 0.52949 | 0.31477 | 0.097498 | -0.12714 | -0.36807 | -0.71465 | -0.77433 | -0.94759 | -1.342 | -1.6776 | -1.8027 | 0.54131 | 0.5412 | 0.52729 | 0.51531 | 0.31499 | 0.097723 | -0.12691 | -0.36785 | -0.71442 | -0.77437 | -0.94882 | -1.3431 | -1.6786 | -1.8035
| AIGAS | CT |  |  | 0.57291 | 0.57286 | 0.55898 | 0.54506 | 0.52212 | 0.4811 | 0.4511 | 0.41938 | 0.38145 | 0.35914 | 0.31685 | 0.20791 | 0.12407 | 0.059373 | 0.54394 | 0.54375 | 0.53526 | 0.52949 | 0.49025 | 0.46114 | 0.43077 | 0.39831 | 0.35964 | 0.33655 | 0.29227 | 0.18009 | 0.093091 | 0.025147 | 0.54131 | 0.5412 | 0.52729 | 0.51531 | 0.48418 | 0.4546 | 0.42375 | 0.39062 | 0.35128 | 0.32748 | 0.28164 | 0.16694 | 0.077594 | 0.0075046
| AIGAS | LW |  |  | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.32922 | 0.11195 | -0.11268 | -0.35362 | -0.7002 | -0.75987 | -0.93079 | -1.3194 | -1.6498 | -1.7736 | 0.54402 | 0.54385 | 0.54357 | 0.5429 | 0.31477 | 0.097498 | -0.12714 | -0.36807 | -0.71465 | -0.77433 | -0.94759 | -1.342 | -1.6776 | -1.8027 | 0.54139 | 0.54132 | 0.54121 | 0.54095 | 0.31499 | 0.097723 | -0.12691 | -0.36785 | -0.71442 | -0.77437 | -0.94882 | -1.3431 | -1.6786 | -1.8035
| AIGAS | ST |  |  | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.56027 | 0.54668 | 0.53377 | 0.48848 | 0.46486 | 0.46001 | 0.448 | 0.39283 | 0.30433 | 0.26833 | 0.54409 | 0.544 | 0.54389 | 0.54368 | 0.53067 | 0.51673 | 0.48866 | 0.47403 | 0.45041 | 0.44368 | 0.42483 | 0.36375 | 0.27297 | 0.23537 | 0.54141 | 0.54138 | 0.54134 | 0.54125 | 0.52842 | 0.51469 | 0.48888 | 0.47426 | 0.44958 | 0.44244 | 0.42377 | 0.36297 | 0.27248 | 0.23516
| AIGAS | SP |  |  | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.54417 | 0.54416 | 0.54414 | 0.54413 | 0.54405 | 0.54395 | 0.54335 | 0.54279 | 0.54207 | 0.54159 | 0.54037 | 0.53967 | 0.53965 | 0.53965 | 0.54144 | 0.54144 | 0.54144 | 0.54143 | 0.5414 | 0.54136 | 0.54113 | 0.5409 | 0.54062 | 0.54039 | 0.53994 | 0.53951 | 0.53951 | 0.53951
ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | YES | 9.7308 | 9.7301 | 9.7293 | 9.7282 | 9.7246 | 9.7204 | 9.7154 | 9.7096 | 9.7031 | 9.6994 | 9.687 | 9.6584 | 9.6112 | 9.5197 | 8.5521 | 8.5514 | 8.5506 | 8.5496 | 8.5459 | 8.5417 | 8.5367 | 8.5309 | 8.5244 | 8.5207 | 8.5083 | 8.4797 | 7.2944 | 7.0631 | 8.7295 | 8.7245 | 8.7172 | 8.7008 | 8.6805 | 8.66 | 8.639 | 8.6081 | 8.577 | 8.5466 | 8.5119 | 8.4636 | 7.2155 | 6.9759
| AIRD | CT |  |  | 9.7308 | 9.7301 | 9.7293 | 9.7282 | 9.7246 | 9.7204 | 9.7154 | 9.7096 | 9.7031 | 9.6994 | 9.687 | 9.6584 | 9.6112 | 9.5197 | 8.5521 | 8.5514 | 8.5506 | 8.5496 | 8.5459 | 8.5417 | 8.5367 | 8.5309 | 8.5244 | 8.5207 | 8.5083 | 8.4797 | 7.2944 | 7.0631 | 8.7295 | 8.7245 | 8.7172 | 8.7008 | 8.6805 | 8.66 | 8.639 | 8.6081 | 8.577 | 8.5466 | 8.5119 | 8.4636 | 7.2155 | 6.9759
| AIRD | LW |  |  | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 9.7317 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.553 | 8.7332 | 8.7312 | 8.728 | 8.7201 | 8.7113 | 8.7026 | 8.6942 | 8.6859 | 8.6779 | 8.6691 | 8.6433 | 8.6016 | 8.5658 | 8.5594
| AIRD | ST |  |  | 9.7314 | 9.7313 | 9.7311 | 9.7309 | 9.7293 | 9.7274 | 9.7251 | 9.7225 | 9.7196 | 9.7187 | 9.7158 | 9.7111 | 9.6862 | 9.6721 | 8.5527 | 8.5526 | 8.5524 | 8.5522 | 8.5506 | 8.5487 | 8.5464 | 8.5438 | 8.541 | 8.54 | 8.5372 | 8.5324 | 8.5075 | 8.4934 | 8.7318 | 8.729 | 8.7252 | 8.7181 | 8.7072 | 8.694 | 8.6778 | 8.6615 | 8.6452 | 8.6266 | 8.5727 | 8.537 | 8.4997 | 8.4731
| AIRD | SP |  |  | 9.7311 | 9.7308 | 9.7305 | 9.7302 | 9.7301 | 9.73 | 9.73 | 9.7299 | 9.7298 | 9.7294 | 9.7278 | 9.7266 | 9.7187 | 9.7015 | 8.5524 | 8.5521 | 8.5518 | 8.5515 | 8.5514 | 8.5514 | 8.5513 | 8.5512 | 8.5512 | 8.5507 | 8.5491 | 8.5479 | 8.54 | 8.5228 | 8.7341 | 8.7334 | 8.7326 | 8.7318 | 8.7291 | 8.7259 | 8.7212 | 8.7167 | 8.7108 | 8.7034 | 8.6819 | 8.6497 | 8.6125 | 8.5677
PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | 0.32275 | 0.32268 | 0.32257 | 0.32204 | 0.32172 | 0.32112 | 0.32002 | 0.28459 | 0.24256 | 0.19987 | 0.32279 | 0.32172 | 0.19987 | 0.32268 | 0.31974 | 0.31971 | 0.31965 | 0.3194 | 0.31925 | 0.31896 | 0.31844 | 0.28912 | 0.25578 | 0.2215 | 0.31976 | 0.31925 | 0.2215 | 0.31971 | 0.32124 | 0.32118 | 0.32108 | 0.32058 | 0.32027 | 0.3197 | 0.31866 | 0.28279 | 0.24032 | 0.19718 | 0.32128 | 0.32027 | 0.19718 | 0.32118
| AIRIGH-NA-BRODAIG | CT |  |  | 0.32277 | 0.32275 | 0.32271 | 0.32253 | 0.32239 | 0.32212 | 0.32162 | 0.31141 | 0.29792 | 0.27897 | 0.32279 | 0.32239 | 0.27897 | 0.32275 | 0.31975 | 0.31974 | 0.31972 | 0.31963 | 0.31957 | 0.31944 | 0.3192 | 0.31084 | 0.29966 | 0.28464 | 0.31976 | 0.31957 | 0.28464 | 0.31974 | 0.32127 | 0.32125 | 0.32121 | 0.32104 | 0.3209 | 0.32065 | 0.32017 | 0.31003 | 0.29611 | 0.27712 | 0.32128 | 0.3209 | 0.27712 | 0.32125
| AIRIGH-NA-BRODAIG | LW |  |  | 0.32275 | 0.32268 | 0.32257 | 0.32204 | 0.32172 | 0.32112 | 0.32002 | 0.28459 | 0.24256 | 0.19987 | 0.32279 | 0.32172 | 0.19987 | 0.32268 | 0.31974 | 0.31971 | 0.31965 | 0.3194 | 0.31925 | 0.31896 | 0.31844 | 0.28912 | 0.25578 | 0.2215 | 0.31976 | 0.31925 | 0.2215 | 0.31971 | 0.32124 | 0.32118 | 0.32108 | 0.32058 | 0.32027 | 0.3197 | 0.31866 | 0.28279 | 0.24032 | 0.19718 | 0.32128 | 0.32027 | 0.19718 | 0.32118
| AIRIGH-NA-BRODAIG | ST |  |  | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128
| AIRIGH-NA-BRODAIG | SP |  |  | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.32279 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.31976 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128 | 0.32128
COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | YES | 7.5819 | 7.5806 | 7.579 | 7.5768 | 7.3811 | 7.173 | 6.9563 | 4.6176 | 3.8851 | 3.4266 | 1.6498 | -1.1658 | -4.0945 | -5.6339 | 6.6108 | 6.6028 | 6.5912 | 6.5652 | 6.2676 | 4.7327 | 4.1109 | 3.4763 | 2.6326 | 2.0626 | -0.040525 | -3.1648 | -6.5335 | -8.259 | 7.1389 | 7.1361 | 7.1324 | 7.125 | 6.8699 | 6.6231 | 4.7015 | 4.096 | 3.2892 | 2.756 | 0.67888 | -2.4992 | -5.8689 | -7.5949
| ALYTH | CT |  |  | 7.5819 | 7.5806 | 7.579 | 7.5768 | 7.4382 | 7.2879 | 7.1279 | 6.9589 | 6.7216 | 4.6313 | 3.4009 | 0.64081 | -3.1852 | -5.6339 | 6.6108 | 6.6028 | 6.5912 | 6.5652 | 6.3704 | 6.1743 | 4.9218 | 4.5245 | 3.9685 | 3.508 | 1.9652 | -1.0537 | -5.4416 | -8.259 | 7.1389 | 7.1361 | 7.1324 | 7.125 | 6.9543 | 6.7766 | 6.5895 | 6.409 | 4.5523 | 4.1218 | 2.6812 | -0.38751 | -4.7767 | -7.5949
| ALYTH | LW |  |  | 7.5838 | 7.5838 | 7.5838 | 7.5838 | 7.3811 | 7.173 | 6.9563 | 4.6176 | 3.8851 | 3.4266 | 1.6498 | -1.1658 | -4.0945 | -5.5336 | 6.6168 | 6.6134 | 6.6081 | 6.5946 | 6.2676 | 4.7327 | 4.1109 | 3.4763 | 2.6326 | 2.0626 | -0.040525 | -3.1648 | -6.5335 | -8.1965 | 7.1417 | 7.141 | 7.1398 | 7.1369 | 6.8699 | 6.6231 | 4.7015 | 4.096 | 3.2892 | 2.756 | 0.67888 | -2.4992 | -5.8689 | -7.5325
| ALYTH | ST |  |  | 7.5835 | 7.5833 | 7.5831 | 7.5828 | 7.4882 | 7.3866 | 7.2894 | 7.1788 | 7.001 | 6.9618 | 3.8534 | 1.7667 | -0.90529 | -3.5457 | 6.6152 | 6.611 | 6.6055 | 6.595 | 6.4384 | 6.294 | 6.1503 | 4.8304 | 4.3506 | 3.9199 | 2.4583 | 0.08847 | -2.9316 | -5.9909 | 7.1411 | 7.14 | 7.1387 | 7.1362 | 7.0151 | 6.8879 | 6.7628 | 6.6289 | 4.9269 | 4.5247 | 3.162 | 0.7813 | -2.2395 | -5.2998
| ALYTH | SP |  |  | 7.5832 | 7.5829 | 7.5825 | 7.5822 | 7.5683 | 7.5549 | 7.5411 | 7.5257 | 7.5003 | 7.4726 | 7.3734 | 7.2818 | 3.373 | 2.5184 | 6.6187 | 6.6178 | 6.6168 | 6.6157 | 6.5696 | 6.5319 | 6.4968 | 6.4603 | 6.4072 | 6.3433 | 4.7034 | 3.8763 | 2.0563 | 1.0702 | 7.1416 | 7.1412 | 7.1407 | 7.1402 | 7.1193 | 7.0978 | 7.0712 | 7.0433 | 7.0013 | 6.9519 | 6.8235 | 4.5077 | 2.734 | 1.7877
FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | 9.1834 | 9.1821 | 9.1769 | 9.1711 | 9.1209 | 9.0532 | 8.9883 | 8.9147 | 8.7976 | 8.7731 | 8.7116 | 8.4781 | 7.1546 | 6.9315 | 8.4925 | 8.4912 | 8.4876 | 8.4832 | 8.43 | 8.3623 | 8.2974 | 8.2237 | 8.1067 | 8.0822 | 7.4531 | 7.1093 | 6.638 | 6.4004 | 8.5492 | 8.5385 | 8.5195 | 8.4821 | 8.4356 | 8.3754 | 8.302 | 8.2219 | 8.0986 | 8.065 | 7.4703 | 7.171 | 6.7456 | 6.5214
| ANNAT | CT |  |  | 9.1834 | 9.1821 | 9.1769 | 9.1711 | 9.1506 | 9.1273 | 9.102 | 9.0745 | 9.0407 | 9.0257 | 8.9873 | 8.8746 | 7.4101 | 7.0625 | 8.4925 | 8.4912 | 8.4876 | 8.4832 | 8.4644 | 8.4429 | 8.4196 | 8.3941 | 8.3624 | 8.3496 | 7.4531 | 7.1627 | 6.8515 | 6.4802 | 8.5492 | 8.5385 | 8.5195 | 8.4821 | 8.4356 | 8.3881 | 8.3634 | 8.3366 | 8.3035 | 8.2893 | 8.2522 | 7.2702 | 6.9529 | 6.5757
| ANNAT | LW |  |  | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 9.1852 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.4942 | 8.5609 | 8.56 | 8.5588 | 8.5556 | 8.552 | 8.5485 | 8.5451 | 8.5418 | 8.5385 | 8.535 | 8.5245 | 8.5077 | 8.4935 | 8.4813
| ANNAT | ST |  |  | 9.1848 | 9.1845 | 9.1843 | 9.1841 | 9.1209 | 9.0532 | 8.9883 | 8.9147 | 8.7976 | 8.7731 | 8.7116 | 8.4781 | 7.1546 | 6.9315 | 8.4939 | 8.4936 | 8.4934 | 8.4931 | 8.43 | 8.3623 | 8.2974 | 8.2237 | 8.1067 | 8.0822 | 7.4592 | 7.1093 | 6.638 | 6.4004 | 8.5566 | 8.5524 | 8.547 | 8.5366 | 8.4597 | 8.3754 | 8.302 | 8.2219 | 8.0986 | 8.065 | 7.4703 | 7.171 | 6.7456 | 6.5214
| ANNAT | SP |  |  | 9.1844 | 9.1839 | 9.1835 | 9.183 | 9.183 | 9.1829 | 9.1828 | 9.1827 | 9.1826 | 9.182 | 9.1798 | 9.1781 | 9.1671 | 9.1432 | 8.4934 | 8.493 | 8.4926 | 8.4921 | 8.4921 | 8.492 | 8.4919 | 8.4918 | 8.4917 | 8.491 | 8.4889 | 8.4871 | 8.4762 | 8.4523 | 8.56 | 8.559 | 8.5579 | 8.5568 | 8.5528 | 8.548 | 8.5448 | 8.5418 | 8.5379 | 8.5323 | 8.516 | 8.4925 | 8.4664 | 8.4283
NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | YES | 7.3255 | 7.3247 | 7.3238 | 7.3223 | 7.0691 | 6.8074 | 6.5368 | 6.2467 | 4.6575 | 4.5857 | 4.3802 | 3.913 | 3.5629 | 3.4362 | 6.2192 | 6.2167 | 6.2135 | 6.2074 | 5.9562 | 5.6915 | 4.8175 | 4.5278 | 4.1111 | 4.0393 | 3.8338 | 3.3666 | 3.0165 | 2.8897 | 6.4031 | 6.4024 | 6.4014 | 6.4 | 6.147 | 5.8854 | 4.9997 | 4.71 | 4.2932 | 4.2215 | 4.0159 | 3.5487 | 3.1987 | 3.0719
| ARDERSIER | CT |  |  | 7.3255 | 7.3247 | 7.3238 | 7.3223 | 7.2841 | 7.2427 | 7.1984 | 7.1497 | 7.0834 | 7.0676 | 7.0274 | 6.8348 | 6.6798 | 6.5435 | 6.2203 | 6.219 | 6.2171 | 6.2136 | 6.1733 | 6.1298 | 6.0834 | 6.0208 | 5.9433 | 5.9159 | 5.8458 | 5.6328 | 4.812 | 4.5526 | 6.4031 | 6.4024 | 6.4014 | 6.4 | 6.3619 | 6.3206 | 6.2764 | 6.2282 | 6.1625 | 6.1473 | 6.1088 | 5.9191 | 5.767 | 4.8401
| ARDERSIER | LW |  |  | 7.3266 | 7.3265 | 7.3263 | 7.3259 | 7.0691 | 6.8074 | 6.5368 | 6.2467 | 4.6575 | 4.5857 | 4.3802 | 3.913 | 3.5629 | 3.4362 | 6.2213 | 6.2205 | 6.2192 | 6.216 | 5.9562 | 5.6915 | 4.8175 | 4.5278 | 4.1111 | 4.0393 | 3.8338 | 3.3666 | 3.0165 | 2.8897 | 6.4042 | 6.4041 | 6.4039 | 6.4036 | 6.147 | 5.8854 | 4.9997 | 4.71 | 4.2932 | 4.2215 | 4.0159 | 3.5487 | 3.1987 | 3.0719
| ARDERSIER | ST |  |  | 7.3261 | 7.3256 | 7.325 | 7.324 | 7.3213 | 7.318 | 7.3147 | 7.311 | 7.3071 | 7.3046 | 7.2973 | 7.2853 | 7.2529 | 7.2316 | 6.2192 | 6.2167 | 6.2135 | 6.2074 | 6.1977 | 6.1862 | 6.1776 | 6.1689 | 6.1599 | 6.1497 | 6.122 | 6.0848 | 6.0522 | 6.0378 | 6.4037 | 6.4033 | 6.4028 | 6.4021 | 6.3996 | 6.3967 | 6.3936 | 6.3902 | 6.3866 | 6.3844 | 6.3783 | 6.3682 | 6.3376 | 6.318
| ARDERSIER | SP |  |  | 7.3262 | 7.326 | 7.3257 | 7.3254 | 7.3252 | 7.325 | 7.3246 | 7.3242 | 7.3237 | 7.3228 | 7.3199 | 7.3163 | 7.3078 | 7.2925 | 6.2214 | 6.221 | 6.2206 | 6.2201 | 6.2189 | 6.2175 | 6.2149 | 6.2123 | 6.209 | 6.2042 | 6.1903 | 6.1729 | 6.1517 | 6.1245 | 6.4038 | 6.4035 | 6.4033 | 6.403 | 6.4029 | 6.4027 | 6.4024 | 6.4021 | 6.4017 | 6.4009 | 6.3985 | 6.3956 | 6.3877 | 6.3731
FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | 2.9615 | 2.9611 | 2.9482 | 2.935 | 2.9203 | 2.9027 | 2.8843 | 2.8637 | 2.8424 | 2.8216 | 2.7797 | 2.4451 | 2.3405 | 2.2185 | 2.7693 | 2.7685 | 2.7576 | 2.7454 | 2.7317 | 2.7157 | 2.6991 | 2.6777 | 2.6564 | 2.495 | 2.4371 | 2.3393 | 2.2364 | 2.116 | 2.7956 | 2.7953 | 2.784 | 2.7725 | 2.7596 | 2.7441 | 2.7279 | 2.7109 | 2.6936 | 2.49 | 2.4198 | 2.3013 | 2.1796 | 2.0408
| ARISAIG | CT |  |  | 2.9615 | 2.9611 | 2.9482 | 2.935 | 2.9203 | 2.9027 | 2.8843 | 2.8637 | 2.8424 | 2.8216 | 2.7797 | 2.4451 | 2.3405 | 2.2185 | 2.7693 | 2.7685 | 2.7576 | 2.7454 | 2.7317 | 2.7157 | 2.6991 | 2.6777 | 2.6564 | 2.495 | 2.4371 | 2.3393 | 2.2364 | 2.116 | 2.7956 | 2.7953 | 2.784 | 2.7725 | 2.7596 | 2.7441 | 2.7279 | 2.7109 | 2.6936 | 2.49 | 2.4198 | 2.3013 | 2.1796 | 2.0408
| ARISAIG | LW |  |  | 2.9619 | 2.9618 | 2.9616 | 2.9611 | 2.9605 | 2.9599 | 2.9594 | 2.9588 | 2.9583 | 2.9577 | 2.956 | 2.9533 | 2.9506 | 2.9478 | 2.7697 | 2.769 | 2.768 | 2.7654 | 2.7625 | 2.7596 | 2.7569 | 2.7542 | 2.7515 | 2.7486 | 2.7401 | 2.7265 | 2.7226 | 2.7226 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796 | 2.796
| ARISAIG | ST |  |  | 2.9619 | 2.9618 | 2.9617 | 2.9615 | 2.9608 | 2.96 | 2.9586 | 2.9571 | 2.9556 | 2.9541 | 2.9496 | 2.9424 | 2.933 | 2.9293 | 2.7699 | 2.7695 | 2.769 | 2.7682 | 2.7666 | 2.7648 | 2.7601 | 2.7555 | 2.7508 | 2.7442 | 2.7249 | 2.7171 | 2.4807 | 2.4397 | 2.796 | 2.7959 | 2.7959 | 2.7958 | 2.7954 | 2.7949 | 2.7943 | 2.7936 | 2.7928 | 2.7926 | 2.7918 | 2.7905 | 2.7839 | 2.4566
| ARISAIG | SP |  |  | 2.962 | 2.962 | 2.9619 | 2.9619 | 2.9618 | 2.9618 | 2.9615 | 2.9612 | 2.9608 | 2.9603 | 2.9587 | 2.9564 | 2.9536 | 2.9502 | 2.7702 | 2.7701 | 2.7701 | 2.77 | 2.7697 | 2.7693 | 2.7679 | 2.7665 | 2.7647 | 2.7622 | 2.7548 | 2.7435 | 2.7323 | 2.7209 | 2.796 | 2.796 | 2.7959 | 2.7959 | 2.7959 | 2.7959 | 2.7959 | 2.7959 | 2.7959 | 2.7959 | 2.7957 | 2.7956 | 2.795 | 2.7936
STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9997 | 11.9997 | 11.9995 | 11.9993 | 11.9991 | 11.9983 | 11.9971 | 11.9959 | 11.9948 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9997 | 11.9997 | 11.9995 | 11.9993 | 11.9991 | 11.9983 | 11.9971 | 11.996 | 11.9948
| ARNISH | CT |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9995 | 11.9993 | 11.9991 | 11.9983 | 11.9971 | 11.9959 | 11.9948 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9995 | 11.9993 | 11.9991 | 11.9983 | 11.9971 | 11.996 | 11.9948
| ARNISH | LW |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9997 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.999 | 11.9986 | 11.9983 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9997 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.999 | 11.9986 | 11.9983
| ARNISH | ST |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9996 | 11.9992 | 11.9984 | 11.9977 | 11.9969 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9996 | 11.9992 | 11.9984 | 11.9977 | 11.9969
| ARNISH | SP |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9997 | 11.9994 | 11.9991 | 11.9989 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9997 | 11.9994 | 11.9991 | 11.9989
ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | 17.0515 | 30.2568 | 30.1841 | 30.094 | 29.9921 | 29.8888 | 29.7837 | 29.6768 | 29.5687 | 29.511 | 29.3843 | 29.1126 | 22.4069 | 20.1552 | 14.2352 | 26.2389 | 26.1567 | 26.0293 | 25.8249 | 25.6299 | 25.434 | 25.2687 | 25.1892 | 25.1465 | 25.0418 | 20.6962 | 17.6711 | 15.1587 | 13.9915 | 25.9884 | 25.9045 | 25.7907 | 25.6397 | 25.4919 | 25.3521 | 25.2093 | 25.0575 | 24.9472 | 24.7844 | 20.2395 | 17.1897 | 14.6556
| ASHGROVE | CT |  |  | 17.0515 | 30.2568 | 30.1841 | 30.094 | 29.9921 | 29.8888 | 29.7837 | 29.6768 | 29.5687 | 29.511 | 29.3843 | 29.1126 | 22.4069 | 20.1552 | 14.2352 | 26.2389 | 26.1567 | 26.0293 | 25.8249 | 25.6299 | 25.434 | 25.2687 | 25.1892 | 25.1465 | 25.0418 | 20.6962 | 17.6711 | 15.1587 | 13.9915 | 25.9884 | 25.9045 | 25.7907 | 25.6397 | 25.4919 | 25.3521 | 25.2093 | 25.0575 | 24.9472 | 24.7844 | 20.2395 | 17.1897 | 14.6556
| ASHGROVE | LW |  |  | 17.1216 | 30.3957 | 30.39 | 30.3834 | 30.3751 | 30.3653 | 30.3538 | 30.3407 | 30.3239 | 30.3122 | 30.2737 | 30.1937 | 30.1069 | 23.0929 | 14.306 | 26.3773 | 26.3664 | 26.3455 | 26.1819 | 26.0186 | 25.862 | 25.7278 | 25.6921 | 25.6847 | 25.6598 | 21.565 | 19.1082 | 18.0885 | 14.0688 | 26.1411 | 26.1328 | 26.1198 | 26.0497 | 25.9785 | 25.9171 | 25.8651 | 25.8 | 25.7398 | 25.6909 | 21.2729 | 18.7999 | 17.7644
| ASHGROVE | ST |  |  | 17.1225 | 30.3976 | 30.3927 | 30.3864 | 30.3721 | 30.3559 | 30.3368 | 30.3157 | 30.2925 | 30.2814 | 30.2454 | 30.1753 | 29.9806 | 29.8625 | 14.2999 | 26.3668 | 26.3508 | 26.3226 | 26.2245 | 26.1219 | 26.0216 | 25.9055 | 25.7712 | 25.6434 | 25.6135 | 25.5562 | 20.5224 | 18.4758 | 14.0671 | 26.1386 | 26.129 | 26.1134 | 26.0656 | 26.0149 | 25.9632 | 25.9041 | 25.8468 | 25.7905 | 25.664 | 25.5929 | 20.2409 | 18.1869
| ASHGROVE | SP |  |  | 17.1184 | 30.3917 | 30.3849 | 30.3781 | 30.3701 | 30.3622 | 30.3543 | 30.3465 | 30.3387 | 30.3291 | 30.2995 | 30.2508 | 30.1505 | 30.0209 | 14.3048 | 26.3777 | 26.3703 | 26.3626 | 26.3323 | 26.2982 | 26.2564 | 26.2153 | 26.163 | 26.0906 | 25.8221 | 25.6451 | 25.5622 | 25.449 | 14.0664 | 26.1389 | 26.1313 | 26.1236 | 26.106 | 26.0869 | 26.0649 | 26.0432 | 26.0171 | 25.982 | 25.8642 | 25.731 | 25.5657 | 25.4348
MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | 20.2228 | 20.2167 | 20.2097 | 20.1997 | 19.988 | 19.7562 | 19.5064 | 19.2397 | 18.8758 | 18.7909 | 18.5687 | 8.065 | 4.8504 | 1.1094 | 17.3732 | 17.3259 | 17.2571 | 17.0994 | 16.6087 | 16.121 | 15.619 | 15.1392 | 14.5798 | 14.4949 | 9.0247 | 5.2466 | 1.5583 | -2.7583 | 17.5346 | 17.5053 | 17.4637 | 17.3707 | 17.0227 | 16.6902 | 16.3412 | 15.9906 | 15.5182 | 15.2974 | 8.8554 | 5.1004 | 1.4577 | -2.8032
| ASHLUDIE | CT |  |  | 20.2228 | 20.2167 | 20.2097 | 20.1997 | 19.988 | 19.7562 | 19.5064 | 19.2397 | 18.8758 | 18.7909 | 18.5687 | 8.065 | 4.8504 | 1.1094 | 17.3732 | 17.3259 | 17.2571 | 17.0994 | 16.6087 | 16.121 | 15.619 | 15.1392 | 14.5798 | 14.4949 | 9.0247 | 5.2466 | 1.5583 | -2.7583 | 17.5346 | 17.5053 | 17.4637 | 17.3707 | 17.0227 | 16.6902 | 16.3412 | 15.9906 | 15.5182 | 15.2974 | 8.8554 | 5.1004 | 1.4577 | -2.8032
| ASHLUDIE | LW |  |  | 20.2316 | 20.2316 | 20.2316 | 20.2316 | 20.2299 | 20.2266 | 20.2214 | 20.214 | 20.2001 | 20.1971 | 20.1843 | 20.1396 | 9.1539 | 7.6724 | 17.4247 | 17.4211 | 17.4153 | 17.4008 | 17.1066 | 16.8136 | 16.522 | 16.2311 | 15.9041 | 15.9011 | 15.8884 | 7.5383 | 6.0154 | 4.2287 | 17.5673 | 17.5653 | 17.5621 | 17.5539 | 17.3879 | 17.2481 | 17.1301 | 17.0112 | 16.8571 | 16.7135 | 16.526 | 7.3984 | 5.9 | 4.1428
| ASHLUDIE | ST |  |  | 20.2292 | 20.2276 | 20.2259 | 20.224 | 20.208 | 20.1885 | 20.1656 | 20.1392 | 20.1078 | 20.0976 | 20.0658 | 19.9936 | 8.6027 | 5.4974 | 17.3889 | 17.3558 | 17.3122 | 17.2293 | 16.9969 | 16.746 | 16.5438 | 16.3111 | 16.016 | 15.8017 | 15.7698 | 8.737 | 5.4315 | 1.7102 | 17.5462 | 17.5269 | 17.5017 | 17.4543 | 17.3167 | 17.1984 | 17.1049 | 16.9973 | 16.8622 | 16.7291 | 16.4075 | 8.5746 | 5.3193 | 1.6574
| ASHLUDIE | SP |  |  | 20.2263 | 20.2236 | 20.2207 | 20.2178 | 20.2173 | 20.2167 | 20.2161 | 20.2155 | 20.2146 | 20.2101 | 20.1942 | 20.1806 | 20.0674 | 19.8969 | 17.4166 | 17.4095 | 17.4016 | 17.3931 | 17.3343 | 17.2657 | 17.1901 | 17.1155 | 17.0175 | 16.9005 | 16.4364 | 15.8846 | 15.7715 | 15.6009 | 17.5605 | 17.5553 | 17.5496 | 17.5435 | 17.5103 | 17.4715 | 17.4288 | 17.3866 | 17.3312 | 17.2723 | 17.08 | 16.8371 | 16.524 | 16.2385
GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | 6.9938 | 6.993 | 6.7217 | 6.5804 | 5.8918 | 5.5634 | 5.2246 | 4.869 | 4.5021 | 4.1274 | 3.4426 | 2.3206 | 1.3152 | 0.29669 | 6.7792 | 6.7783 | 6.5602 | 6.4412 | 5.7324 | 5.4061 | 5.0695 | 4.7091 | 4.3377 | 3.9578 | 3.2526 | 2.0974 | 1.0568 | 0.00331 | 6.839 | 6.8383 | 6.5691 | 5.9629 | 5.7501 | 5.4103 | 5.0564 | 4.6795 | 4.2911 | 3.8938 | 3.1597 | 1.9576 | 0.87737 | -0.21414
| AULTBEA | CT |  |  | 6.9938 | 6.993 | 6.7217 | 6.5804 | 5.8918 | 5.5634 | 5.2246 | 4.869 | 4.5021 | 4.1274 | 3.4426 | 2.3206 | 1.3152 | 0.29669 | 6.7792 | 6.7783 | 6.5602 | 6.4412 | 5.7324 | 5.4061 | 5.0695 | 4.7091 | 4.3377 | 3.9578 | 3.2526 | 2.0974 | 1.0568 | 0.00331 | 6.839 | 6.8383 | 6.5691 | 5.9629 | 5.7501 | 5.4103 | 5.0564 | 4.6795 | 4.2911 | 3.8938 | 3.1597 | 1.9576 | 0.87737 | -0.21414
| AULTBEA | LW |  |  | 6.9947 | 6.9947 | 6.8717 | 6.7487 | 6.678 | 6.6158 | 6.5535 | 5.9853 | 5.8676 | 5.7492 | 5.5089 | 5.1037 | 4.6901 | 4.2668 | 6.7801 | 6.7799 | 6.6776 | 6.5748 | 6.5054 | 6.4461 | 5.9347 | 5.8153 | 5.6966 | 5.577 | 5.3318 | 4.9188 | 4.4975 | 4.0667 | 6.84 | 6.84 | 6.7178 | 6.6003 | 6.488 | 6.3816 | 5.9235 | 5.8297 | 5.7171 | 5.5935 | 5.3374 | 4.906 | 4.4657 | 4.0154
| AULTBEA | ST |  |  | 6.9947 | 6.9946 | 6.9126 | 6.8305 | 6.7484 | 6.6973 | 6.6552 | 6.6128 | 6.5705 | 6.5285 | 5.7985 | 5.377 | 4.9415 | 4.4994 | 6.7801 | 6.78 | 6.7118 | 6.6435 | 6.5749 | 6.5326 | 6.4794 | 6.4264 | 5.9559 | 5.8673 | 5.6015 | 5.1554 | 4.6956 | 4.2294 | 6.8399 | 6.8399 | 6.7583 | 6.6768 | 6.5999 | 6.5239 | 6.4505 | 6.3784 | 5.9489 | 5.8698 | 5.6078 | 5.1655 | 4.6901 | 4.2076
| AULTBEA | SP |  |  | 6.9947 | 6.9946 | 6.951 | 6.9073 | 6.8649 | 6.8245 | 6.7854 | 6.747 | 6.7202 | 6.702 | 6.6504 | 6.5735 | 5.9904 | 5.8661 | 6.7802 | 6.7802 | 6.7439 | 6.7077 | 6.6724 | 6.6388 | 6.6058 | 6.5733 | 6.5417 | 6.516 | 6.448 | 5.943 | 5.7968 | 5.664 | 6.8399 | 6.8399 | 6.7965 | 6.7531 | 6.711 | 6.6709 | 6.6341 | 6.5987 | 6.5645 | 6.5315 | 6.4412 | 5.939 | 5.7925 | 5.6574
BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | YES | 28.3415 | 28.3413 | 28.3124 | 28.2833 | 28.2376 | 28.1452 | 28.0568 | 27.9576 | 27.8035 | 27.7649 | 27.6644 | 27.3292 | 26.7977 | 26.489 | 25.0126 | 25.0059 | 24.9746 | 24.9308 | 24.8638 | 24.7788 | 24.6769 | 24.5646 | 24.3978 | 24.3455 | 24.2055 | 23.8085 | 23.2174 | 22.0232 | 24.9208 | 24.9206 | 24.8739 | 24.827 | 24.7781 | 24.7035 | 24.6098 | 24.5054 | 24.346 | 24.3022 | 24.1857 | 23.8236 | 22.017 | 21.7099
| AVIEMORE | CT |  |  | 28.3415 | 28.3413 | 28.3124 | 28.2833 | 28.2525 | 28.2154 | 28.1771 | 28.1373 | 28.0961 | 28.0548 | 27.979 | 27.8525 | 27.7343 | 27.6032 | 25.0127 | 25.0071 | 24.9746 | 24.9308 | 24.8841 | 24.8333 | 24.782 | 24.7302 | 24.6778 | 24.6239 | 24.4966 | 24.2877 | 24.2212 | 24.1419 | 24.9208 | 24.9206 | 24.8739 | 24.827 | 24.7781 | 24.7191 | 24.658 | 24.595 | 24.5297 | 24.4638 | 24.3438 | 24.1457 | 23.9651 | 23.7737
| AVIEMORE | LW |  |  | 28.3419 | 28.3419 | 28.3292 | 28.3165 | 28.2709 | 28.2247 | 28.1773 | 28.1274 | 28.0612 | 28.0393 | 27.9872 | 27.8839 | 27.7958 | 27.7349 | 25.0126 | 25.0059 | 24.9815 | 24.9408 | 24.8638 | 24.787 | 24.7098 | 24.6307 | 24.536 | 24.4831 | 24.339 | 24.2376 | 24.1588 | 24.1074 | 24.9212 | 24.9212 | 24.9006 | 24.88 | 24.8266 | 24.7725 | 24.7173 | 24.6594 | 24.5854 | 24.5555 | 24.4875 | 24.3573 | 24.2419 | 24.1529
| AVIEMORE | ST |  |  | 28.3418 | 28.3417 | 28.3331 | 28.3245 | 28.2376 | 28.1452 | 28.0568 | 27.9576 | 27.8035 | 27.7649 | 27.6644 | 27.3292 | 26.7977 | 26.5814 | 25.0152 | 25.0118 | 24.9991 | 24.9829 | 24.8849 | 24.7788 | 24.6769 | 24.5646 | 24.3978 | 24.3455 | 24.2055 | 23.8085 | 23.2174 | 22.9467 | 24.9211 | 24.921 | 24.9072 | 24.8933 | 24.8012 | 24.7035 | 24.6098 | 24.5054 | 24.346 | 24.3022 | 24.1857 | 23.8236 | 22.017 | 21.7099
| AVIEMORE | SP |  |  | 28.3416 | 28.3414 | 28.3412 | 28.3411 | 28.3312 | 28.3217 | 28.3053 | 28.287 | 28.2568 | 28.2243 | 28.1084 | 28.0065 | 26.8573 | 26.489 | 25.0182 | 25.0175 | 25.0169 | 25.0161 | 25.0031 | 24.9898 | 24.9689 | 24.9462 | 24.9104 | 24.8724 | 24.7407 | 24.6141 | 23.442 | 22.0232 | 24.9209 | 24.9207 | 24.9205 | 24.9204 | 24.9105 | 24.901 | 24.8846 | 24.8663 | 24.8361 | 24.8036 | 24.6877 | 24.5858 | 23.4366 | 21.9674
ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | 5.7849 | 5.7833 | 5.7816 | 5.7791 | 5.632 | 5.4728 | 5.3037 | 5.1255 | 3.809 | 3.7347 | 3.5293 | 2.5542 | 1.863 | 1.346 | 5.3713 | 5.3598 | 5.3431 | 5.3051 | 5.1197 | 4.9229 | 3.8633 | 3.6343 | 3.3358 | 3.2343 | 2.9638 | 1.9551 | 1.2057 | 0.63135 | 5.5503 | 5.5456 | 5.5391 | 5.5254 | 5.3663 | 5.1953 | 5.0144 | 3.8642 | 3.6154 | 3.5577 | 3.2917 | 2.2657 | 1.5236 | 0.9565
| BALALDIE | CT |  |  | 5.7849 | 5.7833 | 5.7816 | 5.7791 | 5.632 | 5.4728 | 5.3037 | 5.1255 | 3.809 | 3.7347 | 3.5293 | 2.5542 | 1.863 | 1.346 | 5.3713 | 5.3598 | 5.3431 | 5.3051 | 5.1197 | 4.9229 | 3.8633 | 3.6343 | 3.3358 | 3.2343 | 2.9638 | 1.9551 | 1.2057 | 0.63135 | 5.5503 | 5.5456 | 5.5391 | 5.5254 | 5.3663 | 5.1953 | 5.0144 | 3.8642 | 3.6154 | 3.5577 | 3.2917 | 2.2657 | 1.5236 | 0.9565
| BALALDIE | LW |  |  | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7022 | 5.7022 | 5.7022 | 5.3839 | 5.383 | 5.3817 | 5.3783 | 5.3746 | 5.3709 | 5.3674 | 5.3639 | 5.3605 | 5.3568 | 5.3458 | 5.2596 | 5.2419 | 5.2243 | 5.5558 | 5.5555 | 5.5551 | 5.5541 | 5.5529 | 5.5517 | 5.5506 | 5.5495 | 5.5484 | 5.5473 | 5.5438 | 5.4523 | 5.4467 | 5.4411
| BALALDIE | ST |  |  | 5.7866 | 5.7862 | 5.7858 | 5.7854 | 5.7737 | 5.7607 | 5.7475 | 5.7325 | 5.711 | 5.7058 | 5.6917 | 5.6086 | 5.5053 | 5.4564 | 5.3817 | 5.3792 | 5.3761 | 5.3703 | 5.3514 | 5.3298 | 5.3053 | 5.2792 | 5.2468 | 5.2241 | 5.1591 | 5.0023 | 3.8531 | 3.6402 | 5.5547 | 5.5537 | 5.5524 | 5.5503 | 5.5364 | 5.5207 | 5.5039 | 5.4853 | 5.4605 | 5.4497 | 5.4196 | 5.3137 | 5.2105 | 3.9577
| BALALDIE | SP |  |  | 5.786 | 5.7855 | 5.7848 | 5.7842 | 5.7822 | 5.7802 | 5.7782 | 5.776 | 5.7724 | 5.7678 | 5.7514 | 5.7373 | 5.5899 | 5.515 | 5.383 | 5.382 | 5.3809 | 5.3797 | 5.3748 | 5.3694 | 5.3637 | 5.3577 | 5.3493 | 5.3378 | 5.3018 | 5.2569 | 5.0805 | 4.9782 | 5.5547 | 5.554 | 5.5533 | 5.5525 | 5.5495 | 5.5465 | 5.5433 | 5.5399 | 5.5348 | 5.528 | 5.5054 | 5.4817 | 5.3251 | 5.2416
ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | 7.9385 | 10.3593 | 10.2831 | 10.1625 | 10.0383 | 9.9132 | 6.9761 | 6.319 | 6.2471 | 5.7711 | 3.5321 | 2.7629 | 0.21413 | -3.1755 | 7.1534 | 9.5897 | 9.527 | 9.4207 | 9.3094 | 7.0475 | 6.2376 | 5.4307 | 5.3584 | 5.1121 | 2.3737 | 1.547 | -1.8509 | -5.1581 | 7.2812 | 9.699 | 9.6189 | 9.4905 | 9.2767 | 7.0914 | 6.2701 | 5.4517 | 5.3763 | 4.9543 | 2.1679 | 1.3066 | -1.9811 | -5.634
| BALBEGGIE | CT |  |  | 7.9385 | 10.3593 | 10.2831 | 10.1625 | 10.0383 | 9.9132 | 7.4723 | 7.0378 | 6.4476 | 5.7711 | 3.5321 | 2.7629 | 1.106 | -3.1755 | 7.1534 | 9.5897 | 9.527 | 9.4207 | 9.3094 | 9.2071 | 7.1052 | 6.6106 | 5.9263 | 5.1121 | 2.3737 | 1.547 | -0.22182 | -5.1581 | 7.2812 | 9.699 | 9.6189 | 9.4905 | 9.2767 | 7.4083 | 7.0222 | 6.5025 | 5.789 | 4.9543 | 2.1679 | 1.3066 | -0.60855 | -5.634
| BALBEGGIE | LW |  |  | 8.0109 | 10.5044 | 10.4982 | 10.4725 | 10.4417 | 10.4064 | 6.9761 | 6.319 | 6.2471 | 6.192 | 6.0263 | 4.0505 | 2.6639 | 0.081306 | 7.211 | 9.7047 | 9.6979 | 9.6686 | 9.5318 | 7.0475 | 6.2376 | 5.4307 | 5.3584 | 5.3026 | 5.1356 | 2.7727 | 1.3101 | -1.7519 | 7.3559 | 9.8485 | 9.8408 | 9.8116 | 9.5897 | 7.0914 | 6.2701 | 5.4517 | 5.3763 | 5.3173 | 5.1402 | 2.7362 | 1.1421 | -1.9795
| BALBEGGIE | ST |  |  | 8.0129 | 10.5084 | 10.5038 | 10.4874 | 10.4679 | 10.4468 | 10.4235 | 10.3991 | 7.3634 | 6.7607 | 4.6734 | 4.2729 | 0.21413 | -2.114 | 7.2116 | 9.7061 | 9.7 | 9.6801 | 9.5777 | 9.5435 | 9.5072 | 7.2977 | 6.7193 | 5.9739 | 3.3873 | 2.9291 | -1.8509 | -4.5371 | 7.3574 | 9.8516 | 9.8453 | 9.8257 | 9.7298 | 9.6361 | 9.5491 | 7.3449 | 6.7585 | 6.0029 | 3.3812 | 2.91 | -1.9811 | -4.7081
| BALBEGGIE | SP |  |  | 8.0097 | 10.5035 | 10.4974 | 10.4881 | 10.4765 | 10.4649 | 10.4535 | 10.4419 | 10.4315 | 10.4197 | 7.2879 | 6.1276 | 5.0499 | 4.0666 | 7.2109 | 9.7058 | 9.7007 | 9.6924 | 9.6515 | 9.6062 | 9.5745 | 9.5589 | 9.5419 | 9.5201 | 6.6291 | 5.2058 | 3.9035 | 2.7098 | 7.3553 | 9.8489 | 9.8425 | 9.8329 | 9.801 | 9.7664 | 9.7193 | 9.6727 | 9.6158 | 9.5501 | 6.6558 | 5.2056 | 3.8783 | 2.661
MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | 31.7772 | 31.7202 | 31.6706 | 31.6633 | 31.6311 | 30.9511 | 30.6707 | 30.2246 | 29.4562 | 29.2814 | 28.7597 | 27.7907 | 22.5329 | 22.1486 | 29.484 | 29.4189 | 29.3232 | 29.0986 | 28.8326 | 28.492 | 21.913 | 21.4669 | 20.6985 | 20.5237 | 20.002 | 19.033 | 18.2084 | 17.8242 | 29.4121 | 29.393 | 29.366 | 29.3058 | 29.2166 | 28.6036 | 28.2893 | 27.8228 | 21.8641 | 21.6893 | 21.1676 | 20.1986 | 19.374 | 18.9898
| BALDOVIE | CT |  |  | 31.7772 | 31.7202 | 31.6706 | 31.6633 | 31.6311 | 31.5205 | 31.4189 | 31.3121 | 31.1522 | 31.0643 | 30.797 | 29.9803 | 28.9858 | 28.0265 | 29.484 | 29.4189 | 29.3232 | 29.0986 | 28.8326 | 28.492 | 28.1643 | 27.9454 | 27.6755 | 27.4685 | 22.0392 | 21.2226 | 20.2281 | 19.2688 | 29.4121 | 29.393 | 29.366 | 29.3058 | 29.2166 | 29.0499 | 28.8933 | 28.7592 | 28.5725 | 28.4556 | 28.1021 | 27.1458 | 21.3937 | 20.1593
| BALDOVIE | LW |  |  | 31.838 | 31.8335 | 31.8263 | 31.8084 | 31.7752 | 31.6528 | 31.5303 | 31.4072 | 31.278 | 31.1793 | 30.936 | 30.2151 | 29.3984 | 28.9632 | 29.5532 | 29.548 | 29.5398 | 29.5191 | 29.4828 | 29.3574 | 29.2319 | 29.106 | 28.9739 | 28.8722 | 28.5689 | 21.4573 | 20.6407 | 20.2055 | 29.4371 | 29.4348 | 29.431 | 29.4254 | 29.4065 | 29.2981 | 29.1893 | 29.0796 | 28.9635 | 28.879 | 28.6266 | 27.8793 | 21.8063 | 21.3711
| BALDOVIE | ST |  |  | 31.8076 | 31.7781 | 31.7393 | 31.681 | 31.6577 | 31.113 | 30.6707 | 30.2246 | 29.4562 | 29.2814 | 28.7597 | 27.7907 | 22.5329 | 22.1486 | 29.5183 | 29.4845 | 29.4398 | 29.3544 | 29.2168 | 28.5352 | 21.913 | 21.4669 | 20.6985 | 20.5237 | 20.002 | 19.033 | 18.2084 | 17.8242 | 29.424 | 29.415 | 29.4033 | 29.3815 | 29.3303 | 28.7523 | 28.2893 | 27.8228 | 21.8641 | 21.6893 | 21.1676 | 20.1986 | 19.374 | 18.9898
| BALDOVIE | SP |  |  | 31.8329 | 31.8269 | 31.8203 | 31.813 | 31.7739 | 30.9511 | 30.9166 | 30.8811 | 30.059 | 29.8999 | 29.4103 | 28.6028 | 22.9467 | 22.4743 | 29.5478 | 29.5413 | 29.5339 | 29.5258 | 29.4822 | 28.6542 | 28.6159 | 28.5767 | 21.3013 | 21.1422 | 20.6526 | 19.8451 | 18.6222 | 18.1499 | 29.4328 | 29.4288 | 29.4245 | 29.4202 | 29.4018 | 28.6036 | 28.5865 | 28.5682 | 27.7624 | 27.5958 | 21.8182 | 21.0107 | 19.7878 | 19.3155
TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | 20.0874 | 20.0775 | 20.0408 | 19.9576 | 19.6991 | 19.4193 | 19.1262 | 18.803 | 18.4126 | 18.2949 | 18.0177 | 13.8131 | 12.7966 | 11.9892 | 17.352 | 17.3418 | 17.2996 | 17.2104 | 16.943 | 16.6514 | 16.3464 | 16.0062 | 15.5828 | 15.3938 | 13.5973 | 12.4575 | 11.3865 | 10.5251 | 16.0334 | 16.0249 | 15.984 | 15.8996 | 13.6042 | 13.347 | 13.0435 | 12.7029 | 12.2691 | 12.0598 | 11.5265 | 9.9824 | 8.8536 | 7.9359
| BALLATER | CT |  |  | 20.0874 | 20.0775 | 20.0408 | 19.9576 | 19.6991 | 19.4193 | 19.1262 | 18.803 | 18.4126 | 18.2949 | 18.0177 | 13.8131 | 12.7966 | 11.9892 | 17.352 | 17.3418 | 17.2996 | 17.2104 | 16.943 | 16.6514 | 16.3464 | 16.0062 | 15.5828 | 15.3938 | 13.5973 | 12.4575 | 11.3865 | 10.5251 | 16.0334 | 16.0249 | 15.984 | 15.8996 | 13.6042 | 13.347 | 13.0435 | 12.7029 | 12.2691 | 12.0598 | 11.5265 | 9.9824 | 8.8536 | 7.9359
| BALLATER | LW |  |  | 20.0932 | 20.0874 | 20.078 | 20.0226 | 19.9655 | 19.9098 | 19.8547 | 19.7989 | 19.7386 | 19.6756 | 19.5008 | 19.2289 | 19.1352 | 19.0428 | 17.358 | 17.3519 | 17.3423 | 17.286 | 17.2249 | 17.1629 | 17.1017 | 17.0399 | 16.9738 | 16.9044 | 16.7108 | 16.3464 | 16.1254 | 15.912 | 16.0387 | 16.0338 | 16.0261 | 15.9746 | 15.9187 | 15.8619 | 13.7876 | 13.7353 | 13.6688 | 13.5991 | 13.3748 | 12.9588 | 12.686 | 12.3961
| BALLATER | ST |  |  | 20.0951 | 20.0918 | 20.0876 | 20.062 | 19.9819 | 19.895 | 19.8005 | 19.7032 | 19.571 | 19.5024 | 19.3341 | 19.0357 | 18.6637 | 18.5238 | 17.3599 | 17.3566 | 17.3522 | 17.3263 | 17.2459 | 17.1586 | 17.062 | 16.9594 | 16.8221 | 16.7447 | 16.5508 | 16.136 | 15.5946 | 15.3103 | 16.0401 | 16.0374 | 16.0338 | 16.0094 | 15.9311 | 13.7607 | 13.6871 | 13.6067 | 13.4907 | 13.4402 | 13.2262 | 12.7415 | 12.1267 | 11.7092
| BALLATER | SP |  |  | 20.0974 | 20.0965 | 20.0954 | 20.089 | 20.0808 | 20.0721 | 20.0592 | 20.0461 | 20.0329 | 20.0131 | 19.9736 | 19.9078 | 19.8416 | 19.7615 | 17.3623 | 17.3614 | 17.3603 | 17.3538 | 17.3456 | 17.3368 | 17.3236 | 17.3102 | 17.2967 | 17.2764 | 17.2287 | 17.1472 | 17.0663 | 16.9724 | 16.042 | 16.0411 | 16.0402 | 16.0338 | 16.0261 | 16.018 | 16.0063 | 15.9945 | 15.9829 | 15.9655 | 15.9261 | 15.8575 | 13.7554 | 13.638
CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | 1.3396 | 1.3394 | 1.3319 | 1.3241 | 1.3156 | 1.3052 | 0.99646 | 0.98298 | 0.96398 | 0.94211 | 0.90071 | 0.83089 | 0.76325 | 0.68451 | 1.2279 | 1.2278 | 1.2236 | 1.2193 | 1.2142 | 1.2081 | 0.98449 | 0.96316 | 0.9411 | 0.91918 | 0.87425 | 0.79678 | 0.72105 | 0.63428 | 1.4023 | 1.4021 | 1.3908 | 1.3795 | 1.3671 | 0.99269 | 0.97424 | 0.95503 | 0.93507 | 0.91541 | 0.87867 | 0.81641 | 0.75575 | 0.6838
| BALLIEKINE | CT |  |  | 1.3396 | 1.3394 | 1.3319 | 1.3241 | 1.3156 | 1.3052 | 0.99646 | 0.98298 | 0.96398 | 0.94211 | 0.90071 | 0.83089 | 0.76325 | 0.68451 | 1.2279 | 1.2278 | 1.2236 | 1.2193 | 1.2142 | 1.2081 | 0.98449 | 0.96316 | 0.9411 | 0.91918 | 0.87425 | 0.79678 | 0.72105 | 0.63428 | 1.4023 | 1.4021 | 1.3908 | 1.3795 | 1.3671 | 0.99269 | 0.97424 | 0.95503 | 0.93507 | 0.91541 | 0.87867 | 0.81641 | 0.75575 | 0.6838
| BALLIEKINE | LW |  |  | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.3399 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.4025 | 1.4025 | 1.4025 | 1.4024 | 1.4023 | 1.4022 | 1.4021 | 1.402 | 1.4019 | 1.4017 | 1.4014 | 1.4009 | 1.4004 | 1.3999
| BALLIEKINE | ST |  |  | 1.3398 | 1.3398 | 1.3398 | 1.3397 | 1.3394 | 1.3389 | 1.3384 | 1.3379 | 1.3372 | 1.337 | 1.3364 | 1.3354 | 1.3299 | 1.3268 | 1.2282 | 1.2281 | 1.2281 | 1.228 | 1.2277 | 1.2273 | 1.2268 | 1.2262 | 1.2256 | 1.2254 | 1.2247 | 1.2237 | 1.2182 | 0.99782 | 1.4025 | 1.4024 | 1.4024 | 1.4023 | 1.4019 | 1.4015 | 1.4007 | 1.4 | 1.3991 | 1.3986 | 1.3972 | 1.3949 | 1.3882 | 1.3838
| BALLIEKINE | SP |  |  | 1.3397 | 1.3396 | 1.3396 | 1.3395 | 1.3395 | 1.3395 | 1.3394 | 1.3394 | 1.3394 | 1.3393 | 1.3389 | 1.3386 | 1.3365 | 1.3321 | 1.2281 | 1.228 | 1.2279 | 1.2278 | 1.2278 | 1.2278 | 1.2278 | 1.2278 | 1.2277 | 1.2276 | 1.2272 | 1.2269 | 1.2249 | 1.2204 | 1.4024 | 1.4023 | 1.4022 | 1.4022 | 1.4021 | 1.4021 | 1.402 | 1.4019 | 1.4018 | 1.4016 | 1.4009 | 1.4001 | 1.3976 | 1.3927
BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | YES | 15.257 | 15.1876 | 15.075 | 14.931 | 14.7854 | 14.6299 | 14.4742 | 14.3177 | 14.1646 | 14.0415 | 13.8065 | 13.4012 | 12.0174 | 11.7325 | 13.4336 | 13.396 | 13.3386 | 13.2565 | 13.172 | 13.0816 | 12.9906 | 12.8589 | 12.6094 | 12.5465 | 12.3965 | 11.0833 | 10.2289 | 9.8705 | 13.2692 | 13.2013 | 13.096 | 12.9595 | 12.8216 | 12.6749 | 12.5281 | 12.3834 | 12.257 | 11.3852 | 11.088 | 10.5827 | 10.0606 | 9.7036
| BALLINDALLOCH | CT |  |  | 15.257 | 15.1876 | 15.075 | 14.931 | 14.7854 | 14.6299 | 14.4742 | 14.3177 | 14.1646 | 14.0415 | 13.8065 | 13.4012 | 13.1722 | 11.8958 | 13.4336 | 13.396 | 13.3386 | 13.2565 | 13.172 | 13.0816 | 12.9906 | 12.8985 | 12.8085 | 12.7353 | 12.5844 | 11.1659 | 10.8278 | 10.4601 | 13.2692 | 13.2013 | 13.096 | 12.9595 | 12.8216 | 12.6749 | 12.5281 | 12.3834 | 12.257 | 11.3852 | 11.088 | 10.5827 | 10.1785 | 9.7457
| BALLINDALLOCH | LW |  |  | 15.3202 | 15.3145 | 15.309 | 15.2838 | 15.2564 | 15.2276 | 15.1981 | 15.1675 | 15.1337 | 15.0988 | 15.0005 | 14.8058 | 14.692 | 14.5796 | 13.468 | 13.4649 | 13.4619 | 13.4396 | 13.4156 | 13.3904 | 13.365 | 13.3385 | 13.3091 | 13.2787 | 13.1947 | 13.0256 | 12.939 | 12.8535 | 13.3311 | 13.3255 | 13.3201 | 13.295 | 13.2679 | 13.2392 | 13.2099 | 13.1795 | 13.1459 | 13.1112 | 13.0136 | 12.82 | 12.7076 | 12.5964
| BALLINDALLOCH | ST |  |  | 15.3223 | 15.3184 | 15.3145 | 15.2988 | 15.1566 | 15.0053 | 14.8593 | 14.6964 | 14.4446 | 14.3793 | 14.2212 | 13.6902 | 12.0174 | 11.7325 | 13.469 | 13.4669 | 13.4647 | 13.4514 | 13.3115 | 13.1624 | 13.0191 | 12.8589 | 12.6094 | 12.5465 | 12.3965 | 11.0833 | 10.2289 | 9.8705 | 13.3331 | 13.3293 | 13.3255 | 13.31 | 13.1679 | 13.0166 | 12.8707 | 12.708 | 12.4563 | 12.3911 | 12.2334 | 10.9134 | 10.0606 | 9.7036
| BALLINDALLOCH | SP |  |  | 15.3196 | 15.3143 | 15.3091 | 15.3007 | 15.2896 | 15.2715 | 15.2532 | 15.234 | 15.2104 | 15.1848 | 15.1067 | 15.0093 | 14.4149 | 14.1933 | 13.4675 | 13.4646 | 13.4617 | 13.4556 | 13.448 | 13.4333 | 13.4184 | 13.4025 | 13.3822 | 13.3599 | 13.2913 | 13.2125 | 12.6366 | 12.4324 | 13.3305 | 13.3254 | 13.3202 | 13.3119 | 13.301 | 13.283 | 13.2649 | 13.2458 | 13.2224 | 13.197 | 13.1193 | 13.0228 | 12.4293 | 11.489
CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | 3.2855 | 2.4716 | 2.4096 | 2.3324 | 2.1539 | 1.9692 | 1.7657 | 0.9736 | 0.71733 | 0.63732 | 0.48356 | -0.32592 | -0.84377 | -1.0982 | 2.9417 | 2.4903 | 2.4614 | 2.4252 | 2.2825 | 2.0851 | 1.8827 | 1.1951 | 0.94872 | 0.8733 | 0.72174 | -0.047416 | -0.54096 | -0.78582 | 2.9659 | 2.9049 | 2.4501 | 2.3547 | 2.1446 | 1.9254 | 1.7029 | 0.86998 | 0.60533 | 0.5183 | 0.34669 | -0.49694 | -1.0418 | -1.3189
| BALLURE | CT |  |  | 3.2855 | 2.4716 | 2.4096 | 2.3324 | 2.1539 | 1.9692 | 1.7657 | 0.9736 | 0.71733 | 0.63732 | 0.48356 | -0.32592 | -0.84377 | -1.0982 | 2.9417 | 2.4903 | 2.4614 | 2.4252 | 2.2825 | 2.0851 | 1.8827 | 1.1951 | 0.94872 | 0.8733 | 0.72174 | -0.047416 | -0.54096 | -0.78582 | 2.9659 | 2.9049 | 2.4501 | 2.3547 | 2.1446 | 1.9254 | 1.7029 | 0.86998 | 0.60533 | 0.5183 | 0.34669 | -0.49694 | -1.0418 | -1.3189
| BALLURE | LW |  |  | 3.3528 | 3.3462 | 3.3392 | 3.3292 | 2.4083 | 2.2402 | 2.0661 | 1.334 | 1.0684 | 1.0151 | 0.86011 | 0.32286 | -0.055273 | -0.21024 | 2.9742 | 2.9713 | 2.9684 | 2.9651 | 2.3767 | 2.2124 | 2.0424 | 1.5237 | 1.2545 | 1.1973 | 1.0307 | 0.51003 | 0.14943 | -0.0019763 | 3.0256 | 3.0197 | 3.0135 | 3.0047 | 2.4652 | 2.2951 | 2.1181 | 1.3316 | 1.0599 | 0.99998 | 0.82511 | 0.24773 | -0.14834 | -0.31635
| BALLURE | ST |  |  | 3.3551 | 3.3505 | 3.3458 | 3.339 | 3.2589 | 2.4194 | 2.3401 | 1.9785 | 1.8385 | 1.806 | 1.721 | 1.3322 | 0.84689 | 0.66736 | 2.9753 | 2.9733 | 2.9713 | 2.9686 | 2.4655 | 2.3857 | 2.3092 | 2.096 | 1.9586 | 1.9286 | 1.8521 | 1.4408 | 0.95531 | 0.7693 | 3.0276 | 3.0236 | 3.0194 | 3.0133 | 2.9341 | 2.4768 | 2.3967 | 2.0121 | 1.8695 | 1.8326 | 1.7212 | 1.2749 | 0.76963 | 0.57338
| BALLURE | SP |  |  | 3.3531 | 3.3478 | 3.3426 | 3.3372 | 3.3182 | 3.2995 | 3.2801 | 3.2595 | 2.4779 | 2.4504 | 2.3565 | 2.2543 | 1.4661 | 1.1934 | 2.9739 | 2.9712 | 2.9686 | 2.9659 | 2.9512 | 2.9369 | 2.4969 | 2.482 | 2.4593 | 2.4351 | 2.3509 | 2.2677 | 1.4984 | 1.2436 | 3.0259 | 3.0212 | 3.0165 | 3.0118 | 2.9937 | 2.9759 | 2.9574 | 2.9379 | 2.9103 | 2.8806 | 2.4076 | 2.2955 | 1.498 | 1.2096
DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | 7.1055 | 7.1012 | 7.0956 | 7.0844 | 7.0367 | 6.9871 | 6.9339 | 6.8774 | 6.8181 | 6.8002 | 3.0998 | 1.4015 | -1.3343 | -2.8947 | 6.0954 | 6.0779 | 6.0524 | 5.994 | 5.8238 | 5.7205 | 5.684 | 5.6435 | 3.5782 | 3.1708 | 1.6439 | -0.36717 | -3.5756 | -5.2852 | 6.1515 | 6.1469 | 6.141 | 6.129 | 6.0792 | 6.0387 | 6.0022 | 5.9618 | 3.8542 | 3.4535 | 1.9516 | -0.027481 | -3.188 | -4.8946
| BALMEDIE | CT |  |  | 7.1055 | 7.1012 | 7.0956 | 7.0844 | 7.0367 | 6.9871 | 6.9339 | 6.8774 | 6.8181 | 6.8002 | 3.6686 | 2.0816 | -0.80137 | -2.8947 | 6.0954 | 6.0779 | 6.0524 | 5.994 | 5.8238 | 5.7205 | 5.684 | 5.6435 | 3.9438 | 3.5812 | 2.3462 | 0.47668 | -2.88 | -5.2852 | 6.1515 | 6.1469 | 6.141 | 6.129 | 6.0792 | 6.0387 | 6.0022 | 5.9618 | 5.9094 | 3.8563 | 2.641 | 0.79875 | -2.5061 | -4.8946
| BALMEDIE | LW |  |  | 7.1108 | 7.1106 | 7.1103 | 7.1095 | 7.0571 | 7.0033 | 6.9476 | 6.9042 | 6.8541 | 6.8451 | 3.0998 | 1.4015 | -1.3343 | -2.3684 | 6.1141 | 6.1126 | 6.1101 | 6.104 | 5.881 | 5.7402 | 5.7104 | 5.6772 | 3.5782 | 3.1708 | 1.6439 | -0.36717 | -3.5756 | -4.7881 | 6.157 | 6.1568 | 6.1564 | 6.1555 | 6.1002 | 6.0585 | 6.0287 | 5.9954 | 3.8542 | 3.4535 | 1.9516 | -0.027481 | -3.188 | -4.3969
| BALMEDIE | ST |  |  | 7.1083 | 7.1062 | 7.1036 | 7.0989 | 7.0668 | 7.0322 | 6.9993 | 6.9608 | 6.9082 | 6.9003 | 6.8768 | 2.6639 | 0.84815 | -1.1953 | 6.1009 | 6.0885 | 6.0723 | 6.0413 | 5.9102 | 5.7736 | 5.7363 | 5.714 | 5.6813 | 3.8685 | 2.7316 | 1.1216 | -0.99724 | -3.3892 | 6.1544 | 6.1521 | 6.1492 | 6.1441 | 6.1103 | 6.074 | 6.0546 | 6.0322 | 5.9995 | 5.9916 | 3.0222 | 1.4377 | -0.64907 | -3.0026
| BALMEDIE | SP |  |  | 7.1091 | 7.108 | 7.1068 | 7.1056 | 7.0996 | 7.093 | 7.0852 | 7.0772 | 7.0661 | 7.0519 | 6.9961 | 6.9675 | 6.7688 | 3.7889 | 6.1116 | 6.1091 | 6.1062 | 6.1031 | 6.0703 | 6.0326 | 5.9865 | 5.9409 | 5.88 | 5.8051 | 5.7563 | 3.8296 | 3.1059 | 2.5085 | 6.1553 | 6.1541 | 6.153 | 6.1517 | 6.1453 | 6.1381 | 6.1297 | 6.1211 | 6.1091 | 6.0939 | 6.0745 | 6.0587 | 3.3884 | 2.7993
CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | NO | 13.8509 | 13.7687 | 13.6894 | 13.5895 | 13.4926 | 13.399 | 13.3088 | 13.2218 | 13.135 | 13.0895 | 13.021 | 12.9099 | 11.4669 | 11.338 | 13.3385 | 13.2677 | 13.1989 | 13.1108 | 13.0249 | 12.9419 | 12.8617 | 12.7814 | 12.7015 | 12.6562 | 12.5784 | 12.4902 | 12.3954 | 12.2883 | 13.6519 | 13.5561 | 13.4631 | 13.3433 | 13.2265 | 13.1137 | 13.0049 | 12.8948 | 11.4933 | 11.4496 | 11.3823 | 11.273 | 11.0943 | 10.897
| BALNAGASK | CT |  |  | 13.8509 | 13.7687 | 13.6894 | 13.5895 | 13.4926 | 13.399 | 13.3088 | 13.2218 | 13.135 | 13.0895 | 13.021 | 12.9099 | 11.4669 | 11.338 | 13.3385 | 13.2677 | 13.1989 | 13.1108 | 13.0249 | 12.9419 | 12.8617 | 12.7814 | 12.7015 | 12.6562 | 12.5784 | 12.4902 | 12.3954 | 12.2883 | 13.6519 | 13.5561 | 13.4631 | 13.3433 | 13.2265 | 13.1137 | 13.0049 | 12.8948 | 11.4933 | 11.4496 | 11.3823 | 11.273 | 11.0943 | 10.897
| BALNAGASK | LW |  |  | 13.9257 | 13.9188 | 13.9122 | 13.9046 | 13.896 | 13.8866 | 13.8763 | 13.8654 | 13.8534 | 13.841 | 13.8019 | 13.7317 | 13.6525 | 13.5677 | 13.402 | 13.3951 | 13.3877 | 13.3769 | 13.3647 | 13.3519 | 13.3385 | 13.3246 | 13.31 | 13.2946 | 13.247 | 13.1643 | 13.0737 | 12.9787 | 13.7372 | 13.7275 | 13.7169 | 13.7005 | 13.6822 | 13.6631 | 13.6433 | 13.6228 | 13.6013 | 13.5787 | 13.509 | 13.3887 | 13.2745 | 13.1629
| BALNAGASK | ST |  |  | 13.9283 | 13.9237 | 13.9192 | 13.9131 | 13.907 | 13.9012 | 13.894 | 13.887 | 13.8804 | 13.874 | 13.8523 | 13.815 | 14.6221 | 14.585 | 13.4047 | 13.4003 | 13.3957 | 13.3891 | 13.3821 | 13.3748 | 13.3632 | 13.3517 | 13.3407 | 13.331 | 13.3001 | 13.2485 | 14.0411 | 13.9899 | 13.741 | 13.7348 | 13.7284 | 13.719 | 13.7089 | 13.6983 | 13.6804 | 13.663 | 13.6461 | 13.6314 | 13.585 | 13.5079 | 14.2762 | 14.2121
| BALNAGASK | SP |  |  | 13.9252 | 13.9191 | 13.9131 | 13.9069 | 13.898 | 13.8891 | 13.8803 | 13.8717 | 13.8632 | 13.8548 | 14.6723 | 14.6241 | 14.5746 | 14.5269 | 13.4026 | 13.3973 | 13.3921 | 13.3868 | 13.3786 | 13.3705 | 13.3615 | 13.3526 | 13.3434 | 13.3345 | 14.1508 | 14.102 | 14.0527 | 14.0052 | 13.7384 | 13.7313 | 13.7242 | 13.7171 | 13.7059 | 13.6946 | 13.6819 | 13.6693 | 13.6561 | 13.6436 | 14.449 | 14.3804 | 14.3114 | 14.2453
KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | YES | 23.7246 | 23.7199 | 23.7077 | 23.6766 | 23.6038 | 23.5199 | 23.4282 | 23.3277 | 23.21 | 23.1443 | 22.9602 | 22.4674 | 13.3465 | 10.0602 | 19.3019 | 19.2686 | 19.2152 | 19.0835 | 18.7759 | 18.4928 | 18.2568 | 18.0012 | 17.8772 | 17.8144 | 17.6357 | 10.2145 | 6.9905 | 3.515 | 21.4133 | 21.3989 | 21.3725 | 21.3071 | 21.155 | 20.9998 | 20.8377 | 20.6562 | 20.4412 | 20.2923 | 19.83 | 11.6657 | 8.495 | 4.9775
| BANCHORY | CT |  |  | 23.7246 | 23.7199 | 23.7077 | 23.6766 | 23.6038 | 23.5199 | 23.4282 | 23.3277 | 23.21 | 23.1443 | 22.9602 | 22.4674 | 13.4373 | 10.0602 | 19.3019 | 19.2686 | 19.2152 | 19.0835 | 18.7759 | 18.4928 | 18.2568 | 18.0012 | 17.8772 | 17.8144 | 17.6357 | 10.2145 | 7.3408 | 3.515 | 21.4133 | 21.3989 | 21.3725 | 21.3071 | 21.155 | 20.9998 | 20.8377 | 20.6562 | 20.4412 | 20.2923 | 19.83 | 11.6657 | 8.7741 | 4.9775
| BANCHORY | LW |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7132 | 23.6919 | 23.6683 | 23.6431 | 23.6154 | 23.6631 | 23.6358 | 23.5581 | 23.423 | 13.3465 | 11.8255 | 19.3332 | 19.3251 | 19.3123 | 19.2618 | 18.9139 | 18.6007 | 18.3551 | 18.265 | 18.3127 | 18.2854 | 18.2077 | 10.2746 | 6.9905 | 5.2118 | 21.4284 | 21.4257 | 21.4214 | 21.3922 | 21.2614 | 21.1295 | 20.9973 | 20.8637 | 20.8244 | 20.7112 | 20.3156 | 11.7631 | 8.495 | 6.7448
| BANCHORY | ST |  |  | 23.7299 | 23.7287 | 23.7275 | 23.7158 | 23.6932 | 23.6675 | 23.6391 | 23.6081 | 23.5727 | 23.5534 | 23.5093 | 23.4207 | 23.3041 | 12.2694 | 19.3148 | 19.2928 | 19.264 | 19.1988 | 18.9916 | 18.7742 | 18.5896 | 18.4137 | 18.2317 | 18.203 | 18.1589 | 11.964 | 9.1305 | 5.7481 | 21.4211 | 21.4129 | 21.4025 | 21.3728 | 21.2883 | 21.1983 | 21.1091 | 21.0077 | 20.8815 | 20.7651 | 20.4704 | 20.1224 | 10.6153 | 7.2709
| BANCHORY | SP |  |  | 23.7279 | 23.7259 | 23.7238 | 23.7186 | 23.7152 | 23.7118 | 23.7083 | 23.7047 | 23.702 | 23.6959 | 23.6824 | 23.6642 | 23.6563 | 23.5693 | 19.3328 | 19.3278 | 19.3222 | 19.3131 | 19.2591 | 19.1969 | 19.1168 | 19.0375 | 18.9356 | 18.8062 | 18.4253 | 18.3139 | 18.3059 | 18.2189 | 21.4258 | 21.4228 | 21.4195 | 21.413 | 21.3926 | 21.3695 | 21.3403 | 21.3113 | 21.2754 | 21.2279 | 21.0516 | 20.8512 | 20.7224 | 20.5219
TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | 11.5741 | 11.5734 | 11.503 | 11.4322 | 11.3572 | 11.2667 | 11.173 | 11.0761 | 10.9742 | 10.8746 | 10.6894 | 10.38 | 9.9041 | 9.7166 | 10.6429 | 10.6382 | 10.5614 | 10.4808 | 10.396 | 10.296 | 10.1931 | 10.1107 | 10.0109 | 9.968 | 9.859 | 9.4682 | 8.8718 | 7.4739 | 10.9266 | 10.926 | 10.8553 | 10.7843 | 10.7091 | 10.6184 | 10.5244 | 10.4272 | 10.3268 | 10.2354 | 10.0654 | 9.7808 | 9.2567 | 9.0691
| BARCALDINE | CT |  |  | 11.5741 | 11.5734 | 11.503 | 11.4322 | 11.3572 | 11.2667 | 11.173 | 11.0761 | 10.9753 | 10.8746 | 10.6894 | 10.38 | 10.1444 | 9.9294 | 10.6429 | 10.6382 | 10.5614 | 10.4808 | 10.396 | 10.296 | 10.1931 | 10.1107 | 10.0449 | 9.9802 | 9.8593 | 9.6543 | 9.4542 | 9.2165 | 10.9266 | 10.926 | 10.8553 | 10.7843 | 10.7091 | 10.6184 | 10.5244 | 10.4272 | 10.3275 | 10.2354 | 10.0654 | 9.7808 | 9.5115 | 9.2068
| BARCALDINE | LW |  |  | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 11.575 | 10.6471 | 10.6459 | 10.644 | 10.6391 | 10.6338 | 10.6285 | 10.6246 | 10.6211 | 10.6177 | 10.614 | 10.6031 | 10.5854 | 10.5677 | 10.5502 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276 | 10.9276
| BARCALDINE | ST |  |  | 11.5749 | 11.5748 | 11.5747 | 11.5746 | 11.4761 | 11.3708 | 11.2706 | 11.157 | 10.9742 | 10.9365 | 10.8428 | 10.4765 | 9.9041 | 9.7166 | 10.6463 | 10.6445 | 10.6423 | 10.6381 | 10.534 | 10.4223 | 10.3171 | 10.1986 | 10.0109 | 9.968 | 9.859 | 9.4682 | 8.8718 | 7.4739 | 10.9275 | 10.9273 | 10.9273 | 10.9272 | 10.8287 | 10.7234 | 10.6232 | 10.5096 | 10.3268 | 10.2891 | 10.1954 | 9.829 | 9.2567 | 9.0691
| BARCALDINE | SP |  |  | 11.5749 | 11.5749 | 11.5748 | 11.5748 | 11.5619 | 11.5495 | 11.5368 | 11.5226 | 11.4992 | 11.4741 | 11.3846 | 11.3058 | 10.4158 | 10.1344 | 10.6479 | 10.6476 | 10.6473 | 10.6469 | 10.6325 | 10.6182 | 10.6031 | 10.5865 | 10.5601 | 10.532 | 10.4348 | 10.3468 | 9.448 | 9.1584 | 10.9275 | 10.9274 | 10.9274 | 10.9273 | 10.9145 | 10.9021 | 10.8894 | 10.8752 | 10.8518 | 10.8267 | 10.7371 | 10.6584 | 9.7684 | 9.487
STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | YES | 4.2398 | 4.2354 | 4.2291 | 4.216 | 4.1959 | 4.1794 | 4.1662 | 4.1525 | 4.137 | 4.1282 | 4.0987 | 4.0304 | 2.2579 | 1.7962 | 3.7265 | 3.7157 | 3.6999 | 3.6638 | 3.6192 | 3.5783 | 3.5481 | 3.5194 | 3.4893 | 3.4644 | 2.4482 | 2.0845 | 1.6738 | 1.1622 | 3.7417 | 3.7385 | 3.7341 | 3.7304 | 3.7217 | 3.7116 | 3.6997 | 3.686 | 3.6706 | 3.6617 | 3.6322 | 2.2413 | 1.8384 | 1.3343
| BARVAS | CT |  |  | 4.2398 | 4.2354 | 4.2291 | 4.216 | 4.1959 | 4.1794 | 4.1662 | 4.1525 | 4.137 | 4.1282 | 4.0987 | 4.0304 | 2.2579 | 1.7962 | 3.7265 | 3.7157 | 3.6999 | 3.6638 | 3.6192 | 3.5783 | 3.5481 | 3.5194 | 3.4893 | 3.4644 | 2.4482 | 2.0845 | 1.6738 | 1.1622 | 3.7417 | 3.7385 | 3.7341 | 3.7304 | 3.7217 | 3.7116 | 3.6997 | 3.686 | 3.6706 | 3.6617 | 3.6322 | 2.2413 | 1.8384 | 1.3343
| BARVAS | LW |  |  | 4.2451 | 4.2448 | 4.2443 | 4.2431 | 4.2418 | 4.2405 | 4.2392 | 4.2379 | 4.2367 | 4.2354 | 4.2315 | 4.2251 | 4.2188 | 4.2125 | 3.7383 | 3.7374 | 3.7358 | 3.732 | 3.7278 | 3.7236 | 3.7196 | 3.7156 | 3.7117 | 3.7075 | 3.6951 | 3.6751 | 3.655 | 3.635 | 3.7457 | 3.7455 | 3.7453 | 3.7446 | 3.7438 | 3.743 | 3.7423 | 3.7416 | 3.7408 | 3.7401 | 3.7385 | 3.7385 | 3.7385 | 3.7385
| BARVAS | ST |  |  | 4.2447 | 4.2443 | 4.2438 | 4.243 | 4.2393 | 4.2348 | 4.2259 | 4.2164 | 4.2064 | 4.1982 | 4.1771 | 4.1642 | 4.115 | 4.0872 | 3.7382 | 3.7374 | 3.7365 | 3.7349 | 3.7301 | 3.7243 | 3.7057 | 3.6868 | 3.6675 | 3.6456 | 3.5819 | 3.522 | 3.4267 | 2.3273 | 3.7453 | 3.7449 | 3.7444 | 3.7439 | 3.7403 | 3.7362 | 3.7291 | 3.7215 | 3.7147 | 3.7129 | 3.7072 | 3.6977 | 3.6485 | 2.4791
| BARVAS | SP |  |  | 4.2444 | 4.2439 | 4.2434 | 4.2428 | 4.2425 | 4.2423 | 4.2405 | 4.2387 | 4.2365 | 4.2333 | 4.2235 | 4.2104 | 4.1884 | 4.155 | 3.7382 | 3.7376 | 3.737 | 3.7364 | 3.7358 | 3.7351 | 3.7297 | 3.7244 | 3.7176 | 3.7091 | 3.6839 | 3.6468 | 3.6007 | 3.5501 | 3.7449 | 3.7444 | 3.7439 | 3.7433 | 3.7431 | 3.7429 | 3.7418 | 3.7408 | 3.7394 | 3.7372 | 3.7321 | 3.7301 | 3.717 | 3.6885
STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | YES | 19.5686 | 19.5633 | 19.5572 | 19.5482 | 19.4996 | 19.4441 | 19.3813 | 19.3114 | 19.2261 | 19.1905 | 19.075 | 15.3574 | 14.1102 | 12.69 | 18.8238 | 18.7865 | 18.7326 | 18.614 | 18.4657 | 18.3463 | 18.2521 | 18.177 | 18.0916 | 18.0561 | 17.9406 | 14.2391 | 12.8528 | 11.2958 | 19.8132 | 19.7561 | 19.714 | 19.6408 | 19.5825 | 19.5271 | 19.4643 | 19.3944 | 19.309 | 19.2735 | 19.158 | 18.5592 | 14.1054 | 12.5723
| BATTERY POINT | CT |  |  | 19.5686 | 19.5633 | 19.5572 | 19.5482 | 19.4996 | 19.4441 | 19.3813 | 19.3114 | 19.2261 | 19.1905 | 19.075 | 15.3574 | 14.1102 | 12.69 | 18.8238 | 18.7865 | 18.7326 | 18.614 | 18.4657 | 18.3463 | 18.2521 | 18.177 | 18.0916 | 18.0561 | 17.9406 | 14.2391 | 12.8528 | 11.2958 | 19.8132 | 19.7561 | 19.714 | 19.6408 | 19.5825 | 19.5271 | 19.4643 | 19.3944 | 19.309 | 19.2735 | 19.158 | 18.5592 | 14.1054 | 12.5723
| BATTERY POINT | LW |  |  | 19.5763 | 19.5763 | 19.5763 | 19.5763 | 19.5464 | 19.516 | 19.4845 | 19.4507 | 19.4022 | 19.3938 | 19.3618 | 19.1586 | 19.1056 | 19.0869 | 18.861 | 18.8546 | 18.8443 | 18.8187 | 18.7604 | 18.7021 | 18.6433 | 18.5829 | 18.5083 | 18.4732 | 18.3737 | 18.1534 | 18.0801 | 18.0606 | 19.8687 | 19.8583 | 19.8417 | 19.8002 | 19.7249 | 19.6788 | 19.632 | 19.5833 | 19.5201 | 19.4959 | 19.4448 | 19.2471 | 19.1941 | 19.1754
| BATTERY POINT | ST |  |  | 19.5742 | 19.5728 | 19.5714 | 19.5696 | 19.5421 | 19.5108 | 19.4777 | 19.4399 | 19.3897 | 19.3763 | 19.3366 | 19.1078 | 18.8103 | 18.7888 | 18.8496 | 18.8348 | 18.8156 | 18.7797 | 18.7058 | 18.6188 | 18.53 | 18.4418 | 18.3422 | 18.2899 | 18.2022 | 18.0275 | 17.7299 | 14.6867 | 19.8515 | 19.8285 | 19.7983 | 19.7459 | 19.6923 | 19.6298 | 19.561 | 19.5228 | 19.4726 | 19.4593 | 19.4196 | 19.1935 | 18.896 | 18.8745
| BATTERY POINT | SP |  |  | 19.5719 | 19.5696 | 19.5672 | 19.5647 | 19.5623 | 19.5599 | 19.5574 | 19.5546 | 19.5503 | 19.5427 | 19.5164 | 19.4945 | 19.2923 | 19.1169 | 18.8596 | 18.855 | 18.8499 | 18.8444 | 18.8259 | 18.8043 | 18.7809 | 18.7574 | 18.7265 | 18.6886 | 18.5799 | 18.4469 | 18.184 | 17.9855 | 19.8691 | 19.8631 | 19.8563 | 19.8491 | 19.8205 | 19.787 | 19.7506 | 19.7268 | 19.7075 | 19.683 | 19.6074 | 19.5775 | 19.3753 | 19.1999
DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | NO | 3.1926 | 3.0993 | 2.9816 | 2.8406 | 2.4165 | 2.2606 | 2.1078 | 1.9505 | 1.8147 | 1.7218 | 1.5521 | 1.2654 | 1.0145 | -0.1481 | 3.0308 | 2.9613 | 2.8589 | 2.4964 | 2.3837 | 2.2602 | 2.1394 | 2.0123 | 1.9024 | 1.8273 | 1.6748 | 1.4031 | 1.1662 | 0.2348 | 3.0072 | 2.9226 | 2.8077 | 2.3399 | 2.1791 | 2.016 | 1.856 | 1.6893 | 1.5441 | 1.4416 | 1.2551 | 0.94424 | 0.67139 | -0.52599
| BETTYHILL | CT |  |  | 3.1926 | 3.0993 | 2.9816 | 2.8406 | 2.4165 | 2.2606 | 2.1078 | 1.9505 | 1.8147 | 1.7218 | 1.5521 | 1.2654 | 1.0145 | -0.1481 | 3.0308 | 2.9613 | 2.8589 | 2.4964 | 2.3837 | 2.2602 | 2.1394 | 2.0123 | 1.9024 | 1.8273 | 1.6748 | 1.4031 | 1.1662 | 0.2348 | 3.0072 | 2.9226 | 2.8077 | 2.3399 | 2.1791 | 2.016 | 1.856 | 1.6893 | 1.5441 | 1.4416 | 1.2551 | 0.94424 | 0.67139 | -0.52599
| BETTYHILL | LW |  |  | 3.2774 | 3.2696 | 3.2622 | 3.2535 | 3.2405 | 3.2264 | 3.2113 | 3.1951 | 3.179 | 3.1669 | 3.1291 | 3.0601 | 3.002 | 1.6854 | 3.0937 | 3.0877 | 3.0817 | 3.0742 | 3.0625 | 3.05 | 3.0367 | 3.0227 | 3.0082 | 2.9978 | 2.9656 | 2.9072 | 2.8574 | 1.7545 | 3.084 | 3.0769 | 3.07 | 3.0619 | 3.0495 | 3.0362 | 3.0219 | 3.0066 | 2.9912 | 2.9799 | 2.9445 | 2.88 | 2.4413 | 1.4387
| BETTYHILL | ST |  |  | 3.2804 | 3.2752 | 3.27 | 3.2631 | 3.2549 | 3.2466 | 3.237 | 3.2275 | 3.2172 | 3.2094 | 3.1835 | 3.1444 | 3.1055 | 2.2211 | 3.096 | 3.092 | 3.088 | 3.0825 | 3.0755 | 3.0684 | 3.0581 | 3.0479 | 3.0369 | 3.0285 | 3.002 | 2.9603 | 2.918 | 2.1346 | 3.0867 | 3.082 | 3.0773 | 3.071 | 3.0632 | 3.0554 | 3.0459 | 3.0364 | 3.0262 | 3.0185 | 2.9931 | 2.9544 | 2.4913 | 1.9606
| BETTYHILL | SP |  |  | 3.277 | 3.2701 | 3.2632 | 3.2563 | 3.2449 | 3.2336 | 3.2224 | 3.2113 | 3.1993 | 3.1874 | 3.1509 | 3.0886 | 2.9573 | 2.8882 | 3.0936 | 3.0885 | 3.0834 | 3.0782 | 3.0693 | 3.0605 | 3.0509 | 3.0414 | 3.0308 | 3.0204 | 2.9883 | 2.936 | 2.8122 | 2.4266 | 3.0837 | 3.0774 | 3.0712 | 3.065 | 3.0544 | 3.0441 | 3.0336 | 3.0232 | 3.0118 | 3.0006 | 2.966 | 2.9078 | 2.4336 | 2.3447
ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | 14.8204 | 14.8156 | 26.0857 | 26.0673 | 25.6109 | 25.296 | 22.9071 | 22.145 | 21.0053 | 20.3784 | 18.11 | 15.68 | 14.4873 | 11.6732 | 16.7836 | 16.7796 | 26.8503 | 26.8341 | 26.3114 | 25.8434 | 25.4913 | 21.7703 | 20.8394 | 20.338 | 18.5419 | 15.8145 | 14.5719 | 11.3271 | 14.0652 | 14.0628 | 24.1362 | 24.1261 | 23.7306 | 21.9151 | 21.1754 | 20.4131 | 19.2323 | 18.5378 | 15.9598 | 13.2589 | 11.9857 | 8.7341
| BILBOHALL | CT |  |  | 14.8204 | 14.8156 | 26.0857 | 26.0673 | 25.7145 | 25.4718 | 25.2327 | 24.9813 | 22.6409 | 22.1522 | 20.5573 | 17.3162 | 14.4873 | 11.6732 | 16.7836 | 16.7796 | 26.8503 | 26.8341 | 26.5098 | 26.1863 | 25.8502 | 25.5379 | 21.715 | 21.6367 | 20.5648 | 17.7365 | 14.5719 | 11.3271 | 14.0652 | 14.0628 | 24.1362 | 24.1261 | 23.8649 | 23.5949 | 23.3368 | 21.6608 | 20.9053 | 20.417 | 18.6772 | 15.1293 | 11.9857 | 8.7341
| BILBOHALL | LW |  |  | 14.8251 | 14.8242 | 26.1027 | 26.0988 | 25.6109 | 25.296 | 22.9071 | 22.145 | 21.0053 | 20.3784 | 18.11 | 15.68 | 14.6018 | 12.8533 | 16.7877 | 16.787 | 26.8657 | 26.8627 | 26.3114 | 25.8434 | 25.4913 | 21.7703 | 20.8394 | 20.338 | 18.5419 | 15.8145 | 14.6571 | 12.6435 | 14.0678 | 14.0675 | 24.1469 | 24.1455 | 23.7306 | 21.9151 | 21.1754 | 20.4131 | 19.2323 | 18.5378 | 15.9598 | 13.2589 | 12.1045 | 10.0903
| BILBOHALL | ST |  |  | 14.8253 | 14.8246 | 26.1038 | 26.1024 | 25.8432 | 25.6233 | 25.4782 | 25.3132 | 23.2265 | 22.7677 | 21.2285 | 18.7114 | 15.302 | 12.1012 | 16.7878 | 16.7872 | 26.8665 | 26.8654 | 26.6296 | 26.3893 | 26.1488 | 25.87 | 25.5506 | 25.4644 | 21.2012 | 19.1354 | 15.3218 | 11.6148 | 14.0677 | 14.0673 | 24.1469 | 24.1463 | 23.9614 | 23.7689 | 23.5924 | 23.4055 | 21.4941 | 21.0363 | 19.3793 | 16.5663 | 12.7692 | 9.061
| BILBOHALL | SP |  |  | 14.8256 | 14.8253 | 26.105 | 26.1047 | 26.0493 | 25.9903 | 25.909 | 25.8258 | 25.772 | 25.7235 | 25.5498 | 22.7507 | 20.0741 | 18.8387 | 16.788 | 16.7877 | 26.8674 | 26.8671 | 26.8179 | 26.7659 | 26.6959 | 26.6238 | 26.5193 | 26.3895 | 26.0832 | 25.8939 | 19.9761 | 18.8861 | 14.0677 | 14.0675 | 24.1472 | 24.1469 | 24.111 | 24.0743 | 24.0291 | 23.9813 | 23.909 | 23.8368 | 21.9363 | 21.0064 | 18.2713 | 16.9404
RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | 0.066285 | 0.066275 | 0.054956 | 0.039946 | 0.026908 | 0.010849 | -0.0057129 | -0.022784 | -0.040403 | -0.058461 | -0.091026 | -0.14413 | -0.19091 | -0.23707 | 0.060597 | 0.060303 | 0.047479 | 0.034715 | 0.021555 | 0.0057973 | -0.010431 | -0.027274 | -0.044628 | -0.062442 | -0.095244 | -0.14871 | -0.19619 | -0.24308 | 0.061682 | 0.061611 | 0.046335 | 0.034433 | 0.020952 | 0.004655 | -0.012283 | -0.029843 | -0.047939 | -0.066515 | -0.1006 | -0.15616 | -0.20542 | -0.25403
| BLACKMOUNT | CT |  |  | 0.066285 | 0.066275 | 0.054956 | 0.039946 | 0.026908 | 0.010849 | -0.0057129 | -0.022784 | -0.040403 | -0.058461 | -0.091026 | -0.14413 | -0.19091 | -0.23707 | 0.060598 | 0.060348 | 0.047479 | 0.034715 | 0.021555 | 0.0057973 | -0.010431 | -0.027274 | -0.044628 | -0.062442 | -0.095244 | -0.14871 | -0.19619 | -0.24308 | 0.061682 | 0.061611 | 0.046335 | 0.034433 | 0.020952 | 0.004655 | -0.012283 | -0.029843 | -0.047939 | -0.066515 | -0.1006 | -0.15616 | -0.20542 | -0.25403
| BLACKMOUNT | LW |  |  | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.04555 | 0.037022 | 0.02844 | 0.01993 | 0.060597 | 0.060303 | 0.05984 | 0.059507 | 0.059507 | 0.059507 | 0.049633 | 0.047637 | 0.045686 | 0.043575 | 0.037328 | 0.027252 | 0.017093 | 0.0070312 | 0.061698 | 0.061623 | 0.061504 | 0.061206 | 0.061181 | 0.061181 | 0.061181 | 0.048024 | 0.046072 | 0.043961 | 0.037712 | 0.027649 | 0.01752 | 0.0074893
| BLACKMOUNT | ST |  |  | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.049877 | 0.044922 | 0.039962 | 0.060717 | 0.060573 | 0.060381 | 0.060012 | 0.059685 | 0.059529 | 0.059507 | 0.059507 | 0.059507 | 0.059507 | 0.048429 | 0.042433 | 0.036588 | 0.030732 | 0.061728 | 0.061692 | 0.061643 | 0.061548 | 0.061421 | 0.061269 | 0.061181 | 0.061181 | 0.061181 | 0.061181 | 0.048817 | 0.042818 | 0.036972 | 0.031118
| BLACKMOUNT | SP |  |  | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.066306 | 0.060858 | 0.060838 | 0.060815 | 0.060789 | 0.060649 | 0.060482 | 0.060289 | 0.060097 | 0.059852 | 0.059691 | 0.059507 | 0.059507 | 0.059507 | 0.049195 | 0.061764 | 0.061759 | 0.061753 | 0.061747 | 0.061711 | 0.061668 | 0.061619 | 0.06157 | 0.061507 | 0.061427 | 0.061193 | 0.061181 | 0.061181 | 0.049583
BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | 8.2584 | 8.1508 | 8.0469 | 7.9145 | 7.7803 | 7.6489 | 7.5201 | 5.9296 | 5.8268 | 5.7722 | 5.6742 | 5.3956 | 5.0079 | 4.5057 | 7.6268 | 7.5442 | 7.4612 | 7.346 | 7.2262 | 7.1166 | 7.0295 | 6.9452 | 5.8687 | 5.7765 | 5.5624 | 5.1941 | 4.7937 | 4.28 | 7.1149 | 7.0076 | 6.9039 | 6.7718 | 5.8525 | 5.6302 | 5.4122 | 5.2363 | 5.081 | 4.9768 | 4.7421 | 4.3409 | 3.9113 | 3.3677
| BLACKSTAND | CT |  |  | 8.2584 | 8.1508 | 8.0469 | 7.9145 | 7.7803 | 7.6489 | 7.5201 | 5.9296 | 5.8268 | 5.7722 | 5.6742 | 5.3956 | 5.0079 | 4.5057 | 7.6268 | 7.5442 | 7.4612 | 7.346 | 7.2262 | 7.1166 | 7.0295 | 6.9452 | 5.8687 | 5.7765 | 5.5624 | 5.1941 | 4.7937 | 4.28 | 7.1149 | 7.0076 | 6.9039 | 6.7718 | 5.8525 | 5.6302 | 5.4122 | 5.2363 | 5.081 | 4.9768 | 4.7421 | 4.3409 | 3.9113 | 3.3677
| BLACKSTAND | LW |  |  | 8.3569 | 8.3481 | 8.3396 | 8.3298 | 8.3187 | 8.3065 | 8.2933 | 8.2792 | 8.2665 | 8.2532 | 8.2115 | 8.1368 | 8.0689 | 7.996 | 7.7035 | 7.6968 | 7.69 | 7.6814 | 7.6716 | 7.6611 | 7.65 | 7.6382 | 7.6274 | 7.6161 | 7.581 | 7.519 | 7.4618 | 7.4011 | 7.2132 | 7.2044 | 7.1959 | 7.1861 | 7.1751 | 7.1629 | 7.1498 | 7.1357 | 7.123 | 7.1098 | 7.0682 | 6.9936 | 6.9259 | 6.8531
| BLACKSTAND | ST |  |  | 8.3596 | 8.3533 | 8.347 | 8.3386 | 8.3266 | 8.3139 | 8.2988 | 8.283 | 8.2667 | 8.2559 | 8.2201 | 8.1677 | 8.0641 | 7.9946 | 7.7023 | 7.6948 | 7.6864 | 7.673 | 7.6533 | 7.6308 | 7.6096 | 7.5878 | 7.5656 | 7.5497 | 7.5002 | 7.4241 | 7.3146 | 7.2506 | 7.2159 | 7.2096 | 7.2033 | 7.1949 | 7.1829 | 7.1703 | 7.1551 | 7.1394 | 7.1231 | 7.1123 | 7.0766 | 7.0243 | 5.7904 | 5.5886
| BLACKSTAND | SP |  |  | 8.355 | 8.3464 | 8.3378 | 8.3292 | 8.3175 | 8.3059 | 8.2945 | 8.2832 | 8.2721 | 8.2602 | 8.2248 | 8.1597 | 8.0887 | 7.9977 | 7.7015 | 7.6948 | 7.688 | 7.6811 | 7.6699 | 7.6583 | 7.6473 | 7.6364 | 7.6248 | 7.613 | 7.5783 | 7.5179 | 7.4494 | 7.3609 | 7.2113 | 7.2027 | 7.1942 | 7.1856 | 7.1739 | 7.1623 | 7.1509 | 7.1397 | 7.1286 | 7.1167 | 7.0814 | 7.0164 | 6.9455 | 6.8547
COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | YES | 27.1521 | 27.1488 | 27.1383 | 27.1262 | 27.0806 | 27.028 | 26.9698 | 26.9053 | 26.8243 | 22.2046 | 21.2304 | 17.904 | 15.6955 | 12.0199 | 26.789 | 26.7699 | 26.7348 | 26.6654 | 26.3416 | 25.9171 | 25.7047 | 25.5675 | 25.4361 | 20.4421 | 19.3799 | 15.6798 | 13.0543 | 8.733 | 24.6447 | 24.6413 | 24.6292 | 24.6154 | 24.5681 | 24.5135 | 24.4531 | 20.8184 | 19.9866 | 19.2075 | 18.0904 | 14.2403 | 11.6514 | 7.285
| BLAIRGOWRIE | CT |  |  | 27.1521 | 27.1488 | 27.1383 | 27.1262 | 27.0806 | 27.028 | 26.9698 | 26.9053 | 26.8243 | 26.7895 | 21.2304 | 17.904 | 15.6955 | 12.0199 | 26.789 | 26.7699 | 26.7348 | 26.6654 | 26.3987 | 26.1532 | 25.9044 | 25.6577 | 25.4361 | 25.3565 | 19.3799 | 15.6798 | 13.0983 | 8.733 | 24.6447 | 24.6413 | 24.6292 | 24.6154 | 24.5681 | 24.5135 | 24.4531 | 24.3865 | 21.0914 | 20.4394 | 18.0904 | 14.2403 | 11.6514 | 7.285
| BLAIRGOWRIE | LW |  |  | 27.157 | 27.157 | 27.157 | 27.157 | 27.1243 | 27.0887 | 27.0496 | 27.0053 | 26.9371 | 22.2046 | 21.3106 | 19.4243 | 18.627 | 16.8173 | 26.8057 | 26.7999 | 26.7906 | 26.7674 | 26.3416 | 25.9171 | 25.7047 | 25.5675 | 25.4993 | 20.4421 | 19.4224 | 17.3894 | 16.4495 | 14.2284 | 24.6495 | 24.6495 | 24.6495 | 24.6495 | 24.6168 | 24.5812 | 24.5421 | 20.8184 | 19.9866 | 19.2075 | 18.1652 | 16.0101 | 15.0727 | 12.8588
| BLAIRGOWRIE | ST |  |  | 27.156 | 27.1554 | 27.1548 | 27.154 | 27.1334 | 27.1102 | 27.0861 | 27.0583 | 27.0169 | 27.0067 | 21.9916 | 19.2453 | 15.8801 | 13.8479 | 26.803 | 26.7959 | 26.7867 | 26.7694 | 26.5851 | 26.4029 | 26.2042 | 25.9647 | 25.746 | 25.5718 | 20.1898 | 17.0699 | 13.0543 | 10.6209 | 24.6485 | 24.6479 | 24.6473 | 24.6465 | 24.6259 | 24.6027 | 24.5786 | 24.5508 | 24.5094 | 21.0753 | 18.9482 | 15.7353 | 11.7312 | 9.3048
| BLAIRGOWRIE | SP |  |  | 27.1549 | 27.1537 | 27.1526 | 27.1514 | 27.1491 | 27.1468 | 27.1444 | 27.1418 | 27.1374 | 27.1313 | 27.1088 | 27.0882 | 26.8587 | 21.4037 | 26.8078 | 26.8056 | 26.8033 | 26.8007 | 26.754 | 26.7006 | 26.6192 | 26.5387 | 26.4313 | 26.2875 | 25.8285 | 25.6504 | 20.5992 | 19.552 | 24.6474 | 24.6463 | 24.6451 | 24.6439 | 24.6416 | 24.6393 | 24.637 | 24.6343 | 24.63 | 24.6238 | 24.6013 | 20.5996 | 19.3698 | 18.3014
STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | 2.9195 | 2.9195 | 2.9194 | 2.9193 | 2.9113 | 2.8931 | 2.8745 | 2.8537 | 2.8194 | 2.7827 | 2.6518 | 2.3941 | 1.0928 | 0.6849 | 2.7462 | 2.7461 | 2.746 | 2.7458 | 2.7379 | 2.7197 | 2.4845 | 2.4634 | 2.4288 | 2.3916 | 2.2594 | 2.1421 | 0.83863 | 0.42869 | 2.8492 | 2.8491 | 2.8491 | 2.849 | 2.8409 | 2.8228 | 2.8041 | 2.7834 | 2.48 | 2.4428 | 2.3104 | 2.1927 | 0.88892 | 0.47869
| BLAIRLINNANS | CT |  |  | 2.9195 | 2.9195 | 2.9194 | 2.9193 | 2.919 | 2.9187 | 2.9183 | 2.9178 | 2.9173 | 2.9169 | 2.9156 | 2.9131 | 2.8297 | 2.8236 | 2.7462 | 2.7461 | 2.746 | 2.7458 | 2.7454 | 2.745 | 2.7446 | 2.7439 | 2.7432 | 2.7426 | 2.7407 | 2.4998 | 2.4217 | 2.4073 | 2.8492 | 2.8491 | 2.8491 | 2.849 | 2.8488 | 2.8486 | 2.8483 | 2.848 | 2.8476 | 2.8474 | 2.8467 | 2.8452 | 2.456 | 2.4404
| BLAIRLINNANS | LW |  |  | 2.9196 | 2.9196 | 2.9195 | 2.9194 | 2.9193 | 2.9192 | 2.9191 | 2.919 | 2.9189 | 2.9187 | 2.9184 | 2.9178 | 2.8374 | 2.8369 | 2.7462 | 2.7462 | 2.7461 | 2.7459 | 2.7456 | 2.7454 | 2.7452 | 2.745 | 2.7448 | 2.7445 | 2.7438 | 2.7428 | 2.4393 | 2.4338 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.4752 | 2.469
| BLAIRLINNANS | ST |  |  | 2.9196 | 2.9196 | 2.9196 | 2.9195 | 2.9195 | 2.9194 | 2.9194 | 2.9193 | 2.9192 | 2.919 | 2.9187 | 2.9181 | 2.8776 | 2.877 | 2.7462 | 2.7462 | 2.7462 | 2.7461 | 2.746 | 2.7459 | 2.7457 | 2.7456 | 2.7454 | 2.7451 | 2.7444 | 2.7432 | 2.4751 | 2.4692 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8097 | 2.8097
| BLAIRLINNANS | SP |  |  | 2.9196 | 2.9196 | 2.9196 | 2.9196 | 2.9113 | 2.8931 | 2.8745 | 2.8537 | 2.8194 | 2.7827 | 2.6518 | 2.3941 | 1.0928 | 0.6849 | 2.7463 | 2.7463 | 2.7462 | 2.7462 | 2.7379 | 2.7197 | 2.4845 | 2.4634 | 2.4288 | 2.3916 | 2.2594 | 2.1421 | 0.83863 | 0.42869 | 2.8492 | 2.8492 | 2.8492 | 2.8492 | 2.8409 | 2.8228 | 2.8041 | 2.7834 | 2.48 | 2.4428 | 2.3104 | 2.1927 | 0.88892 | 0.47869
BOAT OF GARTEN | BOAT OF GARTEN 11 kV | MINIMUM HEADROOM | NH 95609 19427 | YES | 9.9271 | 9.9251 | 9.9226 | 9.9183 | 9.9085 | 9.8973 | 9.8846 | 9.8689 | 9.8518 | 9.8402 | 9.8031 | 9.7246 | 9.6069 | 7.9627 | 9.2426 | 9.2398 | 9.2359 | 9.2282 | 9.2149 | 9.2001 | 9.184 | 9.1626 | 9.14 | 9.1223 | 9.0673 | 8.9599 | 7.7062 | 7.2932 | 9.5465 | 9.5426 | 9.5372 | 9.5258 | 9.5085 | 9.4899 | 9.4699 | 9.4521 | 9.435 | 9.4234 | 9.3864 | 9.308 | 7.731 | 7.3212
| BOAT OF GARTEN 11 kV | CT |  |  | 9.9271 | 9.9251 | 9.9226 | 9.9183 | 9.9085 | 9.8973 | 9.8846 | 9.8689 | 9.8518 | 9.8402 | 9.8031 | 9.7246 | 9.6069 | 7.9627 | 9.2426 | 9.2398 | 9.2359 | 9.2282 | 9.2149 | 9.2001 | 9.184 | 9.1626 | 9.14 | 9.1223 | 9.0673 | 8.9599 | 7.7062 | 7.2932 | 9.5465 | 9.5426 | 9.5372 | 9.5258 | 9.5085 | 9.4899 | 9.4699 | 9.4521 | 9.435 | 9.4234 | 9.3864 | 9.308 | 7.731 | 7.3212
| BOAT OF GARTEN 11 kV | LW |  |  | 9.9295 | 9.9293 | 9.929 | 9.9281 | 9.9272 | 9.9262 | 9.9253 | 9.9244 | 9.9236 | 9.9226 | 9.9199 | 9.9154 | 9.9109 | 9.9065 | 9.2458 | 9.2452 | 9.2443 | 9.2421 | 9.2396 | 9.2372 | 9.2349 | 9.2325 | 9.2303 | 9.2278 | 9.2206 | 9.209 | 9.1972 | 9.1856 | 9.5504 | 9.5495 | 9.548 | 9.5442 | 9.54 | 9.536 | 9.532 | 9.5281 | 9.5243 | 9.5202 | 9.508 | 9.4986 | 9.4941 | 9.4897
| BOAT OF GARTEN 11 kV | ST |  |  | 9.9287 | 9.9279 | 9.9269 | 9.9253 | 9.9204 | 9.9145 | 9.9076 | 9.9 | 9.8918 | 9.8875 | 9.8744 | 9.8533 | 9.7914 | 9.7514 | 9.2444 | 9.2428 | 9.2409 | 9.2374 | 9.2298 | 9.2208 | 9.21 | 9.1986 | 9.1867 | 9.1784 | 9.1538 | 9.114 | 9.0338 | 7.9773 | 9.5484 | 9.546 | 9.543 | 9.5373 | 9.5269 | 9.5143 | 9.4992 | 9.4836 | 9.475 | 9.4706 | 9.4577 | 9.4366 | 9.3748 | 9.3349
| BOAT OF GARTEN 11 kV | SP |  |  | 9.9286 | 9.928 | 9.9273 | 9.9266 | 9.9261 | 9.9254 | 9.9245 | 9.9236 | 9.9225 | 9.9207 | 9.9151 | 9.9085 | 9.8901 | 9.8551 | 9.245 | 9.2443 | 9.2435 | 9.2427 | 9.2414 | 9.2399 | 9.2377 | 9.2356 | 9.2328 | 9.2295 | 9.2193 | 9.2057 | 9.1807 | 9.1395 | 9.5499 | 9.549 | 9.5481 | 9.5472 | 9.545 | 9.5425 | 9.5389 | 9.5354 | 9.5309 | 9.5258 | 9.5106 | 9.4916 | 9.4733 | 9.4383
PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | NO | 13.8111 | 13.8055 | 13.7974 | 13.7786 | 13.6414 | 13.4844 | 13.4129 | 13.3607 | 13.3264 | 13.3169 | 13.2878 | 13.2423 | 13.1829 | 7.4867 | 13.744 | 13.7364 | 13.725 | 13.6985 | 13.5014 | 13.2776 | 13.0554 | 12.8346 | 12.5556 | 12.4768 | 12.4476 | 12.4021 | 6.1157 | 5.2866 | 13.4553 | 13.4495 | 13.4409 | 13.4211 | 13.2761 | 13.1105 | 12.9457 | 12.7817 | 12.6804 | 12.6174 | 12.3817 | 12.2565 | 6.8595 | 6.0485
| BODDAM | CT |  |  | 13.8111 | 13.8055 | 13.7974 | 13.7786 | 13.6925 | 13.6168 | 13.5412 | 13.4513 | 13.3965 | 13.3394 | 13.2878 | 13.2423 | 13.1829 | 13.0957 | 13.744 | 13.7364 | 13.725 | 13.6985 | 13.5769 | 13.4705 | 13.3645 | 13.2387 | 13.063 | 12.8421 | 12.4476 | 12.4021 | 7.2739 | 5.8799 | 13.4553 | 13.4495 | 13.4409 | 13.4211 | 13.3304 | 13.2508 | 13.1712 | 13.0767 | 12.9449 | 12.7808 | 12.5498 | 12.2728 | 12.1488 | 6.6251
| BODDAM | LW |  |  | 13.8151 | 13.8127 | 13.8089 | 13.7993 | 13.6414 | 13.4844 | 13.4129 | 13.3607 | 13.3264 | 13.3169 | 13.3111 | 13.2905 | 13.2675 | 7.4867 | 13.7495 | 13.746 | 13.7405 | 13.7268 | 13.5014 | 13.2776 | 13.0554 | 12.8346 | 12.5556 | 12.4768 | 12.4709 | 12.4504 | 6.1157 | 5.2866 | 13.4595 | 13.457 | 13.4529 | 13.4428 | 13.2761 | 13.1105 | 12.9457 | 12.7817 | 12.6804 | 12.6174 | 12.3817 | 12.2565 | 6.8595 | 6.0485
| BODDAM | ST |  |  | 13.814 | 13.811 | 13.8071 | 13.7996 | 13.7321 | 13.6659 | 13.6006 | 13.52 | 13.438 | 13.385 | 13.3187 | 13.3041 | 13.2641 | 13.2453 | 13.7479 | 13.7437 | 13.7381 | 13.7274 | 13.6314 | 13.5374 | 13.4447 | 13.3304 | 13.1707 | 12.9623 | 12.4786 | 12.464 | 12.4239 | 6.7849 | 13.4583 | 13.4552 | 13.4511 | 13.4431 | 13.3719 | 13.3022 | 13.2333 | 13.1483 | 13.0295 | 12.8754 | 12.6097 | 12.3751 | 12.23 | 12.2113
| BODDAM | SP |  |  | 13.8167 | 13.8162 | 13.8156 | 13.8149 | 13.7972 | 13.7769 | 13.7473 | 13.7182 | 13.6796 | 13.6276 | 13.444 | 13.3587 | 13.3058 | 13.2914 | 13.7518 | 13.7512 | 13.7503 | 13.7494 | 13.7242 | 13.6952 | 13.6529 | 13.6113 | 13.5561 | 13.4819 | 13.1736 | 12.7818 | 12.4656 | 12.4512 | 13.4612 | 13.4607 | 13.46 | 13.4593 | 13.4407 | 13.4192 | 13.388 | 13.3573 | 13.3165 | 13.2616 | 13.0335 | 12.7437 | 12.6407 | 12.5552
TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | 7.5721 | 7.4675 | 7.2391 | 6.9718 | 6.7005 | 6.4068 | 6.1122 | 5.8176 | 4.816 | 4.5235 | 4.0096 | 3.1694 | 2.3978 | 1.5938 | 7.2505 | 7.1655 | 7.0088 | 6.8239 | 6.6351 | 6.4353 | 6.2359 | 6.0378 | 4.8572 | 4.5717 | 4.0468 | 3.1882 | 2.3923 | 1.565 | 6.2646 | 6.1746 | 5.9267 | 5.6686 | 4.9987 | 4.7089 | 4.3744 | 4.0377 | 3.6966 | 3.3924 | 2.8364 | 1.928 | 1.0865 | 0.21352
| BONSKEID | CT |  |  | 7.5721 | 7.4675 | 7.2391 | 6.9718 | 6.7005 | 6.4068 | 6.1122 | 5.8176 | 4.816 | 4.5235 | 4.0096 | 3.1694 | 2.3978 | 1.5938 | 7.2505 | 7.1655 | 7.0088 | 6.8239 | 6.6351 | 6.4353 | 6.2359 | 6.0378 | 4.8572 | 4.5717 | 4.0468 | 3.1882 | 2.3923 | 1.565 | 6.2646 | 6.1746 | 5.9267 | 5.6686 | 4.9987 | 4.7089 | 4.3744 | 4.0377 | 3.6966 | 3.3924 | 2.8364 | 1.928 | 1.0865 | 0.21352
| BONSKEID | LW |  |  | 7.7485 | 7.653 | 7.5841 | 7.5043 | 7.4218 | 7.3385 | 7.2546 | 7.17 | 7.0852 | 6.9983 | 6.7905 | 6.4475 | 6.1105 | 5.7665 | 7.3975 | 7.3156 | 7.2571 | 7.2026 | 7.1451 | 7.0873 | 7.0292 | 6.9708 | 6.9124 | 6.8519 | 6.6984 | 6.4405 | 6.1739 | 4.8944 | 6.4557 | 6.3392 | 6.2605 | 6.1807 | 6.1002 | 6.0184 | 5.9358 | 5.8521 | 5.782 | 5.7143 | 5.5651 | 4.7121 | 4.3162 | 3.9123
| BONSKEID | ST |  |  | 7.6665 | 7.6565 | 7.6085 | 7.5529 | 7.4777 | 7.3981 | 7.3208 | 7.2416 | 7.1527 | 7.0828 | 6.8744 | 6.5166 | 6.1356 | 5.8069 | 7.3268 | 7.3181 | 7.2767 | 7.2318 | 7.1727 | 7.1086 | 7.0477 | 6.985 | 6.9124 | 6.8582 | 6.6979 | 6.4012 | 6.0739 | 4.8599 | 6.3494 | 6.3444 | 6.2916 | 6.2373 | 6.1675 | 6.0965 | 6.0248 | 5.9509 | 5.8669 | 5.8061 | 5.6428 | 4.7922 | 4.3518 | 3.9523
| BONSKEID | SP |  |  | 7.7508 | 7.6594 | 7.6514 | 7.6433 | 7.6283 | 7.6125 | 7.5969 | 7.5814 | 7.5647 | 7.5468 | 7.4948 | 7.4026 | 7.3085 | 7.2172 | 7.3997 | 7.3216 | 7.3151 | 7.3085 | 7.2957 | 7.2823 | 7.269 | 7.2559 | 7.2415 | 7.2261 | 7.181 | 7.102 | 7.021 | 6.9393 | 6.455 | 6.3391 | 6.3324 | 6.3256 | 6.3158 | 6.3061 | 6.2966 | 6.2872 | 6.2779 | 6.2686 | 6.2411 | 6.1881 | 6.1311 | 6.0717
PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | 7.1482 | 7.1474 | 7.1463 | 7.1449 | 7.1402 | 7.1345 | 7.1279 | 7.1203 | 7.1117 | 7.1068 | 7.0905 | 7.0527 | 6.9905 | 6.4746 | 6.2051 | 6.2042 | 6.2032 | 6.2017 | 6.197 | 6.1914 | 6.1848 | 6.1771 | 6.1686 | 6.1637 | 6.1474 | 6.1096 | 6.0473 | 5.5314 | 5.683 | 5.6821 | 5.6811 | 5.6796 | 5.6749 | 5.6693 | 5.6627 | 5.655 | 5.6465 | 5.6416 | 5.6253 | 5.5875 | 5.5252 | 3.9844
| BOWMORE | CT |  |  | 7.1482 | 7.1474 | 7.1463 | 7.1449 | 7.1402 | 7.1345 | 7.1279 | 7.1203 | 7.1117 | 7.1068 | 7.0905 | 7.0527 | 6.9905 | 6.8697 | 6.2051 | 6.2042 | 6.2032 | 6.2017 | 6.197 | 6.1914 | 6.1848 | 6.1771 | 6.1686 | 6.1637 | 6.1474 | 6.1096 | 6.0473 | 5.9265 | 5.683 | 5.6821 | 5.6811 | 5.6796 | 5.6749 | 5.6693 | 5.6627 | 5.655 | 5.6465 | 5.6416 | 5.6253 | 5.5875 | 5.5252 | 3.9844
| BOWMORE | LW |  |  | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 6.4746 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 6.2063 | 5.5314 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.6842 | 5.0093
| BOWMORE | ST |  |  | 7.1492 | 7.149 | 7.1489 | 7.1486 | 7.147 | 7.1449 | 7.1426 | 7.1399 | 7.1369 | 7.1359 | 7.1329 | 7.1279 | 7.1018 | 7.0871 | 6.2061 | 6.2059 | 6.2057 | 6.2055 | 6.2038 | 6.2018 | 6.1994 | 6.1967 | 6.1937 | 6.1927 | 6.1897 | 6.1847 | 6.1587 | 6.1439 | 5.6839 | 5.6838 | 5.6836 | 5.6834 | 5.6817 | 5.6797 | 5.6773 | 5.6746 | 5.6716 | 5.6706 | 5.6676 | 5.6626 | 5.6365 | 5.6218
| BOWMORE | SP |  |  | 7.149 | 7.1488 | 7.1486 | 7.1483 | 7.1483 | 7.1483 | 7.1482 | 7.1482 | 7.1481 | 7.1477 | 7.1466 | 7.1456 | 7.1397 | 7.1268 | 6.2059 | 6.2057 | 6.2054 | 6.2052 | 6.2051 | 6.2051 | 6.205 | 6.205 | 6.2049 | 6.2046 | 6.2034 | 6.2025 | 6.1966 | 6.1837 | 5.6838 | 5.6835 | 5.6833 | 5.6831 | 5.683 | 5.683 | 5.6829 | 5.6829 | 5.6828 | 5.6825 | 5.6813 | 5.6804 | 5.6744 | 5.6616
WOODHILL | BRAE | MINIMUM HEADROOM | HU 3604068816 | NO | 8.8879 | 8.8072 | 8.7293 | 8.6319 | 8.5352 | 8.4414 | 8.3501 | 8.2595 | 8.1698 | 8.1213 | 8.04 | 7.7452 | 5.7738 | 5.4406 | 7.6036 | 7.5613 | 7.5204 | 7.469 | 7.4168 | 7.3657 | 7.3156 | 7.2612 | 7.207 | 7.1751 | 7.1122 | 5.6506 | 5.3708 | 5.0445 | 7.9162 | 7.843 | 7.7725 | 7.6843 | 7.5966 | 7.5113 | 7.4282 | 7.346 | 7.2645 | 7.2206 | 5.9246 | 5.5196 | 5.2212 | 4.8749
| BRAE | CT |  |  | 8.8879 | 8.8072 | 8.7293 | 8.6319 | 8.5352 | 8.4414 | 8.3501 | 8.2595 | 8.1698 | 8.1213 | 8.04 | 7.7452 | 5.7738 | 5.4406 | 7.6036 | 7.5613 | 7.5204 | 7.469 | 7.4168 | 7.3657 | 7.3156 | 7.2612 | 7.207 | 7.1751 | 7.1122 | 5.6506 | 5.3708 | 5.0445 | 7.9162 | 7.843 | 7.7725 | 7.6843 | 7.5966 | 7.5113 | 7.4282 | 7.346 | 7.2645 | 7.2206 | 5.9246 | 5.5196 | 5.2212 | 4.8749
| BRAE | LW |  |  | 8.9615 | 8.9548 | 8.9482 | 8.9405 | 8.9318 | 8.9223 | 8.912 | 8.9011 | 8.8893 | 8.877 | 8.8385 | 8.6126 | 8.5359 | 8.4556 | 7.642 | 7.6384 | 7.6347 | 7.6301 | 7.6248 | 7.6192 | 7.6131 | 7.6067 | 7.5999 | 7.5928 | 7.5707 | 7.4503 | 7.407 | 7.3619 | 7.9828 | 7.9767 | 7.9708 | 7.9639 | 7.9561 | 7.9475 | 7.9382 | 7.9284 | 7.9177 | 7.9067 | 7.8719 | 7.6678 | 7.5986 | 7.5261
| BRAE | ST |  |  | 8.9639 | 8.9593 | 8.9547 | 8.9485 | 8.9412 | 8.9338 | 8.9241 | 8.9143 | 8.9047 | 8.8964 | 8.8692 | 8.7446 | 8.6853 | 8.633 | 7.6433 | 7.6407 | 7.6382 | 7.6347 | 7.63 | 7.625 | 7.6167 | 7.6082 | 7.5998 | 7.5918 | 7.5668 | 7.4849 | 7.4286 | 7.381 | 7.9849 | 7.9808 | 7.9766 | 7.971 | 7.9643 | 7.9575 | 7.9487 | 7.9397 | 7.9309 | 7.9235 | 7.8991 | 7.7869 | 7.7321 | 7.6845
| BRAE | SP |  |  | 8.9608 | 8.9547 | 8.9486 | 8.9425 | 8.9281 | 8.9141 | 8.8997 | 8.8849 | 8.8661 | 8.8463 | 8.7815 | 8.6976 | 8.2609 | 8.0832 | 7.6417 | 7.6384 | 7.6351 | 7.6319 | 7.6217 | 7.6117 | 7.6009 | 7.5894 | 7.5739 | 7.557 | 7.5008 | 7.4348 | 7.0167 | 6.8564 | 7.9821 | 7.9766 | 7.9711 | 7.9655 | 7.952 | 7.9388 | 7.9253 | 7.9113 | 7.8934 | 7.8746 | 7.8124 | 7.7335 | 7.3019 | 5.9577
BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | YES | 18.631 | 18.6264 | 18.6205 | 18.597 | 18.5346 | 18.4491 | 18.3607 | 18.2783 | 18.2316 | 18.142 | 11.2335 | 9.7033 | 6.5288 | 2.9092 | 14.8575 | 14.8288 | 14.7868 | 14.6773 | 14.2894 | 14.2574 | 14.2213 | 11.0197 | 10.9461 | 10.888 | 8.1592 | 6.6717 | 2.9869 | -0.80029 | 14.9509 | 14.9484 | 14.9457 | 14.9298 | 14.903 | 14.871 | 11.4155 | 10.5995 | 10.5235 | 10.4628 | 7.6313 | 5.9957 | 2.2456 | -1.7294
| BRECHIN | CT |  |  | 18.631 | 18.6264 | 18.6205 | 18.597 | 18.5346 | 18.4717 | 18.4052 | 18.3285 | 18.2316 | 18.142 | 11.2335 | 9.7033 | 7.4422 | 2.9092 | 14.8575 | 14.8288 | 14.7868 | 14.6773 | 14.2894 | 14.2574 | 14.2213 | 14.1805 | 14.134 | 10.9107 | 8.1592 | 6.6717 | 4.3976 | -0.80029 | 14.9509 | 14.9484 | 14.9457 | 14.9298 | 14.903 | 14.871 | 14.8349 | 14.7941 | 11.3255 | 10.4925 | 7.6313 | 5.9957 | 3.5255 | -1.7294
| BRECHIN | LW |  |  | 18.6363 | 18.6356 | 18.6345 | 18.6184 | 18.5351 | 18.4491 | 18.3607 | 18.2783 | 18.2373 | 18.2146 | 18.1453 | 10.8328 | 9.0442 | 6.421 | 14.8819 | 14.8732 | 14.8594 | 14.8117 | 14.3106 | 14.2901 | 14.2666 | 11.0197 | 10.9461 | 10.888 | 10.7142 | 7.9526 | 6.2062 | 3.1768 | 14.9545 | 14.9545 | 14.9545 | 14.9412 | 14.9242 | 14.9037 | 11.4155 | 10.5995 | 10.5235 | 10.4628 | 10.2813 | 7.2896 | 5.3517 | 2.2876
| BRECHIN | ST |  |  | 18.6351 | 18.6336 | 18.6319 | 18.6217 | 18.5806 | 18.5386 | 18.4944 | 18.4419 | 18.3715 | 18.296 | 11.8896 | 11.0489 | 6.5288 | 4.0847 | 14.8769 | 14.8656 | 14.8508 | 14.8153 | 14.4661 | 14.3014 | 14.2841 | 14.265 | 14.2412 | 11.4431 | 8.8901 | 8.0486 | 2.9869 | 0.15382 | 14.9536 | 14.953 | 14.9524 | 14.9444 | 14.9308 | 14.915 | 14.8977 | 14.8786 | 14.8548 | 11.055 | 8.3686 | 7.4512 | 2.2456 | -0.60832
| BRECHIN | SP |  |  | 18.6351 | 18.6341 | 18.633 | 18.6297 | 18.6201 | 18.6094 | 18.5944 | 18.5795 | 18.5612 | 18.5351 | 18.4343 | 18.3333 | 18.236 | 11.3815 | 14.8865 | 14.8841 | 14.8814 | 14.8763 | 14.785 | 14.6806 | 14.5242 | 14.3741 | 14.3225 | 14.3187 | 14.3101 | 10.8117 | 9.5448 | 8.3133 | 14.9528 | 14.9518 | 14.9509 | 14.9477 | 14.9454 | 14.943 | 14.9406 | 14.938 | 14.9361 | 14.9322 | 14.9237 | 10.3721 | 9.0311 | 7.7859
PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | 36.4792 | 36.3489 | 36.2762 | 36.0403 | 51.3328 | 50.699 | 49.8585 | 49.086 | 48.2339 | 47.9351 | 47.04 | 37.9715 | 35.545 | 34.0077 | 32.1492 | 31.9781 | 31.899 | 31.7045 | 46.1862 | 45.5175 | 44.7072 | 43.9064 | 43.0577 | 36.6321 | 35.8175 | 33.7335 | 31.2802 | 29.7165 | 31.8444 | 31.6803 | 31.6024 | 31.4006 | 45.6608 | 45.0654 | 44.2045 | 43.5424 | 42.677 | 42.3638 | 36.2098 | 33.9852 | 31.5245 | 29.9536
| BRIDGE OF DON | CT |  |  | 36.6223 | 36.4713 | 36.3621 | 36.217 | 51.3328 | 50.8093 | 50.5847 | 50.1486 | 49.6386 | 49.351 | 48.6845 | 37.9715 | 35.545 | 34.0077 | 32.2704 | 32.0911 | 31.9793 | 31.8516 | 46.1862 | 45.6811 | 45.4747 | 45.0477 | 44.5467 | 44.2687 | 43.4288 | 33.7335 | 31.2802 | 29.7165 | 31.9693 | 31.7689 | 31.6313 | 31.4181 | 45.6608 | 45.0654 | 44.8606 | 44.4552 | 43.9754 | 43.7203 | 42.9484 | 33.9852 | 31.5245 | 29.9536
| BRIDGE OF DON | LW |  |  | 36.4792 | 36.3489 | 36.2762 | 36.5275 | 51.46 | 50.699 | 49.9077 | 49.086 | 48.2339 | 47.9351 | 47.04 | 38.3088 | 36.6713 | 35.6074 | 32.1492 | 31.9781 | 31.899 | 32.1489 | 46.2799 | 45.5175 | 44.7248 | 43.9064 | 43.0577 | 36.6321 | 35.8175 | 34.1487 | 32.5011 | 31.4272 | 31.8444 | 31.6803 | 31.6024 | 31.8405 | 45.9584 | 45.1831 | 44.3778 | 43.5424 | 42.677 | 42.3638 | 36.2098 | 34.4218 | 32.7715 | 31.6948
| BRIDGE OF DON | ST |  |  | 36.8282 | 36.7725 | 36.6472 | 36.5852 | 51.8562 | 50.7594 | 49.8585 | 49.2345 | 48.9952 | 48.6153 | 47.48 | 45.4738 | 37.9464 | 37.2659 | 32.4856 | 32.4158 | 32.267 | 32.2028 | 46.6842 | 45.5998 | 44.7072 | 44.0914 | 43.8601 | 43.4866 | 36.6346 | 34.9318 | 33.661 | 32.9637 | 32.1829 | 32.1156 | 31.9444 | 31.8526 | 46.2832 | 45.1378 | 44.2045 | 43.5487 | 43.2783 | 42.8735 | 41.7557 | 35.2532 | 33.9777 | 33.2758
| BRIDGE OF DON | SP |  |  | 37.0347 | 37.0137 | 36.9921 | 36.0403 | 51.4592 | 51.3536 | 51.2543 | 51.1553 | 51.0502 | 50.7771 | 49.9588 | 48.8628 | 47.8745 | 47.3523 | 32.7057 | 32.6827 | 32.6589 | 31.7045 | 46.3094 | 46.1873 | 46.0769 | 45.9768 | 45.8704 | 45.5964 | 44.7775 | 43.6929 | 36.6691 | 36.2204 | 32.4007 | 32.378 | 32.3546 | 31.4006 | 46.008 | 45.8888 | 45.779 | 45.6696 | 45.5512 | 45.2683 | 44.4215 | 43.2811 | 42.2514 | 36.6107
BRIDGE OF DUN | BRIDGE OF DUN 11kV | MINIMUM HEADROOM | NO 66018 58883 | YES | 2.9597 | 2.9593 | 2.9587 | 2.9574 | 2.4382 | 2.1924 | 1.948 | 1.7047 | 1.3936 | 1.089 | -0.05783 | -2.0559 | -4.48 | -5.3892 | 2.8043 | 2.8042 | 2.804 | 2.8038 | 2.2536 | 1.9635 | 1.6751 | 1.3882 | 1.022 | 0.66218 | -0.69233 | -2.8307 | -5.6849 | -6.7522 | 2.8191 | 2.8181 | 2.8168 | 2.8136 | 2.2953 | 2.0057 | 1.7179 | 1.4316 | 1.066 | 0.70685 | -0.6451 | -2.9177 | -5.7666 | -6.8319
| BRIDGE OF DUN 11kV | CT |  |  | 2.9597 | 2.9593 | 2.9587 | 2.9574 | 2.9452 | 2.4539 | 2.3547 | 2.2391 | 2.0662 | 1.8411 | 1.0522 | -0.5516 | -2.7736 | -4.196 | 2.8043 | 2.8042 | 2.804 | 2.8038 | 2.3904 | 2.2726 | 2.1557 | 2.0195 | 1.8158 | 1.5499 | 0.61801 | -1.053 | -3.6739 | -5.3459 | 2.8191 | 2.8181 | 2.8168 | 2.8136 | 2.4318 | 2.3143 | 2.1976 | 2.0617 | 1.8583 | 1.593 | 0.66278 | -1.1435 | -3.7595 | -5.4283
| BRIDGE OF DUN 11kV | LW |  |  | 2.9602 | 2.96 | 2.9599 | 2.9594 | 2.4382 | 2.1924 | 1.948 | 1.7047 | 1.3936 | 1.089 | -0.05783 | -2.0559 | -4.48 | -5.3892 | 2.8046 | 2.8046 | 2.8046 | 2.8046 | 2.2536 | 1.9635 | 1.6751 | 1.3882 | 1.022 | 0.66218 | -0.69233 | -2.8307 | -5.6849 | -6.7522 | 2.8199 | 2.8196 | 2.8191 | 2.8179 | 2.2953 | 2.0057 | 1.7179 | 1.4316 | 1.066 | 0.70685 | -0.6451 | -2.9177 | -5.7666 | -6.8319
| BRIDGE OF DUN 11kV | ST |  |  | 2.9601 | 2.96 | 2.9598 | 2.9595 | 2.9498 | 2.4956 | 2.4059 | 2.2905 | 2.1226 | 1.9007 | 1.1213 | -0.19601 | -1.5867 | -3.25 | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 2.4314 | 2.322 | 2.2156 | 2.0794 | 1.8813 | 1.619 | 0.69797 | -0.74707 | -2.3846 | -4.3483 | 2.8198 | 2.8194 | 2.819 | 2.8181 | 2.4728 | 2.3635 | 2.2573 | 2.1214 | 1.9237 | 1.6619 | 0.7426 | -0.76888 | -2.4034 | -4.3633
| BRIDGE OF DUN 11kV | SP |  |  | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 2.9577 | 2.9549 | 2.9507 | 2.9465 | 2.4943 | 2.4159 | 2.0816 | 1.6621 | 1.2774 | 0.93206 | 2.8046 | 2.8046 | 2.8046 | 2.8046 | 2.8045 | 2.4898 | 2.4382 | 2.3875 | 2.3198 | 2.2272 | 1.8321 | 1.3363 | 0.88625 | 0.47961 | 2.8202 | 2.8201 | 2.8201 | 2.82 | 2.8132 | 2.8053 | 2.4796 | 2.4289 | 2.3614 | 2.269 | 1.8746 | 1.3798 | 0.93048 | 0.5246
ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | YES | 16.7282 | 16.7263 | 16.7241 | 16.7209 | 16.6887 | 16.6523 | 16.6123 | 14.4448 | 13.9565 | 13.5094 | 11.7459 | 9.4108 | 8.1805 | 6.2605 | 15.4992 | 15.4814 | 15.4582 | 15.4159 | 15.243 | 15.1553 | 13.4887 | 13.0188 | 12.4134 | 11.8619 | 9.7964 | 7.0746 | 5.648 | 3.4978 | 15.2312 | 15.2293 | 15.227 | 15.2239 | 15.1916 | 13.6674 | 13.2071 | 12.7465 | 12.153 | 11.6135 | 9.5928 | 6.8672 | 5.435 | 3.2781
| BRIDGE OF EARN | CT |  |  | 16.7282 | 16.7263 | 16.7241 | 16.7209 | 16.6887 | 16.6523 | 16.6123 | 16.5681 | 16.5093 | 14.2243 | 12.9284 | 10.8879 | 8.8345 | 6.2605 | 15.4992 | 15.4814 | 15.4582 | 15.4159 | 15.2495 | 15.1553 | 15.1152 | 13.6167 | 13.2179 | 12.7602 | 11.189 | 8.8381 | 6.4699 | 3.4978 | 15.2312 | 15.2293 | 15.227 | 15.2239 | 15.1916 | 15.1553 | 13.6113 | 13.3311 | 12.9398 | 12.4918 | 10.9542 | 8.6389 | 6.2617 | 3.2781
| BRIDGE OF EARN | LW |  |  | 16.731 | 16.731 | 16.731 | 16.731 | 16.6964 | 16.6595 | 16.6198 | 14.4448 | 13.9565 | 13.5094 | 11.7459 | 9.4108 | 8.1805 | 6.783 | 15.5179 | 15.516 | 15.513 | 15.5057 | 15.243 | 15.1625 | 13.4887 | 13.0188 | 12.4134 | 11.8619 | 9.7964 | 7.0746 | 5.648 | 4.0133 | 15.2339 | 15.2339 | 15.2339 | 15.2339 | 15.1993 | 13.6674 | 13.2071 | 12.7465 | 12.153 | 11.6135 | 9.5928 | 6.8672 | 5.435 | 3.7935
| BRIDGE OF EARN | ST |  |  | 16.7303 | 16.7298 | 16.7294 | 16.7288 | 16.709 | 16.687 | 16.6647 | 16.639 | 16.6001 | 16.5909 | 13.3633 | 11.5652 | 9.1886 | 6.497 | 15.5111 | 15.504 | 15.4946 | 15.4769 | 15.3571 | 15.2397 | 15.1677 | 15.142 | 13.5953 | 13.165 | 11.6782 | 9.5842 | 6.8301 | 3.6833 | 15.2332 | 15.2328 | 15.2323 | 15.2318 | 15.212 | 15.19 | 15.1677 | 13.6676 | 13.3109 | 12.8899 | 11.4354 | 9.3852 | 6.622 | 3.4622
| BRIDGE OF EARN | SP |  |  | 16.7297 | 16.729 | 16.7283 | 16.7276 | 16.7234 | 16.7193 | 16.7151 | 16.7104 | 16.7027 | 16.6935 | 16.6602 | 14.3253 | 13.4118 | 12.7139 | 15.5171 | 15.5155 | 15.5138 | 15.5119 | 15.4703 | 15.4345 | 15.3869 | 15.3395 | 15.2751 | 15.1965 | 13.6724 | 12.8508 | 11.7899 | 10.9964 | 15.2326 | 15.232 | 15.2313 | 15.2306 | 15.2264 | 15.2223 | 15.2181 | 15.2134 | 15.2057 | 15.1965 | 13.3877 | 12.5835 | 11.5377 | 10.7584
RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | 0.63851 | 0.63845 | 0.60463 | 0.57205 | 0.54661 | 0.48722 | 0.44587 | 0.40233 | 0.35666 | 0.30951 | 0.22364 | 0.083212 | -0.041537 | -0.16661 | 0.59198 | 0.5915 | 0.56889 | 0.55329 | 0.48687 | 0.4458 | 0.40348 | 0.35922 | 0.31358 | 0.26688 | 0.18091 | 0.040317 | -0.085449 | -0.21165 | 0.59985 | 0.59968 | 0.56562 | 0.53133 | 0.47522 | 0.43787 | 0.39934 | 0.35785 | 0.31082 | 0.26267 | 0.17358 | 0.027403 | -0.10313 | -0.23392
| BRIDGE OF GAUR | CT |  |  | 0.63851 | 0.63845 | 0.60463 | 0.57205 | 0.54661 | 0.48722 | 0.44587 | 0.40233 | 0.35666 | 0.30951 | 0.22364 | 0.083212 | -0.041537 | -0.16661 | 0.59198 | 0.5915 | 0.56889 | 0.55329 | 0.48687 | 0.4458 | 0.40348 | 0.35922 | 0.31358 | 0.26688 | 0.18091 | 0.040317 | -0.085449 | -0.21165 | 0.59985 | 0.59968 | 0.56562 | 0.53133 | 0.47522 | 0.43787 | 0.39934 | 0.35785 | 0.31082 | 0.26267 | 0.17358 | 0.027403 | -0.10313 | -0.23392
| BRIDGE OF GAUR | LW |  |  | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.59204 | 0.59153 | 0.59072 | 0.58868 | 0.58642 | 0.58421 | 0.58264 | 0.58208 | 0.58153 | 0.58094 | 0.58081 | 0.58081 | 0.58081 | 0.48974 | 0.59993 | 0.5998 | 0.59959 | 0.59908 | 0.5985 | 0.59793 | 0.59738 | 0.59684 | 0.59631 | 0.59574 | 0.59504 | 0.59504 | 0.59504 | 0.49304
| BRIDGE OF GAUR | ST |  |  | 0.63859 | 0.63858 | 0.63858 | 0.63857 | 0.6385 | 0.63841 | 0.63832 | 0.63821 | 0.63809 | 0.63805 | 0.63792 | 0.63772 | 0.63665 | 0.63605 | 0.59224 | 0.59198 | 0.59164 | 0.59099 | 0.59005 | 0.58893 | 0.58778 | 0.58664 | 0.5855 | 0.58361 | 0.58111 | 0.57992 | 0.57885 | 0.57825 | 0.59998 | 0.5999 | 0.59982 | 0.59964 | 0.59935 | 0.599 | 0.59863 | 0.59826 | 0.59788 | 0.59737 | 0.59588 | 0.59416 | 0.59308 | 0.59248
| BRIDGE OF GAUR | SP |  |  | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.6386 | 0.59249 | 0.59246 | 0.59242 | 0.59238 | 0.59213 | 0.59184 | 0.59149 | 0.59114 | 0.59069 | 0.58994 | 0.58782 | 0.58454 | 0.58248 | 0.58172 | 0.60005 | 0.60004 | 0.60003 | 0.60002 | 0.59996 | 0.59988 | 0.59979 | 0.5997 | 0.59959 | 0.5994 | 0.59886 | 0.59802 | 0.59723 | 0.59649
BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | 4.9995 | 4.9992 | 4.9958 | 4.9924 | 4.9875 | 4.9817 | 4.9755 | 4.9687 | 4.9614 | 4.9554 | 4.9418 | 4.9153 | 4.8807 | 4.8236 | 5.6276 | 5.6273 | 5.6255 | 5.6237 | 5.6204 | 5.6166 | 5.6123 | 5.6076 | 5.6025 | 5.5987 | 5.5891 | 5.569 | 5.5399 | 4.9129 | 5.6235 | 5.6232 | 5.6181 | 5.6128 | 5.6061 | 5.5981 | 5.5896 | 5.5804 | 5.5707 | 5.5623 | 5.5442 | 5.5105 | 4.9968 | 4.8505
| BROADFORD | CT |  |  | 4.9995 | 4.9992 | 4.9958 | 4.9924 | 4.9875 | 4.9817 | 4.9755 | 4.9687 | 4.9614 | 4.9554 | 4.9418 | 4.9153 | 4.8807 | 4.8236 | 5.6276 | 5.6273 | 5.6255 | 5.6237 | 5.6204 | 5.6166 | 5.6123 | 5.6076 | 5.6025 | 5.5987 | 5.5891 | 5.569 | 5.5399 | 4.9129 | 5.6235 | 5.6232 | 5.6181 | 5.6128 | 5.6061 | 5.5981 | 5.5896 | 5.5804 | 5.5707 | 5.5623 | 5.5442 | 5.5105 | 4.9968 | 4.8505
| BROADFORD | LW |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624
| BROADFORD | ST |  |  | 5 | 4.9999 | 4.9999 | 4.9999 | 4.9995 | 4.9992 | 4.9987 | 4.9982 | 4.9977 | 4.9975 | 4.9969 | 4.996 | 4.9912 | 4.9885 | 5.6281 | 5.628 | 5.628 | 5.628 | 5.6276 | 5.6273 | 5.6268 | 5.6263 | 5.6258 | 5.6256 | 5.625 | 5.6241 | 5.6193 | 5.6166 | 5.624 | 5.6239 | 5.6239 | 5.6239 | 5.6235 | 5.6232 | 5.6227 | 5.6222 | 5.6217 | 5.6215 | 5.6209 | 5.62 | 5.6152 | 5.6125
| BROADFORD | SP |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.6281 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624 | 5.624
CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | YES | 10.2676 | 10.2624 | 10.2489 | 10.2277 | 10.1978 | 10.1648 | 10.1294 | 10.0586 | 10.026 | 10.0019 | 9.9408 | 9.815 | 9.6366 | 7.437 | 9.0035 | 8.9996 | 8.9861 | 8.9676 | 8.9407 | 8.9101 | 8.8771 | 8.8089 | 8.7387 | 8.6738 | 8.548 | 7.249 | 6.68 | 5.9805 | 9.5439 | 9.5419 | 9.5304 | 9.5179 | 9.4973 | 9.4727 | 9.4455 | 9.4157 | 9.3831 | 9.3589 | 9.2978 | 9.1719 | 6.8136 | 6.1149
| BRODICK | CT |  |  | 10.2676 | 10.2624 | 10.2489 | 10.2277 | 10.1978 | 10.1648 | 10.1294 | 10.0586 | 10.026 | 10.0019 | 9.9408 | 9.815 | 9.6366 | 7.437 | 9.0035 | 8.9996 | 8.9861 | 8.9676 | 8.9407 | 8.9101 | 8.8771 | 8.8089 | 8.7387 | 8.6738 | 8.548 | 7.249 | 6.68 | 5.9805 | 9.5439 | 9.5419 | 9.5304 | 9.5179 | 9.4973 | 9.4727 | 9.4455 | 9.4157 | 9.3831 | 9.3589 | 9.2978 | 9.1719 | 6.8136 | 6.1149
| BRODICK | LW |  |  | 10.2703 | 10.2664 | 10.2601 | 10.2446 | 10.2272 | 10.2102 | 10.1937 | 10.1898 | 10.1898 | 10.1898 | 10.1898 | 10.1898 | 10.1898 | 10.1898 | 9.0063 | 9.004 | 9.0004 | 8.9914 | 8.9813 | 8.9715 | 8.9619 | 8.9525 | 8.9433 | 8.9334 | 8.904 | 8.8566 | 8.8269 | 8.802 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469
| BRODICK | ST |  |  | 10.2713 | 10.2689 | 10.2659 | 10.2604 | 10.2494 | 10.2362 | 10.2059 | 10.1752 | 10.1573 | 10.1547 | 10.1469 | 10.134 | 10.0668 | 10.0287 | 9.0066 | 9.005 | 9.0031 | 8.9997 | 8.9914 | 8.9816 | 8.9615 | 8.9408 | 8.9196 | 8.8894 | 8.8027 | 8.722 | 8.6292 | 7.235 | 9.5463 | 9.5458 | 9.5454 | 9.5449 | 9.5405 | 9.5352 | 9.5291 | 9.5222 | 9.5144 | 9.5118 | 9.504 | 9.4911 | 9.4239 | 9.3858
| BRODICK | SP |  |  | 10.2725 | 10.2715 | 10.2705 | 10.2694 | 10.2674 | 10.265 | 10.2568 | 10.2486 | 10.2381 | 10.2185 | 10.1809 | 10.1781 | 10.1599 | 10.1203 | 9.007 | 9.0061 | 9.0052 | 9.0043 | 9.0031 | 9.0016 | 8.9968 | 8.992 | 8.9859 | 8.974 | 8.9392 | 8.8876 | 8.8237 | 8.7582 | 9.5456 | 9.5449 | 9.5442 | 9.5434 | 9.5433 | 9.5432 | 9.543 | 9.5429 | 9.5427 | 9.5416 | 9.538 | 9.5351 | 9.517 | 9.4774
BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | YES | 6.6235 | 6.6224 | 6.6051 | 6.5873 | 6.5647 | 5.5378 | 5.509 | 5.4784 | 5.4459 | 5.4175 | 5.357 | 3.8606 | 3.5584 | 3.187 | 6.6439 | 6.64 | 6.6052 | 6.5643 | 6.5174 | 5.4636 | 5.4075 | 5.3411 | 5.2725 | 5.2083 | 5.0549 | 4.8481 | 3.9026 | 3.6118 | 6.0202 | 6.0136 | 5.9787 | 5.932 | 5.8788 | 4.8197 | 4.7586 | 4.6793 | 4.5984 | 4.5417 | 4.4642 | 3.7823 | 3.4812 | 3.1003
| BRORA | CT |  |  | 6.6235 | 6.6224 | 6.6051 | 6.5873 | 6.5647 | 5.5378 | 5.509 | 5.4784 | 5.4459 | 5.4175 | 5.357 | 3.8606 | 3.5584 | 3.187 | 6.6439 | 6.64 | 6.6052 | 6.5643 | 6.5174 | 5.4636 | 5.4075 | 5.3411 | 5.2725 | 5.2083 | 5.0549 | 4.8481 | 3.9026 | 3.6118 | 6.0202 | 6.0136 | 5.9787 | 5.932 | 5.8788 | 4.8197 | 4.7586 | 4.6793 | 4.5984 | 4.5417 | 4.4642 | 3.7823 | 3.4812 | 3.1003
| BRORA | LW |  |  | 6.6251 | 6.6251 | 6.6251 | 6.6251 | 6.6251 | 5.6251 | 5.6251 | 5.6251 | 5.6251 | 5.6251 | 5.6251 | 5.6251 | 5.6251 | 5.6251 | 6.6477 | 6.6468 | 6.6455 | 6.6421 | 6.6383 | 5.6345 | 5.6309 | 5.6273 | 5.6239 | 5.6201 | 5.609 | 5.5911 | 5.573 | 5.5552 | 6.0262 | 6.0245 | 6.0217 | 6.0149 | 6.0073 | 4.9999 | 4.9926 | 4.9855 | 4.9785 | 4.971 | 4.9487 | 4.9129 | 4.8768 | 4.8575
| BRORA | ST |  |  | 6.6249 | 6.6247 | 6.6245 | 6.6244 | 6.623 | 5.6214 | 5.6194 | 5.6172 | 5.6148 | 5.6139 | 5.6115 | 5.6074 | 5.5862 | 5.5741 | 6.6478 | 6.6473 | 6.6466 | 6.6453 | 6.6425 | 5.6391 | 5.6277 | 5.6163 | 5.6047 | 5.5911 | 5.5515 | 5.4878 | 5.4074 | 5.3365 | 6.0267 | 6.0257 | 6.0244 | 6.0221 | 6.0178 | 5.0127 | 4.9919 | 4.9711 | 4.9505 | 4.9241 | 4.8473 | 4.8242 | 4.7843 | 4.7635
| BRORA | SP |  |  | 6.6248 | 6.6246 | 6.6244 | 6.6243 | 6.6243 | 5.6242 | 5.6242 | 5.6242 | 5.6241 | 5.6239 | 5.6231 | 5.6225 | 5.6185 | 5.6099 | 6.6482 | 6.648 | 6.6477 | 6.6475 | 6.6471 | 5.6465 | 5.6433 | 5.6402 | 5.6361 | 5.6309 | 5.6156 | 5.5925 | 5.5673 | 5.5387 | 6.0274 | 6.0272 | 6.0269 | 6.0266 | 6.0257 | 5.0247 | 5.0183 | 5.012 | 5.0039 | 4.9937 | 4.964 | 4.9183 | 4.872 | 4.8419
MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | 17.2364 | 17.2348 | 17.233 | 17.2304 | 17.2219 | 17.2117 | 17.1998 | 17.1861 | 17.1706 | 17.1618 | 17.1324 | 17.0643 | 16.9521 | 16.7345 | 15.0264 | 14.9973 | 14.9544 | 14.8535 | 14.7393 | 14.6884 | 14.6499 | 14.6226 | 14.5939 | 14.5707 | 14.4988 | 14.3617 | 14.1798 | 13.8936 | 15.0662 | 15.058 | 15.0463 | 15.0201 | 14.9861 | 14.951 | 14.9145 | 14.8883 | 14.8606 | 14.8385 | 14.7699 | 14.6382 | 14.4618 | 14.1809
| BROUGHTY FERRY | CT |  |  | 17.2364 | 17.2348 | 17.233 | 17.2304 | 17.2219 | 17.2117 | 17.1998 | 17.1861 | 17.1706 | 17.1618 | 17.1324 | 17.0643 | 16.9521 | 16.7345 | 15.0264 | 14.9973 | 14.9544 | 14.8535 | 14.7393 | 14.6884 | 14.6499 | 14.6226 | 14.5939 | 14.5707 | 14.4988 | 14.3617 | 14.1798 | 13.8936 | 15.0662 | 15.058 | 15.0463 | 15.0201 | 14.9861 | 14.951 | 14.9145 | 14.8883 | 14.8606 | 14.8385 | 14.7699 | 14.6382 | 14.4618 | 14.1809
| BROUGHTY FERRY | LW |  |  | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 17.2387 | 15.0532 | 15.0467 | 15.0364 | 15.0108 | 14.9823 | 14.9545 | 14.9272 | 14.9005 | 14.8744 | 14.8462 | 14.7627 | 14.7091 | 14.6738 | 14.6388 | 15.0743 | 15.0728 | 15.0703 | 15.0642 | 15.0573 | 15.0506 | 15.044 | 15.0376 | 15.0314 | 15.0246 | 15.0045 | 14.9722 | 14.9396 | 14.9074
| BROUGHTY FERRY | ST |  |  | 17.2382 | 17.2379 | 17.2376 | 17.2373 | 17.2344 | 17.2309 | 17.2269 | 17.2224 | 17.2172 | 17.2155 | 17.2104 | 17.2019 | 17.1576 | 17.1324 | 15.0388 | 15.0213 | 14.9981 | 14.9535 | 14.8906 | 14.8153 | 14.7621 | 14.7182 | 14.7008 | 14.6896 | 14.657 | 14.6042 | 14.5163 | 14.4478 | 15.0705 | 15.0661 | 15.0603 | 15.0493 | 15.032 | 15.0113 | 14.9955 | 14.9793 | 14.9628 | 14.9524 | 14.9219 | 14.8726 | 14.7881 | 14.7229
| BROUGHTY FERRY | SP |  |  | 17.2376 | 17.2371 | 17.2366 | 17.236 | 17.2359 | 17.2358 | 17.2357 | 17.2356 | 17.2355 | 17.2346 | 17.2319 | 17.2297 | 17.216 | 17.1861 | 15.0549 | 15.052 | 15.0488 | 15.0452 | 15.0285 | 15.0086 | 14.9926 | 14.9768 | 14.9565 | 14.9414 | 14.8973 | 14.8301 | 14.7554 | 14.6808 | 15.074 | 15.0729 | 15.0717 | 15.0704 | 15.0663 | 15.0615 | 15.0575 | 15.0536 | 15.0487 | 15.0444 | 15.0317 | 15.0139 | 14.9855 | 14.942
DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | YES | 11.6556 | 11.5914 | 11.5295 | 11.4508 | 11.373 | 11.2973 | 11.2238 | 11.1524 | 11.081 | 9.9805 | 9.8401 | 9.6069 | 9.3551 | 9.0672 | 10.8043 | 10.7655 | 10.728 | 10.6804 | 10.6325 | 10.5857 | 10.54 | 10.4954 | 10.4563 | 9.9492 | 9.812 | 9.584 | 9.3378 | 9.0568 | 10.8736 | 10.8023 | 10.7335 | 10.6461 | 10.5598 | 10.476 | 10.3946 | 9.9152 | 9.8112 | 9.7451 | 9.6097 | 9.3557 | 9.0813 | 8.7713
| BRUCHAG | CT |  |  | 11.6556 | 11.5914 | 11.5295 | 11.4508 | 11.373 | 11.2973 | 11.2238 | 11.1524 | 11.081 | 9.9805 | 9.8401 | 9.6069 | 9.3551 | 9.0672 | 10.8043 | 10.7655 | 10.728 | 10.6804 | 10.6325 | 10.5857 | 10.54 | 10.4954 | 10.4563 | 9.9492 | 9.812 | 9.584 | 9.3378 | 9.0568 | 10.8736 | 10.8023 | 10.7335 | 10.6461 | 10.5598 | 10.476 | 10.3946 | 9.9152 | 9.8112 | 9.7451 | 9.6097 | 9.3557 | 9.0813 | 8.7713
| BRUCHAG | LW |  |  | 11.714 | 11.7087 | 11.7036 | 11.6977 | 11.6911 | 11.6837 | 11.6758 | 11.6673 | 11.6581 | 11.6485 | 11.6182 | 11.564 | 11.5028 | 11.4365 | 10.8397 | 10.8365 | 10.8335 | 10.8299 | 10.8259 | 10.8215 | 10.8167 | 10.8116 | 10.8061 | 10.8003 | 10.7821 | 10.7495 | 10.7127 | 10.6728 | 10.9386 | 10.9327 | 10.927 | 10.9204 | 10.913 | 10.9049 | 10.896 | 10.8866 | 10.8763 | 10.8656 | 10.832 | 10.7716 | 10.7036 | 10.6298
| BRUCHAG | ST |  |  | 11.716 | 11.7125 | 11.7089 | 11.7041 | 11.6992 | 11.6942 | 11.6882 | 11.6823 | 11.6765 | 11.6714 | 11.6539 | 11.6241 | 11.5919 | 11.5603 | 10.8409 | 10.8387 | 10.8366 | 10.8337 | 10.8305 | 10.8274 | 10.8236 | 10.8197 | 10.816 | 10.8128 | 10.802 | 10.7836 | 10.7618 | 10.7414 | 10.9408 | 10.9368 | 10.9328 | 10.9276 | 10.9221 | 10.9166 | 10.91 | 10.9035 | 10.8972 | 10.8915 | 10.8721 | 10.8391 | 10.804 | 10.7693
| BRUCHAG | SP |  |  | 11.7136 | 11.7089 | 11.7041 | 11.6994 | 11.6924 | 11.6855 | 11.6787 | 11.672 | 11.6654 | 11.6589 | 11.6396 | 11.6021 | 11.5633 | 11.5247 | 10.8394 | 10.8366 | 10.8337 | 10.8308 | 10.8266 | 10.8225 | 10.8184 | 10.8143 | 10.8104 | 10.8064 | 10.7947 | 10.772 | 10.7481 | 10.7238 | 10.9381 | 10.9328 | 10.9276 | 10.9223 | 10.9145 | 10.9069 | 10.8993 | 10.8919 | 10.8845 | 10.8772 | 10.8559 | 10.8141 | 10.7711 | 10.7286
KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | YES | 36.4691 | 36.4623 | 36.4319 | 36.4307 | 36.394 | 36.347 | 36.2947 | 36.2287 | 36.1514 | 36.3014 | 36.3093 | 35.6625 | 35.4762 | 34.827 | 32.9899 | 32.9715 | 32.9458 | 32.8892 | 32.7519 | 32.6209 | 32.4856 | 32.2959 | 32.0696 | 32.3077 | 32.0969 | 31.31 | 31.1237 | 19.3563 | 33.3931 | 33.379 | 33.3595 | 33.318 | 33.215 | 33.1148 | 33.01 | 32.8658 | 32.6942 | 32.9 | 32.9315 | 31.6058 | 31.1581 | 19.616
| BUCKIE | CT |  |  | 36.4691 | 36.4623 | 36.4536 | 36.4379 | 36.394 | 36.347 | 36.2947 | 36.2287 | 36.1514 | 36.9313 | 36.7258 | 35.6625 | 35.4762 | 34.827 | 32.9899 | 32.9715 | 32.9458 | 32.8892 | 32.7519 | 32.6209 | 32.4856 | 32.2959 | 32.0696 | 32.6691 | 32.0969 | 31.31 | 31.1237 | 19.3563 | 33.3931 | 33.379 | 33.3595 | 33.318 | 33.215 | 33.1148 | 33.01 | 32.8658 | 32.6942 | 33.36 | 32.9315 | 31.6058 | 31.1581 | 19.616
| BUCKIE | LW |  |  | 36.4775 | 36.4767 | 36.4753 | 36.472 | 36.4448 | 36.4168 | 37.2301 | 37.2003 | 37.1606 | 37.1273 | 37.0036 | 36.3214 | 36.2907 | 36.2771 | 33.0069 | 33.0018 | 32.9938 | 32.9738 | 32.814 | 32.655 | 33.3388 | 33.181 | 32.9835 | 32.791 | 32.3617 | 31.9689 | 31.9382 | 31.9246 | 33.407 | 33.4035 | 33.3979 | 33.384 | 33.2729 | 33.1621 | 33.8934 | 33.7826 | 33.6431 | 33.5091 | 33.1972 | 32.2746 | 31.9726 | 31.959
| BUCKIE | ST |  |  | 36.4764 | 36.4749 | 36.4733 | 36.471 | 36.4517 | 36.4307 | 36.4049 | 36.3749 | 36.3373 | 36.3014 | 37.0251 | 36.4588 | 36.4606 | 36.3724 | 33.0067 | 33.0025 | 32.9972 | 32.9878 | 32.9151 | 32.8417 | 32.7477 | 32.6384 | 32.4976 | 32.3077 | 32.5209 | 31.9459 | 31.9484 | 31.8602 | 33.4065 | 33.4032 | 33.3993 | 33.3925 | 33.3394 | 33.2853 | 33.2164 | 33.1361 | 33.0333 | 32.9 | 33.3051 | 32.5927 | 32.2676 | 32.0669
| BUCKIE | SP |  |  | 36.4763 | 36.4752 | 36.4319 | 36.4307 | 36.4254 | 36.4197 | 36.4113 | 36.4028 | 36.3906 | 36.3734 | 36.3093 | 37.0757 | 36.8182 | 36.8241 | 33.0092 | 33.0076 | 32.9639 | 32.9621 | 32.9422 | 32.9197 | 32.8815 | 32.8435 | 32.7926 | 32.7191 | 32.4417 | 32.9236 | 32.4147 | 32.2364 | 33.408 | 33.4066 | 33.363 | 33.3615 | 33.3469 | 33.3306 | 33.3033 | 33.2761 | 33.2395 | 33.1867 | 32.9876 | 33.5741 | 33.1575 | 33.0685
FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | 2.1281 | 2.1279 | 2.0998 | 2.0809 | 1.9917 | 1.9616 | 1.9305 | 1.8976 | 1.856 | 1.8137 | 1.7364 | 1.6094 | 1.4948 | 1.3766 | 2.0718 | 2.0717 | 2.0539 | 1.987 | 1.9612 | 1.9304 | 1.8986 | 1.8595 | 1.8176 | 1.7749 | 1.6944 | 1.5622 | 1.4403 | 1.3143 | 2.0728 | 2.0726 | 2.0487 | 1.9903 | 1.9627 | 1.9295 | 1.8951 | 1.855 | 1.8116 | 1.7672 | 1.684 | 1.5474 | 1.4224 | 1.2933
| BUNOICH | CT |  |  | 2.1281 | 2.1279 | 2.0998 | 2.0809 | 1.9917 | 1.9616 | 1.9305 | 1.8976 | 1.856 | 1.8137 | 1.7364 | 1.6094 | 1.4948 | 1.3766 | 2.0718 | 2.0717 | 2.0539 | 1.987 | 1.9612 | 1.9304 | 1.8986 | 1.8595 | 1.8176 | 1.7749 | 1.6944 | 1.5622 | 1.4403 | 1.3143 | 2.0728 | 2.0726 | 2.0487 | 1.9903 | 1.9627 | 1.9295 | 1.8951 | 1.855 | 1.8116 | 1.7672 | 1.684 | 1.5474 | 1.4224 | 1.2933
| BUNOICH | LW |  |  | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 1.9928 | 1.9724 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 1.988 | 1.9638 | 1.9398 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 1.9924 | 1.9683 | 1.9443
| BUNOICH | ST |  |  | 2.1282 | 2.1282 | 2.1282 | 2.1282 | 2.1281 | 2.1279 | 2.1278 | 2.1276 | 2.1274 | 2.1274 | 2.1272 | 2.1269 | 2.1253 | 1.9818 | 2.0719 | 2.0719 | 2.0719 | 2.0719 | 2.0718 | 2.0717 | 2.0715 | 2.0714 | 2.0712 | 2.0711 | 2.0709 | 2.0706 | 1.9756 | 1.9515 | 2.0729 | 2.0729 | 2.0729 | 2.0729 | 2.0728 | 2.0726 | 2.0725 | 2.0723 | 2.0721 | 2.0721 | 2.0719 | 2.0716 | 1.98 | 1.956
| BUNOICH | SP |  |  | 2.1282 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.128 | 2.1279 | 2.1278 | 2.1272 | 2.1259 | 2.0719 | 2.0719 | 2.0718 | 2.0718 | 2.0718 | 2.0718 | 2.0718 | 2.0718 | 2.0718 | 2.0718 | 2.0716 | 2.0715 | 2.071 | 2.0697 | 2.0729 | 2.0728 | 2.0728 | 2.0728 | 2.0728 | 2.0728 | 2.0728 | 2.0728 | 2.0728 | 2.0727 | 2.0726 | 2.0725 | 2.0719 | 2.0706
THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | 5.5105 | 5.5102 | 5.51 | 5.5096 | 5.4256 | 5.3386 | 5.2488 | 5.1524 | 5.0137 | 4.9898 | 4.8979 | 4.6469 | 3.4156 | 3.3228 | 4.8811 | 4.88 | 4.8787 | 4.8756 | 4.7867 | 4.696 | 4.6025 | 4.5026 | 4.3604 | 4.3328 | 3.9438 | 3.6928 | 3.0404 | 2.857 | 6.4606 | 6.4595 | 6.4582 | 6.455 | 3.9697 | 3.8806 | 3.7887 | 3.6903 | 3.5497 | 3.5237 | 3.4255 | 3.1639 | 2.4077 | 2.2267
| BURGARHILL | CT |  |  | 5.5105 | 5.5102 | 5.51 | 5.5096 | 5.4528 | 5.3916 | 5.3268 | 5.2588 | 5.1631 | 5.1462 | 5.0982 | 4.6908 | 3.4156 | 3.3228 | 4.8811 | 4.88 | 4.8787 | 4.8756 | 4.8159 | 4.7519 | 4.6843 | 4.6055 | 4.4991 | 4.4713 | 4.3957 | 3.7228 | 3.0404 | 2.857 | 6.4606 | 6.4595 | 6.4582 | 6.455 | 3.998 | 3.9353 | 3.8689 | 3.7948 | 3.693 | 3.6697 | 3.6026 | 3.1639 | 2.4077 | 2.2267
| BURGARHILL | LW |  |  | 5.5108 | 5.5108 | 5.5108 | 5.5108 | 5.4256 | 5.3386 | 5.2488 | 5.1524 | 5.0137 | 4.9898 | 4.8979 | 4.6469 | 3.432 | 3.3672 | 4.8814 | 4.8806 | 4.8792 | 4.8758 | 4.7867 | 4.696 | 4.6025 | 4.5026 | 4.3604 | 4.3328 | 3.9438 | 3.6928 | 3.2457 | 3.1535 | 6.4609 | 6.4601 | 6.4587 | 6.4552 | 3.9697 | 3.8806 | 3.7887 | 3.6903 | 3.5497 | 3.5237 | 3.4255 | 3.1644 | 2.5296 | 2.4548
| BURGARHILL | ST |  |  | 5.5108 | 5.5108 | 5.5108 | 5.5107 | 5.4715 | 5.4295 | 5.3896 | 5.3444 | 5.2716 | 5.2566 | 5.2132 | 5.0224 | 3.9173 | 3.8296 | 4.8817 | 4.8812 | 4.8806 | 4.8794 | 4.8386 | 4.7947 | 4.7452 | 4.6905 | 4.6085 | 4.5859 | 4.5244 | 4.3116 | 3.612 | 3.4667 | 6.4612 | 6.4607 | 6.4601 | 6.4589 | 6.418 | 3.9759 | 3.9306 | 3.8801 | 3.8021 | 3.7828 | 3.7271 | 3.5163 | 3.0039 | 2.8884
| BURGARHILL | SP |  |  | 5.5107 | 5.5107 | 5.5107 | 5.5106 | 5.5067 | 5.5029 | 5.4989 | 5.4946 | 5.4874 | 5.4797 | 5.452 | 5.4277 | 5.1539 | 5.066 | 4.8821 | 4.882 | 4.8819 | 4.8818 | 4.8774 | 4.873 | 4.8659 | 4.8583 | 4.847 | 4.8362 | 4.8 | 4.7625 | 4.4771 | 4.3794 | 6.4616 | 6.4615 | 6.4614 | 6.4613 | 6.4569 | 6.4525 | 6.4453 | 6.4377 | 6.4264 | 6.4156 | 3.9887 | 3.957 | 3.676 | 3.5814
ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | YES | 19.1505 | 19.072 | 18.9941 | 18.8925 | 18.7724 | 18.6537 | 18.5347 | 18.4163 | 18.2925 | 18.2108 | 18.0757 | 12.9262 | 10.1435 | 7.9258 | 17.5144 | 17.4246 | 17.3229 | 17.1879 | 17.0397 | 16.9602 | 16.8791 | 16.797 | 16.7097 | 16.6629 | 13.0414 | 11.1754 | 7.9844 | 5.4904 | 17.2591 | 17.1846 | 17.1123 | 17.0229 | 16.9251 | 16.8269 | 16.7281 | 16.6285 | 16.5283 | 16.4752 | 12.7555 | 10.8682 | 7.6557 | 5.1393
| BURGHEAD | CT |  |  | 19.1505 | 19.072 | 18.9941 | 18.8925 | 18.7724 | 18.6537 | 18.5347 | 18.4163 | 18.2925 | 18.2108 | 18.0757 | 12.9262 | 10.1435 | 7.9258 | 17.5144 | 17.4246 | 17.3229 | 17.1879 | 17.0397 | 16.9602 | 16.8791 | 16.797 | 16.7097 | 16.6629 | 13.0414 | 11.1754 | 7.9844 | 5.4904 | 17.2591 | 17.1846 | 17.1123 | 17.0229 | 16.9251 | 16.8269 | 16.7281 | 16.6285 | 16.5283 | 16.4752 | 12.7555 | 10.8682 | 7.6557 | 5.1393
| BURGHEAD | LW |  |  | 19.223 | 19.2161 | 19.2087 | 19.1983 | 19.164 | 19.1283 | 19.0911 | 19.0524 | 19.0038 | 18.9608 | 18.9087 | 13.433 | 10.9191 | 9.8228 | 17.5951 | 17.5819 | 17.564 | 17.5257 | 17.3615 | 17.2645 | 17.2404 | 17.2148 | 17.1817 | 17.1546 | 13.3121 | 11.4232 | 8.5041 | 7.2465 | 17.3283 | 17.3223 | 17.3166 | 17.3099 | 17.3015 | 17.2913 | 17.2794 | 17.2655 | 17.2475 | 17.2355 | 13.191 | 11.2869 | 8.3509 | 7.0771
| BURGHEAD | ST |  |  | 19.2231 | 19.2167 | 19.2096 | 19.1989 | 19.1721 | 19.1433 | 19.1132 | 19.0797 | 19.0395 | 19.0043 | 18.9045 | 18.838 | 12.9196 | 11.0142 | 17.586 | 17.5666 | 17.5422 | 17.4975 | 17.3953 | 17.3136 | 17.2449 | 17.2197 | 17.1893 | 17.1658 | 17.0972 | 12.791 | 10.8359 | 8.6237 | 17.3295 | 17.3248 | 17.3201 | 17.314 | 17.3017 | 17.2879 | 17.2716 | 17.2538 | 17.2339 | 17.2239 | 17.1911 | 12.6729 | 10.7104 | 8.4906
| BURGHEAD | SP |  |  | 19.2211 | 19.2144 | 19.2076 | 19.2007 | 19.1887 | 19.1761 | 19.1624 | 19.1488 | 19.1335 | 19.1151 | 19.0508 | 18.9553 | 18.8185 | 18.6874 | 17.5977 | 17.5899 | 17.5819 | 17.5735 | 17.5325 | 17.4861 | 17.4292 | 17.3934 | 17.3532 | 17.3038 | 17.2125 | 17.1517 | 17.0473 | 16.9438 | 17.3258 | 17.3194 | 17.3129 | 17.3064 | 17.2984 | 17.2904 | 17.2826 | 17.2748 | 17.267 | 17.2578 | 17.2297 | 17.1817 | 17.0866 | 16.9747
BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | YES | 19.8131 | 19.8015 | 19.7959 | 19.7881 | 19.7613 | 19.7293 | 19.6913 | 19.6471 | 19.5951 | 19.5672 | 19.4736 | 10.2405 | 8.1552 | 4.39 | 16.4115 | 16.3452 | 16.2992 | 16.1946 | 15.9226 | 15.6713 | 15.4502 | 15.2617 | 15.0359 | 11.4975 | 8.9357 | 6.5718 | 4.1384 | -0.20602 | 16.2725 | 16.2469 | 16.231 | 16.1984 | 16.1091 | 16.0211 | 15.9278 | 15.8268 | 15.699 | 15.5751 | 9.2002 | 6.8835 | 4.5032 | 0.25371
| BURGHMUIR | CT |  |  | 19.9578 | 19.8015 | 19.7959 | 19.7881 | 19.7613 | 19.7293 | 19.6913 | 19.6471 | 19.5951 | 19.5672 | 19.4736 | 10.2405 | 8.1552 | 4.39 | 16.5286 | 16.3452 | 16.2992 | 16.1946 | 15.9226 | 15.6713 | 15.4502 | 15.2697 | 15.0359 | 14.963 | 9.7612 | 6.5718 | 4.1384 | -0.20602 | 16.4101 | 16.2469 | 16.231 | 16.1984 | 16.1091 | 16.0211 | 15.9278 | 15.8268 | 15.699 | 15.5751 | 9.9969 | 6.8835 | 4.5032 | 0.25371
| BURGHMUIR | LW |  |  | 19.8131 | 19.8131 | 19.8131 | 19.8131 | 19.8112 | 19.8072 | 19.8011 | 19.7925 | 19.7761 | 19.7726 | 19.7576 | 10.3719 | 9.7785 | 8.081 | 16.4115 | 16.4087 | 16.4043 | 16.3933 | 16.0543 | 15.7167 | 15.4706 | 15.2617 | 15.1727 | 11.4975 | 8.9357 | 6.6293 | 5.9262 | 3.8859 | 16.2725 | 16.2718 | 16.2707 | 16.2679 | 16.1798 | 16.0907 | 16.0003 | 15.9082 | 15.7866 | 15.6775 | 9.2002 | 6.9522 | 6.2659 | 4.2778
| BURGHMUIR | ST |  |  | 19.9629 | 19.8102 | 19.8091 | 19.8076 | 19.7958 | 19.7815 | 19.7646 | 19.7448 | 19.7206 | 19.7129 | 19.6882 | 11.3427 | 8.3035 | 6.4083 | 16.5425 | 16.3714 | 16.3458 | 16.2973 | 16.0965 | 15.8885 | 15.6971 | 15.5038 | 15.311 | 15.1314 | 10.5691 | 7.8158 | 4.2027 | 1.9748 | 16.4175 | 16.2601 | 16.2527 | 16.2393 | 16.1792 | 16.1154 | 16.054 | 15.9813 | 15.8869 | 15.7905 | 10.7894 | 8.1059 | 4.5803 | 2.4068
| BURGHMUIR | SP |  |  | 19.9608 | 19.9588 | 19.8051 | 19.8029 | 19.8026 | 19.8022 | 19.8017 | 19.8012 | 19.8004 | 19.7971 | 19.7846 | 19.7735 | 19.6719 | 19.6912 | 16.5581 | 16.5535 | 16.3969 | 16.3914 | 16.3403 | 16.281 | 16.2042 | 16.1285 | 16.0285 | 15.9007 | 15.4662 | 15.1792 | 11.3269 | 10.4753 | 16.4199 | 16.4172 | 16.2628 | 16.2598 | 16.2465 | 16.231 | 16.2111 | 16.1913 | 16.1653 | 16.1301 | 15.9889 | 15.8118 | 15.566 | 10.6981
CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | 0.10423 | 0.1042 | 0.065254 | 0.026496 | -0.013391 | -0.061505 | -0.11107 | -0.16226 | -0.21505 | -0.2692 | -0.36654 | -0.52521 | -0.66474 | -0.80195 | 0.10168 | 0.10165 | 0.064226 | 0.026739 | -0.011866 | -0.058311 | -0.10613 | -0.15596 | -0.20731 | -0.26002 | -0.356 | -0.51244 | -0.6507 | -0.78681 | 0.10212 | 0.10209 | 0.06277 | 0.023438 | -0.017042 | -0.065843 | -0.11611 | -0.16813 | -0.22177 | -0.2768 | -0.37625 | -0.53934 | -0.68333 | -0.82496
| BUTTERBRIDGE | CT |  |  | 0.10423 | 0.1042 | 0.065254 | 0.026496 | -0.013391 | -0.061505 | -0.11107 | -0.16226 | -0.21505 | -0.2692 | -0.36654 | -0.52521 | -0.66474 | -0.80195 | 0.10168 | 0.10165 | 0.064226 | 0.026739 | -0.011866 | -0.058311 | -0.10613 | -0.15596 | -0.20731 | -0.26002 | -0.356 | -0.51244 | -0.6507 | -0.78681 | 0.10212 | 0.10209 | 0.06277 | 0.023438 | -0.017042 | -0.065843 | -0.11611 | -0.16813 | -0.22177 | -0.2768 | -0.37625 | -0.53934 | -0.68333 | -0.82496
| BUTTERBRIDGE | LW |  |  | 0.10428 | 0.10428 | 0.10428 | 0.099797 | 0.097582 | 0.095415 | 0.093295 | 0.091221 | 0.089185 | 0.086982 | 0.080459 | 0.069956 | 0.059384 | 0.048915 | 0.10173 | 0.10173 | 0.099499 | 0.097159 | 0.094553 | 0.09199 | 0.089483 | 0.087031 | 0.084633 | 0.08204 | 0.074362 | 0.061988 | 0.049535 | 0.037201 | 0.10217 | 0.10217 | 0.099796 | 0.097446 | 0.094832 | 0.092274 | 0.089771 | 0.087324 | 0.084931 | 0.082343 | 0.074683 | 0.062347 | 0.049931 | 0.037636
| BUTTERBRIDGE | ST |  |  | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.099235 | 0.09827 | 0.097329 | 0.095349 | 0.089612 | 0.08039 | 0.071326 | 0.062278 | 0.10173 | 0.10173 | 0.10173 | 0.099852 | 0.098852 | 0.09766 | 0.096497 | 0.095364 | 0.094253 | 0.091912 | 0.085135 | 0.07428 | 0.063602 | 0.052943 | 0.10217 | 0.10217 | 0.10217 | 0.10217 | 0.099146 | 0.097949 | 0.096781 | 0.095643 | 0.094533 | 0.092196 | 0.085432 | 0.074601 | 0.063956 | 0.05333
| BUTTERBRIDGE | SP |  |  | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.09878 | 0.095222 | 0.091904 | 0.088833 | 0.10183 | 0.10181 | 0.10178 | 0.10176 | 0.10173 | 0.10173 | 0.10173 | 0.10173 | 0.099528 | 0.098617 | 0.095963 | 0.091762 | 0.087839 | 0.084219 | 0.10219 | 0.10218 | 0.10217 | 0.10217 | 0.10217 | 0.10217 | 0.10217 | 0.10217 | 0.099825 | 0.09891 | 0.096245 | 0.092046 | 0.08813 | 0.084517
BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | 10.4272 | 10.4226 | 10.3868 | 10.3445 | 10.2935 | 10.2342 | 10.1718 | 10.1078 | 10.0405 | 9.9797 | 9.8437 | 7.5628 | 7.1062 | 6.5249 | 9.5073 | 9.5 | 9.4622 | 9.4122 | 9.3528 | 9.2857 | 9.2257 | 9.1799 | 9.1314 | 9.09 | 8.9903 | 6.9881 | 6.5251 | 5.9367 | 9.67 | 9.668 | 9.6314 | 9.5937 | 9.5479 | 9.4926 | 9.4339 | 9.3717 | 9.3059 | 9.2471 | 7.2511 | 6.7749 | 6.2568 | 5.6151
| CALLANDER | CT |  |  | 10.4272 | 10.4226 | 10.3868 | 10.3445 | 10.2935 | 10.2342 | 10.1718 | 10.1078 | 10.0405 | 9.9797 | 9.8437 | 7.5628 | 7.1062 | 6.5249 | 9.5073 | 9.5 | 9.4622 | 9.4122 | 9.3528 | 9.2857 | 9.2257 | 9.1799 | 9.1314 | 9.09 | 8.9903 | 6.9881 | 6.5251 | 5.9367 | 9.67 | 9.668 | 9.6314 | 9.5937 | 9.5479 | 9.4926 | 9.4339 | 9.3717 | 9.3059 | 9.2471 | 7.2511 | 6.7749 | 6.2568 | 5.6151
| CALLANDER | LW |  |  | 10.4323 | 10.4317 | 10.4306 | 10.428 | 10.4251 | 10.4222 | 10.4194 | 10.4166 | 10.414 | 10.4111 | 10.4025 | 10.3887 | 10.3748 | 10.361 | 9.5148 | 9.5134 | 9.5113 | 9.506 | 9.5002 | 9.4944 | 9.4888 | 9.4833 | 9.4779 | 9.4721 | 9.4548 | 9.4271 | 9.3991 | 9.3714 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728 | 9.6728
| CALLANDER | ST |  |  | 10.4303 | 10.4283 | 10.4256 | 10.4207 | 10.4103 | 10.3977 | 10.3844 | 10.3703 | 10.3554 | 10.3467 | 10.3212 | 10.2798 | 10.1784 | 10.1094 | 9.5115 | 9.5078 | 9.503 | 9.4939 | 9.4777 | 9.4583 | 9.4384 | 9.4178 | 9.3966 | 9.382 | 9.3395 | 9.2708 | 9.1731 | 7.2395 | 9.672 | 9.6716 | 9.6711 | 9.6704 | 9.6656 | 9.6598 | 9.6531 | 9.6453 | 9.6367 | 9.6338 | 9.6252 | 9.6109 | 9.5363 | 7.2816
| CALLANDER | SP |  |  | 10.4416 | 10.4298 | 10.4286 | 10.4273 | 10.4259 | 10.4242 | 10.4219 | 10.4196 | 10.4167 | 10.413 | 10.4015 | 10.3873 | 10.353 | 10.2902 | 9.5352 | 9.5125 | 9.511 | 9.5095 | 9.5069 | 9.5037 | 9.4992 | 9.4948 | 9.4892 | 9.4832 | 9.465 | 9.4404 | 9.3964 | 9.3244 | 9.671 | 9.6701 | 9.6691 | 9.6681 | 9.6679 | 9.6677 | 9.6675 | 9.6673 | 9.6671 | 9.6656 | 9.6607 | 9.6568 | 9.6321 | 9.5784
STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | 5.6046 | 5.6036 | 5.6027 | 5.6012 | 5.5963 | 5.5906 | 5.5838 | 5.576 | 5.5673 | 5.5623 | 5.5455 | 5.5069 | 3.7097 | 3.4463 | 5.1529 | 5.1488 | 5.1431 | 5.1302 | 5.1131 | 5.0954 | 5.0767 | 5.0511 | 5.0306 | 5.0154 | 4.9935 | 4.9464 | 3.1839 | 2.8956 | 5.0538 | 5.0524 | 5.0507 | 5.0476 | 5.0424 | 5.0367 | 5.0299 | 5.0221 | 5.0134 | 5.0084 | 4.9916 | 4.953 | 3.1358 | 2.8601
| CALLANISH | CT |  |  | 5.6046 | 5.6036 | 5.6027 | 5.6012 | 5.5963 | 5.5906 | 5.5838 | 5.576 | 5.5673 | 5.5623 | 5.5455 | 5.5069 | 3.7097 | 3.4463 | 5.1529 | 5.1488 | 5.1431 | 5.1302 | 5.1131 | 5.0954 | 5.0767 | 5.0511 | 5.0306 | 5.0154 | 4.9935 | 4.9464 | 3.1839 | 2.8956 | 5.0538 | 5.0524 | 5.0507 | 5.0476 | 5.0424 | 5.0367 | 5.0299 | 5.0221 | 5.0134 | 5.0084 | 4.9916 | 4.953 | 3.1358 | 2.8601
| CALLANISH | LW |  |  | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 5.6058 | 4.8413 | 4.8413 | 5.157 | 5.1562 | 5.155 | 5.1519 | 5.1484 | 5.1451 | 5.1418 | 5.1386 | 5.1354 | 5.132 | 5.122 | 5.1058 | 3.8649 | 3.8383 | 5.0555 | 5.0554 | 5.0552 | 5.0548 | 5.0542 | 5.0537 | 5.0533 | 5.0528 | 5.0523 | 5.052 | 5.052 | 5.052 | 3.7774 | 3.7528
| CALLANISH | ST |  |  | 5.6058 | 5.6057 | 5.6056 | 5.6056 | 5.605 | 5.6043 | 5.6035 | 5.6026 | 5.6016 | 5.6012 | 5.6002 | 5.5985 | 5.2075 | 5.2025 | 5.1572 | 5.1568 | 5.1562 | 5.1551 | 5.1533 | 5.151 | 5.141 | 5.1309 | 5.121 | 5.1069 | 5.0706 | 5.049 | 3.9121 | 3.8021 | 5.0555 | 5.0554 | 5.0552 | 5.055 | 5.0542 | 5.0533 | 5.0512 | 5.0489 | 5.0477 | 5.0473 | 5.0463 | 5.0446 | 3.9523 | 3.8503
| CALLANISH | SP |  |  | 5.6056 | 5.6055 | 5.6054 | 5.6053 | 5.6053 | 5.6052 | 5.6052 | 5.6052 | 5.6052 | 5.605 | 5.6044 | 5.604 | 5.6011 | 5.5948 | 5.1572 | 5.1568 | 5.1564 | 5.156 | 5.1542 | 5.1522 | 5.1488 | 5.1455 | 5.1413 | 5.1357 | 5.1197 | 5.095 | 5.073 | 5.0535 | 5.0554 | 5.0552 | 5.0551 | 5.0549 | 5.0546 | 5.0543 | 5.0538 | 5.0533 | 5.0526 | 5.0516 | 5.0505 | 5.0501 | 5.0472 | 5.0409
TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | 3.5444 | 3.5442 | 3.3704 | 3.2248 | 3.0943 | 2.3212 | 2.1017 | 1.8757 | 1.6424 | 1.4033 | 0.97485 | 0.2764 | -0.33703 | -0.94035 | 3.4361 | 3.4349 | 3.3058 | 3.1747 | 2.4467 | 2.2475 | 2.0383 | 1.8215 | 1.5978 | 1.3684 | 0.95361 | 0.26075 | -0.35045 | -0.95201 | 3.0523 | 3.051 | 2.91 | 2.4925 | 2.3134 | 2.0973 | 1.8745 | 1.6452 | 1.4085 | 1.1657 | 0.73098 | 0.022216 | -0.60138 | -1.219
| CALVINE | CT |  |  | 3.5444 | 3.5442 | 3.3704 | 3.2248 | 3.0943 | 2.3212 | 2.1017 | 1.8757 | 1.6424 | 1.4033 | 0.97485 | 0.2764 | -0.33703 | -0.94035 | 3.4361 | 3.4349 | 3.3058 | 3.1747 | 2.4467 | 2.2475 | 2.0383 | 1.8215 | 1.5978 | 1.3684 | 0.95361 | 0.26075 | -0.35045 | -0.95201 | 3.0523 | 3.051 | 2.91 | 2.4925 | 2.3134 | 2.0973 | 1.8745 | 1.6452 | 1.4085 | 1.1657 | 0.73098 | 0.022216 | -0.60138 | -1.219
| CALVINE | LW |  |  | 3.5446 | 3.5446 | 3.4676 | 3.3905 | 3.3138 | 3.2475 | 3.187 | 3.1263 | 3.066 | 2.4457 | 2.2923 | 2.0332 | 1.7686 | 1.4976 | 3.4362 | 3.435 | 3.3766 | 3.3154 | 3.2539 | 3.1923 | 3.1308 | 3.0692 | 2.4307 | 2.3571 | 2.2065 | 1.9526 | 1.6934 | 1.4268 | 3.0525 | 3.051 | 2.9871 | 2.9197 | 2.8519 | 2.784 | 2.4556 | 2.3782 | 2.3011 | 2.2236 | 2.0679 | 1.8049 | 1.5364 | 1.2613
| CALVINE | ST |  |  | 3.5446 | 3.5446 | 3.4932 | 3.4418 | 3.3906 | 3.3391 | 3.2902 | 3.2495 | 3.2091 | 3.1673 | 2.4941 | 2.2347 | 1.9686 | 1.6967 | 3.4367 | 3.4361 | 3.3976 | 3.3584 | 3.3188 | 3.2786 | 3.2374 | 3.1961 | 3.155 | 3.1118 | 2.403 | 2.1487 | 1.8881 | 1.6221 | 3.0531 | 3.0523 | 3.0102 | 2.9673 | 2.9238 | 2.8796 | 2.8343 | 2.7888 | 2.4803 | 2.4286 | 2.2727 | 2.0094 | 1.7394 | 1.4635
| CALVINE | SP |  |  | 3.5446 | 3.5445 | 3.5445 | 3.5445 | 3.5445 | 3.5445 | 3.5445 | 3.5445 | 3.5445 | 3.5444 | 3.5443 | 3.5442 | 3.5437 | 3.5425 | 3.4372 | 3.4371 | 3.437 | 3.4369 | 3.4363 | 3.4356 | 3.4345 | 3.4334 | 3.432 | 3.4299 | 3.4238 | 3.4142 | 3.4049 | 3.3954 | 3.0537 | 3.0536 | 3.0535 | 3.0533 | 3.0526 | 3.0518 | 3.0504 | 3.0491 | 3.0473 | 3.0447 | 3.0372 | 3.0255 | 3.0142 | 3.0028
CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | YES | 16.8767 | 16.7257 | 16.5257 | 14.5168 | 14.0726 | 13.5007 | 12.7219 | 11.884 | 10.9755 | 10.6507 | 9.5045 | 4.561 | 1.3171 | -0.56246 | 15.4867 | 15.4073 | 13.7686 | 13.471 | 13.1627 | 12.4128 | 11.6319 | 10.8014 | 9.9025 | 9.5875 | 8.6238 | 4.3323 | 1.1031 | -0.76752 | 16.5086 | 13.7875 | 13.6109 | 13.4215 | 12.9861 | 12.3865 | 11.6 | 10.7631 | 9.8559 | 9.5325 | 8.5416 | 4.4499 | 1.3912 | -0.50714
| CAMPBELTOWN | CT |  |  | 16.9228 | 16.7257 | 16.5257 | 14.5168 | 14.0726 | 13.5007 | 12.9146 | 12.2381 | 11.4186 | 11.0014 | 9.9285 | 4.561 | 1.3171 | -0.56246 | 15.57 | 15.4407 | 13.7987 | 13.6933 | 13.3393 | 12.855 | 12.375 | 11.8706 | 11.1597 | 10.7539 | 9.6805 | 4.3323 | 1.1031 | -0.76752 | 16.5426 | 13.7875 | 13.6109 | 13.4215 | 12.9861 | 12.4225 | 11.8657 | 11.2872 | 10.5672 | 10.24 | 9.4092 | 4.4499 | 1.3912 | -0.50714
| CAMPBELTOWN | LW |  |  | 16.8767 | 16.8021 | 16.7273 | 16.6904 | 14.2654 | 13.5095 | 12.7219 | 11.884 | 10.9755 | 10.6507 | 9.5045 | 7.1649 | 4.8331 | 3.1912 | 15.4867 | 15.4073 | 13.7686 | 13.7417 | 13.1627 | 12.4128 | 11.6319 | 10.8014 | 9.9025 | 9.5875 | 8.6238 | 6.6087 | 4.2819 | 2.643 | 16.5086 | 16.4211 | 13.7553 | 13.7247 | 13.1414 | 12.3865 | 11.6 | 10.7631 | 9.8559 | 9.5325 | 8.5416 | 6.483 | 4.4321 | 3.0667
| CAMPBELTOWN | ST |  |  | 17.248 | 17.2083 | 17.1684 | 17.1451 | 16.9663 | 14.1419 | 13.3191 | 12.4875 | 12.2656 | 11.9164 | 10.8597 | 8.0795 | 4.4491 | 0.6981 | 15.8592 | 15.8167 | 15.7727 | 15.7447 | 15.573 | 13.0365 | 12.2179 | 11.3903 | 11.1725 | 10.8269 | 9.7967 | 7.6243 | 4.3466 | 1.1264 | 16.8837 | 16.8362 | 16.7861 | 16.7434 | 16.5385 | 13.0174 | 12.1953 | 11.3644 | 11.1432 | 10.7946 | 9.7535 | 7.3206 | 4.2362 | 0.65149
| CAMPBELTOWN | SP |  |  | 17.4263 | 17.3997 | 17.3731 | 16.4267 | 14.4831 | 14.3888 | 14.2947 | 14.1993 | 14.0998 | 13.8304 | 13.0037 | 8.7697 | 5.357 | 2.8382 | 16.0427 | 16.0176 | 15.9924 | 13.471 | 13.3843 | 13.2977 | 13.2111 | 13.1231 | 13.0306 | 12.7678 | 11.9604 | 8.8365 | 5.7202 | 3.5366 | 17.0689 | 17.0408 | 17.0125 | 13.4525 | 13.3589 | 13.2655 | 13.1723 | 13.0778 | 12.9792 | 12.7105 | 11.8863 | 8.0078 | 4.9584 | 2.7399
COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | YES | 17.7811 | 17.7794 | 17.731 | 17.6815 | 17.6208 | 17.545 | 17.4619 | 17.3701 | 17.2636 | 17.184 | 17.0202 | 14.4323 | 13.5174 | 11.1941 | 16.2448 | 16.1532 | 16.1136 | 16.0515 | 15.8934 | 15.5427 | 15.2371 | 13.3113 | 13.2876 | 13.2624 | 13.1818 | 13.0583 | 11.7215 | 8.947 | 16.346 | 16.3211 | 16.2732 | 16.2189 | 16.1527 | 16.0726 | 15.9856 | 13.3746 | 13.3509 | 13.3258 | 13.2454 | 12.9434 | 11.7871 | 9.0175
| CAPUTH | CT |  |  | 17.7811 | 17.7794 | 17.731 | 17.6815 | 17.6208 | 17.545 | 17.4619 | 17.3701 | 17.2636 | 17.184 | 17.0202 | 14.4323 | 13.7112 | 12.9719 | 16.2448 | 16.1532 | 16.1136 | 16.0515 | 15.9762 | 15.8917 | 15.8015 | 15.6713 | 15.5289 | 15.4085 | 15.0843 | 13.2215 | 12.4761 | 11.7154 | 16.346 | 16.3211 | 16.2732 | 16.2189 | 16.1527 | 16.0726 | 15.9856 | 15.8821 | 15.7762 | 15.6973 | 15.5346 | 12.9434 | 12.1298 | 11.3032
| CAPUTH | LW |  |  | 17.7837 | 17.7837 | 17.7631 | 17.7424 | 17.7093 | 17.663 | 17.6029 | 17.5259 | 17.4128 | 17.3741 | 17.2663 | 16.9061 | 16.636 | 11.3383 | 16.2503 | 16.162 | 16.1382 | 16.0934 | 16.0321 | 15.9586 | 15.8721 | 15.7696 | 15.6317 | 15.5654 | 15.3655 | 14.8703 | 13.7383 | 9.4018 | 16.3493 | 16.3265 | 16.3043 | 16.2767 | 16.2355 | 16.1815 | 16.1138 | 16.0361 | 15.9231 | 15.8847 | 15.7772 | 15.4155 | 13.605 | 9.2685
| CAPUTH | ST |  |  | 17.7832 | 17.7829 | 17.7689 | 17.7548 | 17.7361 | 17.7143 | 17.6902 | 17.6615 | 17.6226 | 17.6021 | 17.5378 | 17.3087 | 16.9854 | 14.5145 | 16.2493 | 16.2412 | 16.1444 | 16.1175 | 16.0788 | 16.0317 | 15.9688 | 15.9023 | 15.8266 | 15.7641 | 15.5787 | 14.9935 | 13.5341 | 13.1441 | 16.3487 | 16.3464 | 16.3105 | 16.2926 | 16.2682 | 16.2394 | 16.2047 | 16.1712 | 16.1325 | 16.1121 | 16.0482 | 15.8187 | 13.4599 | 13.0393
| CAPUTH | SP |  |  | 17.7829 | 17.7824 | 17.782 | 17.7815 | 17.7813 | 17.781 | 17.7806 | 17.7798 | 17.7783 | 17.7755 | 17.7594 | 17.7364 | 13.5174 | 11.1941 | 16.2565 | 16.2549 | 16.2532 | 16.2514 | 15.8934 | 15.5427 | 15.2371 | 13.3113 | 13.2876 | 13.2624 | 13.1818 | 13.0583 | 11.7215 | 8.947 | 16.3503 | 16.3496 | 16.3488 | 16.348 | 16.2903 | 16.29 | 16.2895 | 13.3746 | 13.3509 | 13.3258 | 13.2454 | 13.122 | 11.7871 | 9.0175
ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | YES | 22.1829 | 22.1783 | 22.1728 | 22.1647 | 22.1382 | 22.1067 | 22.0696 | 22.0269 | 21.9779 | 21.9505 | 21.8592 | 21.6348 | 13.3214 | 11.2842 | 18.3441 | 18.3103 | 18.261 | 18.154 | 18.0336 | 17.9135 | 17.7893 | 17.6668 | 17.5257 | 17.3889 | 17.1945 | 12.6105 | 10.1214 | 7.8391 | 18.0564 | 18.0474 | 18.0354 | 18.0118 | 17.9626 | 17.9096 | 17.8514 | 17.7894 | 17.718 | 17.6773 | 13.6372 | 12.0494 | 9.6155 | 7.375
| CARNOUSTIE | CT |  |  | 22.1829 | 22.1783 | 22.1728 | 22.1647 | 22.1382 | 22.1067 | 22.0696 | 22.0269 | 21.9779 | 21.9505 | 21.8592 | 21.6348 | 13.3214 | 11.2842 | 18.3441 | 18.3103 | 18.261 | 18.154 | 18.0336 | 17.9135 | 17.7893 | 17.6668 | 17.5257 | 17.3889 | 17.1945 | 12.6105 | 10.1214 | 7.8391 | 18.0564 | 18.0474 | 18.0354 | 18.0118 | 17.9626 | 17.9096 | 17.8514 | 17.7894 | 17.718 | 17.6773 | 13.6372 | 12.0494 | 9.6155 | 7.375
| CARNOUSTIE | LW |  |  | 22.1899 | 22.1899 | 22.1899 | 22.1899 | 22.1894 | 22.1882 | 22.1865 | 22.184 | 22.1792 | 22.1782 | 22.1739 | 22.1587 | 22.1416 | 22.134 | 18.3802 | 18.3764 | 18.3704 | 18.3553 | 18.2441 | 18.1541 | 18.0861 | 18.0181 | 17.9329 | 17.8507 | 17.5479 | 17.494 | 12.6024 | 11.9104 | 18.0677 | 18.0671 | 18.0663 | 18.064 | 18.047 | 18.0296 | 18.0118 | 17.9935 | 17.9693 | 17.9486 | 17.9007 | 13.6722 | 12.0546 | 11.3804
| CARNOUSTIE | ST |  |  | 22.1881 | 22.187 | 22.1858 | 22.1843 | 22.1724 | 22.1581 | 22.1415 | 22.1223 | 22.1002 | 22.093 | 22.0709 | 22.0274 | 21.8273 | 13.9965 | 18.3616 | 18.3429 | 18.3184 | 18.2719 | 18.1658 | 18.0859 | 18.0121 | 17.9305 | 17.8344 | 17.7374 | 17.4223 | 17.3627 | 12.4602 | 10.8385 | 18.0634 | 18.0596 | 18.055 | 18.0469 | 18.0205 | 17.9903 | 17.9598 | 17.9255 | 17.8855 | 17.8565 | 17.7977 | 13.3991 | 11.908 | 10.3255
| CARNOUSTIE | SP |  |  | 22.1861 | 22.1841 | 22.182 | 22.1799 | 22.1795 | 22.1791 | 22.1787 | 22.1782 | 22.1777 | 22.1745 | 22.1635 | 22.1545 | 22.0881 | 21.9694 | 18.3768 | 18.3726 | 18.3678 | 18.3628 | 18.3372 | 18.3073 | 18.2707 | 18.2346 | 18.1876 | 18.1469 | 18.0146 | 17.8406 | 17.6273 | 17.3703 | 18.0639 | 18.0616 | 18.0591 | 18.0565 | 18.0524 | 18.0477 | 18.0419 | 18.0361 | 18.0287 | 18.0175 | 17.9771 | 17.9282 | 17.8262 | 17.6962
KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | 1.1157 | 2.6157 | 2.5477 | 2.4607 | 2.3838 | 2.2904 | 2.1938 | 2.094 | 1.991 | 1.8852 | 1.6956 | 1.3871 | 1.1174 | 0.85532 | 1.0628 | 2.5622 | 2.4865 | 2.4133 | 2.338 | 2.2474 | 2.1541 | 2.0575 | 1.958 | 1.8556 | 1.6705 | 1.3694 | 1.1053 | 0.84841 | 1.0787 | 2.5786 | 2.4851 | 2.4181 | 2.3446 | 2.2499 | 2.1522 | 2.0508 | 1.9463 | 1.8389 | 1.6461 | 1.3322 | 1.0565 | 0.78856
| CASHLIE | CT |  |  | 1.1157 | 2.6157 | 2.5477 | 2.4607 | 2.3838 | 2.2904 | 2.1938 | 2.094 | 1.991 | 1.8852 | 1.6956 | 1.3871 | 1.1174 | 0.85532 | 1.0628 | 2.5623 | 2.4865 | 2.4133 | 2.338 | 2.2474 | 2.1541 | 2.0575 | 1.958 | 1.8556 | 1.6705 | 1.3694 | 1.1053 | 0.84841 | 1.0787 | 2.5786 | 2.4851 | 2.4181 | 2.3446 | 2.2499 | 2.1522 | 2.0508 | 1.9463 | 1.8389 | 1.6461 | 1.3322 | 1.0565 | 0.78856
| CASHLIE | LW |  |  | 1.1157 | 2.6157 | 2.587 | 2.5594 | 2.5389 | 2.4934 | 2.4655 | 2.4375 | 2.4097 | 2.3817 | 2.3236 | 2.2242 | 2.1227 | 2.0187 | 1.0628 | 2.5622 | 2.5434 | 2.5289 | 2.4736 | 2.4447 | 2.4159 | 2.3869 | 2.3581 | 2.3291 | 2.2692 | 2.1685 | 2.0658 | 1.9608 | 1.0788 | 2.5786 | 2.5494 | 2.5205 | 2.4756 | 2.45 | 2.4227 | 2.3933 | 2.3641 | 2.3346 | 2.2726 | 2.1682 | 2.0616 | 1.9528
| CASHLIE | ST |  |  | 1.1157 | 2.6157 | 2.5966 | 2.5774 | 2.5595 | 2.5451 | 2.5325 | 2.4945 | 2.4761 | 2.4574 | 2.4009 | 2.3028 | 2.2017 | 2.0982 | 1.063 | 2.5628 | 2.549 | 2.5402 | 2.5316 | 2.4846 | 2.4656 | 2.4466 | 2.4277 | 2.4082 | 2.3496 | 2.2508 | 2.1502 | 2.0472 | 1.0788 | 2.5788 | 2.5594 | 2.54 | 2.5206 | 2.4844 | 2.4673 | 2.4503 | 2.4332 | 2.4159 | 2.3561 | 2.254 | 2.15 | 2.0429
| CASHLIE | SP |  |  | 1.1157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 2.6157 | 1.0633 | 2.5633 | 2.5632 | 2.5632 | 2.5629 | 2.5626 | 2.5622 | 2.5618 | 2.5613 | 2.5606 | 2.5584 | 2.5563 | 2.5554 | 2.5553 | 1.0789 | 2.5789 | 2.5789 | 2.5789 | 2.5788 | 2.5787 | 2.5786 | 2.5785 | 2.5784 | 2.5782 | 2.5777 | 2.5768 | 2.576 | 2.5752
KILLIN | CHAORACH | MINIMUM HEADROOM | NN 4540027553 | YES | 0.6183 | 0.61828 | 0.58141 | 0.54452 | 0.50666 | 0.46097 | 0.4139 | 0.36544 | 0.31545 | 0.26408 | 0.17222 | 0.022788 | -0.10762 | -0.23409 | 1.7726 | 1.7725 | 1.7518 | 1.7309 | 1.7094 | 1.6835 | 1.6569 | 1.6293 | 1.6008 | 1.5715 | 1.5184 | 1.4318 | 1.2719 | 1.0873 | 1.0947 | 1.0946 | 1.0483 | 1.0019 | 0.95415 | 0.89666 | 0.83747 | 0.7763 | 0.71324 | 0.64839 | 0.5317 | 0.30436 | 0.098019 | -0.10176
| CHAORACH | CT |  |  | 0.6183 | 0.61828 | 0.58141 | 0.54452 | 0.50666 | 0.46097 | 0.4139 | 0.36544 | 0.31545 | 0.26408 | 0.17222 | 0.022788 | -0.10762 | -0.23409 | 1.7726 | 1.7725 | 1.7518 | 1.7309 | 1.7094 | 1.6835 | 1.6569 | 1.6293 | 1.6008 | 1.5715 | 1.5184 | 1.4318 | 1.2719 | 1.0873 | 1.0947 | 1.0946 | 1.0483 | 1.0019 | 0.95415 | 0.89666 | 0.83747 | 0.7763 | 0.71324 | 0.64839 | 0.5317 | 0.30436 | 0.098019 | -0.10176
| CHAORACH | LW |  |  | 0.61831 | 0.6183 | 0.60193 | 0.58554 | 0.56922 | 0.55282 | 0.53643 | 0.51997 | 0.50358 | 0.48711 | 0.45396 | 0.39799 | 0.34084 | 0.28229 | 1.7726 | 1.7725 | 1.7631 | 1.7535 | 1.7438 | 1.7342 | 1.7245 | 1.7148 | 1.7051 | 1.6954 | 1.6753 | 1.6414 | 1.6069 | 1.5716 | 1.0947 | 1.0946 | 1.0739 | 1.0529 | 1.032 | 1.0109 | 0.98991 | 0.96881 | 0.94782 | 0.92669 | 0.88365 | 0.81109 | 0.73704 | 0.66128
| CHAORACH | ST |  |  | 0.61831 | 0.61831 | 0.6074 | 0.59649 | 0.58562 | 0.5747 | 0.56378 | 0.55281 | 0.54189 | 0.53091 | 0.49779 | 0.44187 | 0.38478 | 0.32629 | 1.7727 | 1.7726 | 1.7664 | 1.7602 | 1.7539 | 1.7476 | 1.7412 | 1.7349 | 1.7286 | 1.722 | 1.7023 | 1.6691 | 1.6353 | 1.6008 | 1.0948 | 1.0947 | 1.081 | 1.0672 | 1.0534 | 1.0395 | 1.0256 | 1.0116 | 0.99773 | 0.98358 | 0.94096 | 0.86909 | 0.7958 | 0.72079
| CHAORACH | SP |  |  | 0.61832 | 0.61832 | 0.61832 | 0.61832 | 0.61831 | 0.61831 | 0.6183 | 0.61829 | 0.61828 | 0.61827 | 0.61823 | 0.61817 | 0.61811 | 0.61806 | 1.7727 | 1.7727 | 1.7727 | 1.7727 | 1.7726 | 1.7725 | 1.7724 | 1.7724 | 1.7722 | 1.7721 | 1.7715 | 1.7707 | 1.7699 | 1.7691 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 1.0947 | 1.0946 | 1.0946 | 1.0945 | 1.0943 | 1.0942 | 1.0936 | 1.0928 | 1.092 | 1.0913
ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | YES | 16.5011 | 16.4729 | 16.4447 | 15.7784 | 15.7005 | 14.9892 | 14.4029 | 13.8151 | 9.6361 | 9.3987 | 8.6875 | 7.4803 | 6.6566 | 5.4296 | 15.3505 | 15.3174 | 15.2813 | 14.578 | 14.4697 | 13.7264 | 13.0983 | 9.7489 | 8.7768 | 8.5407 | 7.833 | 6.6316 | 5.8307 | 4.6732 | 14.59 | 14.5601 | 14.5293 | 13.8506 | 13.7621 | 13.0383 | 12.4356 | 9.6725 | 8.7003 | 8.4642 | 7.7565 | 6.555 | 5.5396 | 4.1479
| CHARLES AVENUE | CT |  |  | 16.5802 | 16.5554 | 16.5301 | 16.5238 | 16.3979 | 16.1785 | 15.973 | 15.7632 | 15.4954 | 15.3607 | 14.9494 | 9.0888 | 7.0925 | 5.4296 | 15.4141 | 15.3711 | 15.3184 | 15.2547 | 15.069 | 14.7979 | 14.5923 | 14.3825 | 14.1147 | 13.98 | 13.5688 | 8.544 | 6.4485 | 4.6732 | 14.6639 | 14.633 | 14.5985 | 14.5704 | 14.421 | 14.1785 | 13.9503 | 13.7095 | 13.4112 | 13.2434 | 12.7417 | 7.9365 | 5.875 | 4.1479
| CHARLES AVENUE | LW |  |  | 16.5011 | 16.4729 | 16.4447 | 16.4447 | 16.1909 | 15.8139 | 15.4229 | 15.0177 | 14.7037 | 14.546 | 14.0729 | 9.8247 | 8.6859 | 7.9842 | 15.3505 | 15.3174 | 15.2813 | 15.2616 | 14.986 | 14.5878 | 14.1789 | 13.7563 | 13.4253 | 13.2491 | 12.7214 | 8.9667 | 7.8298 | 7.13 | 14.59 | 14.5601 | 14.5293 | 14.5227 | 14.2615 | 13.8774 | 13.4794 | 13.0674 | 12.7467 | 12.5817 | 9.9297 | 8.8902 | 7.7533 | 7.0535
| CHARLES AVENUE | ST |  |  | 16.6691 | 16.6543 | 16.6395 | 15.7784 | 15.7005 | 14.9892 | 14.4029 | 13.8151 | 9.6361 | 9.3987 | 8.6875 | 7.4803 | 6.6566 | 5.8521 | 15.5128 | 15.489 | 15.4622 | 14.578 | 14.4697 | 13.7264 | 13.0983 | 9.7489 | 8.7768 | 8.5407 | 7.833 | 6.6316 | 5.8307 | 5.3126 | 14.7561 | 14.7382 | 14.7194 | 13.8506 | 13.7621 | 13.0383 | 12.4356 | 9.6725 | 8.7003 | 8.4642 | 7.7565 | 6.555 | 5.5396 | 4.6944
| CHARLES AVENUE | SP |  |  | 16.7528 | 16.7447 | 16.7365 | 16.3052 | 16.2698 | 15.2853 | 15.2498 | 15.2143 | 14.2297 | 14.0472 | 13.4989 | 9.3387 | 8.7827 | 8.49 | 15.6052 | 15.5959 | 15.5862 | 15.1533 | 15.109 | 14.114 | 14.0626 | 14.0114 | 13.0066 | 9.9903 | 9.4362 | 8.4798 | 7.9259 | 7.6352 | 14.8427 | 14.8342 | 14.8255 | 14.3937 | 14.3553 | 13.3672 | 13.3264 | 13.2857 | 12.2943 | 9.9139 | 9.3598 | 8.4034 | 7.8494 | 7.5587
CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | 17.5427 | 17.5419 | 17.541 | 17.5398 | 17.4803 | 16.8615 | 16.7223 | 16.3574 | 15.7197 | 15.5766 | 14.1268 | 13.3541 | 12.8373 | 12.5976 | 16.5112 | 16.5084 | 16.5044 | 16.4954 | 16.4207 | 15.8288 | 15.6635 | 15.2862 | 14.6365 | 13.6959 | 13.2627 | 12.4841 | 11.932 | 11.5737 | 16.9737 | 16.9712 | 16.9678 | 16.9605 | 16.8882 | 16.2915 | 16.1308 | 15.7557 | 13.6937 | 13.5484 | 13.1128 | 12.3302 | 11.8036 | 11.5542
| CHARLESTON | CT |  |  | 17.5427 | 17.5419 | 17.541 | 17.5398 | 17.5356 | 17.4663 | 17.409 | 17.3508 | 17.2533 | 17.1976 | 17.0288 | 16.512 | 15.8953 | 14.4114 | 16.5112 | 16.5084 | 16.5044 | 16.4958 | 16.4838 | 16.4068 | 16.342 | 16.2533 | 16.1258 | 16.0497 | 15.822 | 15.2096 | 13.7239 | 13.1265 | 16.9737 | 16.9712 | 16.9678 | 16.9605 | 16.9499 | 16.8743 | 16.8108 | 16.7276 | 16.6054 | 16.523 | 16.2754 | 15.6561 | 15.0394 | 13.2952
| CHARLESTON | LW |  |  | 17.5438 | 17.5438 | 17.5438 | 17.5438 | 17.4803 | 17.3372 | 17.1919 | 17.0418 | 16.8602 | 16.7798 | 16.5408 | 15.8358 | 14.0464 | 13.6461 | 16.5121 | 16.5096 | 16.5055 | 16.4954 | 16.4207 | 16.2667 | 16.1107 | 15.95 | 15.7582 | 15.6666 | 15.4014 | 14.6639 | 13.1773 | 12.7738 | 16.9746 | 16.9725 | 16.9692 | 16.9609 | 16.8882 | 16.7361 | 16.582 | 16.4233 | 16.2332 | 16.1436 | 15.8776 | 13.7983 | 13.024 | 12.6184
| CHARLESTON | ST |  |  | 17.5436 | 17.5435 | 17.5434 | 17.5433 | 17.5423 | 17.087 | 16.7223 | 16.3574 | 15.7197 | 15.5766 | 14.1268 | 13.3541 | 12.8373 | 12.5976 | 16.513 | 16.5116 | 16.5099 | 16.5066 | 16.5013 | 16.0408 | 15.6635 | 15.2862 | 14.6365 | 13.6959 | 13.2627 | 12.4841 | 11.932 | 11.5737 | 16.9753 | 16.9742 | 16.9727 | 16.97 | 16.9655 | 16.5059 | 16.1308 | 15.7557 | 13.6937 | 13.5484 | 13.1128 | 12.3302 | 11.8036 | 11.5542
| CHARLESTON | SP |  |  | 17.5437 | 17.5437 | 17.5437 | 17.5437 | 17.5437 | 16.8615 | 16.8615 | 16.8615 | 16.1794 | 16.0595 | 15.6997 | 14.032 | 13.6095 | 13.4749 | 16.5143 | 16.5141 | 16.5139 | 16.5137 | 16.5124 | 15.8288 | 15.8248 | 15.8207 | 15.1334 | 15.0051 | 14.621 | 13.1709 | 12.7463 | 12.6097 | 16.9764 | 16.9763 | 16.9761 | 16.9759 | 16.9749 | 16.2915 | 16.2882 | 16.2849 | 15.5985 | 15.4716 | 13.6741 | 13.023 | 12.597 | 12.4591
ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | 8.873 | 8.8719 | 7.4134 | 7.4124 | 7.4052 | 7.3971 | 7.3882 | 7.3783 | 7.3658 | 7.3613 | 7.2825 | 7.1331 | 6.4517 | 6.3729 | 8.8546 | 8.8539 | 7.4943 | 7.4921 | 7.4835 | 7.4741 | 7.4639 | 7.4525 | 7.4386 | 7.4325 | 7.3539 | 7.1877 | 6.6931 | 6.6014 | 8.9737 | 8.973 | 7.3433 | 7.3423 | 7.3351 | 7.327 | 7.3181 | 7.2866 | 7.2502 | 7.2197 | 7.1292 | 6.9609 | 6.3488 | 6.2581
| CLACHAN | CT |  |  | 8.873 | 8.8719 | 7.4134 | 7.4124 | 7.4052 | 7.3971 | 7.3882 | 7.3783 | 7.3658 | 7.3613 | 7.2825 | 7.1331 | 6.972 | 6.7686 | 8.8546 | 8.8539 | 7.4943 | 7.4921 | 7.4835 | 7.4741 | 7.4639 | 7.4525 | 7.4386 | 7.4325 | 7.3539 | 7.1877 | 7.0099 | 6.799 | 8.9737 | 8.973 | 7.3433 | 7.3423 | 7.3351 | 7.327 | 7.3181 | 7.2866 | 7.2502 | 7.2197 | 7.1292 | 6.9609 | 6.7809 | 6.5679
| CLACHAN | LW |  |  | 8.8743 | 8.8742 | 7.4156 | 7.4156 | 7.4096 | 7.4035 | 7.3972 | 7.3905 | 7.3807 | 7.3791 | 7.3743 | 7.3634 | 7.3543 | 7.3487 | 8.8554 | 8.8554 | 7.4973 | 7.497 | 7.4906 | 7.4841 | 7.4774 | 7.4703 | 7.4602 | 7.4581 | 7.4521 | 7.4393 | 7.4283 | 7.4208 | 8.9745 | 8.9745 | 7.3455 | 7.3455 | 7.3395 | 7.3334 | 7.3271 | 7.3203 | 7.3106 | 7.309 | 7.3042 | 7.2933 | 7.2595 | 7.2226
| CLACHAN | ST |  |  | 8.8743 | 8.8741 | 8.874 | 7.4153 | 7.412 | 7.4084 | 7.4049 | 7.4008 | 7.3947 | 7.3933 | 7.3898 | 7.3626 | 6.4517 | 6.3729 | 8.8553 | 8.8553 | 8.8552 | 7.4971 | 7.4937 | 7.4899 | 7.4855 | 7.4806 | 7.4737 | 7.4713 | 7.4647 | 7.442 | 6.6931 | 6.6014 | 8.9744 | 8.9744 | 8.9743 | 7.3452 | 7.3419 | 7.3383 | 7.3347 | 7.3307 | 7.3246 | 7.3232 | 7.3101 | 7.2184 | 6.3488 | 6.2581
| CLACHAN | SP |  |  | 8.8742 | 8.8741 | 8.874 | 8.8739 | 8.8734 | 8.8729 | 8.872 | 8.8711 | 8.8699 | 8.8683 | 8.8632 | 8.8576 | 8.8239 | 8.8065 | 8.8552 | 8.8551 | 8.855 | 8.8549 | 8.8545 | 8.854 | 8.8536 | 8.8531 | 8.8524 | 8.8514 | 8.848 | 8.845 | 8.8138 | 8.7989 | 8.9743 | 8.9742 | 8.9741 | 8.974 | 8.9735 | 8.9731 | 8.9727 | 8.9722 | 8.9714 | 8.9705 | 8.9671 | 8.9641 | 8.9329 | 8.9179
CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | 0.36846 | 0.36841 | 0.36836 | 0.36827 | 0.212 | 0.070259 | -0.071015 | -0.21166 | -0.39179 | -0.56807 | -1.2326 | -2.0919 | -3.495 | -4.0168 | 0.35368 | 0.35338 | 0.35293 | 0.35173 | 0.17574 | 0.0089475 | -0.15695 | -0.32197 | -0.53323 | -0.74071 | -1.5227 | -2.5321 | -4.1817 | -4.795 | 0.35485 | 0.35455 | 0.35435 | 0.35393 | 0.17629 | 0.0096976 | -0.15589 | -0.3206 | -0.53127 | -0.73811 | -1.5178 | -2.5241 | -4.1688 | -4.7802
| CLAONAIG | CT |  |  | 0.36846 | 0.36841 | 0.36836 | 0.36827 | 0.29222 | 0.23999 | 0.18809 | 0.12257 | 0.023478 | -0.10599 | -0.56065 | -1.1874 | -2.4719 | -3.2865 | 0.35368 | 0.35338 | 0.35296 | 0.352 | 0.27002 | 0.20876 | 0.14787 | 0.070764 | -0.045488 | -0.19773 | -0.73278 | -1.4679 | -2.9779 | -3.9353 | 0.35485 | 0.35455 | 0.35435 | 0.35393 | 0.27097 | 0.20946 | 0.14836 | 0.071394 | -0.044641 | -0.19659 | -0.73019 | -1.4631 | -2.9686 | -3.9231
| CLAONAIG | LW |  |  | 0.36853 | 0.36853 | 0.36853 | 0.36853 | 0.212 | 0.070259 | -0.071015 | -0.21166 | -0.39179 | -0.56807 | -1.2326 | -2.0919 | -3.495 | -4.0168 | 0.35372 | 0.35341 | 0.35293 | 0.35173 | 0.17574 | 0.0089475 | -0.15695 | -0.32197 | -0.53323 | -0.74071 | -1.5227 | -2.5321 | -4.1817 | -4.795 | 0.35488 | 0.35463 | 0.35444 | 0.35418 | 0.17629 | 0.0096976 | -0.15589 | -0.3206 | -0.53127 | -0.73811 | -1.5178 | -2.5241 | -4.1688 | -4.7802
| CLAONAIG | ST |  |  | 0.36851 | 0.36849 | 0.36848 | 0.36847 | 0.36825 | 0.24984 | 0.19859 | 0.13262 | 0.035769 | -0.092543 | -0.54375 | -1.1571 | -1.9631 | -2.9275 | 0.35382 | 0.35366 | 0.35345 | 0.35306 | 0.28066 | 0.22021 | 0.16007 | 0.082312 | -0.03141 | -0.18232 | -0.71339 | -1.4342 | -2.3797 | -3.5142 | 0.35506 | 0.35481 | 0.35462 | 0.35446 | 0.28166 | 0.22095 | 0.16055 | 0.082923 | -0.030585 | -0.18121 | -0.71085 | -1.4295 | -2.3722 | -3.5033
| CLAONAIG | SP |  |  | 0.36848 | 0.36845 | 0.36843 | 0.3684 | 0.36839 | 0.36838 | 0.36836 | 0.27687 | 0.24413 | 0.19905 | 0.0055447 | -0.23718 | -0.46019 | -0.66123 | 0.35394 | 0.35389 | 0.35384 | 0.35379 | 0.34981 | 0.34979 | 0.28076 | 0.25191 | 0.21344 | 0.1605 | -0.067328 | -0.35277 | -0.61268 | -0.84833 | 0.35526 | 0.3552 | 0.35514 | 0.35507 | 0.35405 | 0.35404 | 0.28175 | 0.25278 | 0.21415 | 0.16098 | -0.066432 | -0.35133 | -0.61049 | -0.84544
CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | 32.5415 | 32.4932 | 32.4289 | 32.3057 | 32.1995 | 31.7439 | 31.3759 | 31.007 | 30.3797 | 30.2371 | 29.8194 | 29.074 | 28.5091 | 28.2393 | 29.0552 | 29.0013 | 28.9295 | 28.7918 | 28.6 | 27.9591 | 27.5092 | 27.0602 | 26.3543 | 26.1896 | 25.6981 | 24.8306 | 22.0054 | 21.7219 | 28.5315 | 28.4769 | 28.4043 | 28.3508 | 28.3272 | 27.823 | 27.4998 | 27.1292 | 26.5002 | 26.3571 | 25.9284 | 25.1831 | 24.6182 | 21.64
| CLAYHILLS | CT |  |  | 32.5653 | 32.5364 | 32.494 | 32.3948 | 32.2808 | 32.1223 | 32.0445 | 31.9719 | 31.8606 | 31.7939 | 31.5903 | 31.013 | 30.3362 | 29.7664 | 29.082 | 29.05 | 29.0028 | 28.8923 | 28.7663 | 28.5793 | 28.4043 | 28.2652 | 28.0906 | 27.9906 | 27.6881 | 26.9512 | 26.0817 | 25.3782 | 28.5587 | 28.5263 | 28.4786 | 28.3668 | 28.3313 | 28.2465 | 28.1719 | 28.0986 | 27.9866 | 27.9192 | 27.7134 | 27.1327 | 26.4453 | 25.8754
| CLAYHILLS | LW |  |  | 32.585 | 32.5713 | 32.5497 | 32.4955 | 32.4353 | 32.3023 | 32.1705 | 32.0401 | 31.9247 | 31.853 | 31.6583 | 31.0739 | 30.3992 | 30.0459 | 29.1037 | 29.0885 | 29.0642 | 29.0037 | 28.9364 | 28.7964 | 28.6579 | 28.5208 | 28.3851 | 28.2592 | 27.8872 | 27.1655 | 26.3526 | 25.8383 | 28.5806 | 28.5652 | 28.5407 | 28.4794 | 28.4113 | 28.2867 | 28.2065 | 28.1264 | 28.0464 | 27.9808 | 27.7843 | 27.1969 | 26.5192 | 26.1549
| CLAYHILLS | ST |  |  | 32.5415 | 32.4932 | 32.4289 | 32.3057 | 32.1995 | 31.7439 | 31.3759 | 31.007 | 30.3797 | 30.2371 | 29.8194 | 29.074 | 28.5091 | 28.2393 | 29.0552 | 29.0013 | 28.9295 | 28.7918 | 28.6 | 27.9591 | 27.5092 | 27.0602 | 26.3543 | 26.1896 | 25.6981 | 24.8306 | 22.0054 | 21.7219 | 28.5315 | 28.4769 | 28.4043 | 28.3508 | 28.3272 | 27.8696 | 27.4998 | 27.1292 | 26.5002 | 26.3571 | 25.9284 | 25.1831 | 24.6182 | 21.64
| CLAYHILLS | SP |  |  | 32.5882 | 32.5817 | 32.5743 | 32.5663 | 32.529 | 31.8397 | 31.7891 | 31.739 | 31.0296 | 30.8962 | 30.4973 | 29.8352 | 29.3975 | 29.1962 | 29.1075 | 29.1004 | 29.0924 | 29.0836 | 29.0419 | 28.3474 | 28.2908 | 28.2349 | 27.5179 | 27.3824 | 26.9773 | 26.2682 | 25.7521 | 25.478 | 28.5845 | 28.5773 | 28.5692 | 28.5603 | 28.5182 | 27.823 | 27.7658 | 27.7103 | 27.0581 | 26.941 | 26.5891 | 25.9633 | 25.5248 | 25.3228
DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | NO | 3.3238 | 3.3235 | 3.3232 | 3.3226 | 3.315 | 3.3062 | 3.2972 | 3.2875 | 3.2737 | 3.271 | 3.2608 | 3.2009 | 3.1525 | 3.1089 | 3.0859 | 3.0855 | 3.0852 | 3.0847 | 3.0773 | 3.0686 | 3.0596 | 3.05 | 3.0363 | 3.0338 | 3.0239 | 2.9664 | 2.9194 | 2.3978 | 3.1153 | 3.115 | 3.1148 | 3.1144 | 3.1073 | 3.0988 | 3.0901 | 3.0807 | 3.0672 | 3.0649 | 3.0557 | 3.0038 | 2.9601 | 2.4327
| COLDBACKIE | CT |  |  | 3.3238 | 3.3235 | 3.3232 | 3.3226 | 3.3157 | 3.3082 | 3.3001 | 3.2908 | 3.2785 | 3.2747 | 3.2634 | 3.2009 | 3.1525 | 3.1089 | 3.0859 | 3.0855 | 3.0852 | 3.0847 | 3.0779 | 3.0705 | 3.0624 | 3.0534 | 3.0414 | 3.0379 | 3.0274 | 2.9664 | 2.9194 | 2.3978 | 3.1153 | 3.115 | 3.1148 | 3.1144 | 3.1077 | 3.1005 | 3.0926 | 3.0842 | 3.0729 | 3.07 | 3.0616 | 3.0038 | 2.9601 | 2.4327
| COLDBACKIE | LW |  |  | 3.3242 | 3.3241 | 3.324 | 3.3237 | 3.315 | 3.3062 | 3.2972 | 3.2875 | 3.2737 | 3.271 | 3.2608 | 3.229 | 3.2053 | 3.1959 | 3.0862 | 3.0861 | 3.086 | 3.0858 | 3.0773 | 3.0686 | 3.0596 | 3.05 | 3.0363 | 3.0338 | 3.0239 | 2.9925 | 2.9693 | 2.9604 | 3.1156 | 3.1156 | 3.1156 | 3.1156 | 3.1073 | 3.0988 | 3.0901 | 3.0807 | 3.0672 | 3.0649 | 3.0557 | 3.0254 | 3.0033 | 2.9955
| COLDBACKIE | ST |  |  | 3.3242 | 3.3241 | 3.3241 | 3.3239 | 3.3199 | 3.3155 | 3.311 | 3.3059 | 3.2982 | 3.296 | 3.2898 | 3.2652 | 3.2303 | 3.2167 | 3.0862 | 3.0861 | 3.0861 | 3.086 | 3.082 | 3.0777 | 3.0733 | 3.0684 | 3.0608 | 3.0588 | 3.0531 | 3.0294 | 2.9955 | 2.9828 | 3.1156 | 3.1156 | 3.1156 | 3.1155 | 3.1116 | 3.1074 | 3.1034 | 3.0988 | 3.0916 | 3.0901 | 3.0857 | 3.0641 | 3.0322 | 3.0216
| COLDBACKIE | SP |  |  | 3.3242 | 3.3241 | 3.3241 | 3.3241 | 3.3235 | 3.3229 | 3.3221 | 3.3212 | 3.3199 | 3.3185 | 3.3137 | 3.309 | 3.2678 | 3.2529 | 3.0862 | 3.0861 | 3.0861 | 3.0861 | 3.0855 | 3.0849 | 3.0842 | 3.0834 | 3.0821 | 3.0808 | 3.0762 | 3.0718 | 3.031 | 3.0164 | 3.1155 | 3.1155 | 3.1155 | 3.1155 | 3.1149 | 3.1143 | 3.1138 | 3.1131 | 3.1121 | 3.1109 | 3.1068 | 3.1032 | 3.0631 | 3.0493
DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | 0.56639 | 0.56631 | 0.5662 | 0.56607 | 0.56558 | 0.56501 | 0.56434 | 0.56358 | 0.56273 | 0.56222 | 0.56056 | 0.55677 | 0.49115 | 0.46525 | 0.5462 | 0.54595 | 0.54561 | 0.54489 | 0.54379 | 0.54266 | 0.54151 | 0.54006 | 0.53921 | 0.5387 | 0.53704 | 0.48957 | 0.46697 | 0.43867 | 0.54869 | 0.54835 | 0.54813 | 0.54777 | 0.54712 | 0.54656 | 0.54588 | 0.54512 | 0.54427 | 0.54377 | 0.5421 | 0.49174 | 0.46908 | 0.4407
| COLINTRAIVE | CT |  |  | 0.56639 | 0.56631 | 0.5662 | 0.56607 | 0.56558 | 0.56501 | 0.56434 | 0.56358 | 0.56273 | 0.56222 | 0.56056 | 0.55677 | 0.49115 | 0.46525 | 0.5462 | 0.54595 | 0.54561 | 0.54489 | 0.54379 | 0.54266 | 0.54151 | 0.54006 | 0.53921 | 0.5387 | 0.53704 | 0.48957 | 0.46697 | 0.43867 | 0.54869 | 0.54835 | 0.54813 | 0.54777 | 0.54712 | 0.54656 | 0.54588 | 0.54512 | 0.54427 | 0.54377 | 0.5421 | 0.49174 | 0.46908 | 0.4407
| COLINTRAIVE | LW |  |  | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.54631 | 0.54611 | 0.54579 | 0.545 | 0.54416 | 0.54346 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.54879 | 0.54852 | 0.54839 | 0.54808 | 0.54806 | 0.54806 | 0.54806 | 0.54806 | 0.54806 | 0.54806 | 0.54806 | 0.54806 | 0.54806 | 0.54806
| COLINTRAIVE | ST |  |  | 0.56651 | 0.5665 | 0.5665 | 0.56649 | 0.56641 | 0.56632 | 0.56622 | 0.56611 | 0.56597 | 0.56593 | 0.5658 | 0.56559 | 0.56447 | 0.56383 | 0.54638 | 0.54627 | 0.54614 | 0.54588 | 0.54547 | 0.54497 | 0.54449 | 0.54399 | 0.54353 | 0.54241 | 0.54228 | 0.54207 | 0.54094 | 0.49368 | 0.54891 | 0.54874 | 0.54854 | 0.54841 | 0.5482 | 0.54795 | 0.54777 | 0.54765 | 0.54751 | 0.54747 | 0.54735 | 0.54713 | 0.54601 | 0.49584
| COLINTRAIVE | SP |  |  | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.56652 | 0.54649 | 0.54647 | 0.54646 | 0.54644 | 0.54634 | 0.54623 | 0.5461 | 0.54597 | 0.5458 | 0.54528 | 0.54385 | 0.543 | 0.543 | 0.543 | 0.54907 | 0.54905 | 0.54903 | 0.549 | 0.54885 | 0.54867 | 0.54851 | 0.54846 | 0.5484 | 0.54819 | 0.54806 | 0.54806 | 0.54806 | 0.54806
STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | 2.2875 | 2.2854 | 2.283 | 2.2796 | 2.1256 | 1.9574 | 1.7835 | 1.597 | 1.3288 | 1.2826 | 1.1054 | -0.46506 | -1.0951 | -1.6624 | 1.8786 | 1.8467 | 1.7996 | 1.6894 | 1.4559 | 1.2137 | 0.9648 | 0.77156 | 0.52351 | 0.43128 | 0.17914 | -1.2181 | -1.8847 | -2.4881 | 1.9407 | 1.9369 | 1.9319 | 1.9222 | 1.7802 | 1.6118 | 1.4248 | 1.2349 | 0.98251 | 0.90132 | 0.65956 | -0.9612 | -1.6108 | -2.2004
| COLL | CT |  |  | 2.2875 | 2.2854 | 2.283 | 2.2796 | 2.1609 | 2.032 | 1.8472 | 1.661 | 1.4199 | 1.3352 | 1.1054 | -0.46506 | -1.0951 | -1.6624 | 1.8786 | 1.8467 | 1.7996 | 1.6894 | 1.4559 | 1.2137 | 0.9648 | 0.77156 | 0.52351 | 0.43128 | 0.17914 | -1.2181 | -1.8847 | -2.4881 | 1.9407 | 1.9369 | 1.9319 | 1.9222 | 1.7969 | 1.6502 | 1.4248 | 1.2349 | 0.99006 | 0.90132 | 0.65956 | -0.9612 | -1.6108 | -2.2004
| COLL | LW |  |  | 2.2905 | 2.2905 | 2.2905 | 2.2905 | 2.1256 | 1.9574 | 1.7835 | 1.597 | 1.3288 | 1.2826 | 1.1503 | 0.13228 | -0.087301 | -0.16495 | 1.9142 | 1.9134 | 1.9119 | 1.9084 | 1.7396 | 1.5676 | 1.39 | 1.1998 | 0.928 | 0.87795 | 0.73422 | -0.17204 | -0.41016 | -0.50617 | 1.9457 | 1.9456 | 1.9455 | 1.9453 | 1.7802 | 1.6118 | 1.4377 | 1.251 | 0.98251 | 0.93609 | 0.80313 | -0.152 | -0.37266 | -0.45138
| COLL | ST |  |  | 2.2897 | 2.2892 | 2.2886 | 2.288 | 2.2071 | 2.12 | 2.036 | 1.9407 | 1.7908 | 1.759 | 1.6782 | 0.86606 | 0.25446 | -0.05025 | 1.8928 | 1.874 | 1.8492 | 1.8018 | 1.6574 | 1.4941 | 1.3764 | 1.2481 | 1.0659 | 1.0007 | 0.82293 | 0.076314 | -0.55834 | -0.886 | 1.9436 | 1.9421 | 1.9401 | 1.9367 | 1.8522 | 1.7606 | 1.6746 | 1.5774 | 1.4257 | 1.3919 | 1.2735 | 0.42177 | -0.20217 | -0.51916
| COLL | SP |  |  | 2.2887 | 2.2878 | 2.2868 | 2.2858 | 2.2743 | 2.2632 | 2.2518 | 2.2391 | 2.2182 | 2.1947 | 2.111 | 2.0379 | 1.2292 | 0.93005 | 1.9095 | 1.9058 | 1.9018 | 1.8974 | 1.8676 | 1.8347 | 1.8114 | 1.7868 | 1.7509 | 1.7144 | 1.5933 | 1.4615 | 0.59765 | 0.24634 | 1.9437 | 1.9426 | 1.9414 | 1.9402 | 1.9277 | 1.9153 | 1.9032 | 1.8898 | 1.8681 | 1.8438 | 1.7579 | 1.6814 | 0.86946 | 0.56727
CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | 28.4706 | 28.4345 | 28.3948 | 27.6894 | 27.6036 | 26.8296 | 26.1901 | 25.5509 | 24.5002 | 22.2967 | 21.5597 | 20.3054 | 19.4685 | 19.042 | 26.1679 | 26.1274 | 26.0808 | 25.3779 | 25.2847 | 24.5017 | 23.8513 | 23.2014 | 20.4694 | 20.2224 | 19.4814 | 18.221 | 17.3781 | 16.9455 | 25.4532 | 25.421 | 25.3877 | 24.68 | 24.6009 | 23.835 | 23.2053 | 22.5757 | 20.3827 | 20.1355 | 19.3938 | 18.1322 | 17.2882 | 16.8545
| COMMERCE STREET | CT |  |  | 28.5614 | 28.5338 | 28.5039 | 28.4865 | 28.3545 | 28.1256 | 27.9165 | 27.7063 | 27.4382 | 27.295 | 26.8663 | 24.5404 | 21.3964 | 20.7372 | 26.259 | 26.2279 | 26.1926 | 26.1626 | 26.017 | 25.7748 | 25.5527 | 25.3289 | 25.0473 | 24.8897 | 24.4181 | 20.6884 | 19.2916 | 18.6227 | 25.5437 | 25.5194 | 25.4942 | 25.4883 | 25.3686 | 25.1517 | 24.9543 | 24.7565 | 24.5005 | 24.3704 | 23.9804 | 20.5977 | 19.1991 | 18.5284
| COMMERCE STREET | LW |  |  | 28.4706 | 28.4345 | 28.3948 | 28.3711 | 28.0733 | 27.6425 | 27.1973 | 26.7375 | 26.2632 | 26.067 | 25.4868 | 24.278 | 21.3734 | 20.6252 | 26.1679 | 26.1274 | 26.0808 | 26.0396 | 25.7224 | 25.2727 | 24.8089 | 24.3309 | 23.8389 | 23.6234 | 22.979 | 20.4907 | 19.255 | 18.4941 | 25.4532 | 25.421 | 25.3877 | 25.3797 | 25.0994 | 24.6858 | 24.2574 | 23.814 | 23.3558 | 23.1769 | 22.6406 | 20.398 | 19.0896 | 18.0833
| COMMERCE STREET | ST |  |  | 28.6539 | 28.6359 | 28.6169 | 27.6894 | 27.6036 | 26.8296 | 26.1901 | 25.5509 | 24.5002 | 22.2967 | 21.5597 | 20.3054 | 19.4685 | 19.042 | 26.3531 | 26.3328 | 26.3109 | 25.3779 | 25.2847 | 24.5017 | 23.8513 | 23.2014 | 20.4694 | 20.2224 | 19.4814 | 18.221 | 17.3781 | 16.9455 | 25.6349 | 25.6188 | 25.6024 | 24.68 | 24.6009 | 23.835 | 23.2053 | 22.5757 | 20.3827 | 20.1355 | 19.3938 | 18.1322 | 17.2882 | 16.8545
| COMMERCE STREET | SP |  |  | 28.7472 | 28.7393 | 28.7312 | 28.2707 | 28.2301 | 27.1583 | 27.1161 | 27.0739 | 25.9998 | 25.7983 | 25.1942 | 22.1729 | 21.4965 | 21.2544 | 26.4485 | 26.4402 | 26.4318 | 25.9709 | 25.9282 | 24.8539 | 24.8084 | 24.7629 | 23.6845 | 23.4791 | 21.1274 | 20.1015 | 19.4228 | 19.1787 | 25.7263 | 25.7186 | 25.7108 | 25.2507 | 25.212 | 24.1425 | 24.1033 | 24.0641 | 22.9938 | 22.7958 | 21.0415 | 20.0152 | 19.3361 | 19.0916
ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | 0.061457 | 0.061457 | 0.058619 | 0.055825 | 0.053762 | 0.047731 | 0.044194 | 0.040562 | 0.036823 | 0.032971 | 0.025912 | 0.014445 | 0.0042647 | -0.0055911 | 0.056042 | 0.055909 | 0.054122 | 0.052854 | 0.047107 | 0.043521 | 0.03984 | 0.036065 | 0.032184 | 0.02818 | 0.020739 | 0.0086555 | -0.0020991 | -0.012572 | 0.055862 | 0.05581 | 0.053029 | 0.049218 | 0.046108 | 0.042437 | 0.038669 | 0.034761 | 0.030744 | 0.0266 | 0.018854 | 0.0062757 | -0.0048644 | -0.015653
| COMRIE | CT |  |  | 0.061457 | 0.061457 | 0.058619 | 0.055825 | 0.053762 | 0.047731 | 0.044194 | 0.040562 | 0.036823 | 0.032971 | 0.025912 | 0.014445 | 0.0042647 | -0.0055911 | 0.056051 | 0.055944 | 0.054122 | 0.052854 | 0.047107 | 0.043521 | 0.03984 | 0.036065 | 0.032184 | 0.02818 | 0.020739 | 0.0086555 | -0.0020991 | -0.012572 | 0.055866 | 0.055823 | 0.053029 | 0.049218 | 0.046108 | 0.042437 | 0.038669 | 0.034761 | 0.030744 | 0.0266 | 0.018854 | 0.0062757 | -0.0048644 | -0.015653
| COMRIE | LW |  |  | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.047585 | 0.04369 | 0.039833 | 0.056042 | 0.055909 | 0.05573 | 0.05554 | 0.05554 | 0.05554 | 0.05554 | 0.049994 | 0.049113 | 0.04816 | 0.045339 | 0.040795 | 0.036223 | 0.031694 | 0.055862 | 0.05581 | 0.055733 | 0.055637 | 0.055637 | 0.055637 | 0.055637 | 0.055637 | 0.049166 | 0.048238 | 0.045477 | 0.040932 | 0.036358 | 0.031828
| COMRIE | ST |  |  | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.056096 | 0.056031 | 0.055944 | 0.055795 | 0.05563 | 0.055547 | 0.05554 | 0.05554 | 0.05554 | 0.05554 | 0.05554 | 0.048898 | 0.046917 | 0.044932 | 0.055883 | 0.055858 | 0.055824 | 0.055758 | 0.055696 | 0.055637 | 0.055637 | 0.055637 | 0.055637 | 0.055637 | 0.055637 | 0.048957 | 0.047027 | 0.04507
| COMRIE | SP |  |  | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.061457 | 0.056159 | 0.05615 | 0.05614 | 0.056128 | 0.056065 | 0.05599 | 0.055902 | 0.055826 | 0.055736 | 0.055649 | 0.055547 | 0.05554 | 0.05554 | 0.05554 | 0.055908 | 0.055905 | 0.055901 | 0.055896 | 0.055871 | 0.055842 | 0.055807 | 0.055773 | 0.055735 | 0.055707 | 0.055637 | 0.055637 | 0.055637 | 0.055637
TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | 5.7228 | 5.7221 | 5.7213 | 5.72 | 5.7108 | 5.7005 | 5.689 | 5.6764 | 5.6604 | 5.6549 | 5.638 | 5.1972 | 3.9563 | 3.7376 | 5.062 | 5.059 | 5.0548 | 5.0454 | 5.0274 | 5.0086 | 4.9917 | 4.9652 | 4.9361 | 4.9169 | 4.8703 | 3.8388 | 3.6204 | 3.3833 | 5.2331 | 5.2323 | 5.2315 | 5.2303 | 5.2211 | 5.2107 | 5.1993 | 5.1867 | 5.1707 | 5.1651 | 5.1482 | 3.8764 | 3.6117 | 3.3812
| CONNEL | CT |  |  | 5.7228 | 5.7221 | 5.7213 | 5.72 | 5.7108 | 5.7005 | 5.689 | 5.6764 | 5.6604 | 5.6549 | 5.638 | 5.1972 | 3.9563 | 3.7376 | 5.062 | 5.059 | 5.0548 | 5.0454 | 5.0274 | 5.0086 | 4.9917 | 4.9652 | 4.9361 | 4.9169 | 4.8703 | 3.8388 | 3.6204 | 3.3833 | 5.2331 | 5.2323 | 5.2315 | 5.2303 | 5.2211 | 5.2107 | 5.1993 | 5.1867 | 5.1707 | 5.1651 | 5.1482 | 3.8764 | 3.6117 | 3.3812
| CONNEL | LW |  |  | 5.7239 | 5.7239 | 5.7239 | 5.7239 | 5.7159 | 5.7078 | 5.6994 | 5.6904 | 5.6774 | 5.6752 | 5.6688 | 5.2684 | 5.1815 | 5.174 | 5.0642 | 5.0628 | 5.0604 | 5.0546 | 5.0402 | 5.0258 | 5.0112 | 4.9971 | 4.9803 | 4.9739 | 4.9553 | 3.91 | 3.8615 | 3.854 | 5.2341 | 5.2341 | 5.2341 | 5.2341 | 5.2262 | 5.2181 | 5.2097 | 5.2006 | 5.1877 | 5.1855 | 5.1791 | 4.7729 | 4.6849 | 3.9948
| CONNEL | ST |  |  | 5.7236 | 5.7235 | 5.7233 | 5.7232 | 5.7181 | 5.7124 | 5.7067 | 5.7002 | 5.6908 | 5.6886 | 5.6826 | 5.4718 | 5.3877 | 5.3658 | 5.0641 | 5.0628 | 5.0611 | 5.058 | 5.049 | 5.0386 | 5.0177 | 5.0006 | 4.9817 | 4.9698 | 4.9377 | 4.7956 | 3.9402 | 3.9183 | 5.2339 | 5.2338 | 5.2336 | 5.2334 | 5.2283 | 5.2227 | 5.217 | 5.2105 | 5.2011 | 5.1988 | 5.1928 | 4.9791 | 4.8945 | 3.9954
| CONNEL | SP |  |  | 5.7235 | 5.7232 | 5.723 | 5.7228 | 5.7222 | 5.7216 | 5.7211 | 5.7204 | 5.7194 | 5.718 | 5.713 | 5.7088 | 5.6653 | 5.6412 | 5.065 | 5.0646 | 5.0642 | 5.0638 | 5.0621 | 5.0602 | 5.0545 | 5.0488 | 5.0414 | 5.0341 | 5.0153 | 4.9938 | 4.9351 | 4.897 | 5.2337 | 5.2335 | 5.2333 | 5.2331 | 5.2325 | 5.2319 | 5.2313 | 5.2307 | 5.2296 | 5.2282 | 5.2233 | 5.2191 | 5.1756 | 5.1515
BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | YES | 8.8714 | 8.8689 | 8.866 | 8.8618 | 8.8479 | 8.8313 | 8.8121 | 8.7898 | 8.7648 | 8.7504 | 8.7027 | 5.9488 | 5.4466 | 4.7786 | 7.8348 | 7.8173 | 7.792 | 7.7342 | 7.6626 | 7.5893 | 7.5143 | 7.456 | 5.7482 | 5.6562 | 5.3787 | 4.617 | 4.0573 | 3.3327 | 7.4897 | 7.4799 | 7.4661 | 7.4359 | 7.394 | 7.3499 | 7.3035 | 7.2661 | 7.2346 | 7.2169 | 5.4948 | 4.6701 | 4.138 | 3.4405
| CONON BRIDGE | CT |  |  | 8.8714 | 8.8689 | 8.866 | 8.8618 | 8.8479 | 8.8313 | 8.8121 | 8.7898 | 8.7648 | 8.7504 | 8.7027 | 5.9488 | 5.4466 | 4.7786 | 7.8348 | 7.8173 | 7.792 | 7.7342 | 7.6626 | 7.5893 | 7.5143 | 7.456 | 5.7482 | 5.6562 | 5.3787 | 4.617 | 4.0573 | 3.3327 | 7.4897 | 7.4799 | 7.4661 | 7.4359 | 7.394 | 7.3499 | 7.3035 | 7.2661 | 7.2346 | 7.2169 | 5.4948 | 4.6701 | 4.138 | 3.4405
| CONON BRIDGE | LW |  |  | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.8751 | 8.5382 | 8.5382 | 8.5382 | 7.8543 | 7.8533 | 7.8517 | 7.8477 | 7.8432 | 7.8389 | 7.8346 | 7.8305 | 7.8264 | 7.822 | 7.809 | 7.5135 | 7.4924 | 7.4715 | 7.5011 | 7.5006 | 7.4998 | 7.4979 | 7.4957 | 7.4936 | 7.4916 | 7.4895 | 7.4876 | 7.4854 | 7.4791 | 7.1201 | 7.1099 | 7.0997
| CONON BRIDGE | ST |  |  | 8.8743 | 8.8737 | 8.8731 | 8.8724 | 8.8668 | 8.8601 | 8.8522 | 8.8432 | 8.8332 | 8.8299 | 8.8199 | 8.6348 | 8.5481 | 8.499 | 7.8478 | 7.8417 | 7.8337 | 7.8187 | 7.7936 | 7.7636 | 7.7307 | 7.6972 | 7.6631 | 7.6345 | 7.5513 | 5.6124 | 5.288 | 5.0022 | 7.4975 | 7.4942 | 7.49 | 7.4824 | 7.4673 | 7.4493 | 7.4293 | 7.4084 | 7.3866 | 7.3711 | 7.3255 | 5.6636 | 5.3566 | 5.088
| CONON BRIDGE | SP |  |  | 8.8736 | 8.8728 | 8.8719 | 8.871 | 8.8709 | 8.8707 | 8.8706 | 8.8704 | 8.8702 | 8.8689 | 8.8647 | 8.8614 | 8.8401 | 8.7938 | 7.8525 | 7.8509 | 7.8491 | 7.8472 | 7.8413 | 7.8344 | 7.8259 | 7.8174 | 7.8067 | 7.7956 | 7.7629 | 7.7154 | 7.6523 | 7.5665 | 7.4994 | 7.4982 | 7.4969 | 7.4955 | 7.4926 | 7.4892 | 7.485 | 7.4808 | 7.4755 | 7.4694 | 7.4513 | 7.4266 | 7.385 | 7.3195
GRUDIE BRIDGE | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | 0.80689 | 0.80683 | 0.72217 | 0.6544 | 0.59092 | 0.41914 | 0.31745 | 0.21128 | 0.096656 | -0.021321 | -0.23292 | -0.57761 | -0.87991 | -1.1759 | 0.73517 | 0.73493 | 0.68807 | 0.65701 | 0.48263 | 0.38317 | 0.27978 | 0.17226 | 0.061379 | -0.052449 | -0.2581 | -0.5931 | -0.8878 | -1.1765 | 0.71007 | 0.70994 | 0.63002 | 0.56177 | 0.44056 | 0.33649 | 0.22924 | 0.11803 | 0.0023395 | -0.11638 | -0.33066 | -0.68081 | -0.98807 | -1.2888
| CONON FALLS | CT |  |  | 0.80689 | 0.80683 | 0.72217 | 0.6544 | 0.59092 | 0.41914 | 0.31745 | 0.21128 | 0.096656 | -0.021321 | -0.23292 | -0.57761 | -0.87991 | -1.1759 | 0.73517 | 0.73493 | 0.68807 | 0.65701 | 0.48263 | 0.38317 | 0.27978 | 0.17226 | 0.061379 | -0.052449 | -0.2581 | -0.5931 | -0.8878 | -1.1765 | 0.71007 | 0.70994 | 0.63002 | 0.56177 | 0.44056 | 0.33649 | 0.22924 | 0.11803 | 0.0023395 | -0.11638 | -0.33066 | -0.68081 | -0.98807 | -1.2888
| CONON FALLS | LW |  |  | 0.80698 | 0.80698 | 0.76944 | 0.73191 | 0.69452 | 0.66553 | 0.63738 | 0.60914 | 0.5831 | 0.47476 | 0.4027 | 0.28109 | 0.15645 | 0.022383 | 0.73524 | 0.73502 | 0.70473 | 0.69006 | 0.67528 | 0.66049 | 0.64572 | 0.63093 | 0.475 | 0.43857 | 0.36477 | 0.24026 | 0.11317 | -0.016941 | 0.71015 | 0.71007 | 0.67253 | 0.6362 | 0.605 | 0.57371 | 0.54245 | 0.46939 | 0.43215 | 0.39471 | 0.31875 | 0.19063 | 0.059869 | -0.07526
| CONON FALLS | ST |  |  | 0.80698 | 0.80698 | 0.78195 | 0.75693 | 0.73201 | 0.70699 | 0.68501 | 0.66583 | 0.64674 | 0.62648 | 0.49623 | 0.37333 | 0.24794 | 0.11954 | 0.73532 | 0.73522 | 0.71376 | 0.70051 | 0.69109 | 0.68153 | 0.67123 | 0.66093 | 0.6507 | 0.63909 | 0.45957 | 0.33299 | 0.20389 | 0.071734 | 0.71019 | 0.71014 | 0.68515 | 0.66011 | 0.63728 | 0.61671 | 0.59542 | 0.57408 | 0.55286 | 0.49315 | 0.4159 | 0.28533 | 0.15219 | 0.015912
| CONON FALLS | SP |  |  | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.73543 | 0.73541 | 0.7354 | 0.73538 | 0.73527 | 0.73515 | 0.73485 | 0.73454 | 0.73416 | 0.73348 | 0.73157 | 0.72859 | 0.72574 | 0.7232 | 0.71023 | 0.71022 | 0.71021 | 0.71021 | 0.71017 | 0.71012 | 0.71 | 0.70988 | 0.70973 | 0.70946 | 0.70871 | 0.70754 | 0.70641 | 0.70536
DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | 23.4367 | 23.4087 | 23.3807 | 22.722 | 22.6511 | 21.9528 | 21.3799 | 20.8067 | 19.8571 | 19.6317 | 18.9555 | 14.0972 | 13.4455 | 13.0477 | 22.0966 | 22.0586 | 22.0148 | 21.3292 | 21.2224 | 20.4814 | 19.8463 | 19.2124 | 14.6035 | 14.3781 | 13.702 | 12.5523 | 11.9006 | 11.5028 | 20.5489 | 20.5081 | 20.4597 | 19.7664 | 19.6493 | 18.9009 | 18.3279 | 17.7547 | 14.62 | 14.392 | 13.7081 | 12.546 | 11.8821 | 11.4722
| CONSTABLE STREET | CT |  |  | 23.5198 | 23.498 | 23.4763 | 23.4751 | 23.3664 | 23.1682 | 22.9869 | 22.8049 | 22.5689 | 22.4521 | 22.1002 | 19.9999 | 18.8076 | 14.4096 | 22.1778 | 22.1456 | 22.1083 | 22.07 | 21.9214 | 21.6842 | 21.4647 | 21.2345 | 20.9513 | 20.7834 | 20.28 | 14.7463 | 13.5541 | 12.8647 | 20.6295 | 20.5944 | 20.5525 | 20.5036 | 20.3436 | 20.1162 | 19.935 | 19.753 | 19.517 | 19.4001 | 19.0483 | 14.7303 | 13.5186 | 12.8099
| CONSTABLE STREET | LW |  |  | 23.4367 | 23.4087 | 23.3807 | 23.3807 | 23.1286 | 22.7544 | 22.3662 | 21.9639 | 21.5477 | 21.3911 | 21.0478 | 20.0243 | 18.9043 | 14.5093 | 22.0966 | 22.0586 | 22.0148 | 21.9753 | 21.6793 | 21.262 | 20.8317 | 20.3883 | 19.9318 | 19.7317 | 19.2596 | 14.7708 | 13.6508 | 12.9643 | 20.5489 | 20.5081 | 20.4597 | 20.4088 | 20.1002 | 19.7024 | 19.3142 | 18.912 | 18.4957 | 18.3392 | 17.9958 | 14.7602 | 13.6237 | 12.9209
| CONSTABLE STREET | ST |  |  | 23.6046 | 23.5905 | 23.5764 | 22.722 | 22.6511 | 21.9528 | 21.3799 | 20.8067 | 19.8571 | 19.6317 | 18.9555 | 14.0972 | 13.4455 | 13.0477 | 22.2622 | 22.2378 | 22.21 | 21.3292 | 21.2224 | 20.4814 | 19.8463 | 19.2124 | 14.6035 | 14.3781 | 13.702 | 12.5523 | 11.9006 | 11.5028 | 20.7138 | 20.6865 | 20.6547 | 19.7664 | 19.6493 | 18.9009 | 18.3279 | 17.7547 | 14.62 | 14.392 | 13.7081 | 12.546 | 11.8821 | 11.4722
| CONSTABLE STREET | SP |  |  | 23.6885 | 23.6814 | 23.6743 | 23.2471 | 23.2121 | 22.2354 | 22.2003 | 22.1653 | 21.1886 | 21.009 | 20.47 | 19.5339 | 19.0399 | 18.8144 | 22.3569 | 22.3489 | 22.3408 | 21.9124 | 21.871 | 20.8868 | 20.8338 | 20.781 | 19.7814 | 19.5883 | 19.0103 | 14.2804 | 13.7863 | 13.5608 | 20.8116 | 20.8034 | 20.7949 | 20.3662 | 20.323 | 19.3366 | 19.2784 | 19.2205 | 18.2144 | 18.0174 | 17.4283 | 14.3074 | 13.8089 | 13.5792
ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11202 | 0.11199 | 0.11193 | 0.11178 | 0.11161 | 0.11145 | 0.11132 | 0.11119 | 0.11107 | 0.11098 | 0.11084 | 0.11082 | 0.11082 | 0.11082 | 0.1126 | 0.11259 | 0.11256 | 0.11251 | 0.11244 | 0.11238 | 0.11231 | 0.11225 | 0.11221 | 0.11217 | 0.11205 | 0.11203 | 0.11203 | 0.11203
| CONTULLICH | CT |  |  | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11203 | 0.112 | 0.11195 | 0.11184 | 0.11172 | 0.11161 | 0.1115 | 0.1114 | 0.11132 | 0.11122 | 0.11099 | 0.11083 | 0.11082 | 0.11082 | 0.1126 | 0.11259 | 0.11257 | 0.11253 | 0.11249 | 0.11244 | 0.1124 | 0.11235 | 0.11231 | 0.11226 | 0.11217 | 0.11203 | 0.11203 | 0.11203
| CONTULLICH | LW |  |  | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11202 | 0.11199 | 0.11193 | 0.11178 | 0.11161 | 0.11145 | 0.11132 | 0.11119 | 0.11107 | 0.11098 | 0.11084 | 0.11082 | 0.11082 | 0.11082 | 0.1126 | 0.11259 | 0.11256 | 0.11251 | 0.11244 | 0.11238 | 0.11231 | 0.11225 | 0.11221 | 0.11217 | 0.11205 | 0.11203 | 0.11203 | 0.11203
| CONTULLICH | ST |  |  | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11204 | 0.11202 | 0.112 | 0.11195 | 0.11188 | 0.11181 | 0.11173 | 0.11166 | 0.11159 | 0.11151 | 0.11132 | 0.11104 | 0.11089 | 0.11083 | 0.11261 | 0.1126 | 0.11259 | 0.11257 | 0.11255 | 0.11252 | 0.11249 | 0.11246 | 0.11243 | 0.1124 | 0.11231 | 0.1122 | 0.11212 | 0.11203
| CONTULLICH | SP |  |  | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11873 | 0.11206 | 0.11206 | 0.11205 | 0.11205 | 0.11203 | 0.11201 | 0.11198 | 0.11196 | 0.11193 | 0.1119 | 0.11181 | 0.11167 | 0.11154 | 0.11142 | 0.11262 | 0.11262 | 0.11261 | 0.11261 | 0.11261 | 0.1126 | 0.11259 | 0.11258 | 0.11257 | 0.11255 | 0.11252 | 0.11246 | 0.11241 | 0.11236
FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | 3.0594 | 2.9447 | 2.4807 | 2.2911 | 2.0943 | 1.8994 | 1.709 | 1.5393 | 1.3888 | 1.2918 | 1.114 | 0.81793 | 0.5301 | 0.19825 | 3.128 | 3.0669 | 2.9901 | 2.4614 | 2.3096 | 2.1579 | 2.0061 | 1.8745 | 1.7531 | 1.675 | 1.5255 | 1.275 | 1.0257 | 0.73281 | 3.2644 | 3.1563 | 2.4375 | 2.2694 | 2.0679 | 1.8678 | 1.6722 | 1.4979 | 1.3426 | 1.2412 | 1.0551 | 0.74246 | 0.43273 | 0.079572
| CORRAN | CT |  |  | 3.0594 | 2.9447 | 2.4807 | 2.2911 | 2.0943 | 1.8994 | 1.709 | 1.5393 | 1.3888 | 1.2918 | 1.114 | 0.81793 | 0.5301 | 0.19825 | 3.128 | 3.0669 | 2.9901 | 2.4614 | 2.3096 | 2.1579 | 2.0061 | 1.8745 | 1.7531 | 1.675 | 1.5255 | 1.275 | 1.0257 | 0.73281 | 3.2644 | 3.1563 | 2.4375 | 2.2694 | 2.0679 | 1.8678 | 1.6722 | 1.4979 | 1.3426 | 1.2412 | 1.0551 | 0.74246 | 0.43273 | 0.079572
| CORRAN | LW |  |  | 3.1639 | 3.1544 | 3.1452 | 3.1347 | 3.1227 | 3.1096 | 3.0954 | 3.0802 | 3.066 | 3.0513 | 3.005 | 2.9221 | 2.4266 | 2.3062 | 3.1871 | 3.1792 | 3.1732 | 3.1658 | 3.1576 | 3.1489 | 3.1396 | 3.1299 | 3.1208 | 3.1112 | 3.0814 | 3.0293 | 2.9818 | 2.4287 | 3.363 | 3.3539 | 3.3449 | 3.3337 | 3.3211 | 3.3074 | 3.2927 | 3.2772 | 3.2627 | 3.2475 | 3.2002 | 3.1195 | 2.4093 | 2.2873
| CORRAN | ST |  |  | 3.1673 | 3.1609 | 3.1544 | 3.1458 | 3.1361 | 3.1263 | 3.1145 | 3.1027 | 3.0909 | 3.0811 | 3.0482 | 3 | 2.4196 | 2.3232 | 3.1875 | 3.18 | 3.1722 | 3.1625 | 3.1498 | 3.1357 | 3.1255 | 3.1152 | 3.1049 | 3.0964 | 3.0686 | 3.0297 | 2.4532 | 2.3606 | 3.3648 | 3.3574 | 3.3495 | 3.3377 | 3.3235 | 3.3082 | 3.2947 | 3.2812 | 3.2688 | 3.2584 | 3.224 | 3.1731 | 2.3853 | 2.2803
| CORRAN | SP |  |  | 3.1628 | 3.154 | 3.1453 | 3.1365 | 3.124 | 3.1116 | 3.0994 | 3.0873 | 3.0754 | 3.0633 | 3.0277 | 2.9595 | 2.8945 | 2.4353 | 3.1862 | 3.179 | 3.1733 | 3.1684 | 3.1601 | 3.1514 | 3.1441 | 3.137 | 3.1295 | 3.1218 | 3.099 | 3.0576 | 3.0149 | 2.9645 | 3.362 | 3.3537 | 3.3454 | 3.337 | 3.324 | 3.3108 | 3.2987 | 3.2868 | 3.2748 | 3.2626 | 3.2266 | 3.159 | 3.0958 | 2.419
KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | 3.8686 | 3.868 | 3.8379 | 3.8075 | 3.7741 | 3.7337 | 3.6917 | 3.6479 | 3.6021 | 3.5578 | 3.4734 | 2.2757 | 1.4974 | 1.1127 | 3.6576 | 3.6506 | 3.6207 | 3.5779 | 3.5306 | 3.4788 | 3.4262 | 3.3555 | 2.4503 | 2.3687 | 2.1706 | 1.8265 | 1.195 | 0.82692 | 3.3384 | 3.3377 | 3.2928 | 3.2475 | 3.1988 | 2.44 | 2.3747 | 2.3071 | 2.2295 | 2.145 | 1.9534 | 1.5524 | 0.70363 | 0.26481
| COSHIEVILLE | CT |  |  | 3.8686 | 3.868 | 3.8379 | 3.8075 | 3.7741 | 3.7337 | 3.6917 | 3.6479 | 3.6021 | 3.5578 | 3.4734 | 2.2757 | 1.4974 | 1.1127 | 3.6576 | 3.651 | 3.6207 | 3.5779 | 3.5306 | 3.4788 | 3.4262 | 3.3555 | 2.4503 | 2.3687 | 2.1706 | 1.8265 | 1.195 | 0.82692 | 3.3384 | 3.3377 | 3.2928 | 3.2475 | 3.1988 | 2.44 | 2.3747 | 2.3071 | 2.2295 | 2.145 | 1.9534 | 1.5524 | 0.70363 | 0.26481
| COSHIEVILLE | LW |  |  | 3.8695 | 3.8695 | 3.8565 | 3.8434 | 3.8304 | 3.8174 | 3.8044 | 3.7913 | 3.7782 | 3.7651 | 3.7388 | 3.6943 | 2.1668 | 1.9736 | 3.6579 | 3.6506 | 3.6297 | 3.5914 | 3.5498 | 3.5088 | 3.4686 | 3.429 | 3.3901 | 3.3487 | 2.4302 | 2.2379 | 1.73 | 1.5362 | 3.3392 | 3.3392 | 3.3196 | 3.3 | 3.2804 | 3.2608 | 3.2411 | 3.2214 | 3.2018 | 2.4843 | 2.3676 | 2.1414 | 1.47 | 1.241
| COSHIEVILLE | ST |  |  | 3.8694 | 3.8693 | 3.8605 | 3.8517 | 3.8421 | 3.8323 | 3.8224 | 3.8122 | 3.8018 | 3.7926 | 3.7646 | 3.7175 | 3.459 | 2.3874 | 3.6608 | 3.6571 | 3.6461 | 3.6306 | 3.6112 | 3.5891 | 3.5619 | 3.535 | 3.5084 | 3.475 | 3.377 | 2.4119 | 2.0782 | 1.9065 | 3.3391 | 3.339 | 3.3258 | 3.3126 | 3.2987 | 3.2845 | 3.2701 | 3.2555 | 3.2408 | 3.2271 | 2.489 | 2.3431 | 1.9115 | 1.7057
| COSHIEVILLE | SP |  |  | 3.8693 | 3.8692 | 3.869 | 3.8689 | 3.8689 | 3.8689 | 3.8689 | 3.8688 | 3.8688 | 3.8686 | 3.868 | 3.8676 | 3.8646 | 3.8581 | 3.6642 | 3.6636 | 3.6629 | 3.6622 | 3.6586 | 3.6544 | 3.6474 | 3.6404 | 3.6314 | 3.6205 | 3.5892 | 3.5404 | 3.4925 | 3.4441 | 3.339 | 3.3389 | 3.3388 | 3.3387 | 3.3386 | 3.3386 | 3.3386 | 3.3386 | 3.3385 | 3.3384 | 3.3378 | 3.3373 | 3.3343 | 3.3278
COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | YES | 10.5846 | 10.5255 | 10.4683 | 10.3759 | 10.275 | 10.1717 | 7.639 | 6.9898 | 6.1646 | 5.3544 | 4.2469 | 2.2283 | 0.23538 | -3.1465 | 10.6616 | 10.6339 | 10.6069 | 10.5555 | 10.4941 | 6.9163 | 6.1679 | 5.4225 | 4.4752 | 3.543 | 2.5258 | 0.44046 | -2.2658 | -5.6335 | 10.2978 | 10.2419 | 10.1877 | 10.0995 | 10.0026 | 9.9031 | 6.7748 | 6.0379 | 5.1016 | 4.1802 | 3.0182 | 0.80806 | -1.7381 | -5.3778
| COUPAR ANGUS | CT |  |  | 10.5846 | 10.5255 | 10.4683 | 10.3759 | 10.275 | 10.1717 | 10.0676 | 7.748 | 7.1665 | 6.4931 | 4.2469 | 2.2283 | 0.95128 | -3.1465 | 10.6616 | 10.6339 | 10.6069 | 10.5555 | 10.4941 | 7.353 | 6.9651 | 6.4987 | 5.8587 | 5.0967 | 2.5258 | 0.44046 | -0.96569 | -5.6335 | 10.2978 | 10.2419 | 10.1877 | 10.0995 | 10.0026 | 9.9031 | 9.8027 | 6.9759 | 6.3269 | 5.5664 | 3.0182 | 0.80806 | -0.63454 | -5.3778
| COUPAR ANGUS | LW |  |  | 10.639 | 10.6343 | 10.6296 | 10.6076 | 10.5812 | 10.5507 | 7.639 | 6.9898 | 6.1646 | 5.3544 | 5.1941 | 2.8086 | 1.8794 | -0.59211 | 10.6875 | 10.6854 | 10.6833 | 10.6642 | 10.641 | 6.9163 | 6.1679 | 5.4225 | 4.4752 | 3.543 | 3.3816 | 0.84538 | -0.18315 | -3.0037 | 10.3494 | 10.3449 | 10.3405 | 10.3188 | 10.2927 | 10.2626 | 6.7748 | 6.0379 | 5.1016 | 4.1802 | 4.0125 | 1.3558 | 0.30254 | -2.5675
| COUPAR ANGUS | ST |  |  | 10.6405 | 10.637 | 10.6336 | 10.6198 | 10.6029 | 10.5847 | 10.5645 | 10.5434 | 10.5182 | 7.4513 | 5.364 | 3.9571 | 0.23538 | -1.955 | 10.688 | 10.6863 | 10.6846 | 10.6731 | 10.6585 | 10.6425 | 10.625 | 7.1777 | 6.6499 | 5.9532 | 3.5416 | 2.0195 | -2.2658 | -4.8195 | 10.3507 | 10.3475 | 10.3442 | 10.3306 | 10.314 | 10.296 | 10.2761 | 10.2552 | 7.2504 | 6.5625 | 4.1819 | 2.6022 | -1.7381 | -4.2931
| COUPAR ANGUS | SP |  |  | 10.6381 | 10.6334 | 10.6288 | 10.6213 | 10.6123 | 10.6032 | 10.5942 | 10.5852 | 10.577 | 10.5677 | 10.5446 | 6.8046 | 5.7386 | 4.7646 | 10.6867 | 10.6844 | 10.6821 | 10.6769 | 10.6713 | 10.6656 | 10.66 | 10.6542 | 10.6494 | 10.6432 | 6.5429 | 5.2188 | 4.0081 | 2.8985 | 10.3484 | 10.344 | 10.3396 | 10.3324 | 10.3237 | 10.315 | 10.3063 | 10.2976 | 10.2898 | 10.2808 | 7.1369 | 5.8233 | 4.6204 | 3.5179
CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | 26.1986 | 26.1947 | 26.1903 | 26.1837 | 26.1623 | 26.1369 | 26.1072 | 26.0729 | 26.0343 | 26.0122 | 25.9389 | 25.7685 | 23.2529 | 22.3446 | 23.971 | 23.9327 | 23.8767 | 23.7547 | 23.6829 | 23.6575 | 23.6278 | 23.5935 | 23.5549 | 23.5328 | 22.0368 | 21.436 | 20.7207 | 19.7489 | 24.1706 | 24.1531 | 24.1284 | 24.0774 | 24.0221 | 23.9634 | 23.9244 | 23.8901 | 23.8515 | 23.8294 | 23.7561 | 21.5842 | 20.8688 | 19.8969
| CRAIGIEBUCKLER | CT |  |  | 26.1986 | 26.1947 | 26.1903 | 26.1837 | 26.1623 | 26.1369 | 26.1072 | 26.0729 | 26.0343 | 26.0122 | 25.9389 | 25.7685 | 23.2529 | 22.3446 | 23.971 | 23.9327 | 23.8767 | 23.7547 | 23.6829 | 23.6575 | 23.6278 | 23.5935 | 23.5549 | 23.5328 | 22.0368 | 21.436 | 20.7207 | 19.7489 | 24.1706 | 24.1531 | 24.1284 | 24.0774 | 24.0221 | 23.9634 | 23.9244 | 23.8901 | 23.8515 | 23.8294 | 23.7561 | 21.5842 | 20.8688 | 19.8969
| CRAIGIEBUCKLER | LW |  |  | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 26.2043 | 24.0142 | 24.0132 | 24.0116 | 24.0075 | 24.003 | 23.9985 | 23.9942 | 23.99 | 23.9858 | 23.9814 | 23.9681 | 23.9468 | 23.9253 | 23.9041 | 24.191 | 24.1906 | 24.19 | 24.1884 | 24.1866 | 24.1849 | 24.1832 | 24.1815 | 24.1799 | 24.1781 | 24.1729 | 24.1645 | 24.1561 | 24.1477
| CRAIGIEBUCKLER | ST |  |  | 26.2024 | 26.2014 | 26.2001 | 26.1986 | 26.1871 | 26.1731 | 26.1568 | 26.1383 | 26.1173 | 26.1106 | 26.0899 | 26.0555 | 25.8762 | 25.7745 | 23.9825 | 23.955 | 23.9187 | 23.8495 | 23.7546 | 23.6936 | 23.6774 | 23.6589 | 23.6379 | 23.6312 | 23.6105 | 23.5761 | 21.9105 | 21.5365 | 24.1774 | 24.166 | 24.1509 | 24.1228 | 24.0796 | 24.0375 | 24.0076 | 23.9756 | 23.9414 | 23.9278 | 23.9071 | 23.8727 | 22.0588 | 21.6848
| CRAIGIEBUCKLER | SP |  |  | 26.2002 | 26.198 | 26.1958 | 26.1935 | 26.1931 | 26.1927 | 26.1923 | 26.1918 | 26.1913 | 26.188 | 26.1768 | 26.1681 | 26.1122 | 25.9905 | 24.0061 | 24.0006 | 23.9944 | 23.9877 | 23.9636 | 23.935 | 23.9171 | 23.8994 | 23.8768 | 23.8595 | 23.8079 | 23.743 | 23.639 | 23.5111 | 24.1854 | 24.1819 | 24.1781 | 24.1741 | 24.1644 | 24.1529 | 24.1455 | 24.1383 | 24.1291 | 24.1203 | 24.0932 | 24.063 | 23.9919 | 23.856
CLAYHILLS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | 37.6475 | 37.5943 | 37.5377 | 37.3323 | 37.0631 | 36.3948 | 35.7035 | 34.9892 | 28.473 | 28.1996 | 27.3796 | 25.5652 | 23.5538 | 22.3607 | 31.0193 | 30.9662 | 30.9096 | 30.7041 | 30.4351 | 29.7669 | 29.0756 | 26.9664 | 26.253 | 25.9796 | 25.1596 | 23.3452 | 21.3338 | 20.1407 | 31.6441 | 31.5969 | 31.5497 | 31.3251 | 31.1249 | 30.4823 | 29.8162 | 27.1811 | 26.4677 | 26.1944 | 25.3743 | 23.56 | 21.5486 | 20.3555
| CRAIGINCHES | CT |  |  | 37.7886 | 37.7477 | 37.7044 | 37.6862 | 37.4873 | 37.1288 | 36.8018 | 36.4582 | 36.0188 | 35.7813 | 35.0788 | 25.825 | 23.5538 | 22.4165 | 31.1604 | 31.1196 | 31.0763 | 31.0581 | 30.8593 | 30.5008 | 30.1739 | 29.8303 | 29.391 | 29.1535 | 27.1959 | 23.605 | 21.3338 | 20.1888 | 31.7848 | 31.7487 | 31.7126 | 31.7116 | 31.5311 | 31.1906 | 30.8812 | 30.5711 | 30.1647 | 29.9628 | 27.4107 | 23.8197 | 21.5486 | 20.4112
| CRAIGINCHES | LW |  |  | 37.6475 | 37.5943 | 37.5377 | 37.5141 | 37.0631 | 36.3948 | 35.7035 | 34.9892 | 28.473 | 28.1996 | 27.3796 | 25.5652 | 23.5738 | 22.3607 | 31.0193 | 30.9662 | 30.9096 | 30.886 | 30.4351 | 29.7669 | 29.0756 | 26.9664 | 26.253 | 25.9796 | 25.1596 | 23.3452 | 21.3538 | 20.1407 | 31.6441 | 31.5969 | 31.5497 | 31.5497 | 31.1249 | 30.4823 | 29.8162 | 27.1811 | 26.4677 | 26.1944 | 25.3743 | 23.56 | 21.5685 | 20.3555
| CRAIGINCHES | ST |  |  | 37.9329 | 37.9063 | 37.8787 | 37.8712 | 37.7422 | 37.6111 | 36.5703 | 35.5297 | 35.3899 | 34.9653 | 27.9382 | 25.886 | 24.5104 | 23.8115 | 31.3048 | 31.2782 | 31.2506 | 31.2431 | 31.1141 | 30.9831 | 29.9422 | 27.442 | 27.3224 | 26.9213 | 25.7182 | 23.666 | 22.2904 | 21.5915 | 31.9272 | 31.9035 | 31.8798 | 31.8797 | 31.7608 | 31.6417 | 30.6219 | 29.602 | 27.5371 | 27.136 | 25.9329 | 23.8807 | 22.5051 | 21.8063
| CRAIGINCHES | SP |  |  | 38.2292 | 38.065 | 38.0527 | 37.3323 | 37.2704 | 37.208 | 37.1422 | 37.0764 | 37.0086 | 36.6785 | 35.6889 | 28.1313 | 27.0241 | 26.6291 | 31.6008 | 31.4369 | 31.4245 | 30.7041 | 30.6423 | 30.5799 | 30.5141 | 30.4483 | 30.3806 | 30.0504 | 27.5866 | 25.9113 | 24.8041 | 24.4091 | 32.0932 | 32.0569 | 32.045 | 31.3251 | 31.266 | 31.207 | 31.148 | 31.089 | 31.03 | 30.7092 | 29.7466 | 26.126 | 25.0189 | 24.6238
CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | 15.9726 | 15.8731 | 15.7768 | 15.6518 | 14.4753 | 14.3316 | 14.176 | 14.0046 | 13.7874 | 13.631 | 12.935 | 9.2594 | 4.5707 | -0.13108 | 14.4273 | 13.7603 | 13.715 | 13.6559 | 13.578 | 13.3756 | 13.1159 | 12.8332 | 12.4774 | 12.2143 | 11.4438 | 8.1482 | 3.8724 | -0.28274 | 14.557 | 13.7322 | 13.6456 | 13.5333 | 13.403 | 13.263 | 13.0471 | 12.7424 | 12.3609 | 12.0845 | 11.299 | 7.5002 | 2.5959 | -2.246
| CRAIGTON | CT |  |  | 15.9726 | 15.8731 | 15.7768 | 15.6518 | 14.4753 | 14.3316 | 14.176 | 14.0046 | 13.7874 | 13.631 | 12.935 | 9.2594 | 4.5707 | -0.13108 | 14.4273 | 13.7603 | 13.715 | 13.6559 | 13.578 | 13.3756 | 13.1159 | 12.8332 | 12.4774 | 12.2143 | 11.4438 | 8.1482 | 3.8724 | -0.28274 | 14.557 | 13.7322 | 13.6456 | 13.5333 | 13.403 | 13.263 | 13.0471 | 12.7424 | 12.3609 | 12.0845 | 11.299 | 7.5002 | 2.5959 | -2.246
| CRAIGTON | LW |  |  | 16.0643 | 16.0562 | 16.0484 | 16.0394 | 16.0288 | 16.0168 | 16.0032 | 15.9756 | 15.922 | 15.8969 | 14.367 | 12.7153 | 11.3649 | 10.7428 | 14.5146 | 14.5064 | 14.4973 | 14.4833 | 14.3911 | 14.3007 | 14.2467 | 13.7555 | 13.5408 | 13.3538 | 12.6552 | 11.0678 | 9.5492 | 8.8802 | 14.6566 | 14.6475 | 14.6384 | 14.6264 | 14.5826 | 14.5387 | 14.5041 | 14.4555 | 13.6323 | 13.4439 | 12.7356 | 10.9577 | 9.4115 | 8.7136
| CRAIGTON | ST |  |  | 16.0666 | 16.0608 | 16.0549 | 16.047 | 16.0348 | 16.0215 | 16.0058 | 15.9829 | 15.9361 | 15.9173 | 14.4871 | 10.5211 | 7.5453 | 4.2244 | 14.504 | 14.4873 | 14.4664 | 14.4293 | 14.3475 | 14.2685 | 14.2402 | 13.7327 | 13.5454 | 13.3671 | 12.7715 | 9.373 | 6.6464 | 3.6432 | 14.6541 | 14.6434 | 14.631 | 14.6108 | 14.5705 | 14.5332 | 14.5007 | 14.4593 | 13.6452 | 13.4674 | 12.8678 | 8.8054 | 5.6996 | 2.2237
| CRAIGTON | SP |  |  | 16.0621 | 16.0539 | 16.0458 | 16.0376 | 16.0268 | 16.0162 | 16.0056 | 15.9942 | 15.979 | 15.961 | 15.8886 | 12.7357 | 10.7184 | 8.9725 | 14.5119 | 14.5036 | 14.4951 | 14.4863 | 14.4592 | 14.4292 | 14.3952 | 14.3606 | 14.3146 | 13.7928 | 13.733 | 11.6 | 9.7884 | 8.273 | 14.6541 | 14.6451 | 14.636 | 14.6268 | 14.6085 | 14.5891 | 14.5682 | 14.5465 | 14.5181 | 14.4856 | 13.74 | 11.2179 | 9.167 | 7.3884
BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | 20.5359 | 20.5327 | 20.5153 | 20.4962 | 20.4639 | 20.4247 | 20.3806 | 20.3313 | 20.2741 | 20.2354 | 14.4267 | 13.5152 | 12.7594 | 10.7078 | 17.4111 | 17.3926 | 17.3597 | 17.3076 | 17.0632 | 16.9255 | 13.7814 | 12.932 | 12.933 | 12.8025 | 10.6691 | 9.6039 | 8.7603 | 6.1178 | 18.4419 | 18.4387 | 18.4221 | 18.4036 | 18.3721 | 18.3338 | 18.2906 | 13.4811 | 13.4823 | 13.2926 | 11.1502 | 10.0627 | 9.1994 | 6.6875
| CRIEFF | CT |  |  | 20.5359 | 20.5327 | 20.5153 | 20.4962 | 20.4639 | 20.4247 | 20.3806 | 20.3313 | 20.2741 | 20.2354 | 14.4267 | 13.5152 | 12.7594 | 11.8075 | 17.4111 | 17.3926 | 17.3597 | 17.3076 | 17.1084 | 16.9255 | 16.886 | 16.8477 | 13.6928 | 12.8025 | 10.6691 | 9.6039 | 8.7603 | 7.7293 | 18.4419 | 18.4387 | 18.4221 | 18.4036 | 18.3721 | 18.3338 | 18.2906 | 18.2422 | 18.186 | 13.2926 | 11.1502 | 10.0627 | 9.1994 | 8.1495
| CRIEFF | LW |  |  | 20.5405 | 20.5405 | 20.5405 | 20.5405 | 20.5375 | 20.5315 | 20.5222 | 20.509 | 20.5549 | 20.5496 | 20.5268 | 14.3632 | 13.4301 | 10.7078 | 17.4263 | 17.4196 | 17.4089 | 17.3872 | 17.0632 | 16.9907 | 13.7814 | 12.932 | 12.933 | 12.8793 | 12.7131 | 10.4347 | 9.3176 | 6.1178 | 18.4465 | 18.4465 | 18.4465 | 18.4465 | 18.4435 | 18.4375 | 18.4282 | 13.4811 | 13.4823 | 13.4287 | 13.263 | 10.9916 | 9.8777 | 6.6875
| CRIEFF | ST |  |  | 20.5395 | 20.539 | 20.5384 | 20.5376 | 20.5312 | 20.5231 | 20.5135 | 20.5017 | 20.4856 | 20.4805 | 20.4634 | 20.4001 | 13.5185 | 12.5469 | 17.4215 | 17.412 | 17.3995 | 17.3821 | 17.2401 | 17.1001 | 16.9727 | 16.9609 | 16.9448 | 13.3123 | 11.3776 | 10.714 | 9.458 | 8.3149 | 18.4455 | 18.445 | 18.4444 | 18.4436 | 18.4372 | 18.4291 | 18.4195 | 18.4077 | 18.3916 | 18.3865 | 11.9314 | 11.2696 | 10.017 | 8.8774
| CRIEFF | SP |  |  | 20.5385 | 20.5374 | 20.5363 | 20.5352 | 20.535 | 20.5348 | 20.5345 | 20.5341 | 20.5336 | 20.5316 | 20.5233 | 20.5147 | 20.4843 | 14.0072 | 17.429 | 17.4267 | 17.4242 | 17.4214 | 17.3729 | 17.3312 | 17.268 | 17.2058 | 17.1233 | 17.0126 | 16.9825 | 12.6074 | 11.2464 | 9.9974 | 18.4445 | 18.4434 | 18.4423 | 18.4412 | 18.441 | 18.4408 | 18.4405 | 18.4402 | 18.4396 | 18.4376 | 18.4293 | 13.1576 | 11.8006 | 10.5555
PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | 1.7772 | 1.7769 | 1.7714 | 1.7657 | 1.7586 | 1.7501 | 1.741 | 1.7313 | 1.7211 | 1.7121 | 1.6931 | 1.6578 | 1.616 | 0.99548 | 1.7885 | 1.7882 | 1.7855 | 1.7827 | 1.7786 | 1.7736 | 1.7682 | 1.7623 | 1.756 | 1.751 | 1.7391 | 1.7155 | 0.93161 | 0.79131 | 1.5456 | 1.5434 | 1.5329 | 1.5184 | 1.5021 | 1.4839 | 1.4653 | 1.4363 | 0.99993 | 0.98742 | 0.96224 | 0.91698 | 0.86245 | 0.70797
| CRINAN | CT |  |  | 1.7772 | 1.7769 | 1.7714 | 1.7657 | 1.7586 | 1.7501 | 1.741 | 1.7313 | 1.7211 | 1.7121 | 1.6931 | 1.6578 | 1.616 | 0.99548 | 1.7885 | 1.7882 | 1.7855 | 1.7827 | 1.7786 | 1.7736 | 1.7682 | 1.7623 | 1.756 | 1.751 | 1.7391 | 1.7155 | 0.93161 | 0.79131 | 1.5456 | 1.5434 | 1.5329 | 1.5184 | 1.5021 | 1.4839 | 1.4653 | 1.4363 | 0.99993 | 0.98742 | 0.96224 | 0.91698 | 0.86245 | 0.70797
| CRINAN | LW |  |  | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.7777 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.789 | 1.5459 | 1.5437 | 1.5402 | 1.5315 | 1.5219 | 1.5124 | 1.5057 | 1.5048 | 1.504 | 1.5031 | 1.5005 | 1.4963 | 1.492 | 1.4878
| CRINAN | ST |  |  | 1.7776 | 1.7775 | 1.7775 | 1.7774 | 1.7767 | 1.7759 | 1.775 | 1.7739 | 1.7728 | 1.7724 | 1.7712 | 1.7692 | 1.759 | 1.7533 | 1.7889 | 1.7888 | 1.7887 | 1.7887 | 1.788 | 1.7872 | 1.7863 | 1.7852 | 1.784 | 1.7836 | 1.7825 | 1.7805 | 1.7703 | 1.7646 | 1.5466 | 1.5455 | 1.5439 | 1.541 | 1.5366 | 1.5312 | 1.5164 | 1.5021 | 1.4997 | 1.4983 | 1.4941 | 1.4872 | 1.4722 | 1.4617
| CRINAN | SP |  |  | 1.7777 | 1.7776 | 1.7776 | 1.7776 | 1.7776 | 1.7776 | 1.7776 | 1.7776 | 1.7776 | 1.7775 | 1.7774 | 1.7774 | 1.7768 | 1.7756 | 1.7889 | 1.7889 | 1.7889 | 1.7889 | 1.7889 | 1.7889 | 1.7888 | 1.7888 | 1.7888 | 1.7888 | 1.7887 | 1.7886 | 1.7881 | 1.7869 | 1.5478 | 1.5476 | 1.5474 | 1.5472 | 1.5461 | 1.5448 | 1.5402 | 1.5357 | 1.5299 | 1.5254 | 1.5124 | 1.5043 | 1.502 | 1.4992
PORT ANN | CROMALT | MINIMUM HEADROOM | NN 0839507755 | YES | 3.2323 | 3.232 | 3.2317 | 3.2313 | 3.2299 | 3.2283 | 3.2263 | 3.2241 | 3.2216 | 3.2202 | 3.2154 | 3.2044 | 3.1862 | 3.1509 | 3.0047 | 3.0042 | 3.0036 | 3.0025 | 3.0003 | 2.9979 | 2.9952 | 2.991 | 2.9864 | 2.9828 | 2.9716 | 2.9517 | 2.9335 | 2.4355 | 3.0288 | 3.0274 | 3.0253 | 3.0195 | 3.0131 | 3.0068 | 3.0006 | 2.9892 | 2.9858 | 2.9844 | 2.9797 | 2.9686 | 2.9504 | 2.9151
| CROMALT | CT |  |  | 3.2323 | 3.232 | 3.2317 | 3.2313 | 3.2299 | 3.2283 | 3.2263 | 3.2241 | 3.2216 | 3.2202 | 3.2154 | 3.2044 | 3.1862 | 3.1509 | 3.0047 | 3.0042 | 3.0036 | 3.0025 | 3.0003 | 2.9979 | 2.9952 | 2.991 | 2.9864 | 2.9828 | 2.9716 | 2.9517 | 2.9335 | 2.4355 | 3.0288 | 3.0274 | 3.0253 | 3.0207 | 3.0148 | 3.0087 | 3.0025 | 2.9892 | 2.9858 | 2.9844 | 2.9797 | 2.9686 | 2.9504 | 2.9151
| CROMALT | LW |  |  | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 3.005 | 3.0048 | 3.0044 | 3.0034 | 3.0022 | 3.0012 | 3.0001 | 2.999 | 2.998 | 2.9969 | 2.9937 | 2.9884 | 2.9831 | 2.98 | 3.0291 | 3.0276 | 3.0253 | 3.0195 | 3.0131 | 3.0068 | 3.0006 | 2.9968 | 2.9968 | 2.9968 | 2.9968 | 2.9968 | 2.9968 | 2.9968
| CROMALT | ST |  |  | 3.2326 | 3.2325 | 3.2325 | 3.2325 | 3.2321 | 3.2318 | 3.2313 | 3.2308 | 3.2302 | 3.23 | 3.2294 | 3.2285 | 3.2234 | 3.2206 | 3.0051 | 3.0049 | 3.0047 | 3.0044 | 3.0036 | 3.0027 | 3.0017 | 3.0007 | 2.9996 | 2.9979 | 2.9932 | 2.9855 | 2.9739 | 2.9679 | 3.0296 | 3.0289 | 3.0279 | 3.026 | 3.0232 | 3.0199 | 3.0163 | 3.0127 | 3.0092 | 3.0007 | 2.9936 | 2.9927 | 2.9876 | 2.9848
| CROMALT | SP |  |  | 3.2325 | 3.2325 | 3.2324 | 3.2324 | 3.2324 | 3.2323 | 3.2323 | 3.2323 | 3.2323 | 3.2322 | 3.232 | 3.2317 | 3.2303 | 3.2273 | 3.0051 | 3.0051 | 3.005 | 3.0049 | 3.0048 | 3.0046 | 3.0044 | 3.0042 | 3.004 | 3.0034 | 3.0014 | 2.9987 | 2.9949 | 2.9896 | 3.0303 | 3.0301 | 3.03 | 3.0298 | 3.0291 | 3.0282 | 3.0272 | 3.0261 | 3.0248 | 3.0215 | 3.0117 | 2.9971 | 2.9946 | 2.9915
ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | YES | 19.2874 | 19.2664 | 19.1005 | 18.896 | 18.519 | 18.0995 | 17.6635 | 17.2132 | 16.7077 | 16.423 | 15.8504 | 13.4431 | 11.8491 | 10.369 | 17.2103 | 17.1926 | 17.0603 | 16.8995 | 16.5664 | 16.2039 | 15.8274 | 15.4663 | 15.0765 | 13.751 | 13.0278 | 11.2407 | 9.714 | 8.2856 | 16.694 | 16.6718 | 16.4858 | 16.2586 | 15.8942 | 15.491 | 15.0844 | 14.6737 | 13.4182 | 13.0351 | 12.1735 | 10.1618 | 8.4236 | 6.8026
| CROSSHILLS | CT |  |  | 19.2874 | 19.2664 | 19.1005 | 18.896 | 18.519 | 18.0995 | 17.6635 | 17.2132 | 16.7077 | 16.423 | 15.8504 | 13.4431 | 11.8491 | 10.369 | 17.2103 | 17.1926 | 17.0603 | 16.8995 | 16.5664 | 16.2039 | 15.8274 | 15.4663 | 15.0765 | 13.751 | 13.0278 | 11.2407 | 9.714 | 8.2856 | 16.694 | 16.6718 | 16.4858 | 16.2586 | 15.8942 | 15.491 | 15.0844 | 14.6737 | 13.4182 | 13.0351 | 12.1735 | 10.1618 | 8.4236 | 6.8026
| CROSSHILLS | LW |  |  | 19.308 | 19.3041 | 19.2377 | 19.1619 | 18.8504 | 18.5344 | 18.2106 | 17.8691 | 17.412 | 17.2688 | 16.9039 | 16.162 | 14.101 | 13.806 | 17.228 | 17.2248 | 17.177 | 17.1239 | 16.8344 | 16.5407 | 16.2393 | 15.9204 | 15.4858 | 15.365 | 15.0409 | 13.359 | 12.9043 | 12.462 | 16.7158 | 16.7116 | 16.6367 | 16.5518 | 16.231 | 15.9057 | 15.5727 | 15.2219 | 14.7556 | 13.7835 | 13.4596 | 12.7712 | 12.1847 | 11.8047
| CROSSHILLS | ST |  |  | 19.3049 | 19.299 | 19.2514 | 19.1974 | 19.0797 | 18.8948 | 18.6992 | 18.4878 | 18.2002 | 18.0581 | 17.729 | 17.0077 | 15.9899 | 14.2397 | 17.2252 | 17.2203 | 17.181 | 17.1414 | 17.0368 | 16.8642 | 16.6771 | 16.4745 | 16.1956 | 16.0528 | 15.696 | 15.1466 | 13.2551 | 12.5299 | 16.7126 | 16.7064 | 16.6529 | 16.5926 | 16.4682 | 16.2764 | 16.0728 | 15.8744 | 15.6057 | 15.5042 | 15.2189 | 13.505 | 12.1987 | 11.3423
| CROSSHILLS | SP |  |  | 19.3087 | 19.3069 | 19.2836 | 19.2602 | 19.2277 | 19.1957 | 19.1565 | 19.1168 | 19.0688 | 19.0107 | 18.8321 | 18.6109 | 17.9133 | 17.585 | 17.2281 | 17.2264 | 17.2089 | 17.1948 | 17.1705 | 17.1461 | 17.1123 | 17.0778 | 17.034 | 16.9776 | 16.8038 | 16.5766 | 15.8571 | 15.5215 | 16.7167 | 16.7149 | 16.6887 | 16.6624 | 16.6269 | 16.5919 | 16.5493 | 16.5062 | 16.4547 | 16.3925 | 16.2316 | 16.0747 | 15.4033 | 15.0749
KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | 10.1815 | 10.1797 | 10.1776 | 10.1739 | 10.1105 | 10.0402 | 9.9655 | 7.4473 | 6.753 | 6.1581 | 3.9408 | 1.0067 | -3.4257 | -5.2359 | 9.4082 | 9.404 | 9.3983 | 9.3861 | 9.141 | 7.4474 | 6.8577 | 6.2458 | 5.4458 | 4.7309 | 2.0639 | -1.4472 | -6.471 | -8.5921 | 9.4167 | 9.4143 | 9.4113 | 9.4055 | 9.2694 | 7.445 | 6.8182 | 6.1896 | 5.3777 | 4.665 | 2.0059 | -1.495 | -6.62 | -8.7347
| CULLEN | CT |  |  | 10.1815 | 10.1797 | 10.1776 | 10.1739 | 10.1187 | 10.0625 | 10.0014 | 9.9356 | 9.8448 | 9.8234 | 5.9693 | 3.4764 | -1.5765 | -4.7083 | 9.4082 | 9.404 | 9.3983 | 9.3861 | 9.1608 | 9.0939 | 7.4779 | 7.4121 | 7.0022 | 6.4532 | 4.4968 | 1.5487 | -4.2635 | -7.9062 | 9.4167 | 9.4143 | 9.4113 | 9.4055 | 9.2945 | 9.2213 | 9.1602 | 7.4998 | 6.9813 | 6.4054 | 4.4317 | 1.4915 | -4.4196 | -8.0521
| CULLEN | LW |  |  | 10.1836 | 10.1832 | 10.1826 | 10.1811 | 10.1105 | 10.0402 | 9.9655 | 7.4473 | 6.753 | 6.1581 | 3.9408 | 1.0067 | -3.4257 | -5.2359 | 9.4102 | 9.4068 | 9.4015 | 9.3881 | 9.141 | 7.4474 | 6.8577 | 6.2458 | 5.4458 | 4.7309 | 2.0639 | -1.4472 | -6.471 | -8.5921 | 9.4188 | 9.4177 | 9.4159 | 9.4114 | 9.2694 | 7.445 | 6.8182 | 6.1896 | 5.3777 | 4.665 | 2.0059 | -1.495 | -6.62 | -8.7347
| CULLEN | ST |  |  | 10.1833 | 10.1828 | 10.1823 | 10.1813 | 10.1428 | 10.1064 | 10.0708 | 10.0299 | 9.9651 | 9.9509 | 6.2567 | 4.0225 | 0.84534 | -2.5284 | 9.411 | 9.409 | 9.4066 | 9.4019 | 9.2138 | 9.1404 | 9.1012 | 9.0603 | 7.1947 | 6.6777 | 4.8138 | 2.1444 | -1.5283 | -5.5156 | 9.4188 | 9.4179 | 9.4169 | 9.415 | 9.3298 | 9.2653 | 9.2296 | 9.1887 | 7.1791 | 6.633 | 4.7481 | 2.0864 | -1.634 | -5.6095
| CULLEN | SP |  |  | 10.1831 | 10.1827 | 10.1822 | 10.1817 | 10.1725 | 10.1664 | 10.1619 | 10.1568 | 10.1483 | 10.1387 | 10.1034 | 7.4689 | 6.3827 | 5.5721 | 9.4123 | 9.4116 | 9.4109 | 9.4102 | 9.3649 | 9.3138 | 9.2323 | 9.1957 | 9.1802 | 9.1691 | 7.2322 | 6.2392 | 5.0104 | 4.0593 | 9.419 | 9.4184 | 9.4179 | 9.4173 | 9.3991 | 9.3791 | 9.3487 | 9.3182 | 9.3072 | 9.2975 | 7.2092 | 6.1768 | 4.9435 | 3.9949
INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | 23.7276 | 23.7218 | 23.7147 | 31.9846 | 31.9516 | 31.9124 | 31.8664 | 31.8135 | 31.7537 | 31.7196 | 31.6062 | 31.3427 | 31.0104 | 30.1694 | 20.7663 | 20.6575 | 20.6071 | 27.5735 | 27.4291 | 27.3001 | 27.1725 | 27.0634 | 26.9483 | 26.8543 | 26.5634 | 22.075 | 20.9612 | 19.352 | 20.2719 | 20.2303 | 20.2096 | 27.2469 | 27.1788 | 27.105 | 27.025 | 26.9487 | 26.8658 | 26.8068 | 26.6194 | 26.2798 | 21.4505 | 19.8973
| CULLODEN | CT |  |  | 23.7276 | 23.7218 | 23.7147 | 31.9846 | 31.9516 | 31.9124 | 31.8664 | 31.8135 | 31.7537 | 31.7196 | 31.6062 | 31.3427 | 31.0104 | 30.1694 | 20.7663 | 20.6575 | 20.6071 | 27.5735 | 27.4291 | 27.3001 | 27.1725 | 27.0634 | 26.9483 | 26.8543 | 26.5634 | 22.075 | 20.9612 | 19.352 | 20.2719 | 20.2303 | 20.2096 | 27.2469 | 27.1788 | 27.105 | 27.025 | 26.9487 | 26.8658 | 26.8068 | 26.6194 | 26.2798 | 21.4505 | 19.8973
| CULLODEN | LW |  |  | 23.7365 | 23.7365 | 23.7365 | 32.0165 | 32.0165 | 32.0165 | 32.0165 | 32.0165 | 32.1175 | 32.1175 | 32.1175 | 32.1175 | 32.1175 | 32.1175 | 20.8063 | 20.7309 | 20.7287 | 27.8033 | 27.7972 | 27.7913 | 27.7855 | 27.7799 | 27.8754 | 27.8694 | 27.8518 | 27.8233 | 27.7946 | 27.7662 | 20.2959 | 20.2635 | 20.2628 | 27.3411 | 27.3392 | 27.3373 | 27.3355 | 27.3337 | 27.433 | 27.4312 | 27.4256 | 27.4166 | 27.4076 | 27.3986
| CULLODEN | ST |  |  | 23.7339 | 23.7323 | 23.7305 | 32.0085 | 31.992 | 31.9722 | 31.9493 | 31.923 | 31.8933 | 31.8836 | 31.8543 | 31.8055 | 31.6523 | 31.5081 | 20.7863 | 20.7688 | 20.6717 | 27.7086 | 27.6364 | 27.5498 | 27.4673 | 27.3825 | 27.3069 | 27.2578 | 27.1136 | 26.8801 | 26.5434 | 26.3364 | 20.2848 | 20.2755 | 20.2408 | 27.3058 | 27.2718 | 27.2309 | 27.1892 | 27.1445 | 27.0967 | 27.0706 | 26.9934 | 26.8676 | 26.638 | 26.4451
| CULLODEN | SP |  |  | 23.731 | 23.7281 | 23.7251 | 32.002 | 32.0015 | 32.0009 | 32.0003 | 31.9997 | 31.999 | 31.9946 | 31.9795 | 31.9677 | 32.1956 | 32.0318 | 20.7987 | 20.7935 | 20.7137 | 27.7876 | 27.7709 | 27.751 | 27.7312 | 27.7115 | 27.6864 | 27.6617 | 27.588 | 27.4844 | 27.6304 | 27.4048 | 20.2893 | 20.2853 | 20.2503 | 27.3262 | 27.3206 | 27.314 | 27.3073 | 27.3007 | 27.2923 | 27.2815 | 27.2479 | 27.2072 | 27.4078 | 27.2183
CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | 26.8876 | 26.8847 | 26.8785 | 26.8707 | 26.851 | 26.8271 | 26.7995 | 26.7678 | 26.7305 | 26.7089 | 22.2139 | 20.0369 | 16.0517 | 13.9271 | 25.3734 | 25.3488 | 25.3105 | 25.2256 | 25.0141 | 24.8276 | 24.7277 | 24.6292 | 24.5008 | 21.6397 | 19.6933 | 17.173 | 12.7251 | 10.4405 | 24.8084 | 24.8022 | 24.7912 | 24.7718 | 24.7236 | 24.6741 | 24.6212 | 24.582 | 21.642 | 21.1178 | 19.1484 | 16.5987 | 12.0028 | 9.6741
| CULTER | CT |  |  | 26.8876 | 26.8847 | 26.8785 | 26.8707 | 26.851 | 26.8271 | 26.7995 | 26.7678 | 26.7305 | 26.7089 | 22.8115 | 20.8376 | 16.6652 | 13.9271 | 25.3734 | 25.3488 | 25.3105 | 25.2256 | 25.0141 | 24.8276 | 24.7277 | 24.6292 | 24.5008 | 22.0429 | 20.4568 | 18.1722 | 13.5447 | 10.4405 | 24.8084 | 24.8022 | 24.7912 | 24.7718 | 24.7236 | 24.6741 | 24.6212 | 24.582 | 21.9868 | 21.5154 | 19.9082 | 17.5935 | 12.8141 | 9.6741
| CULTER | LW |  |  | 26.892 | 26.892 | 26.892 | 26.892 | 26.8905 | 26.8875 | 26.8828 | 26.8761 | 26.8635 | 26.8608 | 22.2139 | 20.0369 | 16.0517 | 14.7171 | 25.4003 | 25.3984 | 25.3954 | 25.388 | 25.1279 | 24.8838 | 24.7711 | 24.6574 | 24.5685 | 21.6397 | 19.6933 | 17.173 | 12.7251 | 11.1793 | 24.8161 | 24.8158 | 24.8154 | 24.8143 | 24.7744 | 24.7334 | 24.6971 | 24.6904 | 21.642 | 21.1178 | 19.1484 | 16.5987 | 12.0028 | 10.4389
| CULTER | ST |  |  | 26.8908 | 26.89 | 26.8892 | 26.8883 | 26.8803 | 26.8705 | 26.859 | 26.8455 | 26.8288 | 26.8234 | 23.199 | 21.5005 | 18.9594 | 16.2989 | 25.3796 | 25.3607 | 25.3358 | 25.2883 | 25.1207 | 24.945 | 24.837 | 24.7547 | 24.6468 | 24.5317 | 20.8964 | 18.8795 | 16.0426 | 12.9688 | 24.812 | 24.8086 | 24.8042 | 24.7963 | 24.7646 | 24.7302 | 24.6985 | 24.6611 | 24.6431 | 21.8409 | 20.3663 | 18.326 | 15.4096 | 12.3004
| CULTER | SP |  |  | 26.8893 | 26.8879 | 26.8864 | 26.8849 | 26.8847 | 26.8844 | 26.8841 | 26.8837 | 26.8832 | 26.8808 | 26.8721 | 26.8641 | 26.79 | 23.1303 | 25.3959 | 25.3921 | 25.3879 | 25.3833 | 25.3411 | 25.2922 | 25.2327 | 25.174 | 25.0966 | 25.0023 | 24.7673 | 24.5691 | 21.569 | 20.8387 | 24.8132 | 24.8114 | 24.8095 | 24.8076 | 24.8011 | 24.7936 | 24.7845 | 24.7755 | 24.7635 | 24.7475 | 24.6864 | 21.8087 | 21.047 | 20.3092
ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | YES | 33.8471 | 33.8357 | 33.8182 | 33.7715 | 33.7197 | 33.6689 | 33.6192 | 33.5598 | 33.4753 | 33.3908 | 33.192 | 33.0966 | 32.9627 | 32.7376 | 26.149 | 26.1432 | 26.1349 | 26.1161 | 26.0923 | 26.0668 | 26.0403 | 25.9958 | 25.9504 | 25.9082 | 25.7803 | 25.5554 | 25.2908 | 24.9469 | 26.5375 | 26.5343 | 26.5298 | 26.521 | 26.5064 | 26.4907 | 26.4736 | 26.4482 | 26.4214 | 26.3994 | 26.3312 | 26.2029 | 26.0358 | 25.778
| CUMMING STREET | CT |  |  | 33.8471 | 33.8357 | 33.8193 | 33.7817 | 33.7364 | 33.6906 | 33.6441 | 33.5598 | 33.4753 | 33.3908 | 33.192 | 33.0966 | 32.9627 | 32.7376 | 26.149 | 26.1432 | 26.1349 | 26.1168 | 26.0923 | 26.0668 | 26.0403 | 25.9958 | 25.9504 | 25.9082 | 25.7803 | 25.5554 | 25.2908 | 24.9469 | 26.5375 | 26.5343 | 26.5298 | 26.521 | 26.5064 | 26.4907 | 26.4736 | 26.4482 | 26.4214 | 26.3994 | 26.3312 | 26.2029 | 26.0358 | 25.778
| CUMMING STREET | LW |  |  | 33.8486 | 33.8368 | 33.8182 | 33.7715 | 33.7197 | 33.6689 | 33.6192 | 33.5707 | 33.5232 | 33.4719 | 33.3199 | 33.2691 | 33.2449 | 33.2209 | 26.1508 | 26.1455 | 26.1371 | 26.1161 | 26.0928 | 26.07 | 26.0477 | 26.0258 | 26.0045 | 25.9814 | 25.9131 | 25.803 | 25.6923 | 25.5826 | 26.5393 | 26.5371 | 26.5336 | 26.5249 | 26.5152 | 26.5057 | 26.4964 | 26.4873 | 26.4784 | 26.4688 | 26.4403 | 26.3945 | 26.3483 | 26.3026
| CUMMING STREET | ST |  |  | 33.8521 | 33.8452 | 33.8362 | 33.819 | 33.7943 | 33.7649 | 33.7242 | 33.6841 | 33.6444 | 33.5927 | 33.4423 | 33.2629 | 33.2152 | 33.1784 | 26.1522 | 26.149 | 26.1449 | 26.137 | 26.1251 | 26.1108 | 26.0912 | 26.0718 | 26.0524 | 26.0286 | 25.9594 | 25.8487 | 25.7194 | 25.6011 | 26.5398 | 26.5384 | 26.5366 | 26.5332 | 26.5273 | 26.5202 | 26.5107 | 26.5011 | 26.4913 | 26.4809 | 26.4504 | 26.4014 | 26.333 | 26.2755
| CUMMING STREET | SP |  |  | 33.8585 | 33.8574 | 33.8561 | 33.8548 | 33.8485 | 33.841 | 33.8284 | 33.8159 | 33.7998 | 33.7794 | 33.7203 | 33.6283 | 33.5378 | 33.4468 | 26.155 | 26.1544 | 26.1537 | 26.153 | 26.1501 | 26.1468 | 26.1411 | 26.1354 | 26.1282 | 26.1188 | 26.0917 | 26.0498 | 26.0063 | 25.959 | 26.5409 | 26.5405 | 26.5401 | 26.5397 | 26.5385 | 26.537 | 26.5346 | 26.5323 | 26.5292 | 26.5251 | 26.5132 | 26.4953 | 26.4741 | 26.4477
ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | 7.9856 | 7.9843 | 7.9641 | 7.9432 | 7.9171 | 7.8857 | 7.8523 | 7.8168 | 7.7791 | 7.7459 | 7.6759 | 7.5461 | 7.3915 | 5.7567 | 7.2398 | 7.2342 | 7.2025 | 7.1612 | 7.1135 | 7.0597 | 7.0039 | 6.95 | 6.8939 | 6.8411 | 6.7465 | 5.8329 | 5.4779 | 5.0448 | 7.6808 | 7.678 | 7.6486 | 7.6155 | 7.5767 | 7.5311 | 7.4834 | 7.4348 | 7.3838 | 7.3366 | 7.2367 | 5.7633 | 5.3803 | 4.9202
| DALCHONZIE | CT |  |  | 7.9856 | 7.9843 | 7.9641 | 7.9432 | 7.9171 | 7.8857 | 7.8523 | 7.8168 | 7.7791 | 7.7459 | 7.6759 | 7.5461 | 7.3915 | 5.7567 | 7.2398 | 7.2342 | 7.2025 | 7.1612 | 7.1135 | 7.0597 | 7.0039 | 6.95 | 6.8939 | 6.8411 | 6.7465 | 5.8329 | 5.4779 | 5.0448 | 7.6808 | 7.678 | 7.6486 | 7.6155 | 7.5767 | 7.5311 | 7.4834 | 7.4348 | 7.3838 | 7.3366 | 7.2367 | 5.7633 | 5.3803 | 4.9202
| DALCHONZIE | LW |  |  | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.9874 | 7.2452 | 7.2441 | 7.2424 | 7.238 | 7.2332 | 7.2285 | 7.2238 | 7.2193 | 7.2149 | 7.2101 | 7.1959 | 7.173 | 7.1501 | 7.1273 | 7.6838 | 7.6835 | 7.6828 | 7.6813 | 7.6796 | 7.678 | 7.6764 | 7.6748 | 7.6733 | 7.6716 | 7.6667 | 7.6587 | 7.6507 | 7.6428
| DALCHONZIE | ST |  |  | 7.9869 | 7.9866 | 7.9864 | 7.986 | 7.9831 | 7.9796 | 7.9756 | 7.971 | 7.9659 | 7.9641 | 7.959 | 7.9504 | 7.906 | 7.8808 | 7.2435 | 7.2412 | 7.2382 | 7.2327 | 7.2228 | 7.2109 | 7.1998 | 7.1882 | 7.1762 | 7.1663 | 7.1374 | 7.0907 | 7.0086 | 6.9459 | 7.683 | 7.6819 | 7.6807 | 7.6786 | 7.6732 | 7.6669 | 7.6604 | 7.6533 | 7.6458 | 7.6412 | 7.6278 | 7.606 | 7.5484 | 7.5102
| DALCHONZIE | SP |  |  | 7.9866 | 7.9862 | 7.9857 | 7.9853 | 7.9852 | 7.9851 | 7.9851 | 7.985 | 7.9849 | 7.9842 | 7.9821 | 7.9804 | 7.9696 | 7.946 | 7.2451 | 7.2444 | 7.2436 | 7.2428 | 7.2407 | 7.2383 | 7.2358 | 7.2334 | 7.2303 | 7.2264 | 7.215 | 7.1988 | 7.1744 | 7.1381 | 7.6833 | 7.6828 | 7.6822 | 7.6816 | 7.6809 | 7.68 | 7.679 | 7.6781 | 7.677 | 7.6752 | 7.6699 | 7.6631 | 7.6476 | 7.6196
NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | YES | 17.5065 | 17.5058 | 17.505 | 17.5038 | 17.4997 | 17.4947 | 17.4888 | 17.4818 | 17.4734 | 17.4691 | 17.4545 | 14.4615 | 13.2535 | 12.7348 | 15.7559 | 15.7424 | 15.7225 | 15.6756 | 15.5618 | 15.4583 | 15.3173 | 15.2263 | 15.1975 | 13.6816 | 13.0041 | 12.1239 | 10.7036 | 10.1325 | 15.6315 | 15.6292 | 15.6259 | 15.6187 | 15.6004 | 15.5826 | 15.564 | 15.546 | 15.5224 | 13.764 | 13.3213 | 12.4958 | 11.1166 | 10.5556
| DALCROSS | CT |  |  | 17.5065 | 17.5058 | 17.505 | 17.5038 | 17.4997 | 17.4947 | 17.4888 | 17.4818 | 17.4734 | 17.4691 | 17.4545 | 17.4094 | 13.6069 | 12.7348 | 15.7559 | 15.7424 | 15.7225 | 15.6756 | 15.5618 | 15.4583 | 15.3553 | 15.2634 | 15.1975 | 15.1931 | 13.3276 | 12.5712 | 11.1411 | 10.1325 | 15.6315 | 15.6292 | 15.6259 | 15.6187 | 15.6004 | 15.5826 | 15.564 | 15.546 | 15.5224 | 15.4985 | 13.5846 | 12.9167 | 11.5377 | 10.5556
| DALCROSS | LW |  |  | 17.5076 | 17.5076 | 17.5076 | 17.5076 | 17.5071 | 17.5061 | 17.5045 | 17.5022 | 17.498 | 17.497 | 17.4931 | 14.4615 | 13.2535 | 12.7889 | 15.7695 | 15.7677 | 15.7648 | 15.7576 | 15.6098 | 15.463 | 15.3173 | 15.2263 | 15.222 | 13.6816 | 13.0041 | 12.1239 | 10.7036 | 10.1576 | 15.6342 | 15.634 | 15.6336 | 15.6327 | 15.613 | 15.5931 | 15.5727 | 15.5519 | 15.5243 | 13.764 | 13.3213 | 12.4958 | 11.1166 | 10.5863
| DALCROSS | ST |  |  | 17.5073 | 17.5072 | 17.507 | 17.5068 | 17.505 | 17.5029 | 17.5004 | 17.4973 | 17.4934 | 17.4921 | 17.4881 | 17.4753 | 14.3419 | 13.4579 | 15.7644 | 15.7587 | 15.7511 | 15.7365 | 15.6617 | 15.5861 | 15.5183 | 15.4359 | 15.3232 | 15.2162 | 13.5612 | 12.8803 | 11.9914 | 10.9538 | 15.6334 | 15.6325 | 15.6313 | 15.6293 | 15.618 | 15.6063 | 15.5953 | 15.5819 | 15.5639 | 15.5442 | 13.7061 | 13.2073 | 12.3658 | 11.3579
| DALCROSS | SP |  |  | 17.5072 | 17.5069 | 17.5067 | 17.5065 | 17.5064 | 17.5064 | 17.5063 | 17.5063 | 17.5061 | 17.5057 | 17.5041 | 17.5024 | 17.484 | 17.4669 | 15.7697 | 15.7687 | 15.7675 | 15.7663 | 15.7467 | 15.7241 | 15.6943 | 15.665 | 15.6262 | 15.5752 | 15.3655 | 15.2265 | 13.7234 | 13.4903 | 15.6339 | 15.6336 | 15.6332 | 15.6328 | 15.6303 | 15.6273 | 15.6234 | 15.6195 | 15.6143 | 15.6074 | 15.5787 | 15.5425 | 13.7751 | 13.663
TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | 1.1059 | 1.1058 | 1.0466 | 0.92217 | 0.83147 | 0.722 | 0.60919 | 0.49306 | 0.3732 | 0.25025 | 0.029458 | -0.33092 | -0.64694 | -0.95632 | 1.0742 | 1.0738 | 0.98669 | 0.90175 | 0.81436 | 0.70909 | 0.60064 | 0.48819 | 0.37222 | 0.25318 | 0.038019 | -0.31245 | -0.62073 | -0.92276 | 1.0822 | 1.0817 | 0.98447 | 0.89868 | 0.80854 | 0.69893 | 0.58448 | 0.46633 | 0.34443 | 0.21933 | -0.0054573 | -0.3716 | -0.69285 | -1.0073
| DALMALLY | CT |  |  | 1.1059 | 1.1058 | 1.0466 | 0.92217 | 0.83147 | 0.722 | 0.60919 | 0.49306 | 0.3732 | 0.25025 | 0.029458 | -0.33092 | -0.64694 | -0.95632 | 1.0742 | 1.0738 | 0.98669 | 0.90175 | 0.81436 | 0.70909 | 0.60064 | 0.48819 | 0.37222 | 0.25318 | 0.038019 | -0.31245 | -0.62073 | -0.92276 | 1.0822 | 1.0817 | 0.98447 | 0.89868 | 0.80854 | 0.69893 | 0.58448 | 0.46633 | 0.34443 | 0.21933 | -0.0054573 | -0.3716 | -0.69285 | -1.0073
| DALMALLY | LW |  |  | 1.106 | 1.106 | 1.0771 | 1.0519 | 0.9816 | 0.94249 | 0.90339 | 0.86412 | 0.82501 | 0.78574 | 0.70651 | 0.57192 | 0.43452 | 0.29379 | 1.0743 | 1.0738 | 1.0506 | 0.99516 | 0.95682 | 0.91836 | 0.87992 | 0.84134 | 0.80295 | 0.76431 | 0.68551 | 0.55269 | 0.41716 | 0.27849 | 1.0822 | 1.0818 | 1.0492 | 0.99256 | 0.95774 | 0.91888 | 0.87908 | 0.83879 | 0.79868 | 0.75833 | 0.67617 | 0.53766 | 0.39632 | 0.25168
| DALMALLY | ST |  |  | 1.106 | 1.106 | 1.0869 | 1.0687 | 1.0518 | 0.99438 | 0.9682 | 0.9419 | 0.91569 | 0.88947 | 0.81036 | 0.67586 | 0.53738 | 0.39607 | 1.0744 | 1.0742 | 1.0565 | 1.0464 | 0.99591 | 0.97042 | 0.94416 | 0.91781 | 0.89157 | 0.86542 | 0.78664 | 0.65391 | 0.51763 | 0.37869 | 1.0825 | 1.0821 | 1.0608 | 1.0391 | 0.99253 | 0.97044 | 0.94443 | 0.91829 | 0.89134 | 0.86406 | 0.78192 | 0.64347 | 0.50135 | 0.3564
| DALMALLY | SP |  |  | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.0747 | 1.0746 | 1.0746 | 1.0746 | 1.0744 | 1.0741 | 1.0734 | 1.0727 | 1.0719 | 1.0711 | 1.0694 | 1.0691 | 1.0691 | 1.0691 | 1.0828 | 1.0828 | 1.0827 | 1.0826 | 1.0823 | 1.0819 | 1.0816 | 1.0814 | 1.0811 | 1.0811 | 1.0811 | 1.0811 | 1.0811 | 1.0811
INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | NO | 19.8301 | 19.8248 | 19.8185 | 19.8094 | 19.7797 | 19.7442 | 19.7028 | 19.655 | 19.601 | 19.5705 | 19.468 | 19.2306 | 18.8397 | 18.0812 | 17.3677 | 17.3295 | 17.2739 | 17.1472 | 16.9909 | 16.831 | 16.6671 | 16.5215 | 16.3916 | 16.2973 | 16.0056 | 15.5271 | 11.5078 | 9.9287 | 17.5186 | 17.5049 | 17.4861 | 17.4469 | 17.3849 | 17.3177 | 17.245 | 17.1722 | 17.0936 | 17.0365 | 16.8552 | 16.4898 | 11.8407 | 10.3295
| DALNEIGH | CT |  |  | 19.8301 | 19.8248 | 19.8185 | 19.8094 | 19.7797 | 19.7442 | 19.7028 | 19.655 | 19.601 | 19.5705 | 19.468 | 19.2306 | 18.8397 | 18.0812 | 17.3677 | 17.3295 | 17.2739 | 17.1472 | 16.9909 | 16.831 | 16.6671 | 16.5215 | 16.3916 | 16.2973 | 16.0056 | 15.5271 | 11.5078 | 9.9287 | 17.5186 | 17.5049 | 17.4861 | 17.4469 | 17.3849 | 17.3177 | 17.245 | 17.1722 | 17.0936 | 17.0365 | 16.8552 | 16.4898 | 11.8407 | 10.3295
| DALNEIGH | LW |  |  | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 19.8381 | 17.4081 | 17.4036 | 17.3965 | 17.3787 | 17.3588 | 17.3394 | 17.3204 | 17.3018 | 17.2837 | 17.264 | 17.2059 | 17.1123 | 17.018 | 16.9247 | 17.5349 | 17.5338 | 17.532 | 17.5274 | 17.5223 | 17.5174 | 17.5125 | 17.5078 | 17.5031 | 17.4981 | 17.4833 | 17.4594 | 17.4353 | 17.4115
| DALNEIGH | ST |  |  | 19.8359 | 19.8344 | 19.833 | 19.8312 | 19.8169 | 19.7996 | 19.7796 | 19.7568 | 19.7311 | 19.7227 | 19.6972 | 19.6548 | 19.4339 | 19.3086 | 17.3887 | 17.3687 | 17.3426 | 17.2933 | 17.2144 | 17.1199 | 17.0415 | 16.9615 | 16.8798 | 16.8026 | 16.5773 | 16.316 | 15.9003 | 15.6108 | 17.5283 | 17.5221 | 17.5144 | 17.5004 | 17.4697 | 17.4327 | 17.3978 | 17.3603 | 17.3204 | 17.2943 | 17.2179 | 17.0935 | 16.7914 | 16.5853
| DALNEIGH | SP |  |  | 19.8333 | 19.8308 | 19.8282 | 19.8255 | 19.8251 | 19.8246 | 19.8241 | 19.8235 | 19.8229 | 19.819 | 19.8059 | 19.7957 | 19.7302 | 19.5876 | 17.4037 | 17.3985 | 17.3927 | 17.3866 | 17.3671 | 17.3441 | 17.3243 | 17.3047 | 17.2795 | 17.2489 | 17.1582 | 17.0265 | 16.8469 | 16.5971 | 17.5302 | 17.527 | 17.5236 | 17.52 | 17.5148 | 17.5085 | 17.503 | 17.4976 | 17.4907 | 17.4801 | 17.4471 | 17.4059 | 17.3113 | 17.1413
COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | YES | 3.5541 | 3.5537 | 3.5126 | 3.4713 | 3.4277 | 3.3751 | 3.3207 | 3.2644 | 3.206 | 3.1475 | 3.0417 | 2.1828 | 1.9381 | 1.6772 | 3.2435 | 3.2372 | 3.2157 | 3.1826 | 3.1466 | 3.1077 | 3.0683 | 3.0154 | 2.4639 | 2.3953 | 2.2405 | 1.9309 | 1.6816 | 1.4162 | 3.3118 | 3.3071 | 3.2676 | 3.2194 | 3.1681 | 3.1096 | 3.0499 | 2.9788 | 2.465 | 2.3848 | 2.1999 | 1.8077 | 1.5108 | 1.1985
| DALRULZION | CT |  |  | 3.5541 | 3.5537 | 3.5126 | 3.4713 | 3.4277 | 3.3751 | 3.3207 | 3.2644 | 3.206 | 3.1475 | 3.0417 | 2.1828 | 1.9381 | 1.6772 | 3.2435 | 3.2381 | 3.2157 | 3.1826 | 3.1466 | 3.1077 | 3.0683 | 3.0154 | 2.4639 | 2.3953 | 2.2405 | 1.9309 | 1.6816 | 1.4162 | 3.3118 | 3.3076 | 3.2676 | 3.2194 | 3.1681 | 3.1096 | 3.0499 | 2.9788 | 2.465 | 2.3848 | 2.1999 | 1.8077 | 1.5108 | 1.1985
| DALRULZION | LW |  |  | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.5545 | 3.4696 | 3.4696 | 3.4696 | 3.2435 | 3.2372 | 3.2273 | 3.2023 | 3.1746 | 3.1474 | 3.1209 | 3.1169 | 3.1169 | 3.1169 | 3.1169 | 2.3955 | 2.2622 | 2.1303 | 3.312 | 3.3071 | 3.2994 | 3.2801 | 3.2587 | 3.2441 | 3.2399 | 3.2358 | 3.2318 | 3.2275 | 3.2147 | 2.394 | 2.2625 | 2.1323
| DALRULZION | ST |  |  | 3.5545 | 3.5544 | 3.5544 | 3.5543 | 3.5538 | 3.5533 | 3.5526 | 3.5519 | 3.551 | 3.5507 | 3.5499 | 3.506 | 3.4988 | 3.4946 | 3.246 | 3.2429 | 3.2387 | 3.2308 | 3.2197 | 3.2064 | 3.1908 | 3.1755 | 3.1604 | 3.1382 | 3.1123 | 3.0865 | 2.4648 | 2.3598 | 3.3139 | 3.3114 | 3.3082 | 3.3021 | 3.2933 | 3.283 | 3.2707 | 3.2587 | 3.2469 | 3.2394 | 3.2286 | 3.1682 | 2.4722 | 2.3685
| DALRULZION | SP |  |  | 3.5544 | 3.5543 | 3.5543 | 3.5542 | 3.5542 | 3.5542 | 3.5541 | 3.5541 | 3.5541 | 3.554 | 3.5536 | 3.5534 | 3.5515 | 3.5476 | 3.249 | 3.2485 | 3.2479 | 3.2473 | 3.2443 | 3.2407 | 3.2365 | 3.2323 | 3.227 | 3.218 | 3.1925 | 3.1532 | 3.1147 | 3.11 | 3.3161 | 3.3157 | 3.3153 | 3.3148 | 3.3124 | 3.3097 | 3.3064 | 3.3032 | 3.2991 | 3.2921 | 3.2723 | 3.244 | 3.2364 | 3.227
BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | 1.4563 | 1.4562 | 1.4297 | 1.4032 | 1.3756 | 1.3423 | 1.3078 | 1.2723 | 0.95848 | 0.88604 | 0.75223 | 0.5332 | 0.33805 | 0.14138 | 1.4083 | 1.4082 | 1.3727 | 1.3505 | 1.3365 | 1.3197 | 1.3023 | 1.284 | 0.93802 | 0.87071 | 0.73931 | 0.51624 | 0.31569 | 0.11348 | 1.3123 | 1.3122 | 1.2731 | 1.2339 | 1.1933 | 0.98763 | 0.92199 | 0.85137 | 0.77873 | 0.70428 | 0.56404 | 0.33372 | 0.1255 | -0.084186
| DALWHINNIE | CT |  |  | 1.4563 | 1.4562 | 1.4297 | 1.4032 | 1.3756 | 1.3423 | 1.3078 | 1.2723 | 0.95848 | 0.88604 | 0.75223 | 0.5332 | 0.33805 | 0.14138 | 1.4083 | 1.4082 | 1.3727 | 1.3505 | 1.3365 | 1.3197 | 1.3023 | 1.284 | 0.93802 | 0.87071 | 0.73931 | 0.51624 | 0.31569 | 0.11348 | 1.3123 | 1.3122 | 1.2731 | 1.2339 | 1.1933 | 0.98763 | 0.92199 | 0.85137 | 0.77873 | 0.70428 | 0.56404 | 0.33372 | 0.1255 | -0.084186
| DALWHINNIE | LW |  |  | 1.4564 | 1.4564 | 1.4448 | 1.4331 | 1.4215 | 1.4098 | 1.3981 | 1.3864 | 1.3747 | 1.363 | 1.3394 | 1.2996 | 0.98036 | 0.89685 | 1.4084 | 1.4084 | 1.3927 | 1.3771 | 1.3614 | 1.3534 | 1.3475 | 1.3415 | 1.3356 | 1.3297 | 1.3174 | 1.2968 | 0.92458 | 0.83968 | 1.3125 | 1.3125 | 1.2952 | 1.2779 | 1.2606 | 1.2433 | 1.226 | 1.2087 | 1.1914 | 1.174 | 0.95673 | 0.86772 | 0.77706 | 0.68467
| DALWHINNIE | ST |  |  | 1.4564 | 1.4564 | 1.4486 | 1.4408 | 1.433 | 1.4251 | 1.4172 | 1.4093 | 1.4013 | 1.3935 | 1.3698 | 1.3297 | 1.2878 | 0.94974 | 1.4084 | 1.4084 | 1.3979 | 1.3875 | 1.377 | 1.3664 | 1.3573 | 1.3533 | 1.3492 | 1.3451 | 1.3326 | 1.3116 | 0.9804 | 0.89288 | 1.3124 | 1.3124 | 1.3009 | 1.2893 | 1.2778 | 1.2662 | 1.2545 | 1.2428 | 1.2311 | 1.2195 | 1.1844 | 0.93273 | 0.8393 | 0.74458
| DALWHINNIE | SP |  |  | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4564 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125
WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | 32.3802 | 32.2779 | 32.1716 | 32.0137 | 31.8547 | 31.7003 | 31.5503 | 31.4095 | 31.2708 | 31.1744 | 30.9642 | 30.6234 | 30.2706 | 30.0303 | 27.395 | 27.3163 | 27.2314 | 27.0965 | 26.959 | 26.825 | 26.6946 | 26.5732 | 26.4537 | 26.3609 | 26.1347 | 25.7679 | 25.3895 | 24.9926 | 26.4056 | 26.3004 | 26.1898 | 26.0223 | 25.8531 | 25.6886 | 25.5289 | 25.3793 | 25.232 | 25.1241 | 24.8742 | 24.6796 | 24.5088 | 24.3157
| DENBURN | CT |  |  | 32.3802 | 32.2779 | 32.1716 | 32.0137 | 31.8547 | 31.7003 | 31.5503 | 31.4095 | 31.2708 | 31.1744 | 30.9642 | 30.6234 | 30.2706 | 30.0303 | 27.395 | 27.3163 | 27.2314 | 27.0965 | 26.959 | 26.825 | 26.6946 | 26.5732 | 26.4537 | 26.3609 | 26.1347 | 25.7679 | 25.3895 | 24.9926 | 26.4056 | 26.3004 | 26.1898 | 26.0223 | 25.8531 | 25.6886 | 25.5289 | 25.3793 | 25.232 | 25.1241 | 24.8742 | 24.6796 | 24.5088 | 24.3157
| DENBURN | LW |  |  | 32.4613 | 32.4388 | 32.4076 | 32.3391 | 32.2628 | 32.187 | 32.1118 | 32.0373 | 31.9632 | 31.8836 | 31.6455 | 31.2714 | 31.052 | 30.9395 | 27.4529 | 27.4302 | 27.3974 | 27.322 | 27.238 | 27.155 | 27.0731 | 26.9923 | 26.9125 | 26.8265 | 26.5702 | 26.1522 | 25.7257 | 25.2994 | 26.4873 | 26.4621 | 26.4267 | 26.3476 | 26.2595 | 26.1722 | 26.0858 | 26.0002 | 25.9153 | 25.8241 | 25.6103 | 25.482 | 25.3451 | 25.2041
| DENBURN | ST |  |  | 32.4577 | 32.4348 | 32.4058 | 32.353 | 32.2831 | 32.2009 | 32.1073 | 32.0156 | 31.9259 | 31.8853 | 31.7641 | 31.5688 | 31.3791 | 31.1958 | 27.4476 | 27.4233 | 27.392 | 27.334 | 27.2563 | 27.1643 | 27.0598 | 26.9574 | 26.8571 | 26.8134 | 26.684 | 26.4765 | 26.2652 | 26.0577 | 26.4827 | 26.4566 | 26.4234 | 26.3625 | 26.2816 | 26.1863 | 26.0778 | 25.9715 | 25.8676 | 25.8212 | 25.683 | 25.5993 | 25.5255 | 25.455
| DENBURN | SP |  |  | 32.4729 | 32.4645 | 32.4559 | 32.447 | 32.425 | 32.4008 | 32.3658 | 32.3312 | 32.2896 | 32.2669 | 32.2009 | 32.0878 | 31.9749 | 31.8639 | 27.4666 | 27.4598 | 27.4527 | 27.4454 | 27.4243 | 27.4006 | 27.3645 | 27.3287 | 27.2847 | 27.2625 | 27.1981 | 27.0907 | 26.9844 | 26.8797 | 26.5011 | 26.4923 | 26.4833 | 26.474 | 26.4498 | 26.423 | 26.3835 | 26.3445 | 26.2971 | 26.272 | 26.199 | 26.075 | 25.952 | 25.8316
TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42445123 | YES | 7.8207 | 7.8177 | 7.813 | 7.8005 | 7.7866 | 7.773 | 7.7597 | 7.7418 | 7.7172 | 7.6926 | 7.6476 | 7.5787 | 6.8571 | 6.7963 | 6.0278 | 6.0273 | 6.0268 | 6.0261 | 6.0237 | 6.0209 | 6.0176 | 6.0137 | 6.0094 | 6.0069 | 5.9987 | 5.9491 | 3.4167 | 3.2257 | 6.2618 | 6.2611 | 6.2601 | 6.2584 | 6.2548 | 6.2509 | 6.2465 | 6.2402 | 6.2336 | 6.2285 | 6.2128 | 6.1257 | 3.6983 | 3.5074
| DERVAIG | CT |  |  | 7.8207 | 7.8177 | 7.8134 | 7.8036 | 7.7915 | 7.7791 | 7.7665 | 7.7418 | 7.7172 | 7.6926 | 7.6476 | 7.5787 | 6.8571 | 6.7963 | 6.0278 | 6.0273 | 6.0268 | 6.0261 | 6.0237 | 6.0209 | 6.0176 | 6.0137 | 6.0094 | 6.0069 | 5.9987 | 5.9491 | 3.4167 | 3.2257 | 6.2618 | 6.2611 | 6.2601 | 6.2584 | 6.2548 | 6.2509 | 6.2465 | 6.2402 | 6.2336 | 6.2285 | 6.2128 | 6.1257 | 3.6983 | 3.5074
| DERVAIG | LW |  |  | 7.8211 | 7.818 | 7.813 | 7.8005 | 7.7866 | 7.773 | 7.7597 | 7.7467 | 7.734 | 7.7203 | 7.6796 | 7.6274 | 6.9371 | 6.9371 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 6.0284 | 5.9978 | 3.6223 | 3.5492 | 6.2624 | 6.2621 | 6.2615 | 6.26 | 6.2584 | 6.2568 | 6.2553 | 6.2538 | 6.2523 | 6.2507 | 6.246 | 6.1827 | 3.917 | 3.8362
| DERVAIG | ST |  |  | 7.8223 | 7.8206 | 7.8185 | 7.8145 | 7.8083 | 7.801 | 7.7864 | 7.7718 | 7.7574 | 7.7423 | 7.6987 | 7.6423 | 7.285 | 7.2781 | 6.0283 | 6.0282 | 6.0281 | 6.028 | 6.0272 | 6.0263 | 6.0252 | 6.0239 | 6.0225 | 6.0221 | 6.0206 | 6.003 | 3.976 | 3.8876 | 6.2625 | 6.2622 | 6.2619 | 6.2613 | 6.2599 | 6.2582 | 6.2555 | 6.2528 | 6.2498 | 6.2477 | 6.2414 | 6.2033 | 5.7977 | 5.783
| DERVAIG | SP |  |  | 7.8237 | 7.8234 | 7.8231 | 7.8227 | 7.8212 | 7.8194 | 7.8149 | 7.8104 | 7.8047 | 7.7987 | 7.7816 | 7.7553 | 7.7287 | 7.7009 | 6.0282 | 6.0281 | 6.0281 | 6.028 | 6.028 | 6.0279 | 6.0279 | 6.0279 | 6.0279 | 6.0277 | 6.0273 | 6.0269 | 6.0247 | 6.0198 | 6.2626 | 6.2625 | 6.2624 | 6.2622 | 6.262 | 6.2618 | 6.2613 | 6.2607 | 6.2601 | 6.2592 | 6.2569 | 6.2535 | 6.2484 | 6.2409
BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | YES | 18.7892 | 18.7821 | 18.7727 | 18.7541 | 18.6047 | 18.4428 | 18.2701 | 18.0895 | 17.8471 | 17.7828 | 17.6423 | 12.6381 | 11.394 | 10.2122 | 17.2742 | 17.2445 | 17.2013 | 17.1021 | 16.866 | 16.6362 | 16.4765 | 16.3065 | 16.0746 | 13.7567 | 13.4248 | 11.391 | 10.13 | 8.9315 | 17.4665 | 17.4526 | 17.4331 | 17.3904 | 17.2149 | 17.0275 | 16.8297 | 13.6658 | 13.4339 | 13.381 | 13.0147 | 10.807 | 9.4842 | 8.2248
| DINGWALL | CT |  |  | 18.7892 | 18.7821 | 18.7727 | 18.7541 | 18.6047 | 18.4428 | 18.2701 | 18.0895 | 17.8471 | 17.7828 | 17.6423 | 12.6381 | 11.394 | 10.2122 | 17.2742 | 17.2445 | 17.2013 | 17.1021 | 16.866 | 16.6362 | 16.4765 | 16.3065 | 16.0746 | 16.0217 | 13.4248 | 11.391 | 10.13 | 8.9315 | 17.4665 | 17.4526 | 17.4331 | 17.3904 | 17.2149 | 17.0275 | 16.8297 | 13.6658 | 13.4339 | 13.381 | 13.0147 | 10.807 | 9.4842 | 8.2248
| DINGWALL | LW |  |  | 19.1929 | 19.1923 | 19.1913 | 19.1887 | 19.0073 | 18.8225 | 18.6316 | 18.4271 | 18.1341 | 18.0813 | 17.9298 | 13.5257 | 13.2103 | 13.0987 | 17.6417 | 17.6369 | 17.6292 | 17.6102 | 17.4105 | 17.2077 | 16.9992 | 16.7775 | 16.4677 | 13.7567 | 13.6135 | 12.9023 | 12.5868 | 12.4753 | 17.8766 | 17.8747 | 17.8717 | 17.8642 | 17.6773 | 17.4871 | 17.2909 | 17.0812 | 13.5393 | 13.4893 | 13.3461 | 12.3191 | 12.0036 | 11.8921
| DINGWALL | ST |  |  | 18.7957 | 18.7935 | 18.7909 | 18.7865 | 18.6919 | 18.5891 | 18.488 | 18.3743 | 18.2013 | 18.1577 | 18.0441 | 14.2261 | 13.5849 | 13.1151 | 17.2958 | 17.2851 | 17.2711 | 17.2447 | 17.1203 | 16.9817 | 16.8373 | 16.6813 | 16.4668 | 16.3747 | 16.253 | 13.4244 | 12.412 | 11.806 | 17.4775 | 17.4728 | 17.4668 | 17.4558 | 17.3522 | 17.2387 | 17.1246 | 16.9982 | 13.7402 | 13.7042 | 13.6123 | 12.9247 | 11.9389 | 11.2942
| DINGWALL | SP |  |  | 18.7958 | 18.7944 | 18.7928 | 18.7912 | 18.7775 | 18.7638 | 18.7492 | 18.7332 | 18.7078 | 18.679 | 18.5786 | 18.4852 | 14.3327 | 13.9552 | 17.3043 | 17.3017 | 17.2987 | 17.2955 | 17.2733 | 17.2496 | 17.2207 | 17.1907 | 17.1472 | 17.0994 | 16.9441 | 16.765 | 13.4688 | 13.0913 | 17.4802 | 17.4784 | 17.4764 | 17.4743 | 17.458 | 17.4414 | 17.4225 | 17.4023 | 17.3714 | 17.3369 | 17.2201 | 17.101 | 13.0148 | 12.6373
CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | 1.3178 | 1.8175 | 1.8172 | 1.8167 | 1.8151 | 1.8133 | 1.8111 | 1.8086 | 1.8058 | 1.8042 | 1.7988 | 1.7863 | 1.7658 | 1.4292 | 1.2499 | 1.7492 | 1.7483 | 1.7463 | 1.7431 | 1.7397 | 1.736 | 1.7264 | 1.7195 | 1.7179 | 1.7125 | 1.7 | 1.4403 | 1.3356 | 1.2559 | 1.7549 | 1.7536 | 1.7521 | 1.7499 | 1.7474 | 1.7447 | 1.742 | 1.7392 | 1.7376 | 1.7322 | 1.7197 | 1.4453 | 1.3403
| DIPPEN | CT |  |  | 1.3178 | 1.8175 | 1.8172 | 1.8167 | 1.8151 | 1.8133 | 1.8111 | 1.8086 | 1.8058 | 1.8042 | 1.7988 | 1.7863 | 1.7658 | 1.4292 | 1.2499 | 1.7492 | 1.7483 | 1.7463 | 1.7431 | 1.7397 | 1.736 | 1.7264 | 1.7195 | 1.7179 | 1.7125 | 1.7 | 1.4403 | 1.3356 | 1.2559 | 1.7549 | 1.7536 | 1.7521 | 1.7499 | 1.7474 | 1.7447 | 1.742 | 1.7392 | 1.7376 | 1.7322 | 1.7197 | 1.4453 | 1.3403
| DIPPEN | LW |  |  | 1.3182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.8182 | 1.2503 | 1.7498 | 1.749 | 1.7469 | 1.7446 | 1.7424 | 1.7402 | 1.7382 | 1.7365 | 1.7346 | 1.7319 | 1.7319 | 1.7319 | 1.7319 | 1.2563 | 1.7554 | 1.7541 | 1.7533 | 1.7524 | 1.7516 | 1.7516 | 1.7516 | 1.7516 | 1.7516 | 1.7516 | 1.7516 | 1.7516 | 1.7516
| DIPPEN | ST |  |  | 1.3182 | 1.8181 | 1.8181 | 1.818 | 1.8177 | 1.8172 | 1.8167 | 1.8161 | 1.8154 | 1.8152 | 1.8145 | 1.8134 | 1.8075 | 1.8042 | 1.2505 | 1.7502 | 1.7498 | 1.7491 | 1.7478 | 1.7463 | 1.7439 | 1.7414 | 1.7388 | 1.7337 | 1.7282 | 1.7271 | 1.7212 | 1.7179 | 1.2565 | 1.7561 | 1.7555 | 1.7544 | 1.7533 | 1.7524 | 1.7511 | 1.7498 | 1.7488 | 1.7486 | 1.7479 | 1.7468 | 1.7409 | 1.7376
| DIPPEN | SP |  |  | 1.3181 | 1.818 | 1.818 | 1.8179 | 1.8179 | 1.8179 | 1.8178 | 1.8178 | 1.8178 | 1.8177 | 1.8173 | 1.8171 | 1.8153 | 1.8114 | 1.2507 | 1.7506 | 1.7504 | 1.7503 | 1.7501 | 1.7498 | 1.7491 | 1.7484 | 1.7476 | 1.7453 | 1.7388 | 1.7307 | 1.729 | 1.7251 | 1.2569 | 1.7567 | 1.7566 | 1.7565 | 1.756 | 1.7556 | 1.7545 | 1.7536 | 1.7533 | 1.7523 | 1.7507 | 1.7504 | 1.7487 | 1.7448
BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | 6.611 | 6.6091 | 6.6069 | 6.6027 | 6.5939 | 6.5838 | 6.5725 | 6.5589 | 6.544 | 6.5338 | 6.5015 | 6.4332 | 6.331 | 6.1479 | 5.763 | 5.7588 | 5.753 | 5.7404 | 5.7225 | 5.7035 | 5.6834 | 5.6575 | 5.6305 | 5.6072 | 5.536 | 5.4342 | 5.3332 | 5.1659 | 5.5201 | 5.5184 | 5.5163 | 5.5126 | 5.5041 | 5.4945 | 5.4836 | 5.4706 | 5.4563 | 5.4468 | 5.4173 | 5.3649 | 5.2787 | 3.8987
| DORNOCH | CT |  |  | 6.611 | 6.6091 | 6.6069 | 6.6027 | 6.5939 | 6.5838 | 6.5725 | 6.5589 | 6.544 | 6.5338 | 6.5015 | 6.4332 | 6.331 | 6.1479 | 5.763 | 5.7588 | 5.753 | 5.7404 | 5.7225 | 5.7035 | 5.6834 | 5.6575 | 5.6305 | 5.6072 | 5.536 | 5.4342 | 5.3332 | 5.1659 | 5.5201 | 5.5184 | 5.5163 | 5.5126 | 5.5041 | 5.4945 | 5.4836 | 5.4706 | 5.4563 | 5.4468 | 5.4173 | 5.3649 | 5.2787 | 3.8987
| DORNOCH | LW |  |  | 6.6131 | 6.6129 | 6.6125 | 6.6116 | 6.6106 | 6.6096 | 6.6087 | 6.6077 | 6.6068 | 6.6058 | 6.6028 | 6.5981 | 6.5933 | 6.5885 | 5.7669 | 5.7657 | 5.7639 | 5.7594 | 5.7544 | 5.7495 | 5.7447 | 5.7399 | 5.7353 | 5.7304 | 5.7156 | 5.6919 | 5.668 | 5.6444 | 5.5222 | 5.522 | 5.5217 | 5.5209 | 5.5201 | 5.5193 | 5.5186 | 5.5178 | 5.5171 | 5.5163 | 5.5139 | 5.51 | 5.5062 | 5.5024
| DORNOCH | ST |  |  | 6.6127 | 6.6121 | 6.6115 | 6.6104 | 6.6073 | 6.6036 | 6.5991 | 6.5942 | 6.589 | 6.5857 | 6.5761 | 6.5603 | 6.5212 | 6.4946 | 5.7657 | 5.7638 | 5.7614 | 5.7569 | 5.7491 | 5.7398 | 5.7278 | 5.7155 | 5.703 | 5.6911 | 5.6562 | 5.6001 | 5.5236 | 5.4951 | 5.5217 | 5.5212 | 5.5207 | 5.5198 | 5.5169 | 5.5135 | 5.5094 | 5.5049 | 5.5 | 5.4972 | 5.4887 | 5.475 | 5.4456 | 5.4291
| DORNOCH | SP |  |  | 6.6129 | 6.6126 | 6.6123 | 6.612 | 6.6116 | 6.6111 | 6.6105 | 6.6098 | 6.6089 | 6.6077 | 6.6041 | 6.5993 | 6.5899 | 6.5738 | 5.7672 | 5.7667 | 5.7662 | 5.7656 | 5.7638 | 5.7617 | 5.7585 | 5.7554 | 5.7513 | 5.7467 | 5.7333 | 5.7132 | 5.6893 | 5.6597 | 5.5219 | 5.5216 | 5.5213 | 5.521 | 5.5207 | 5.5203 | 5.5198 | 5.5192 | 5.5185 | 5.5175 | 5.5143 | 5.5103 | 5.5016 | 5.4862
CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | 2.9462 | 2.945 | 2.9249 | 2.9028 | 2.8876 | 2.8693 | 2.4956 | 2.4573 | 2.418 | 2.3789 | 2.2899 | 2.1398 | 1.986 | 1.8066 | 2.9105 | 2.9054 | 2.8773 | 2.8541 | 2.8371 | 2.8166 | 2.7951 | 2.7727 | 2.7491 | 2.7268 | 2.4358 | 2.2903 | 2.1417 | 1.9674 | 2.9809 | 2.9805 | 2.9579 | 2.9352 | 2.9103 | 2.4765 | 2.4444 | 2.4036 | 2.3616 | 2.3198 | 2.2276 | 2.0642 | 1.8923 | 1.6944
| DOUGLAS PIER | CT |  |  | 2.9462 | 2.945 | 2.9249 | 2.9028 | 2.8876 | 2.8693 | 2.4956 | 2.4573 | 2.418 | 2.3789 | 2.2899 | 2.1398 | 1.986 | 1.8066 | 2.9105 | 2.9054 | 2.8773 | 2.8541 | 2.8371 | 2.8166 | 2.7951 | 2.7727 | 2.7491 | 2.7268 | 2.4358 | 2.2903 | 2.1417 | 1.9674 | 2.9809 | 2.9805 | 2.9579 | 2.9352 | 2.9103 | 2.4765 | 2.4444 | 2.4036 | 2.3616 | 2.3198 | 2.2276 | 2.0642 | 1.8923 | 1.6944
| DOUGLAS PIER | LW |  |  | 2.9476 | 2.9474 | 2.9471 | 2.9463 | 2.9455 | 2.9447 | 2.9439 | 2.9431 | 2.9424 | 2.9416 | 2.9391 | 2.9352 | 2.9313 | 2.9301 | 2.9153 | 2.9141 | 2.9124 | 2.908 | 2.9031 | 2.8983 | 2.8942 | 2.8905 | 2.8868 | 2.8849 | 2.8849 | 2.8849 | 2.8849 | 2.8849 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815 | 2.9815
| DOUGLAS PIER | ST |  |  | 2.9475 | 2.9473 | 2.9471 | 2.9467 | 2.9453 | 2.9436 | 2.9413 | 2.9387 | 2.936 | 2.9343 | 2.9294 | 2.9213 | 2.9 | 2.4971 | 2.9156 | 2.9149 | 2.9141 | 2.9125 | 2.9096 | 2.9061 | 2.8995 | 2.8929 | 2.8866 | 2.881 | 2.8744 | 2.8712 | 2.8547 | 2.8454 | 2.9813 | 2.9812 | 2.9811 | 2.981 | 2.9799 | 2.9786 | 2.9771 | 2.9754 | 2.9735 | 2.9729 | 2.971 | 2.9678 | 2.9513 | 2.4684
| DOUGLAS PIER | SP |  |  | 2.9474 | 2.9473 | 2.9471 | 2.9469 | 2.9468 | 2.9467 | 2.9464 | 2.9461 | 2.9457 | 2.945 | 2.9431 | 2.9406 | 2.9349 | 2.9249 | 2.916 | 2.9157 | 2.9155 | 2.9152 | 2.9147 | 2.914 | 2.9123 | 2.9106 | 2.9085 | 2.9058 | 2.8979 | 2.8877 | 2.8786 | 2.8701 | 2.9812 | 2.9811 | 2.9809 | 2.9808 | 2.9807 | 2.9807 | 2.9807 | 2.9806 | 2.9806 | 2.9804 | 2.9796 | 2.979 | 2.9751 | 2.9667
DOUNREAY | DOUNREAY | MINIMUM HEADROOM | NC 98156665 | NO | 19.8997 | 19.7962 | 19.6961 | 19.5677 | 19.4357 | 19.3091 | 19.186 | 19.0682 | 18.9642 | 18.9159 | 18.8415 | 18.6724 | 18.5369 | 18.4212 | 18.5417 | 18.4801 | 18.4202 | 18.342 | 18.255 | 18.1697 | 18.0863 | 18.0086 | 17.9372 | 17.9059 | 17.8559 | 17.7259 | 17.6224 | 17.5403 | 18.747 | 18.6533 | 18.563 | 18.4485 | 18.3268 | 18.2081 | 18.0926 | 17.9804 | 17.881 | 17.8353 | 17.7652 | 17.6067 | 17.4805 | 17.3744
| DOUNREAY | CT |  |  | 19.8997 | 19.7962 | 19.6961 | 19.5677 | 19.4357 | 19.3091 | 19.186 | 19.0682 | 18.9642 | 18.9159 | 18.8415 | 18.6724 | 18.5369 | 18.4212 | 18.5417 | 18.4801 | 18.4202 | 18.342 | 18.255 | 18.1697 | 18.0863 | 18.0086 | 17.9372 | 17.9059 | 17.8559 | 17.7259 | 17.6224 | 17.5403 | 18.747 | 18.6533 | 18.563 | 18.4485 | 18.3268 | 18.2081 | 18.0926 | 17.9804 | 17.881 | 17.8353 | 17.7652 | 17.6067 | 17.4805 | 17.3744
| DOUNREAY | LW |  |  | 19.9938 | 19.9852 | 19.977 | 19.9675 | 19.9402 | 19.9115 | 19.8812 | 19.8488 | 19.8096 | 19.7922 | 19.7387 | 19.6323 | 19.5367 | 19.4564 | 18.5978 | 18.5928 | 18.5879 | 18.5824 | 18.5595 | 18.5356 | 18.5106 | 18.4838 | 18.4496 | 18.4375 | 18.4006 | 18.3239 | 18.2549 | 18.2032 | 18.832 | 18.8242 | 18.8167 | 18.808 | 18.7817 | 18.754 | 18.7248 | 18.6936 | 18.6554 | 18.6391 | 18.5892 | 18.4891 | 18.399 | 18.3248
| DOUNREAY | ST |  |  | 19.9964 | 19.9901 | 19.9837 | 19.9747 | 19.9575 | 19.9396 | 19.9223 | 19.9041 | 19.8809 | 19.8696 | 19.8341 | 19.7629 | 19.6732 | 19.624 | 18.5988 | 18.5946 | 18.5902 | 18.5837 | 18.5687 | 18.5527 | 18.5387 | 18.5239 | 18.5038 | 18.4956 | 18.4708 | 18.4147 | 18.3385 | 18.3009 | 18.835 | 18.8298 | 18.8246 | 18.8176 | 18.803 | 18.7881 | 18.772 | 18.7551 | 18.7331 | 18.7228 | 18.6905 | 18.6241 | 18.5387 | 18.4934
| DOUNREAY | SP |  |  | 19.9931 | 19.9854 | 19.9776 | 19.9699 | 19.957 | 19.9442 | 19.9319 | 19.9197 | 19.9068 | 19.8939 | 19.8549 | 19.787 | 19.6462 | 19.5644 | 18.5973 | 18.5926 | 18.588 | 18.5833 | 18.5748 | 18.5663 | 18.5584 | 18.5506 | 18.542 | 18.5333 | 18.5067 | 18.4634 | 18.3429 | 18.2803 | 18.8315 | 18.8245 | 18.8175 | 18.8106 | 18.7992 | 18.788 | 18.7769 | 18.7658 | 18.754 | 18.7421 | 18.706 | 18.644 | 18.508 | 18.4307
ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | 3.3397 | 3.3395 | 3.3392 | 3.3388 | 3.3374 | 3.3357 | 3.3338 | 3.3315 | 3.329 | 3.3276 | 3.3227 | 3.3116 | 2.4858 | 2.407 | 2.9774 | 2.9767 | 2.9757 | 2.9737 | 2.9705 | 2.9672 | 2.9636 | 2.9523 | 2.9409 | 2.9372 | 2.9324 | 2.9213 | 2.2887 | 2.1958 | 3.2006 | 3.2003 | 3.2 | 3.1996 | 3.1982 | 3.1965 | 3.1946 | 3.1924 | 3.1899 | 3.1884 | 3.1836 | 3.1725 | 2.3914 | 2.3317
| DRIMORE | CT |  |  | 3.3397 | 3.3395 | 3.3392 | 3.3388 | 3.3374 | 3.3357 | 3.3338 | 3.3315 | 3.329 | 3.3276 | 3.3227 | 3.3116 | 2.4858 | 2.407 | 2.9774 | 2.9767 | 2.9757 | 2.9737 | 2.9705 | 2.9672 | 2.9636 | 2.9523 | 2.9409 | 2.9372 | 2.9324 | 2.9213 | 2.2887 | 2.1958 | 3.2006 | 3.2003 | 3.2 | 3.1996 | 3.1982 | 3.1965 | 3.1946 | 3.1924 | 3.1899 | 3.1884 | 3.1836 | 3.1725 | 2.3914 | 2.3317
| DRIMORE | LW |  |  | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.0673 | 3.0673 | 2.9777 | 2.9772 | 2.9763 | 2.974 | 2.9716 | 2.9692 | 2.9668 | 2.9645 | 2.9622 | 2.9598 | 2.9526 | 2.9498 | 2.4703 | 2.4558 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 2.4383 | 2.4383
| DRIMORE | ST |  |  | 3.3401 | 3.3401 | 3.3401 | 3.34 | 3.3399 | 3.3397 | 3.3395 | 3.3393 | 3.339 | 3.3389 | 3.3387 | 3.3382 | 3.1996 | 3.1984 | 2.9779 | 2.9776 | 2.9773 | 2.9765 | 2.9754 | 2.9741 | 2.9699 | 2.9658 | 2.9616 | 2.9552 | 2.9483 | 2.9479 | 2.8709 | 2.4877 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2007 | 3.2006 | 3.2004 | 3.2001 | 3.1999 | 3.1998 | 3.1995 | 3.1991 | 3.0582 | 3.057
| DRIMORE | SP |  |  | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 3.3401 | 2.9782 | 2.9782 | 2.9781 | 2.9781 | 2.9778 | 2.9775 | 2.9761 | 2.9747 | 2.973 | 2.9705 | 2.9633 | 2.9522 | 2.9498 | 2.9498 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009 | 3.2009
CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | 4.9547 | 4.9537 | 4.9467 | 4.9392 | 4.9029 | 4.8625 | 4.8193 | 4.7734 | 4.7139 | 4.6932 | 4.6454 | 4.4685 | 4.2788 | 3.9871 | 4.5754 | 4.5709 | 4.5555 | 4.5322 | 4.4792 | 4.4216 | 4.3595 | 4.2835 | 4.1946 | 4.1419 | 3.9969 | 3.6623 | 3.3125 | 2.9718 | 4.4363 | 4.4353 | 4.426 | 4.4161 | 4.3775 | 4.3342 | 4.264 | 4.1807 | 4.0842 | 4.0237 | 3.8633 | 3.5026 | 3.1282 | 2.7638
| DRUMNADROCHIT | CT |  |  | 4.9547 | 4.9537 | 4.9467 | 4.9392 | 4.9029 | 4.8625 | 4.8193 | 4.7734 | 4.7139 | 4.6932 | 4.6454 | 4.4685 | 4.2788 | 3.9871 | 4.5754 | 4.5709 | 4.5555 | 4.5322 | 4.4792 | 4.4216 | 4.3595 | 4.2835 | 4.1946 | 4.1419 | 3.9969 | 3.6623 | 3.3125 | 2.9718 | 4.4363 | 4.4353 | 4.426 | 4.4161 | 4.3775 | 4.3342 | 4.264 | 4.1807 | 4.0842 | 4.0237 | 3.8633 | 3.5026 | 3.1282 | 2.7638
| DRUMNADROCHIT | LW |  |  | 4.9562 | 4.9562 | 4.9562 | 4.9562 | 4.918 | 4.8791 | 4.8389 | 4.7957 | 4.7336 | 4.7229 | 4.6923 | 4.6227 | 4.5475 | 4.5209 | 4.5777 | 4.5775 | 4.5772 | 4.5732 | 4.5306 | 4.4873 | 4.4427 | 4.3954 | 4.3292 | 4.3141 | 4.2653 | 4.1494 | 4.0276 | 3.9549 | 4.4378 | 4.4378 | 4.4378 | 4.4378 | 4.3996 | 4.3607 | 4.3204 | 4.2773 | 4.2152 | 4.2045 | 4.1739 | 4.0804 | 3.957 | 3.8827
| DRUMNADROCHIT | ST |  |  | 4.9558 | 4.9556 | 4.9554 | 4.9551 | 4.9353 | 4.9138 | 4.8929 | 4.8691 | 4.8326 | 4.8246 | 4.804 | 4.7321 | 4.5784 | 4.5205 | 4.5771 | 4.5753 | 4.5721 | 4.566 | 4.5383 | 4.5075 | 4.4772 | 4.436 | 4.3799 | 4.3493 | 4.2634 | 4.0866 | 3.829 | 3.6675 | 4.4374 | 4.4372 | 4.437 | 4.4367 | 4.4169 | 4.3954 | 4.3745 | 4.3507 | 4.3116 | 4.2803 | 4.1921 | 4.0116 | 3.7504 | 3.5844
| DRUMNADROCHIT | SP |  |  | 4.9554 | 4.9549 | 4.9545 | 4.954 | 4.9513 | 4.9487 | 4.946 | 4.9431 | 4.9382 | 4.9324 | 4.912 | 4.8942 | 4.7016 | 4.6083 | 4.5769 | 4.5764 | 4.5759 | 4.5754 | 4.5721 | 4.5668 | 4.561 | 4.5549 | 4.5462 | 4.5364 | 4.5044 | 4.4589 | 4.2291 | 4.1005 | 4.4369 | 4.4365 | 4.4361 | 4.4356 | 4.4329 | 4.4303 | 4.4276 | 4.4246 | 4.4198 | 4.414 | 4.3936 | 4.3758 | 4.1601 | 4.0303
GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | 0.33398 | 1.6339 | 1.6068 | 1.5806 | 1.5595 | 1.5351 | 1.4703 | 1.4359 | 1.4004 | 1.3642 | 1.2964 | 1.1841 | 1.0843 | 0.9844 | 0.27196 | 1.5717 | 1.5565 | 1.5458 | 1.4906 | 1.458 | 1.4245 | 1.3892 | 1.3528 | 1.3155 | 1.2472 | 1.1354 | 1.0356 | 0.93548 | 0.26905 | 1.5689 | 1.5426 | 1.5201 | 1.4817 | 1.4483 | 1.4138 | 1.3775 | 1.34 | 1.3012 | 1.2301 | 1.1137 | 1.01 | 0.90615
| DRUMRUNIE | CT |  |  | 0.33398 | 1.6339 | 1.6068 | 1.5806 | 1.5595 | 1.5351 | 1.4703 | 1.4359 | 1.4004 | 1.3642 | 1.2964 | 1.1841 | 1.0843 | 0.9844 | 0.27196 | 1.5717 | 1.5565 | 1.5458 | 1.4906 | 1.458 | 1.4245 | 1.3892 | 1.3528 | 1.3155 | 1.2472 | 1.1354 | 1.0356 | 0.93548 | 0.26905 | 1.5689 | 1.5426 | 1.5201 | 1.4817 | 1.4483 | 1.4138 | 1.3775 | 1.34 | 1.3012 | 1.2301 | 1.1137 | 1.01 | 0.90615
| DRUMRUNIE | LW |  |  | 0.33405 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 0.27201 | 1.5718 | 1.5714 | 1.5706 | 1.5696 | 1.5687 | 1.5679 | 1.5672 | 1.5665 | 1.5659 | 1.5649 | 1.5648 | 1.5648 | 1.5648 | 0.26911 | 1.569 | 1.5689 | 1.5685 | 1.5682 | 1.5678 | 1.5674 | 1.5671 | 1.5669 | 1.5667 | 1.5659 | 1.5659 | 1.5659 | 1.5659
| DRUMRUNIE | ST |  |  | 0.33405 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 0.2721 | 1.572 | 1.5718 | 1.5716 | 1.5712 | 1.5708 | 1.5702 | 1.5697 | 1.5692 | 1.5681 | 1.5656 | 1.5648 | 1.5648 | 1.5648 | 0.26914 | 1.5691 | 1.569 | 1.5689 | 1.5688 | 1.5686 | 1.5684 | 1.5682 | 1.568 | 1.5675 | 1.5665 | 1.5659 | 1.5659 | 1.5659
| DRUMRUNIE | SP |  |  | 0.33405 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 1.634 | 0.2722 | 1.5722 | 1.5722 | 1.5722 | 1.572 | 1.5719 | 1.5714 | 1.5709 | 1.5703 | 1.5698 | 1.5684 | 1.5666 | 1.5655 | 1.5649 | 0.26918 | 1.5692 | 1.5692 | 1.5692 | 1.5691 | 1.5691 | 1.5689 | 1.5687 | 1.5684 | 1.5682 | 1.5677 | 1.5669 | 1.5664 | 1.5659
STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | 8.2708 | 8.2206 | 8.1704 | 8.1018 | 8.0319 | 7.9627 | 7.8948 | 7.8278 | 7.7555 | 7.7161 | 7.6471 | 7.5176 | 7.3529 | 5.9465 | 7.388 | 7.3598 | 7.3307 | 7.2899 | 7.2465 | 7.203 | 7.1597 | 7.1066 | 5.9618 | 5.898 | 5.7474 | 5.4865 | 5.1898 | 4.8676 | 7.7194 | 7.6679 | 7.6162 | 7.5453 | 7.4729 | 7.4014 | 7.3312 | 5.9722 | 5.8842 | 5.8268 | 5.7025 | 5.4837 | 5.2289 | 4.9472
| DRYMEN | CT |  |  | 8.2708 | 8.2206 | 8.1704 | 8.1018 | 8.0319 | 7.9627 | 7.8948 | 7.8278 | 7.7555 | 7.7161 | 7.6471 | 7.5176 | 7.3529 | 5.9465 | 7.388 | 7.3598 | 7.3307 | 7.2899 | 7.2465 | 7.203 | 7.1597 | 7.1066 | 5.9618 | 5.898 | 5.7474 | 5.4865 | 5.1898 | 4.8676 | 7.7194 | 7.6679 | 7.6162 | 7.5453 | 7.4729 | 7.4014 | 7.3312 | 5.9722 | 5.8842 | 5.8268 | 5.7025 | 5.4837 | 5.2289 | 4.9472
| DRYMEN | LW |  |  | 8.317 | 8.3129 | 8.309 | 8.3044 | 8.2993 | 8.2936 | 8.2874 | 8.2809 | 8.2731 | 8.265 | 8.2395 | 8.235 | 8.1795 | 8.1111 | 7.4135 | 7.4103 | 7.4067 | 7.4005 | 7.3936 | 7.3865 | 7.3792 | 7.3718 | 7.3638 | 7.3553 | 7.3294 | 7.3264 | 7.2768 | 7.2204 | 7.7665 | 7.762 | 7.7574 | 7.7514 | 7.7446 | 7.7373 | 7.7296 | 7.7215 | 7.7121 | 7.7024 | 7.6719 | 7.6593 | 7.5954 | 7.5184
| DRYMEN | ST |  |  | 8.3183 | 8.3154 | 8.3125 | 8.3085 | 8.303 | 8.2973 | 8.2904 | 8.2832 | 8.2754 | 8.2701 | 8.2526 | 8.2227 | 8.1691 | 8.1661 | 7.4127 | 7.4091 | 7.4049 | 7.3978 | 7.3872 | 7.3751 | 7.3623 | 7.3493 | 7.3359 | 7.3238 | 7.2871 | 7.2273 | 7.144 | 5.9137 | 7.7674 | 7.7637 | 7.7598 | 7.754 | 7.746 | 7.7372 | 7.7274 | 7.7173 | 7.7067 | 7.6981 | 7.6709 | 7.6255 | 7.5566 | 7.5383
| DRYMEN | SP |  |  | 8.3164 | 8.3125 | 8.3086 | 8.3047 | 8.299 | 8.2933 | 8.2877 | 8.2821 | 8.2764 | 8.2704 | 8.2524 | 8.2207 | 8.1638 | 8.1575 | 7.4135 | 7.4111 | 7.4086 | 7.4061 | 7.4013 | 7.3961 | 7.3904 | 7.3846 | 7.378 | 7.3709 | 7.3497 | 7.3157 | 7.2578 | 7.2505 | 7.7661 | 7.7621 | 7.758 | 7.7539 | 7.7475 | 7.741 | 7.7344 | 7.7277 | 7.7207 | 7.7134 | 7.6914 | 7.6534 | 7.5906 | 7.5786
DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | 3.389 | 3.3862 | 3.3705 | 3.3502 | 3.3079 | 3.2613 | 3.2124 | 3.1651 | 3.1075 | 2.4794 | 2.3924 | 1.5713 | 1.3431 | 1.0989 | 3.088 | 3.086 | 3.0732 | 3.0573 | 3.0197 | 2.9782 | 2.4424 | 2.383 | 2.3141 | 2.2716 | 2.1555 | 1.4126 | 1.1662 | 0.90566 | 3.5055 | 3.4909 | 3.4623 | 3.449 | 3.4144 | 3.3753 | 3.3336 | 3.2898 | 2.4831 | 2.445 | 2.3529 | 1.5372 | 1.289 | 1.0254
| DRYNOCH | CT |  |  | 3.389 | 3.3862 | 3.3705 | 3.3502 | 3.3079 | 3.2613 | 3.2124 | 3.1651 | 3.1075 | 2.4794 | 2.3924 | 1.5713 | 1.3431 | 1.0989 | 3.088 | 3.086 | 3.0732 | 3.0573 | 3.0197 | 2.9782 | 2.4424 | 2.383 | 2.3141 | 2.2716 | 2.1555 | 1.4126 | 1.1662 | 0.90566 | 3.5055 | 3.4909 | 3.4623 | 3.449 | 3.4144 | 3.3753 | 3.3336 | 3.2898 | 2.4831 | 2.445 | 2.3529 | 1.5372 | 1.289 | 1.0254
| DRYNOCH | LW |  |  | 3.3921 | 3.3917 | 3.3911 | 3.3897 | 3.3603 | 3.3303 | 3.2995 | 3.2665 | 3.2197 | 3.2104 | 3.1834 | 1.9626 | 1.9255 | 1.9118 | 3.0903 | 3.0901 | 3.0898 | 3.0889 | 3.06 | 3.0306 | 3.0003 | 2.9679 | 2.9216 | 2.9129 | 2.4987 | 1.9162 | 1.8287 | 1.7657 | 3.5198 | 3.5174 | 3.5136 | 3.5042 | 3.4657 | 3.427 | 3.3913 | 3.3598 | 3.3144 | 3.3066 | 3.2843 | 1.9597 | 1.9225 | 1.9094
| DRYNOCH | ST |  |  | 3.3914 | 3.3906 | 3.3896 | 3.3877 | 3.375 | 3.3611 | 3.3476 | 3.3328 | 3.3113 | 3.3045 | 3.2863 | 2.3489 | 2.2567 | 2.1716 | 3.0899 | 3.0894 | 3.0887 | 3.0874 | 3.0757 | 3.0628 | 3.0503 | 3.0365 | 3.0159 | 3.0101 | 2.9948 | 2.1726 | 2.0259 | 1.9191 | 3.5164 | 3.5116 | 3.5053 | 3.4931 | 3.4665 | 3.4552 | 3.4444 | 3.4322 | 3.4133 | 3.4092 | 3.3987 | 2.3401 | 2.2464 | 2.1772
| DRYNOCH | SP |  |  | 3.3919 | 3.3917 | 3.3914 | 3.391 | 3.3902 | 3.3879 | 3.3856 | 3.3831 | 3.3794 | 3.3754 | 3.3619 | 3.3481 | 3.2432 | 3.1996 | 3.0901 | 3.0899 | 3.0897 | 3.0894 | 3.0889 | 3.0869 | 3.0849 | 3.0828 | 3.0795 | 3.0759 | 3.0635 | 3.0514 | 2.9481 | 2.4787 | 3.5208 | 3.5199 | 3.5188 | 3.5176 | 3.5122 | 3.5046 | 3.4971 | 3.4895 | 3.4794 | 3.4693 | 3.4557 | 3.4466 | 3.3461 | 3.3066
KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | YES | 10.7701 | 10.6653 | 10.5633 | 10.431 | 10.1831 | 9.9197 | 9.6395 | 9.3393 | 8.9396 | 8.824 | 8.6064 | 3.9537 | -0.00073991 | -4.1093 | 8.6862 | 8.6025 | 8.519 | 8.4035 | 8.1704 | 7.9211 | 7.6542 | 7.3393 | 6.927 | 6.7817 | 4.8706 | 2.895 | -0.70134 | -4.2224 | 7.7865 | 7.6681 | 7.551 | 7.3923 | 7.1176 | 6.8281 | 6.5434 | 6.2477 | 5.8531 | 4.9468 | 4.5897 | 2.4234 | -1.754 | -5.9817
| DUFFTOWN | CT |  |  | 10.7701 | 10.6653 | 10.5633 | 10.431 | 10.1831 | 9.9197 | 9.6395 | 9.3393 | 8.9396 | 8.824 | 8.6064 | 3.9537 | -0.00073991 | -4.1093 | 8.6862 | 8.6025 | 8.519 | 8.4035 | 8.1704 | 7.9211 | 7.6542 | 7.3393 | 6.927 | 6.7817 | 4.8706 | 2.895 | -0.70134 | -4.2224 | 7.7865 | 7.6681 | 7.551 | 7.3923 | 7.1176 | 6.8281 | 6.5434 | 6.2477 | 5.8531 | 4.9468 | 4.5897 | 2.4234 | -1.754 | -5.9817
| DUFFTOWN | LW |  |  | 10.8658 | 10.8571 | 10.8488 | 10.8392 | 10.668 | 10.4927 | 10.3107 | 10.1022 | 9.7884 | 9.7175 | 9.4907 | 8.8668 | 8.3067 | 8.009 | 8.7598 | 8.7494 | 8.737 | 8.7144 | 8.5289 | 8.3398 | 8.1447 | 7.9237 | 7.5981 | 7.5144 | 7.2506 | 4.6369 | 4.1356 | 3.9045 | 7.8917 | 7.8787 | 7.8638 | 7.8388 | 7.6506 | 7.4585 | 7.26 | 7.0352 | 6.7052 | 6.6168 | 6.3382 | 4.9097 | 4.3353 | 3.9509
| DUFFTOWN | ST |  |  | 10.8689 | 10.863 | 10.8571 | 10.8492 | 10.7668 | 10.6792 | 10.5938 | 10.4918 | 10.3137 | 10.2684 | 10.1392 | 7.7686 | 2.5028 | -0.24312 | 8.7636 | 8.7573 | 8.7503 | 8.7394 | 8.6523 | 8.5587 | 8.4543 | 8.3339 | 8.1378 | 8.0645 | 7.8549 | 4.1664 | 1.6466 | -0.7505 | 7.8966 | 7.8884 | 7.8796 | 7.8665 | 7.7772 | 7.6816 | 7.5755 | 7.4533 | 7.2556 | 7.1811 | 6.9671 | 3.7099 | 0.85885 | -1.9955
| DUFFTOWN | SP |  |  | 10.8648 | 10.8569 | 10.849 | 10.8411 | 10.8187 | 10.7968 | 10.7748 | 10.7506 | 10.7147 | 10.6754 | 10.5263 | 8.2152 | 2.8243 | 1.1117 | 8.7624 | 8.7561 | 8.7498 | 8.7434 | 8.722 | 8.7007 | 8.674 | 8.6453 | 8.6029 | 8.5543 | 8.3788 | 4.8632 | 2.2356 | 0.57537 | 7.894 | 7.8851 | 7.8763 | 7.8673 | 7.8421 | 7.8172 | 7.7873 | 7.7553 | 7.7098 | 7.6583 | 7.4743 | 4.356 | 1.5217 | -0.37154
BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | 19.8526 | 19.7644 | 19.6526 | 19.5203 | 19.2085 | 18.8756 | 18.5284 | 18.1677 | 17.7207 | 11.8811 | 8.5218 | 4.4687 | -1.1075 | -6.3667 | 17.0412 | 16.933 | 16.7852 | 16.5469 | 15.9587 | 15.3787 | 14.8707 | 14.5062 | 10.2819 | 9.2311 | 5.3771 | 1.0017 | -4.8915 | -10.85 | 15.9848 | 15.8836 | 15.7534 | 15.5791 | 15.1719 | 14.7529 | 10.7415 | 9.9572 | 8.8886 | 7.8416 | 3.9368 | -0.49754 | -6.8611 | -12.8706
| DUNBLANE | CT |  |  | 19.8526 | 19.7644 | 19.6526 | 19.5203 | 19.2085 | 18.8756 | 18.5284 | 18.1677 | 17.7207 | 11.9727 | 9.2642 | 4.4687 | -1.1075 | -6.3667 | 17.0412 | 16.933 | 16.7852 | 16.5469 | 15.9587 | 15.3787 | 14.8707 | 14.5062 | 10.6384 | 9.6931 | 6.6301 | 1.353 | -4.8915 | -10.85 | 15.9848 | 15.8836 | 15.7534 | 15.5791 | 15.1719 | 14.7529 | 10.7415 | 9.9572 | 8.9279 | 8.0059 | 4.8955 | -0.4946 | -6.8611 | -12.8706
| DUNBLANE | LW |  |  | 19.9359 | 19.929 | 19.9224 | 19.9147 | 19.6578 | 19.3923 | 19.1146 | 18.8138 | 18.38 | 11.8811 | 8.5218 | 4.648 | 1.2842 | -1.3786 | 17.1471 | 17.1385 | 17.1284 | 17.1103 | 16.4728 | 15.831 | 15.2103 | 14.8463 | 10.2819 | 9.2311 | 5.3771 | 1.0017 | -2.8272 | -5.9106 | 16.0811 | 16.0731 | 16.0649 | 16.0533 | 15.6758 | 15.2909 | 11.2009 | 10.2028 | 8.8886 | 7.8416 | 3.9368 | -0.49754 | -4.3579 | -7.4526
| DUNBLANE | ST |  |  | 20.3572 | 19.9298 | 19.9236 | 19.9155 | 19.7805 | 19.6343 | 19.4893 | 19.3253 | 19.076 | 19.0054 | 11.3875 | 7.6967 | 2.7321 | -2.3399 | 17.4589 | 17.0817 | 17.038 | 16.9571 | 16.5808 | 16.1824 | 15.8455 | 15.4527 | 15.1253 | 11.3418 | 8.5612 | 4.3724 | -1.2375 | -7.1509 | 16.5016 | 16.0562 | 16.0378 | 16.0062 | 15.7947 | 15.5686 | 15.3625 | 15.1702 | 10.7029 | 9.9267 | 7.1601 | 2.9209 | -2.738 | -8.6434
| DUNBLANE | SP |  |  | 20.3509 | 20.3418 | 20.3326 | 20.3232 | 20.2969 | 20.2711 | 20.2449 | 20.2168 | 20.1765 | 20.1302 | 19.9701 | 19.7932 | 11.8168 | 10.1343 | 17.5339 | 17.4694 | 17.4568 | 17.4436 | 17.3544 | 17.2554 | 17.1458 | 17.0356 | 16.8863 | 16.7077 | 16.0011 | 15.6586 | 9.1082 | 7.2721 | 16.5207 | 16.4936 | 16.4829 | 16.4719 | 16.425 | 16.3754 | 16.3222 | 16.2675 | 16.1922 | 16.1036 | 15.8271 | 10.6505 | 7.7936 | 5.933
DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | YES | 27.5728 | 27.4208 | 27.2609 | 26.9123 | 26.7278 | 26.1534 | 25.5918 | 22.8191 | 21.9886 | 21.7851 | 21.1714 | 20.138 | 19.3886 | 18.1035 | 24.8563 | 24.7391 | 24.6162 | 24.1876 | 24.0946 | 23.4588 | 21.6567 | 21.1507 | 20.3213 | 20.1184 | 19.5087 | 18.1623 | 16.4072 | 14.9621 | 25.0145 | 24.8818 | 24.7475 | 24.3736 | 24.2896 | 23.6649 | 21.679 | 21.1689 | 20.3355 | 20.1286 | 19.5057 | 18.3749 | 16.5037 | 15.0578
| DUNOON | CT |  |  | 27.5728 | 27.4208 | 27.2609 | 27.0463 | 26.7278 | 26.3361 | 25.9629 | 25.5902 | 25.1931 | 23.2706 | 22.8641 | 20.8286 | 19.4607 | 18.1035 | 24.8563 | 24.7391 | 24.6162 | 24.4866 | 24.2657 | 23.9811 | 23.7419 | 23.5022 | 21.7817 | 21.5243 | 20.8113 | 18.2787 | 16.4072 | 14.9621 | 25.0145 | 24.8818 | 24.7475 | 24.5903 | 24.3327 | 24.0008 | 23.6861 | 23.3725 | 21.75 | 21.5031 | 20.8385 | 18.3749 | 16.5037 | 15.0578
| DUNOON | LW |  |  | 27.6174 | 27.576 | 27.5306 | 27.4915 | 27.2231 | 26.8489 | 26.4619 | 26.0621 | 25.6522 | 23.272 | 22.8252 | 21.874 | 20.849 | 20.1927 | 24.8703 | 24.8338 | 24.7949 | 24.7689 | 24.5152 | 24.1557 | 23.7833 | 23.3982 | 21.7741 | 21.6303 | 21.1982 | 20.2494 | 19.0384 | 18.1983 | 25.0435 | 25.0076 | 24.9706 | 24.952 | 24.7064 | 24.3545 | 23.9894 | 23.6112 | 21.7758 | 21.6263 | 21.1764 | 20.2209 | 19.1907 | 18.3824
| DUNOON | ST |  |  | 27.7663 | 27.7379 | 27.7065 | 26.9123 | 26.8054 | 26.1534 | 25.5918 | 22.8191 | 21.9886 | 21.7851 | 21.1714 | 20.138 | 19.3886 | 18.9913 | 25.0198 | 24.9964 | 24.971 | 24.1876 | 24.0946 | 23.4588 | 21.6567 | 21.1507 | 20.3213 | 20.1184 | 19.5087 | 18.1623 | 17.0951 | 16.381 | 25.1949 | 25.1733 | 25.1508 | 24.3736 | 24.2896 | 23.6649 | 21.679 | 21.1689 | 20.3355 | 20.1286 | 19.5057 | 18.3882 | 17.381 | 16.711
| DUNOON | SP |  |  | 27.8457 | 27.8294 | 27.813 | 27.4217 | 27.3692 | 26.5068 | 26.4457 | 26.3849 | 23.1544 | 22.9893 | 22.4943 | 21.6318 | 21.0395 | 20.7732 | 25.0968 | 25.0831 | 25.0691 | 24.6805 | 24.6343 | 23.7789 | 23.7273 | 23.676 | 21.5108 | 21.3498 | 20.8667 | 20.0292 | 19.4567 | 19.1987 | 25.2682 | 25.2532 | 25.2382 | 24.8484 | 24.8028 | 23.9486 | 23.9005 | 23.8526 | 21.5179 | 21.3522 | 20.8555 | 19.9915 | 19.3971 | 19.1289
DUNVEGAN | DUNVEGAN GRID | MINIMUM HEADROOM | NG 27604720 | YES | 4 | 4 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.0864 | 3.0864 | 3.0864 | 4 | 4 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.2708 | 3.2708 | 3.2708 | 4 | 4 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.0822 | 3.0822 | 3.0822
| DUNVEGAN GRID | CT |  |  | 4 | 4 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.0864 | 3.0864 | 3.0864 | 4 | 4 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.2708 | 3.2708 | 3.2708 | 4 | 4 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.0822 | 3.0822 | 3.0822
| DUNVEGAN GRID | LW |  |  | 4 | 4 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.0864 | 3.0864 | 3.0864 | 4 | 4 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.2708 | 3.2708 | 3.2708 | 4 | 4 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.0822 | 3.0822 | 3.0822
| DUNVEGAN GRID | ST |  |  | 4 | 4 | 4 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1695 | 3.1279 | 3.1279 | 3.1279 | 4 | 4 | 4 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.3371 | 3.304 | 3.304 | 3.304 | 4 | 4 | 4 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1239 | 3.1239 | 3.1239
| DUNVEGAN GRID | SP |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | YES | 33.9665 | 33.923 | 33.8775 | 33.688 | 33.4007 | 32.7494 | 31.8134 | 30.8469 | 30.6428 | 30.1844 | 23.087 | 21.2254 | 19.8398 | 18.5568 | 27.0421 | 26.9995 | 26.9553 | 26.7645 | 26.5452 | 25.9937 | 25.1035 | 24.2121 | 24.1008 | 21.7706 | 20.0048 | 17.1309 | 13.1068 | 10.4087 | 27.1583 | 27.1158 | 27.0718 | 26.8808 | 26.6285 | 26.0064 | 25.0834 | 24.1386 | 23.9613 | 21.8072 | 20.0817 | 17.2594 | 13.2878 | 10.6263
| DYCE NORTH | CT |  |  | 34.0654 | 34.0143 | 33.9537 | 33.8833 | 33.6098 | 33.2026 | 32.8213 | 32.4553 | 31.9829 | 31.6734 | 30.7666 | 21.9629 | 19.8398 | 18.5568 | 27.1454 | 27.0989 | 27.0452 | 27.0324 | 26.8675 | 26.5611 | 26.2793 | 25.9942 | 25.6221 | 25.436 | 21.6885 | 17.2288 | 13.1068 | 10.4087 | 27.2623 | 27.2165 | 27.1638 | 27.1125 | 26.8704 | 26.4923 | 26.1398 | 25.7972 | 25.4071 | 25.221 | 21.8011 | 17.3579 | 13.2878 | 10.6263
| DYCE NORTH | LW |  |  | 33.9665 | 33.923 | 33.8775 | 33.8638 | 33.4007 | 32.7494 | 32.0785 | 31.388 | 30.6522 | 30.2937 | 29.1832 | 21.9569 | 20.2141 | 19.1579 | 27.0421 | 26.9995 | 26.9553 | 26.9451 | 26.5452 | 25.9948 | 25.4236 | 24.8316 | 24.2171 | 21.7706 | 20.158 | 17.2897 | 13.6922 | 11.8653 | 27.1583 | 27.1158 | 27.0718 | 27.0622 | 26.6285 | 26.0064 | 25.3644 | 24.7024 | 24.002 | 21.8122 | 20.2654 | 17.4171 | 13.8677 | 12.0608
| DYCE NORTH | ST |  |  | 34.1971 | 34.1662 | 34.1317 | 34.1045 | 33.9292 | 32.7703 | 31.8134 | 30.8469 | 30.6428 | 30.1844 | 23.087 | 21.2254 | 19.9383 | 19.2835 | 27.275 | 27.2466 | 27.2157 | 27.1951 | 27.0782 | 25.9937 | 25.1035 | 24.2121 | 24.1008 | 21.7833 | 20.0048 | 17.1309 | 14.6031 | 12.4956 | 27.3915 | 27.3636 | 27.3331 | 27.3135 | 27.1584 | 26.021 | 25.0834 | 24.1386 | 23.9613 | 21.8072 | 20.0817 | 17.2594 | 14.7639 | 12.694
| DYCE NORTH | SP |  |  | 34.3265 | 34.3142 | 34.3015 | 33.688 | 33.6191 | 33.5471 | 33.4698 | 33.3929 | 33.3077 | 32.989 | 31.9976 | 30.3391 | 23.2742 | 22.8798 | 27.4018 | 27.3898 | 27.3776 | 26.7645 | 26.7003 | 26.6338 | 26.5633 | 26.5105 | 26.4601 | 26.1806 | 25.3412 | 21.9598 | 20.6083 | 19.8821 | 27.5179 | 27.506 | 27.4939 | 26.8808 | 26.8174 | 26.7516 | 26.6822 | 26.613 | 26.5378 | 26.2305 | 25.2831 | 21.952 | 20.6548 | 19.9528
THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1988 | 1.1987 | 1.1986 | 1.1985 | 1.1984 | 1.1983 | 1.1981 | 1.1976 | 1.1967 | 1.195 | 1.1294 | 1.1292 | 1.1289 | 1.1281 | 1.1272 | 1.1263 | 1.1254 | 1.1245 | 1.1234 | 1.122 | 1.1185 | 1.1152 | 1.1141 | 1.1124 | 1.1601 | 1.16 | 1.16 | 1.1599 | 1.1597 | 1.1595 | 1.1593 | 1.159 | 1.1587 | 1.1584 | 1.1576 | 1.1561 | 1.1542 | 1.1515
| EDAY | CT |  |  | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1988 | 1.1987 | 1.1986 | 1.1985 | 1.1984 | 1.1983 | 1.1981 | 1.1976 | 1.1967 | 1.195 | 1.1294 | 1.1293 | 1.129 | 1.1284 | 1.1277 | 1.1269 | 1.1262 | 1.1248 | 1.1234 | 1.122 | 1.1185 | 1.1152 | 1.1141 | 1.1124 | 1.1601 | 1.16 | 1.16 | 1.1599 | 1.1597 | 1.1595 | 1.1593 | 1.159 | 1.1587 | 1.1584 | 1.1576 | 1.1561 | 1.1542 | 1.1515
| EDAY | LW |  |  | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1294 | 1.1292 | 1.1289 | 1.1281 | 1.1272 | 1.1263 | 1.1254 | 1.1245 | 1.1237 | 1.1228 | 1.1207 | 1.1179 | 1.1165 | 1.1163 | 1.1601 | 1.16 | 1.16 | 1.1599 | 1.1597 | 1.1596 | 1.1595 | 1.1593 | 1.1592 | 1.1591 | 1.1587 | 1.158 | 1.1574 | 1.1567
| EDAY | ST |  |  | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1295 | 1.1294 | 1.1293 | 1.129 | 1.1287 | 1.1283 | 1.1278 | 1.1274 | 1.127 | 1.1261 | 1.1234 | 1.1199 | 1.1175 | 1.1165 | 1.1601 | 1.1601 | 1.16 | 1.16 | 1.16 | 1.1599 | 1.1598 | 1.1598 | 1.1597 | 1.1596 | 1.1592 | 1.1585 | 1.1579 | 1.1573
| EDAY | SP |  |  | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1989 | 1.1296 | 1.1296 | 1.1296 | 1.1296 | 1.1295 | 1.1294 | 1.1292 | 1.1291 | 1.1289 | 1.1285 | 1.1275 | 1.1258 | 1.1243 | 1.1229 | 1.1601 | 1.1601 | 1.1601 | 1.1601 | 1.1601 | 1.1601 | 1.16 | 1.16 | 1.16 | 1.1599 | 1.1598 | 1.1595 | 1.1593 | 1.1591
FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | 9.5007 | 9.4973 | 9.4925 | 9.482 | 9.1083 | 7.3649 | 6.9182 | 6.4736 | 5.9057 | 5.3494 | 3.257 | 0.92714 | 0.40694 | -2.2962 | 7.2205 | 7.2162 | 7.2101 | 7.1965 | 6.6891 | 6.1782 | 5.6664 | 5.1441 | 4.478 | 3.8233 | 1.361 | -1.1817 | -1.795 | -4.929 | 7.1079 | 7.1036 | 7.0975 | 7.0839 | 6.5797 | 6.0719 | 5.5672 | 5.0651 | 4.4247 | 3.7957 | 1.43 | -1.1203 | -1.7069 | -4.7307
| EDZELL | CT |  |  | 9.5007 | 9.4973 | 9.4925 | 9.482 | 9.3068 | 9.1578 | 7.7001 | 7.4636 | 7.1222 | 6.6873 | 5.1749 | 2.6067 | 0.48128 | -2.2962 | 7.2205 | 7.2162 | 7.2101 | 7.1965 | 6.9611 | 6.7616 | 6.5626 | 6.2948 | 5.908 | 5.4024 | 3.6246 | 0.8082 | -1.6832 | -4.929 | 7.1079 | 7.1036 | 7.0975 | 7.0839 | 6.8499 | 6.6517 | 6.4538 | 6.1875 | 5.803 | 5.3117 | 3.6033 | 0.78858 | -1.6072 | -4.7307
| EDZELL | LW |  |  | 9.5027 | 9.5005 | 9.497 | 9.4883 | 9.1083 | 7.3649 | 6.9182 | 6.4736 | 5.9057 | 5.3494 | 3.257 | 0.92714 | 0.40694 | -1.2497 | 7.2228 | 7.2198 | 7.2151 | 7.2032 | 6.6891 | 6.1782 | 5.6664 | 5.1441 | 4.478 | 3.8233 | 1.361 | -1.1817 | -1.7919 | -3.739 | 7.1101 | 7.1071 | 7.1024 | 7.0907 | 6.5797 | 6.0719 | 5.5672 | 5.0651 | 4.4247 | 3.7957 | 1.43 | -1.1203 | -1.7069 | -3.5782
| EDZELL | ST |  |  | 9.5033 | 9.502 | 9.5004 | 9.4974 | 9.3498 | 9.2098 | 7.7555 | 7.5295 | 7.2078 | 6.7889 | 5.3267 | 3.1005 | 0.48053 | -1.0476 | 7.2237 | 7.2221 | 7.2199 | 7.216 | 7.0167 | 6.828 | 6.6234 | 6.3667 | 6.0013 | 5.5161 | 3.7949 | 1.275 | -1.795 | -3.5876 | 7.111 | 7.1094 | 7.1072 | 7.1033 | 6.9053 | 6.7177 | 6.5143 | 6.2591 | 5.896 | 5.4223 | 3.7687 | 1.294 | -1.6584 | -3.382
| EDZELL | SP |  |  | 9.5041 | 9.5037 | 9.5033 | 9.5028 | 9.4645 | 9.4206 | 9.3499 | 9.2803 | 9.1876 | 9.0761 | 7.1345 | 6.3451 | 5.615 | 4.9493 | 7.2249 | 7.2244 | 7.2239 | 7.2234 | 7.1715 | 7.1121 | 7.0163 | 6.9221 | 6.7966 | 6.6276 | 5.9158 | 4.991 | 4.1404 | 3.3619 | 7.1122 | 7.1117 | 7.1112 | 7.1107 | 7.0591 | 7.0001 | 6.9049 | 6.8112 | 6.6865 | 6.5186 | 5.8111 | 4.9184 | 4.0993 | 3.3503
MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | NO | 13.0978 | 13.0957 | 13.0934 | 13.0899 | 13.0786 | 13.0652 | 13.0494 | 13.0313 | 13.0108 | 12.9992 | 12.9604 | 12.8701 | 12.7218 | 12.4338 | 12.2529 | 12.2355 | 12.2102 | 12.152 | 12.0817 | 12.0102 | 11.9373 | 11.8851 | 11.831 | 11.783 | 11.6364 | 11.3997 | 9.5966 | 9.0238 | 12.3184 | 12.3103 | 12.2989 | 12.2739 | 12.2394 | 12.2031 | 12.1649 | 12.1333 | 12.0997 | 12.0737 | 11.9925 | 11.8333 | 9.9248 | 9.3718
| EDZELL STREET | CT |  |  | 13.0978 | 13.0957 | 13.0934 | 13.0899 | 13.0786 | 13.0652 | 13.0494 | 13.0313 | 13.0108 | 12.9992 | 12.9604 | 12.8701 | 12.7218 | 12.4338 | 12.2529 | 12.2355 | 12.2102 | 12.152 | 12.0817 | 12.0102 | 11.9373 | 11.8851 | 11.831 | 11.783 | 11.6364 | 11.3997 | 9.5966 | 9.0238 | 12.3184 | 12.3103 | 12.2989 | 12.2739 | 12.2394 | 12.2031 | 12.1649 | 12.1333 | 12.0997 | 12.0737 | 11.9925 | 11.8333 | 9.9248 | 9.3718
| EDZELL STREET | LW |  |  | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 13.1008 | 12.2727 | 12.2724 | 12.2718 | 12.2703 | 12.2687 | 12.2671 | 12.2655 | 12.264 | 12.2625 | 12.2609 | 12.2561 | 12.2484 | 12.2406 | 12.233 | 12.328 | 12.3279 | 12.3277 | 12.3271 | 12.3264 | 12.3258 | 12.3252 | 12.3246 | 12.324 | 12.3234 | 12.3215 | 12.3185 | 12.3154 | 12.3124
| EDZELL STREET | ST |  |  | 13.1 | 13.0995 | 13.099 | 13.0984 | 13.0932 | 13.087 | 13.0799 | 13.0717 | 13.0625 | 13.0595 | 13.0504 | 13.0352 | 12.9561 | 12.9112 | 12.2651 | 12.2584 | 12.2496 | 12.2331 | 12.2064 | 12.1744 | 12.1425 | 12.1102 | 12.0771 | 12.0501 | 11.9713 | 11.844 | 11.6535 | 11.4977 | 12.3246 | 12.3216 | 12.3178 | 12.311 | 12.2973 | 12.281 | 12.2641 | 12.2464 | 12.2278 | 12.2154 | 12.1788 | 12.1195 | 11.9966 | 11.9081
| EDZELL STREET | SP |  |  | 13.099 | 13.0981 | 13.0971 | 13.0961 | 13.096 | 13.0958 | 13.0956 | 13.0954 | 13.0952 | 13.0938 | 13.0889 | 13.0851 | 13.0608 | 13.0079 | 12.27 | 12.2681 | 12.2661 | 12.2639 | 12.2574 | 12.2496 | 12.2413 | 12.2331 | 12.2226 | 12.2119 | 12.1801 | 12.1342 | 12.0703 | 11.98 | 12.3259 | 12.3246 | 12.3232 | 12.3217 | 12.3191 | 12.3159 | 12.3125 | 12.3092 | 12.3049 | 12.2998 | 12.2844 | 12.264 | 12.2241 | 12.1565
ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | YES | 13.0613 | 13.0584 | 13.055 | 13.0502 | 13.0336 | 13.0136 | 12.9898 | 12.962 | 12.929 | 9.9797 | 8.191 | 5.8547 | 4.6363 | 1.8301 | 12.4467 | 12.4377 | 12.4254 | 12.3992 | 12.2199 | 12.1694 | 9.9458 | 9.4967 | 8.9247 | 8.3623 | 6.2494 | 3.514 | 2.0921 | -1.0422 | 12.5546 | 12.5501 | 12.5444 | 12.5341 | 12.4819 | 12.4108 | 12.3653 | 9.6278 | 9.0703 | 8.5224 | 6.4641 | 3.7985 | 2.4122 | -0.69188
| ELGIN | CT |  |  | 13.0613 | 13.0584 | 13.055 | 13.0502 | 13.0336 | 13.0136 | 12.9898 | 12.962 | 12.929 | 12.9115 | 9.2704 | 7.0825 | 4.788 | 1.8301 | 12.4467 | 12.4377 | 12.4254 | 12.3992 | 12.2429 | 12.1694 | 12.1456 | 12.1179 | 9.8237 | 9.3068 | 7.5457 | 5.0069 | 2.3565 | -1.0422 | 12.5546 | 12.5501 | 12.5444 | 12.5341 | 12.4819 | 12.4314 | 12.3775 | 12.3044 | 9.9433 | 9.4393 | 7.7224 | 5.245 | 2.6569 | -0.69188
| ELGIN | LW |  |  | 13.0656 | 13.0656 | 13.0656 | 13.0656 | 13.064 | 13.0607 | 13.0557 | 13.0485 | 13.035 | 9.9797 | 8.191 | 5.8547 | 4.6363 | 3.2041 | 12.4557 | 12.4537 | 12.4505 | 12.4426 | 12.2199 | 12.2166 | 9.9458 | 9.4967 | 8.9247 | 8.3623 | 6.2494 | 3.514 | 2.0921 | 0.41443 | 12.5601 | 12.5596 | 12.5587 | 12.5567 | 12.4842 | 12.4108 | 12.3653 | 9.6278 | 9.0703 | 8.5224 | 6.4641 | 3.7985 | 2.4122 | 0.7649
| ELGIN | ST |  |  | 13.0647 | 13.064 | 13.0634 | 13.0627 | 13.0563 | 13.0484 | 13.0391 | 13.028 | 13.014 | 13.0095 | 9.6703 | 7.7682 | 5.2744 | 2.3963 | 12.48 | 12.4478 | 12.4421 | 12.4316 | 12.3085 | 12.212 | 12.1949 | 12.1839 | 12.1699 | 9.6061 | 7.997 | 5.7648 | 2.8629 | -0.50303 | 12.5656 | 12.5569 | 12.555 | 12.5518 | 12.5155 | 12.4789 | 12.4379 | 12.3883 | 12.3236 | 9.7334 | 8.1657 | 5.9902 | 3.1598 | -0.1528
| ELGIN | SP |  |  | 13.064 | 13.0632 | 13.0624 | 13.0615 | 13.0613 | 13.0611 | 13.0609 | 13.0607 | 13.0603 | 13.0588 | 13.053 | 13.0473 | 9.9782 | 9.3279 | 12.483 | 12.4816 | 12.4524 | 12.4508 | 12.4195 | 12.3836 | 12.3274 | 12.2721 | 12.2234 | 12.2147 | 12.2088 | 9.1865 | 8.37 | 7.6007 | 12.5659 | 12.5649 | 12.5568 | 12.5557 | 12.5476 | 12.5383 | 12.5238 | 12.5095 | 12.4905 | 12.4632 | 12.3626 | 9.3256 | 8.5288 | 7.7778
ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | 11.0707 | 10.9794 | 10.8913 | 10.7707 | 10.6387 | 10.5001 | 10.3523 | 10.1919 | 9.9829 | 9.9 | 9.7467 | 6.4621 | 3.612 | -0.58672 | 10.5427 | 10.441 | 10.3293 | 10.1658 | 10.0467 | 9.9406 | 9.8239 | 9.7073 | 9.5517 | 9.4968 | 9.3848 | 7.0845 | 4.5446 | 0.99291 | 11.4425 | 11.3374 | 11.2299 | 11.0659 | 10.8874 | 10.7033 | 10.5107 | 10.3378 | 10.1205 | 10.03 | 9.856 | 6.5925 | 4.1464 | 0.0031694
| ELLIOT DEPOT | CT |  |  | 11.0707 | 10.9794 | 10.8913 | 10.7707 | 10.6387 | 10.5001 | 10.3523 | 10.1919 | 9.9829 | 9.9 | 9.7467 | 6.4621 | 3.612 | -0.58672 | 10.5427 | 10.441 | 10.3293 | 10.1658 | 10.0467 | 9.9406 | 9.8239 | 9.7073 | 9.5517 | 9.4968 | 9.3848 | 7.0845 | 4.5446 | 0.99291 | 11.4425 | 11.3374 | 11.2299 | 11.0659 | 10.8874 | 10.7033 | 10.5107 | 10.3378 | 10.1205 | 10.03 | 9.856 | 6.5925 | 4.1464 | 0.0031694
| ELLIOT DEPOT | LW |  |  | 11.1542 | 11.1467 | 11.1395 | 11.1312 | 11.1218 | 11.1115 | 11.1003 | 11.0779 | 11.0329 | 11.0098 | 10.9232 | 10.7044 | 10.4687 | 10.2795 | 10.6387 | 10.6299 | 10.6199 | 10.6029 | 10.584 | 10.5645 | 10.5445 | 10.5136 | 10.4609 | 10.4293 | 10.318 | 10.0786 | 9.8364 | 9.6797 | 11.5399 | 11.5311 | 11.5219 | 11.5089 | 11.4943 | 11.4788 | 11.4626 | 11.4351 | 11.3852 | 11.3567 | 11.2542 | 11.0095 | 10.747 | 10.5306
| ELLIOT DEPOT | ST |  |  | 11.1565 | 11.1511 | 11.1458 | 11.1386 | 11.1282 | 11.1173 | 11.1042 | 11.0854 | 11.0456 | 11.029 | 10.9725 | 6.659 | 4.6723 | 2.1693 | 10.6869 | 10.6115 | 10.5904 | 10.5525 | 10.5 | 10.4524 | 10.4274 | 10.3969 | 10.3458 | 10.3172 | 10.2266 | 8.8941 | 5.764 | 3.5834 | 11.563 | 11.5259 | 11.513 | 11.4915 | 11.4616 | 11.4273 | 11.4021 | 11.3713 | 11.3199 | 11.2911 | 11.1991 | 6.7049 | 4.8892 | 2.7339
| ELLIOT DEPOT | SP |  |  | 11.1524 | 11.145 | 11.1376 | 11.1302 | 11.1202 | 11.1104 | 11.1007 | 11.0903 | 11.2031 | 11.1874 | 11.1253 | 7.3805 | 6.0123 | 4.8613 | 10.6949 | 10.6866 | 10.6196 | 10.6107 | 10.5886 | 10.5639 | 10.5476 | 10.5305 | 10.6344 | 10.6097 | 10.5216 | 9.3617 | 7.1295 | 6.1703 | 11.564 | 11.5555 | 11.5208 | 11.5121 | 11.4957 | 11.4783 | 11.4646 | 11.4502 | 11.5581 | 11.5375 | 11.4611 | 7.4069 | 6.0701 | 4.9556
DYCE | ELLON 11 kV | MINIMUM HEADROOM | NJ 95510 30054 | YES | 22.1355 | 21.9839 | 21.934 | 33.0309 | 32.9089 | 32.781 | 32.6439 | 32.5026 | 32.3336 | 32.2359 | 32.0209 | 22.3224 | 20.935 | 19.312 | 18.3515 | 18.2396 | 18.0582 | 28.4486 | 28.0727 | 27.7838 | 27.5337 | 27.2939 | 27.0406 | 22.0354 | 19.5232 | 17.3135 | 15.7653 | 13.9842 | 17.7058 | 17.5603 | 17.4878 | 27.9861 | 27.8115 | 27.6361 | 27.4521 | 27.27 | 21.8615 | 20.8416 | 18.3336 | 15.9363 | 14.39 | 12.6106
| ELLON 11 kV | CT |  |  | 22.1355 | 22.1215 | 21.934 | 33.0309 | 32.9089 | 32.781 | 32.6439 | 32.5026 | 32.3336 | 32.2359 | 32.0209 | 22.3224 | 20.935 | 19.312 | 18.3515 | 18.3007 | 18.0582 | 28.4486 | 28.0727 | 27.7838 | 27.5337 | 27.2939 | 27.0406 | 22.0354 | 19.5232 | 17.3135 | 15.7653 | 13.9842 | 17.7058 | 17.6852 | 17.4878 | 27.9861 | 27.8115 | 27.6361 | 27.4521 | 27.27 | 21.8615 | 20.8416 | 18.3336 | 15.9363 | 14.39 | 12.6106
| ELLON 11 kV | LW |  |  | 22.153 | 21.9839 | 21.9827 | 33.1117 | 33.0069 | 32.8987 | 32.7877 | 32.6723 | 32.6054 | 32.5645 | 32.4447 | 31.4649 | 31.2976 | 21.181 | 18.4135 | 18.2396 | 18.2308 | 28.7659 | 28.2971 | 27.9314 | 27.6661 | 27.3979 | 27.3246 | 27.2766 | 27.1531 | 20.2189 | 18.9918 | 15.8186 | 17.7301 | 17.5603 | 17.558 | 28.1094 | 27.9392 | 27.7662 | 27.5912 | 27.4325 | 27.3687 | 27.331 | 27.2207 | 18.8375 | 17.6124 | 14.4453
| ELLON 11 kV | ST |  |  | 22.1457 | 22.1395 | 21.9632 | 33.0917 | 33.0152 | 32.9323 | 32.8523 | 32.7608 | 32.6455 | 32.5456 | 32.4512 | 31.9646 | 23.2106 | 21.8809 | 18.3773 | 18.348 | 18.142 | 28.638 | 28.3497 | 28.0895 | 27.8866 | 27.7011 | 27.4601 | 27.2524 | 21.0981 | 19.8891 | 18.1246 | 16.5635 | 17.7187 | 17.7085 | 17.5268 | 28.07 | 27.9554 | 27.8332 | 27.7206 | 27.59 | 27.4225 | 22.0658 | 19.9064 | 18.604 | 16.8421 | 15.2836
| ELLON 11 kV | SP |  |  | 22.1472 | 22.1436 | 22.1398 | 33.1186 | 33.1029 | 33.0854 | 33.0646 | 33.044 | 33.0191 | 32.9841 | 32.856 | 32.6925 | 32.5074 | 32.3 | 18.4068 | 18.3993 | 18.3912 | 28.79 | 28.7145 | 28.6321 | 28.5313 | 28.4316 | 28.3026 | 28.1677 | 27.7552 | 27.3969 | 21.5104 | 19.9506 | 17.7241 | 17.72 | 17.7156 | 28.1187 | 28.0929 | 28.0638 | 28.0286 | 27.9938 | 27.9502 | 27.8918 | 27.6682 | 21.9384 | 20.318 | 18.7608
TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | 0.25232 | 0.25229 | 0.22937 | 0.18216 | 0.14793 | 0.1066 | 0.06401 | 0.020153 | -0.025097 | -0.071518 | -0.15463 | -0.29029 | -0.40965 | -0.52691 | 0.2368 | 0.23671 | 0.22088 | 0.17163 | 0.13881 | 0.099231 | 0.058443 | 0.016125 | -0.027517 | -0.072302 | -0.15308 | -0.28474 | -0.40067 | -0.51458 | 0.2408 | 0.24067 | 0.21396 | 0.17043 | 0.13641 | 0.095337 | 0.052997 | 0.0084412 | -0.037522 | -0.084683 | -0.16936 | -0.30738 | -0.42864 | -0.54767
| EREDINE | CT |  |  | 0.25232 | 0.25229 | 0.22937 | 0.18216 | 0.14793 | 0.1066 | 0.06401 | 0.020153 | -0.025097 | -0.071518 | -0.15463 | -0.29029 | -0.40965 | -0.52691 | 0.2368 | 0.23671 | 0.22088 | 0.17163 | 0.13881 | 0.099231 | 0.058443 | 0.016125 | -0.027517 | -0.072302 | -0.15308 | -0.28474 | -0.40067 | -0.51458 | 0.2408 | 0.24067 | 0.21396 | 0.17043 | 0.13641 | 0.095337 | 0.052997 | 0.0084412 | -0.037522 | -0.084683 | -0.16936 | -0.30738 | -0.42864 | -0.54767
| EREDINE | LW |  |  | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.23684 | 0.23676 | 0.23664 | 0.23634 | 0.23601 | 0.23568 | 0.23536 | 0.23507 | 0.23482 | 0.23455 | 0.23413 | 0.23413 | 0.23413 | 0.23413 | 0.24083 | 0.24071 | 0.24052 | 0.24036 | 0.24023 | 0.2401 | 0.24008 | 0.24008 | 0.24008 | 0.24008 | 0.24008 | 0.24008 | 0.24008 | 0.24008
| EREDINE | ST |  |  | 0.25235 | 0.25234 | 0.25233 | 0.25232 | 0.25224 | 0.25214 | 0.25203 | 0.25189 | 0.25174 | 0.25169 | 0.25154 | 0.2513 | 0.25002 | 0.24929 | 0.23686 | 0.23681 | 0.23675 | 0.23665 | 0.23643 | 0.23619 | 0.23571 | 0.23522 | 0.23472 | 0.23421 | 0.23331 | 0.23306 | 0.23178 | 0.23105 | 0.24087 | 0.2408 | 0.24071 | 0.24055 | 0.24032 | 0.24017 | 0.23991 | 0.23963 | 0.23946 | 0.2394 | 0.23926 | 0.23901 | 0.23773 | 0.237
| EREDINE | SP |  |  | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.25236 | 0.23691 | 0.2369 | 0.2369 | 0.23689 | 0.23685 | 0.23681 | 0.23669 | 0.23658 | 0.23643 | 0.23622 | 0.23563 | 0.23478 | 0.23413 | 0.23413 | 0.24094 | 0.24093 | 0.24092 | 0.24091 | 0.24085 | 0.24078 | 0.2406 | 0.24046 | 0.2404 | 0.24031 | 0.24008 | 0.24008 | 0.24008 | 0.24008
INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | NO | 1.5679 | 1.5678 | 1.5636 | 1.5594 | 1.5546 | 1.5489 | 1.543 | 1.5368 | 1.5306 | 1.5258 | 1.4938 | 1.0043 | 0.97125 | 0.93232 | 1.5427 | 1.5424 | 1.5386 | 1.5349 | 1.5319 | 1.5286 | 1.5251 | 1.5213 | 1.4993 | 1.4914 | 1.4735 | 1.0891 | 1.0584 | 1.0216 | 1.5441 | 1.5439 | 1.5396 | 1.5352 | 1.5302 | 1.5243 | 1.519 | 1.5135 | 1.4966 | 1.4874 | 1.4658 | 0.97154 | 0.93418 | 0.89082
| ERROGIE | CT |  |  | 1.5679 | 1.5678 | 1.5636 | 1.5594 | 1.5546 | 1.5489 | 1.543 | 1.5368 | 1.5306 | 1.5258 | 1.4938 | 1.0043 | 0.97125 | 0.93232 | 1.5427 | 1.5424 | 1.5386 | 1.5349 | 1.5319 | 1.5286 | 1.5251 | 1.5213 | 1.4993 | 1.4914 | 1.4735 | 1.0891 | 1.0584 | 1.0216 | 1.5441 | 1.5439 | 1.5396 | 1.5352 | 1.5302 | 1.5243 | 1.519 | 1.5135 | 1.4966 | 1.4874 | 1.4658 | 0.97154 | 0.93418 | 0.89082
| ERROGIE | LW |  |  | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.0806 | 1.076 | 1.0714 | 1.5428 | 1.5426 | 1.5423 | 1.5416 | 1.5408 | 1.5401 | 1.5395 | 1.5391 | 1.5387 | 1.5386 | 1.5386 | 1.1502 | 1.1441 | 1.1381 | 1.5442 | 1.5441 | 1.544 | 1.5437 | 1.5434 | 1.5431 | 1.5428 | 1.5426 | 1.5424 | 1.5422 | 1.5422 | 1.0586 | 1.053 | 1.0475
| ERROGIE | ST |  |  | 1.568 | 1.568 | 1.568 | 1.568 | 1.5679 | 1.5678 | 1.5677 | 1.5676 | 1.5675 | 1.5674 | 1.5673 | 1.3045 | 1.2932 | 1.2822 | 1.5429 | 1.5428 | 1.5426 | 1.5424 | 1.542 | 1.5415 | 1.5408 | 1.5401 | 1.5395 | 1.5384 | 1.5378 | 1.3265 | 1.3136 | 1.3013 | 1.5442 | 1.5442 | 1.5441 | 1.544 | 1.5438 | 1.5436 | 1.5432 | 1.5428 | 1.5425 | 1.542 | 1.5414 | 1.282 | 1.2687 | 1.2559
| ERROGIE | SP |  |  | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.5681 | 1.543 | 1.543 | 1.543 | 1.5429 | 1.5429 | 1.5427 | 1.5425 | 1.5423 | 1.5421 | 1.5414 | 1.5398 | 1.5386 | 1.5386 | 1.5386 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5442 | 1.5442 | 1.5441 | 1.544 | 1.5439 | 1.5437 | 1.5429 | 1.5422 | 1.5422 | 1.5422
ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | YES | 6.957 | 6.9489 | 6.9432 | 6.9332 | 6.9212 | 6.907 | 6.8904 | 6.8713 | 6.8497 | 6.8375 | 6.7965 | 4.711 | 4.3098 | 3.7656 | 6.3626 | 6.3162 | 6.2897 | 6.2611 | 6.2222 | 6.1816 | 6.139 | 6.104 | 6.0772 | 6.065 | 6.024 | 4.3102 | 3.8613 | 3.2701 | 6.8819 | 6.8731 | 6.867 | 6.8547 | 6.8334 | 6.81 | 6.7844 | 6.7598 | 6.7328 | 6.7147 | 6.6564 | 4.3565 | 3.931 | 3.363
| ERROL | CT |  |  | 6.957 | 6.9489 | 6.9432 | 6.9332 | 6.9212 | 6.907 | 6.8904 | 6.8713 | 6.8497 | 6.8375 | 6.7965 | 4.711 | 4.3098 | 3.7656 | 6.3626 | 6.3162 | 6.2897 | 6.2611 | 6.2222 | 6.1816 | 6.139 | 6.104 | 6.0772 | 6.065 | 6.024 | 4.3102 | 3.8613 | 3.2701 | 6.8819 | 6.8731 | 6.867 | 6.8547 | 6.8334 | 6.81 | 6.7844 | 6.7598 | 6.7328 | 6.7147 | 6.6564 | 4.3565 | 3.931 | 3.363
| ERROL | LW |  |  | 6.9623 | 6.9582 | 6.9577 | 6.9562 | 6.9546 | 6.9531 | 6.9515 | 6.9501 | 6.9486 | 6.947 | 6.9446 | 6.5623 | 6.5623 | 6.5623 | 6.3893 | 6.3511 | 6.3468 | 6.3361 | 6.3242 | 6.3126 | 6.3012 | 6.2945 | 6.2899 | 6.2848 | 6.27 | 5.9765 | 5.9538 | 5.9527 | 6.8874 | 6.8828 | 6.8822 | 6.8806 | 6.8789 | 6.8771 | 6.8754 | 6.8738 | 6.8722 | 6.8704 | 6.8653 | 6.4712 | 6.4628 | 6.4545
| ERROL | ST |  |  | 6.9598 | 6.9576 | 6.951 | 6.946 | 6.937 | 6.9309 | 6.9237 | 6.9156 | 6.9064 | 6.9035 | 6.8944 | 6.6881 | 6.6094 | 4.9634 | 6.3682 | 6.3548 | 6.3093 | 6.2869 | 6.2626 | 6.2335 | 6.2135 | 6.1928 | 6.1713 | 6.1573 | 6.1218 | 5.997 | 4.7499 | 4.5223 | 6.8847 | 6.8823 | 6.8751 | 6.8696 | 6.8578 | 6.8437 | 6.8321 | 6.8195 | 6.8061 | 6.7993 | 6.779 | 6.553 | 4.8243 | 4.6114
| ERROL | SP |  |  | 6.9605 | 6.9593 | 6.958 | 6.9567 | 6.9549 | 6.9528 | 6.9512 | 6.9497 | 6.9478 | 6.945 | 6.9361 | 6.9285 | 6.9038 | 6.85 | 6.3876 | 6.3838 | 6.3794 | 6.3746 | 6.3582 | 6.3433 | 6.3332 | 6.3232 | 6.3104 | 6.2987 | 6.2766 | 6.2532 | 6.21 | 6.1388 | 6.8856 | 6.8844 | 6.8831 | 6.8817 | 6.8797 | 6.8773 | 6.8757 | 6.874 | 6.8719 | 6.8689 | 6.8596 | 6.849 | 6.8178 | 6.758
TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | 0.13503 | 0.13501 | 0.13498 | 0.13496 | 0.13487 | 0.13476 | 0.13465 | 0.1345 | 0.13433 | 0.13425 | 0.13394 | 0.13324 | 0.093493 | 0.082423 | 0.1258 | 0.12552 | 0.12507 | 0.12394 | 0.12318 | 0.12285 | 0.12256 | 0.12223 | 0.12206 | 0.12198 | 0.12167 | 0.090946 | 0.079257 | 0.066605 | 0.12011 | 0.12003 | 0.11992 | 0.11965 | 0.11932 | 0.11904 | 0.11878 | 0.11863 | 0.11846 | 0.11838 | 0.09553 | 0.085118 | 0.073427 | 0.06077
| FINCASTLE | CT |  |  | 0.13503 | 0.13501 | 0.13498 | 0.13496 | 0.13487 | 0.13476 | 0.13465 | 0.1345 | 0.13433 | 0.13425 | 0.13394 | 0.13324 | 0.093493 | 0.082423 | 0.1258 | 0.12555 | 0.12519 | 0.12434 | 0.12338 | 0.12289 | 0.12256 | 0.12223 | 0.12206 | 0.12198 | 0.12167 | 0.090946 | 0.079257 | 0.066605 | 0.12011 | 0.12003 | 0.11992 | 0.11969 | 0.11937 | 0.11904 | 0.11878 | 0.11863 | 0.11846 | 0.11838 | 0.096266 | 0.085118 | 0.073427 | 0.06077
| FINCASTLE | LW |  |  | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.096119 | 0.087894 | 0.1258 | 0.12552 | 0.12507 | 0.12394 | 0.12318 | 0.12285 | 0.12278 | 0.12278 | 0.12278 | 0.12278 | 0.12278 | 0.091619 | 0.081821 | 0.072117 | 0.12012 | 0.12005 | 0.11993 | 0.11965 | 0.11932 | 0.11918 | 0.11918 | 0.11918 | 0.11918 | 0.11918 | 0.09553 | 0.085792 | 0.07599 | 0.066283
| FINCASTLE | ST |  |  | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.12592 | 0.12578 | 0.1256 | 0.12524 | 0.12476 | 0.12418 | 0.12362 | 0.12328 | 0.12314 | 0.12291 | 0.12278 | 0.12278 | 0.098153 | 0.091623 | 0.12015 | 0.12012 | 0.12007 | 0.11998 | 0.11985 | 0.11971 | 0.11956 | 0.11942 | 0.11929 | 0.11918 | 0.11918 | 0.098898 | 0.092327 | 0.085796
| FINCASTLE | SP |  |  | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.13505 | 0.12606 | 0.12604 | 0.12602 | 0.12599 | 0.12585 | 0.12569 | 0.12551 | 0.12532 | 0.12508 | 0.12474 | 0.12373 | 0.12303 | 0.12278 | 0.12278 | 0.12019 | 0.12018 | 0.12018 | 0.12017 | 0.12013 | 0.12009 | 0.12005 | 0.12 | 0.11994 | 0.11985 | 0.11959 | 0.11919 | 0.11918 | 0.11918
SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | 7.1307 | 8.6303 | 8.6298 | 8.6291 | 8.627 | 8.6245 | 8.6216 | 8.6174 | 8.6128 | 8.6096 | 8.5995 | 8.5784 | 8.5478 | 8.4978 | 6.8781 | 8.3777 | 8.3773 | 8.3767 | 8.3747 | 8.3724 | 8.3697 | 8.3665 | 8.363 | 8.3609 | 8.3542 | 8.3385 | 8.3128 | 8.2627 | 6.9119 | 8.4115 | 8.4111 | 8.4105 | 8.4085 | 8.4062 | 8.4035 | 8.4003 | 8.3968 | 8.3947 | 8.388 | 8.3723 | 8.3465 | 8.2965
| FIRTH | CT |  |  | 7.1307 | 8.6303 | 8.6298 | 8.6291 | 8.627 | 8.6245 | 8.6216 | 8.6174 | 8.6128 | 8.6096 | 8.5995 | 8.5784 | 8.5478 | 8.4978 | 6.8781 | 8.3777 | 8.3773 | 8.3767 | 8.3747 | 8.3724 | 8.3697 | 8.3665 | 8.363 | 8.3609 | 8.3542 | 8.3385 | 8.3128 | 8.2627 | 6.9119 | 8.4115 | 8.4111 | 8.4105 | 8.4085 | 8.4062 | 8.4035 | 8.4003 | 8.3968 | 8.3947 | 8.388 | 8.3723 | 8.3465 | 8.2965
| FIRTH | LW |  |  | 7.1313 | 8.6312 | 8.6311 | 8.631 | 8.6308 | 8.6306 | 8.6305 | 8.6303 | 8.6301 | 8.6299 | 8.6294 | 8.6286 | 8.6277 | 8.6269 | 6.8786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 8.3786 | 6.9124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124 | 8.4124
| FIRTH | ST |  |  | 7.1311 | 8.631 | 8.6309 | 8.6308 | 8.6299 | 8.6289 | 8.6276 | 8.626 | 8.6244 | 8.6232 | 8.6197 | 8.6139 | 8.5988 | 8.5888 | 6.8785 | 8.3784 | 8.3783 | 8.3782 | 8.3775 | 8.3766 | 8.3755 | 8.3743 | 8.373 | 8.3725 | 8.3712 | 8.3689 | 8.3573 | 8.3507 | 6.9123 | 8.4122 | 8.4121 | 8.412 | 8.4113 | 8.4104 | 8.4093 | 8.4081 | 8.4067 | 8.4063 | 8.405 | 8.4027 | 8.3911 | 8.3845
| FIRTH | SP |  |  | 7.1311 | 8.6311 | 8.631 | 8.6309 | 8.6308 | 8.6308 | 8.6307 | 8.6306 | 8.6304 | 8.63 | 8.6287 | 8.6271 | 8.6239 | 8.6183 | 6.8784 | 8.3784 | 8.3783 | 8.3782 | 8.3782 | 8.3782 | 8.3782 | 8.3781 | 8.3781 | 8.378 | 8.3776 | 8.3773 | 8.3753 | 8.3709 | 6.9122 | 8.4122 | 8.4121 | 8.412 | 8.412 | 8.412 | 8.4119 | 8.4119 | 8.4119 | 8.4118 | 8.4114 | 8.4111 | 8.4091 | 8.4047
THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | 0.48867 | 0.48862 | 0.48856 | 0.48845 | 0.48213 | 0.47536 | 0.46836 | 0.46086 | 0.45006 | 0.44821 | 0.44288 | -0.45037 | -0.48478 | -0.50136 | 0.4594 | 0.45935 | 0.45929 | 0.45918 | 0.45286 | 0.44609 | 0.4391 | 0.43159 | 0.4208 | 0.41894 | 0.41362 | -0.29369 | -0.32893 | -0.34633 | 0.46127 | 0.46093 | 0.46042 | 0.45903 | 0.45085 | 0.44257 | 0.4341 | 0.42515 | 0.41294 | 0.40955 | 0.3997 | -0.49382 | -0.52718 | -0.54269
| FLOTTA | CT |  |  | 0.48868 | 0.48863 | 0.48856 | 0.48845 | 0.48383 | 0.47881 | 0.47345 | 0.46783 | 0.45998 | 0.45845 | 0.45481 | 0.41399 | 0.37814 | 0.35336 | 0.45942 | 0.45936 | 0.45929 | 0.45918 | 0.45456 | 0.44954 | 0.44419 | 0.43856 | 0.43071 | 0.42918 | 0.42554 | 0.38101 | 0.34147 | 0.31426 | 0.46127 | 0.46093 | 0.46043 | 0.45932 | 0.45362 | 0.44754 | 0.44115 | 0.43369 | 0.42404 | 0.42056 | 0.41117 | 0.36103 | 0.32564 | 0.30252
| FLOTTA | LW |  |  | 0.48877 | 0.48877 | 0.48877 | 0.48877 | 0.48213 | 0.47536 | 0.46836 | 0.46086 | 0.45006 | 0.44821 | 0.44288 | 0.41868 | 0.39652 | 0.3817 | 0.4595 | 0.4595 | 0.4595 | 0.4595 | 0.45286 | 0.44609 | 0.4391 | 0.43159 | 0.4208 | 0.41894 | 0.41362 | 0.38928 | 0.36104 | 0.34432 | 0.46133 | 0.46098 | 0.46042 | 0.45903 | 0.45085 | 0.44257 | 0.4341 | 0.42515 | 0.41294 | 0.40955 | 0.3997 | 0.36821 | 0.3432 | 0.32969
| FLOTTA | ST |  |  | 0.48872 | 0.4887 | 0.48868 | 0.48865 | 0.48539 | 0.48188 | 0.47848 | 0.47462 | 0.46858 | 0.46729 | 0.46402 | -0.45037 | -0.48478 | -0.50136 | 0.45946 | 0.45944 | 0.45942 | 0.45938 | 0.45612 | 0.45261 | 0.44921 | 0.44536 | 0.43931 | 0.43803 | 0.43475 | -0.29369 | -0.32893 | -0.34633 | 0.46143 | 0.46124 | 0.46099 | 0.46052 | 0.45666 | 0.45244 | 0.44835 | 0.44383 | 0.43712 | 0.43455 | 0.42756 | -0.49382 | -0.52718 | -0.54269
| FLOTTA | SP |  |  | 0.48867 | 0.48862 | 0.48857 | 0.48852 | 0.48805 | 0.48761 | 0.48714 | 0.48663 | 0.48579 | 0.48482 | 0.48139 | 0.4784 | 0.44555 | 0.43285 | 0.4594 | 0.45935 | 0.4593 | 0.45925 | 0.45879 | 0.45834 | 0.45788 | 0.45736 | 0.45652 | 0.45555 | 0.45213 | 0.44913 | 0.41629 | 0.40358 | 0.46154 | 0.46147 | 0.46139 | 0.46131 | 0.46068 | 0.46003 | 0.45934 | 0.45859 | 0.45746 | 0.45598 | 0.45106 | 0.44577 | 0.41077 | 0.39606
ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | YES | 18.5893 | 18.5874 | 18.585 | 18.5817 | 18.5702 | 18.5565 | 18.5403 | 18.5212 | 18.4984 | 18.4864 | 13.7544 | 12.237 | 9.7147 | 8.3037 | 16.5396 | 16.5054 | 16.4984 | 16.4838 | 16.4396 | 16.412 | 16.3959 | 16.3768 | 13.4268 | 13.0436 | 11.6116 | 9.7485 | 6.7497 | 5.1899 | 17.0621 | 17.0289 | 17.022 | 17.0078 | 16.9646 | 16.9374 | 16.9212 | 16.9021 | 16.8794 | 13.7259 | 12.4339 | 10.583 | 7.5491 | 5.9782
| FOCHABERS | CT |  |  | 18.5893 | 18.5874 | 18.585 | 18.5817 | 18.5702 | 18.5565 | 18.5403 | 18.5212 | 18.4984 | 18.4864 | 14.2835 | 12.9144 | 10.2662 | 8.3037 | 16.5396 | 16.5054 | 16.4984 | 16.4838 | 16.4396 | 16.412 | 16.3959 | 16.3768 | 16.354 | 13.4939 | 12.3136 | 10.6086 | 7.4721 | 5.1899 | 17.0621 | 17.0289 | 17.022 | 17.0078 | 16.9646 | 16.9374 | 16.9212 | 16.9021 | 16.8794 | 16.8674 | 13.0768 | 11.4422 | 8.2841 | 5.9782
| FOCHABERS | LW |  |  | 18.5923 | 18.5923 | 18.5923 | 18.5923 | 18.5912 | 18.589 | 18.5856 | 18.5808 | 18.5717 | 18.5698 | 13.7544 | 12.237 | 9.7147 | 8.7385 | 16.5454 | 16.5156 | 16.5144 | 16.5116 | 16.4598 | 16.4446 | 16.4412 | 16.4364 | 13.4268 | 13.0436 | 11.6116 | 9.7485 | 6.7497 | 5.5894 | 17.0677 | 17.0389 | 17.0378 | 17.035 | 16.9848 | 16.9699 | 16.9665 | 16.9617 | 16.9526 | 13.7259 | 12.4339 | 10.583 | 7.5491 | 6.3752
| FOCHABERS | ST |  |  | 18.5915 | 18.591 | 18.5905 | 18.5899 | 18.5849 | 18.5787 | 18.5714 | 18.5628 | 18.552 | 18.5486 | 18.5375 | 13.4451 | 11.8258 | 9.9263 | 16.5724 | 16.5411 | 16.5092 | 16.5042 | 16.4748 | 16.4443 | 16.427 | 16.4183 | 16.4076 | 16.4042 | 12.7286 | 11.234 | 9.2849 | 7.0327 | 17.0939 | 17.0635 | 17.0327 | 17.0278 | 16.9991 | 16.9694 | 16.9523 | 16.9437 | 16.933 | 16.9295 | 13.4486 | 12.0611 | 10.1155 | 7.8374
| FOCHABERS | SP |  |  | 18.591 | 18.5904 | 18.5897 | 18.589 | 18.5888 | 18.5887 | 18.5885 | 18.5884 | 18.5881 | 18.5869 | 18.5824 | 18.5782 | 18.5339 | 18.487 | 16.5736 | 16.5727 | 16.5427 | 16.5417 | 16.5353 | 16.5279 | 16.517 | 16.5062 | 16.4919 | 16.4727 | 16.438 | 16.4337 | 13.2537 | 12.7329 | 17.095 | 17.0942 | 17.0651 | 17.0641 | 17.0579 | 17.0508 | 17.0401 | 17.0297 | 17.0158 | 16.9972 | 16.9634 | 16.9591 | 16.9148 | 13.4456
NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | YES | 24.6498 | 24.4128 | 24.1834 | 23.8878 | 23.5062 | 23.1011 | 22.6678 | 22.1982 | 21.6326 | 21.4289 | 21.025 | 13.9455 | 9.2564 | 3.1839 | 19.8463 | 19.642 | 19.4334 | 19.1321 | 18.7371 | 18.3177 | 17.9117 | 17.5016 | 16.9913 | 16.802 | 13.2289 | 9.9604 | 5.8052 | 0.54982 | 22.3614 | 22.1176 | 21.8789 | 21.5637 | 21.1612 | 20.7356 | 20.2822 | 19.7954 | 19.2129 | 13.7044 | 13.3183 | 11.0907 | 6.2913 | 0.12922
| FORRES | CT |  |  | 24.6498 | 24.4128 | 24.1834 | 23.8878 | 23.5062 | 23.1011 | 22.6678 | 22.1982 | 21.6326 | 21.4289 | 21.025 | 13.9455 | 9.2564 | 3.1839 | 19.8463 | 19.642 | 19.4334 | 19.1321 | 18.7371 | 18.3177 | 17.9117 | 17.5016 | 16.9913 | 16.802 | 13.2289 | 9.9604 | 5.8052 | 0.54982 | 22.3614 | 22.1176 | 21.8789 | 21.5637 | 21.1612 | 20.7356 | 20.2822 | 19.7954 | 19.2129 | 13.7044 | 13.3183 | 11.0907 | 6.2913 | 0.12922
| FORRES | LW |  |  | 24.8679 | 24.8487 | 24.8301 | 24.8086 | 24.6872 | 24.5404 | 24.3657 | 24.1337 | 23.7755 | 23.6797 | 23.3542 | 21.9389 | 21.1832 | 20.7374 | 20.0353 | 20.0166 | 19.9963 | 19.9647 | 19.8322 | 19.6752 | 19.4911 | 19.2506 | 18.8844 | 18.7798 | 18.4294 | 17.1129 | 13.4594 | 9.808 | 22.5859 | 22.5656 | 22.5454 | 22.5201 | 22.3945 | 22.2435 | 22.0646 | 21.8286 | 21.4664 | 21.3664 | 21.0282 | 19.5868 | 13.3573 | 11.4411
| FORRES | ST |  |  | 24.8732 | 24.859 | 24.8447 | 24.8259 | 24.7567 | 24.6788 | 24.5936 | 24.4842 | 24.2944 | 24.2339 | 24.0428 | 22.508 | 14.1221 | 10.7542 | 20.03 | 20.008 | 19.9823 | 19.9398 | 19.8369 | 19.7179 | 19.6043 | 19.4671 | 19.25 | 19.1502 | 18.8469 | 17.3725 | 10.6827 | 7.5288 | 22.5891 | 22.5722 | 22.5544 | 22.5287 | 22.4503 | 22.3614 | 22.2681 | 22.1507 | 21.9531 | 21.8819 | 21.6597 | 20.0309 | 11.2595 | 7.9613
| FORRES | SP |  |  | 24.8625 | 24.8431 | 24.8236 | 24.8041 | 24.773 | 24.7422 | 24.7112 | 24.6778 | 24.6331 | 24.581 | 24.3755 | 22.5004 | 14.1501 | 11.709 | 20.0316 | 20.0145 | 19.9972 | 19.9796 | 19.6977 | 19.3791 | 19.3431 | 19.3047 | 19.2518 | 19.1881 | 18.9763 | 17.6679 | 11.1166 | 8.7052 | 22.5809 | 22.5609 | 22.5409 | 22.5207 | 22.4273 | 22.3251 | 22.2914 | 22.2552 | 22.207 | 22.1506 | 21.9326 | 20.0233 | 11.2805 | 8.9258
DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | NO | 0.92466 | 0.92439 | 0.9241 | 0.92365 | 0.59212 | 0.25271 | -0.10633 | -0.49143 | -1.0454 | -1.1408 | -1.4196 | -2.1181 | -2.7238 | -2.9577 | 0.69282 | 0.69254 | 0.69226 | 0.68723 | 0.36028 | 0.020862 | -0.34196 | -0.73202 | -1.2908 | -1.3914 | -1.6858 | -2.4092 | -3.1591 | -3.4518 | 0.92279 | 0.9219 | 0.92069 | 0.91804 | 0.58843 | 0.24812 | -0.11181 | -0.49777 | -1.0526 | -1.1489 | -1.4304 | -2.1332 | -2.7611 | -3.0027
| FORSS | CT |  |  | 0.92466 | 0.92439 | 0.9241 | 0.92365 | 0.69326 | 0.44514 | 0.17734 | -0.10303 | -0.49992 | -0.56678 | -0.71298 | -1.9548 | -2.7238 | -2.9577 | 0.69282 | 0.69254 | 0.69226 | 0.68723 | 0.4433 | 0.18189 | -0.098979 | -0.38802 | -0.79339 | -0.86944 | -1.0428 | -2.3306 | -3.1591 | -3.4518 | 0.92279 | 0.9219 | 0.92069 | 0.91804 | 0.68529 | 0.43485 | 0.16477 | -0.11711 | -0.51548 | -0.58395 | -0.73487 | -1.9844 | -2.7611 | -3.0027
| FORSS | LW |  |  | 0.92505 | 0.92505 | 0.92505 | 0.92505 | 0.59212 | 0.25271 | -0.10633 | -0.49143 | -1.0454 | -1.1408 | -1.4196 | -2.1181 | -2.674 | -2.8705 | 0.69321 | 0.69321 | 0.69321 | 0.69321 | 0.36028 | 0.020862 | -0.34196 | -0.73202 | -1.2908 | -1.3914 | -1.6858 | -2.4092 | -2.9903 | -3.2118 | 0.92366 | 0.92345 | 0.92312 | 0.92229 | 0.58843 | 0.24812 | -0.11181 | -0.49777 | -1.0526 | -1.1489 | -1.4304 | -2.1332 | -2.6935 | -2.8944
| FORSS | ST |  |  | 0.92501 | 0.92498 | 0.92495 | 0.9249 | 0.77821 | 0.62142 | 0.47069 | 0.29984 | 0.02419 | -0.03246 | -0.17479 | -0.77745 | -1.6791 | -1.9686 | 0.69316 | 0.69313 | 0.6931 | 0.69306 | 0.54636 | 0.38379 | 0.22699 | 0.050188 | -0.2313 | -0.29402 | -0.45393 | -1.0847 | -2.0142 | -2.3314 | 0.92343 | 0.92306 | 0.92258 | 0.92167 | 0.77379 | 0.6156 | 0.46381 | 0.29192 | 0.015251 | -0.042457 | -0.18785 | -0.79542 | -1.7019 | -1.9963
| FORSS | SP |  |  | 0.925 | 0.92497 | 0.92494 | 0.92491 | 0.91118 | 0.8979 | 0.88429 | 0.86908 | 0.84407 | 0.81722 | 0.72146 | 0.6368 | -0.49347 | -0.86507 | 0.69315 | 0.69312 | 0.69309 | 0.69306 | 0.67933 | 0.66606 | 0.65245 | 0.63724 | 0.61222 | 0.58537 | 0.48887 | 0.39345 | -0.74696 | -1.128 | 0.92374 | 0.92367 | 0.92357 | 0.92348 | 0.90941 | 0.89572 | 0.88176 | 0.86621 | 0.84075 | 0.81348 | 0.71651 | 0.62998 | -0.50206 | -0.87531
BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | NO | 7.9073 | 7.9063 | 7.9052 | 7.9037 | 7.8984 | 7.892 | 7.8845 | 7.8757 | 7.865 | 6.2799 | 5.6371 | 4.7976 | 3.4535 | 2.8197 | 7.365 | 7.2738 | 7.2727 | 7.2711 | 7.2659 | 6.2928 | 6.1292 | 5.9666 | 5.7616 | 5.5593 | 4.8055 | 3.8225 | 2.2474 | 1.5539 | 7.2359 | 7.2319 | 7.2308 | 7.2292 | 7.224 | 6.1609 | 6.009 | 5.8581 | 5.6607 | 5.4583 | 4.7042 | 3.7209 | 2.1453 | 1.4517
| FORTEVIOT | CT |  |  | 7.9073 | 7.9063 | 7.9052 | 7.9037 | 7.8984 | 7.892 | 7.8845 | 7.8757 | 7.865 | 7.8595 | 5.9682 | 5.217 | 3.8294 | 2.8197 | 7.365 | 7.2738 | 7.2727 | 7.2711 | 7.2659 | 7.2595 | 6.2428 | 6.1335 | 5.9875 | 5.8096 | 5.2033 | 4.3309 | 2.7158 | 1.5539 | 7.2359 | 7.2319 | 7.2308 | 7.2292 | 7.224 | 6.2084 | 6.1128 | 6.0109 | 5.8748 | 5.7087 | 5.1021 | 4.2296 | 2.6139 | 1.4517
| FORTEVIOT | LW |  |  | 7.9086 | 7.9086 | 7.9086 | 7.9086 | 7.908 | 7.9069 | 7.9052 | 7.9027 | 7.898 | 6.2799 | 5.6371 | 4.7976 | 3.4535 | 2.9272 | 7.371 | 7.276 | 7.276 | 7.276 | 7.2755 | 6.2928 | 6.1292 | 5.9666 | 5.7616 | 5.5593 | 4.8055 | 3.8225 | 2.2474 | 1.6308 | 7.2381 | 7.2342 | 7.2342 | 7.2342 | 7.2336 | 6.1609 | 6.009 | 5.8581 | 5.6607 | 5.4583 | 4.7042 | 3.7209 | 2.1453 | 1.5285
| FORTEVIOT | ST |  |  | 7.9083 | 7.908 | 7.9078 | 7.9075 | 7.9052 | 7.9024 | 7.899 | 7.895 | 7.89 | 7.8884 | 6.1436 | 5.4845 | 4.6216 | 3.626 | 7.368 | 7.3643 | 7.2753 | 7.275 | 7.2727 | 7.2698 | 7.2665 | 6.2504 | 6.1202 | 5.9581 | 5.4018 | 4.6306 | 3.6267 | 2.4625 | 7.2373 | 7.2364 | 7.2334 | 7.2331 | 7.2308 | 6.2863 | 6.2109 | 6.1207 | 5.9996 | 5.8492 | 5.3007 | 4.5293 | 3.5251 | 2.3605
| FORTEVIOT | SP |  |  | 7.9079 | 7.9076 | 7.9073 | 7.9069 | 7.9068 | 7.9068 | 7.9067 | 7.9066 | 7.9064 | 7.9058 | 7.9035 | 7.9013 | 7.8785 | 7.8544 | 7.371 | 7.3702 | 7.3693 | 7.3683 | 7.3573 | 7.3467 | 7.3338 | 7.3211 | 7.3043 | 7.2822 | 7.271 | 6.247 | 5.9632 | 5.6943 | 7.2376 | 7.2371 | 7.2367 | 7.2362 | 7.2341 | 7.2323 | 7.2322 | 7.2321 | 7.232 | 7.2314 | 7.2291 | 6.1179 | 5.8532 | 5.5933
INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | NO | 2.4865 | 2.3902 | 2.2478 | 2.0324 | 1.818 | 1.589 | 1.3609 | 1.1334 | 0.9233 | 0.75185 | 0.45837 | -0.018209 | -0.43016 | -0.84195 | 2.5774 | 2.4358 | 2.2923 | 2.1169 | 1.9429 | 1.7445 | 1.5435 | 1.3411 | 1.1522 | 0.99363 | 0.71815 | 0.27052 | -0.1188 | -0.50748 | 2.4581 | 2.3488 | 2.1639 | 1.9505 | 1.7391 | 1.5154 | 1.2933 | 1.0706 | 0.86619 | 0.69178 | 0.39134 | -0.10379 | -0.5325 | -0.9608
| FOYERS | CT |  |  | 2.4865 | 2.3902 | 2.2478 | 2.0324 | 1.818 | 1.589 | 1.3609 | 1.1334 | 0.9233 | 0.75185 | 0.45837 | -0.018209 | -0.43016 | -0.84195 | 2.5774 | 2.4358 | 2.2923 | 2.1169 | 1.9429 | 1.7445 | 1.5435 | 1.3411 | 1.1522 | 0.99363 | 0.71815 | 0.27052 | -0.1188 | -0.50748 | 2.4581 | 2.3488 | 2.1639 | 1.9505 | 1.7391 | 1.5154 | 1.2933 | 1.0706 | 0.86619 | 0.69178 | 0.39134 | -0.10379 | -0.5325 | -0.9608
| FOYERS | LW |  |  | 2.758 | 2.7493 | 2.7007 | 2.6508 | 2.4737 | 2.4274 | 2.3745 | 2.3207 | 2.2685 | 2.2157 | 2.0947 | 1.8861 | 1.683 | 1.4726 | 2.647 | 2.6397 | 2.6168 | 2.4895 | 2.4536 | 2.4169 | 2.3695 | 2.321 | 2.2737 | 2.2259 | 2.119 | 1.9358 | 1.7555 | 1.5645 | 2.644 | 2.6358 | 2.5926 | 2.4564 | 2.4084 | 2.3591 | 2.3089 | 2.2576 | 2.208 | 2.1578 | 2.04 | 1.8362 | 1.6281 | 1.4126
| FOYERS | ST |  |  | 2.7613 | 2.7555 | 2.7229 | 2.6884 | 2.6541 | 2.4877 | 2.4631 | 2.4276 | 2.3925 | 2.3574 | 2.2486 | 2.0731 | 1.8975 | 1.7243 | 2.6495 | 2.6446 | 2.6289 | 2.6116 | 2.4908 | 2.4664 | 2.4411 | 2.4159 | 2.3847 | 2.3526 | 2.2537 | 2.0926 | 1.9303 | 1.7691 | 2.6471 | 2.6417 | 2.6127 | 2.4916 | 2.4591 | 2.4264 | 2.3919 | 2.3575 | 2.3237 | 2.2893 | 2.1826 | 2.0114 | 1.8402 | 1.661
| FOYERS | SP |  |  | 2.7575 | 2.7498 | 2.7421 | 2.7344 | 2.7231 | 2.7118 | 2.7008 | 2.6899 | 2.6791 | 2.4911 | 2.4625 | 2.4061 | 2.3597 | 2.3124 | 2.6468 | 2.6406 | 2.6344 | 2.6282 | 2.6194 | 2.6109 | 2.6023 | 2.5938 | 2.5851 | 2.5763 | 2.4949 | 2.4366 | 2.3881 | 2.3421 | 2.6435 | 2.6362 | 2.6289 | 2.6216 | 2.6108 | 2.6001 | 2.4959 | 2.4839 | 2.4719 | 2.4599 | 2.4248 | 2.3568 | 2.3005 | 2.247
FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | 50.6071 | 50.5232 | 50.4383 | 50.3221 | 50.16 | 49.9961 | 49.8271 | 49.647 | 49.4481 | 49.3125 | 48.9347 | 47.6869 | 36.2466 | 31.8835 | 46.7184 | 46.6066 | 46.469 | 46.2046 | 46.038 | 45.942 | 45.8393 | 45.729 | 45.6078 | 45.5443 | 45.3736 | 33.4645 | 29.6882 | 24.8752 | 45.0249 | 44.9298 | 44.8292 | 44.6773 | 44.4454 | 44.2177 | 43.986 | 43.7334 | 43.4457 | 43.2027 | 42.8182 | 33.2792 | 29.4869 | 24.591
| FRASERBURGH | CT |  |  | 50.6071 | 50.5232 | 50.4383 | 50.3221 | 50.16 | 49.9961 | 49.8271 | 49.647 | 49.4481 | 49.3125 | 48.9347 | 47.6869 | 36.2466 | 31.8835 | 46.7184 | 46.6066 | 46.469 | 46.2046 | 46.038 | 45.942 | 45.8393 | 45.729 | 45.6078 | 45.5443 | 45.3736 | 33.4645 | 29.6882 | 24.8752 | 45.0249 | 44.9298 | 44.8292 | 44.6773 | 44.4454 | 44.2177 | 43.986 | 43.7334 | 43.4457 | 43.2027 | 42.8182 | 33.2792 | 29.4869 | 24.591
| FRASERBURGH | LW |  |  | 50.687 | 50.6798 | 50.6721 | 50.6605 | 50.6026 | 50.5427 | 50.4805 | 50.4155 | 50.3305 | 50.2631 | 50.0194 | 49.131 | 48.9564 | 37.6198 | 46.8217 | 46.8037 | 46.7778 | 46.7185 | 46.3066 | 46.2931 | 46.2773 | 46.2584 | 46.2298 | 46.2193 | 46.1832 | 34.6328 | 32.8806 | 30.8645 | 45.12 | 45.1086 | 45.0943 | 45.0719 | 44.9298 | 44.7866 | 44.642 | 44.4956 | 44.3099 | 44.141 | 43.9088 | 34.5582 | 32.8076 | 30.7722
| FRASERBURGH | ST |  |  | 50.6863 | 50.6792 | 50.6716 | 50.6605 | 50.6159 | 50.5676 | 50.5113 | 50.4472 | 50.3685 | 50.3032 | 50.088 | 48.8047 | 38.375 | 34.8487 | 46.8161 | 46.796 | 46.7707 | 46.725 | 46.4859 | 46.2986 | 46.2333 | 46.1984 | 46.1567 | 46.1417 | 46.0946 | 36.1377 | 32.0514 | 28.0536 | 45.118 | 45.1062 | 45.0925 | 45.0738 | 44.9913 | 44.9052 | 44.8045 | 44.6887 | 44.5431 | 44.3851 | 43.8593 | 35.9931 | 31.8408 | 27.7823
| FRASERBURGH | SP |  |  | 51.062 | 50.6742 | 50.6658 | 50.6573 | 50.6432 | 50.6283 | 50.6098 | 50.5915 | 50.5698 | 50.54 | 50.4333 | 50.2866 | 50.0281 | 49.7383 | 47.5253 | 46.8172 | 46.8078 | 46.7979 | 46.7318 | 46.6565 | 46.5412 | 46.4275 | 46.3232 | 46.2696 | 46.2395 | 46.2003 | 46.0386 | 45.8398 | 45.4245 | 45.109 | 45.0996 | 45.09 | 45.06 | 45.0329 | 44.9952 | 44.9579 | 44.9113 | 44.8476 | 44.6102 | 44.2905 | 43.8797 | 43.5237
LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | NO | 7.6692 | 7.5539 | 7.4368 | 7.2521 | 7.0428 | 6.8321 | 4.8895 | 4.7131 | 6.9031 | 4.9159 | 3.4853 | -0.34879 | -5.3739 | -11.8074 | 6.7157 | 6.6244 | 6.5703 | 6.4869 | 6.3884 | 4.9094 | 4.6308 | 4.2416 | 4.5494 | 4.0419 | 1.9668 | -1.3622 | -6.0686 | -12.12 | 6.6806 | 4.9504 | 4.8257 | 4.6217 | 4.2478 | 3.8926 | 3.5295 | 3.1412 | 3.4602 | 2.9947 | 1.476 | -2.4701 | -7.9293 | -14.845
| FRIOCKHEIM | CT |  |  | 7.6692 | 7.5539 | 7.4368 | 7.2521 | 7.0428 | 6.8321 | 4.8895 | 4.7131 | 6.9031 | 4.9159 | 3.4853 | -0.24409 | -5.3739 | -11.8074 | 6.7157 | 6.6244 | 6.5703 | 6.4869 | 6.3884 | 4.9094 | 4.6308 | 4.2416 | 4.5494 | 4.0419 | 2.4111 | -1.2643 | -6.0686 | -12.12 | 6.6806 | 4.9504 | 4.8257 | 4.6217 | 4.2478 | 3.8926 | 3.5295 | 3.1412 | 3.4602 | 2.9947 | 1.5468 | -2.4213 | -7.9293 | -14.845
| FRIOCKHEIM | LW |  |  | 7.7753 | 7.7651 | 7.7542 | 7.7278 | 7.5434 | 7.4213 | 7.2977 | 7.1692 | 7.896 | 7.8499 | 3.5119 | 0.39651 | -2.3091 | -3.8797 | 6.8014 | 6.7929 | 6.7834 | 6.758 | 6.6897 | 6.669 | 4.8032 | 4.3532 | 4.6064 | 4.049 | 1.9668 | -1.3622 | -4.2808 | -6.0534 | 6.7677 | 6.76 | 6.7525 | 6.7336 | 4.7439 | 4.3592 | 3.9755 | 3.5814 | 3.9053 | 3.4185 | 1.476 | -2.0374 | -5.1021 | -6.9104
| FRIOCKHEIM | ST |  |  | 7.7751 | 7.7651 | 7.7537 | 7.7298 | 7.6141 | 7.5565 | 7.496 | 7.4197 | 7.2999 | 7.1832 | 4.3344 | -0.34879 | -3.1666 | -8.2564 | 6.7997 | 6.7902 | 6.7791 | 6.7548 | 6.7037 | 6.6898 | 6.6741 | 6.6523 | 4.9346 | 4.5099 | 3.0462 | -1.2295 | -3.859 | -8.8699 | 6.7703 | 6.7648 | 6.7594 | 6.7465 | 4.9538 | 4.7855 | 4.6122 | 4.3971 | 4.0839 | 3.7153 | 2.4463 | -2.4701 | -5.5613 | -11.1555
| FRIOCKHEIM | SP |  |  | 7.7745 | 7.7657 | 7.7568 | 7.7459 | 7.7029 | 7.6554 | 7.5951 | 7.5634 | 7.5229 | 7.4721 | 7.2687 | 3.3383 | 1.2221 | -0.6066 | 6.8008 | 6.7937 | 6.7863 | 6.7772 | 6.7304 | 6.7006 | 6.693 | 6.6845 | 6.6734 | 6.6598 | 4.9007 | 2.6501 | 0.63231 | -1.0756 | 6.7665 | 6.7592 | 6.7519 | 6.7428 | 6.7309 | 6.719 | 4.9473 | 4.8636 | 4.7546 | 4.6137 | 4.0356 | 1.3761 | -0.79053 | -2.6736
KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | YES | 3.06 | 3.0515 | 3.0391 | 3.0109 | 2.9161 | 2.8135 | 2.7004 | 2.3616 | 1.6977 | 1.6762 | 0.52999 | -0.96506 | -2.931 | -5.5836 | 1.5692 | 1.5565 | 1.5378 | 1.4942 | 1.383 | 1.2642 | 1.0022 | 0.45698 | -0.29733 | -0.32011 | -0.65238 | -2.2652 | -3.9994 | -6.9392 | 2.2254 | 2.2135 | 2.1962 | 2.156 | 2.0484 | 1.9331 | 1.811 | 1.3884 | 0.63076 | 0.60794 | -0.38073 | -1.9699 | -3.9702 | -6.8979
| FYVIE | CT |  |  | 3.06 | 3.0515 | 3.0391 | 3.0109 | 2.9161 | 2.8135 | 2.7004 | 2.5823 | 1.873 | 1.8166 | 0.87471 | -0.96506 | -2.931 | -3.3699 | 1.5692 | 1.5565 | 1.5378 | 1.4942 | 1.383 | 1.2642 | 1.1386 | 1.0115 | 0.40385 | 0.33791 | -0.47579 | -2.2652 | -3.9994 | -4.4542 | 2.2254 | 2.2135 | 2.1962 | 2.156 | 2.0484 | 1.9331 | 1.811 | 1.6868 | 0.96961 | 0.90678 | -0.05699 | -1.9699 | -3.9702 | -4.4101
| FYVIE | LW |  |  | 3.0683 | 3.0666 | 3.064 | 3.0575 | 2.952 | 2.8349 | 2.7041 | 2.5536 | 1.7741 | 1.727 | 0.78534 | -0.47022 | -2.2436 | -5.5836 | 1.5814 | 1.5788 | 1.5747 | 1.5643 | 1.4546 | 1.3334 | 1.1985 | 1.044 | 0.37241 | 0.32111 | -0.47464 | -1.5826 | -3.0967 | -6.9392 | 2.2367 | 2.2343 | 2.2305 | 2.221 | 2.1122 | 1.9919 | 1.8579 | 1.7043 | 0.92108 | 0.8707 | -0.08162 | -1.3538 | -3.1446 | -6.8979
| FYVIE | ST |  |  | 3.0635 | 3.058 | 3.0509 | 3.0375 | 2.9813 | 2.917 | 2.8549 | 2.7849 | 2.4047 | 2.3665 | 0.52999 | -0.51735 | -1.7706 | -2.0408 | 1.574 | 1.5656 | 1.5545 | 1.5334 | 1.4668 | 1.39 | 1.3167 | 1.2358 | 0.90173 | 0.85726 | -0.65238 | -1.7388 | -2.883 | -3.1739 | 2.2299 | 2.2221 | 2.2119 | 2.1924 | 2.1282 | 2.0541 | 1.9832 | 1.9046 | 1.5167 | 1.4743 | -0.38073 | -1.5117 | -2.7871 | -3.0685
| FYVIE | SP |  |  | 3.8987 | 3.8976 | 3.8963 | 3.8949 | 3.6722 | 3.3626 | 2.8584 | 2.3616 | 1.6977 | 1.6762 | 1.6009 | 0.75147 | -1.3055 | -3.3722 | 2.2445 | 2.243 | 2.2412 | 2.2392 | 1.9187 | 1.5531 | 1.0022 | 0.45698 | -0.29733 | -0.32011 | -0.3991 | -1.3592 | -3.6035 | -5.9223 | 3.036 | 3.0355 | 3.035 | 3.0345 | 2.7682 | 2.4315 | 1.9244 | 1.3884 | 0.63076 | 0.60794 | 0.52881 | -0.43542 | -2.7184 | -5.1001
GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10123 | 0.10122 | 0.1012 | 0.10117 | 0.10113 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.099706 | 0.099383 | 0.10118 | 0.10118 | 0.10117 | 0.10115 | 0.10114 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.09972 | 0.099405
| GARBAT FOREST | CT |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10123 | 0.10122 | 0.10121 | 0.10118 | 0.10115 | 0.10113 | 0.10112 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.099881 | 0.10118 | 0.10118 | 0.10117 | 0.10116 | 0.10115 | 0.10114 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.09989
| GARBAT FOREST | LW |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10123 | 0.10122 | 0.1012 | 0.10117 | 0.10113 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.099706 | 0.099383 | 0.10118 | 0.10118 | 0.10117 | 0.10115 | 0.10114 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.10113 | 0.09972 | 0.099405
| GARBAT FOREST | ST |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10123 | 0.10122 | 0.10122 | 0.10121 | 0.10119 | 0.10117 | 0.10116 | 0.10114 | 0.10113 | 0.10112 | 0.10111 | 0.10111 | 0.10111 | 0.10111 | 0.10118 | 0.10118 | 0.10118 | 0.10117 | 0.10117 | 0.10116 | 0.10115 | 0.10115 | 0.10114 | 0.10114 | 0.10113 | 0.10113 | 0.10113 | 0.10113
| GARBAT FOREST | SP |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10123 | 0.10123 | 0.10123 | 0.10123 | 0.10123 | 0.10122 | 0.10122 | 0.10121 | 0.1012 | 0.10119 | 0.10117 | 0.10114 | 0.10112 | 0.10111 | 0.10118 | 0.10118 | 0.10118 | 0.10118 | 0.10118 | 0.10118 | 0.10118 | 0.10117 | 0.10117 | 0.10117 | 0.10116 | 0.10115 | 0.10114 | 0.10113
STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | 2.3305 | 3.8303 | 3.83 | 3.8297 | 3.8284 | 3.8269 | 3.8253 | 3.8233 | 3.8211 | 3.8199 | 3.8157 | 3.8059 | 3.7899 | 3.1907 | 2.0935 | 3.5928 | 3.592 | 3.5902 | 3.5873 | 3.5844 | 3.5812 | 3.5719 | 3.5624 | 3.5532 | 3.5257 | 3.485 | 3.4487 | 2.8996 | 1.8685 | 3.3682 | 3.3676 | 3.3667 | 3.3649 | 3.3628 | 3.3606 | 3.3557 | 3.3506 | 3.3463 | 3.3329 | 3.3121 | 3.2874 | 2.4491
| GISLA | CT |  |  | 2.3305 | 3.8303 | 3.83 | 3.8297 | 3.8284 | 3.8269 | 3.8253 | 3.8233 | 3.8211 | 3.8199 | 3.8157 | 3.8059 | 3.7899 | 3.7588 | 2.0935 | 3.5928 | 3.592 | 3.5902 | 3.5873 | 3.5844 | 3.5812 | 3.5719 | 3.5624 | 3.5532 | 3.5257 | 3.485 | 3.4487 | 3.4105 | 1.8685 | 3.3682 | 3.3676 | 3.3667 | 3.3649 | 3.3628 | 3.3606 | 3.3557 | 3.3506 | 3.3463 | 3.3329 | 3.3121 | 3.2874 | 3.2563
| GISLA | LW |  |  | 2.3308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.8308 | 3.1907 | 2.0937 | 3.5932 | 3.5924 | 3.5904 | 3.5882 | 3.5861 | 3.5839 | 3.5819 | 3.5798 | 3.5776 | 3.5711 | 3.5607 | 3.5501 | 2.8996 | 1.8688 | 3.3686 | 3.3683 | 3.3675 | 3.3667 | 3.3658 | 3.365 | 3.3642 | 3.3634 | 3.3625 | 3.3599 | 3.3558 | 3.3517 | 2.4491
| GISLA | ST |  |  | 2.3308 | 3.8308 | 3.8307 | 3.8307 | 3.8305 | 3.8303 | 3.8301 | 3.8298 | 3.8295 | 3.8294 | 3.8291 | 3.8286 | 3.8258 | 3.8243 | 2.0939 | 3.5937 | 3.5933 | 3.5927 | 3.5916 | 3.5904 | 3.5851 | 3.5798 | 3.5746 | 3.5693 | 3.5539 | 3.5307 | 3.5085 | 3.4911 | 1.8689 | 3.3688 | 3.3686 | 3.3684 | 3.3679 | 3.3672 | 3.365 | 3.3627 | 3.3605 | 3.3584 | 3.3521 | 3.342 | 3.3331 | 3.3255
| GISLA | SP |  |  | 2.3308 | 3.8307 | 3.8307 | 3.8307 | 3.8307 | 3.8307 | 3.8307 | 3.8307 | 3.8307 | 3.8306 | 3.8305 | 3.8304 | 3.8298 | 3.8286 | 2.0941 | 3.5941 | 3.594 | 3.594 | 3.5937 | 3.5934 | 3.5917 | 3.59 | 3.5879 | 3.5858 | 3.5798 | 3.5706 | 3.5613 | 3.5519 | 1.869 | 3.3689 | 3.3689 | 3.3689 | 3.3688 | 3.3686 | 3.368 | 3.3673 | 3.3665 | 3.3656 | 3.3632 | 3.3595 | 3.3555 | 3.351
ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | 3.8317 | 3.8286 | 3.8241 | 3.814 | 3.8014 | 3.7885 | 3.7753 | 3.7563 | 3.7371 | 3.7187 | 3.6612 | 3.558 | 2.6215 | 2.4744 | 4.5731 | 4.5708 | 4.5675 | 4.5603 | 4.5508 | 4.541 | 4.5308 | 4.5164 | 4.5018 | 3.9895 | 3.915 | 3.7879 | 3.0096 | 2.8423 | 4.7184 | 4.7174 | 4.716 | 4.7132 | 4.7084 | 4.7033 | 4.6977 | 4.6903 | 4.6826 | 4.6765 | 4.6676 | 3.8858 | 2.9294 | 2.7589
| GLASTULLICH | CT |  |  | 3.8317 | 3.8286 | 3.8241 | 3.814 | 3.8014 | 3.7885 | 3.7753 | 3.7563 | 3.7371 | 3.7187 | 3.6612 | 3.558 | 2.6215 | 2.4744 | 4.5731 | 4.5708 | 4.5675 | 4.5603 | 4.5508 | 4.541 | 4.5308 | 4.5164 | 4.5018 | 3.9895 | 3.915 | 3.7879 | 3.0096 | 2.8423 | 4.7184 | 4.7174 | 4.716 | 4.7132 | 4.7084 | 4.7033 | 4.6977 | 4.6903 | 4.6826 | 4.6765 | 4.6676 | 3.8858 | 2.9294 | 2.7589
| GLASTULLICH | LW |  |  | 3.8348 | 3.8342 | 3.8332 | 3.8309 | 3.8283 | 3.8257 | 3.8232 | 3.8208 | 3.8184 | 3.8158 | 3.8082 | 3.7959 | 2.9703 | 2.9569 | 4.5754 | 4.575 | 4.5743 | 4.5727 | 4.5709 | 4.5691 | 4.5674 | 4.5657 | 4.5641 | 4.5623 | 4.5571 | 4.5486 | 3.4227 | 3.4061 | 4.7196 | 4.7195 | 4.7193 | 4.7187 | 4.7182 | 4.7176 | 4.7171 | 4.7166 | 4.716 | 4.7155 | 4.7138 | 4.7111 | 3.3529 | 3.3357
| GLASTULLICH | ST |  |  | 3.8349 | 3.8345 | 3.8341 | 3.8332 | 3.8314 | 3.8293 | 3.8219 | 3.8145 | 3.807 | 3.7961 | 3.7644 | 3.7132 | 3.2397 | 3.1805 | 4.5754 | 4.5751 | 4.5748 | 4.5742 | 4.5727 | 4.571 | 4.5656 | 4.56 | 4.5545 | 4.5468 | 4.5246 | 3.9767 | 3.582 | 3.5099 | 4.7195 | 4.7194 | 4.7192 | 4.719 | 4.718 | 4.7168 | 4.7144 | 4.7118 | 4.7091 | 4.7064 | 4.6984 | 4.6894 | 3.5868 | 3.5127
| GLASTULLICH | SP |  |  | 3.8351 | 3.8349 | 3.8347 | 3.8346 | 3.8343 | 3.8339 | 3.8318 | 3.8297 | 3.827 | 3.8227 | 3.8104 | 3.7916 | 3.7713 | 3.7484 | 4.5755 | 4.5754 | 4.5752 | 4.5751 | 4.5748 | 4.5746 | 4.5731 | 4.5717 | 4.5698 | 4.5668 | 4.5581 | 4.545 | 4.5301 | 4.5123 | 4.7195 | 4.7194 | 4.7192 | 4.7191 | 4.719 | 4.7189 | 4.7184 | 4.718 | 4.7174 | 4.7163 | 4.7131 | 4.7087 | 4.7019 | 4.6918
SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | 4.1569 | 4.1565 | 4.0926 | 4.0284 | 3.8145 | 3.5227 | 2.4983 | 2.1577 | 1.7243 | 1.5229 | 1.1176 | -0.056698 | -0.89803 | -1.4764 | 3.3991 | 3.3985 | 3.2834 | 3.1821 | 2.968 | 2.3324 | 2.0455 | 1.7387 | 1.3038 | 1.1704 | 0.77697 | -0.40914 | -1.2638 | -1.8554 | 3.6687 | 3.668 | 3.5417 | 3.4146 | 3.1361 | 2.3314 | 2.0308 | 1.7182 | 1.2541 | 1.1214 | 0.72166 | -0.44348 | -1.3008 | -1.905
| GLEDFIELD | CT |  |  | 4.1569 | 4.1565 | 4.0926 | 4.0284 | 3.8146 | 3.5755 | 2.4983 | 2.1577 | 1.7388 | 1.5229 | 1.1176 | -0.056698 | -0.89803 | -1.4764 | 3.3991 | 3.3985 | 3.2834 | 3.1821 | 2.968 | 2.3956 | 2.092 | 1.7687 | 1.3679 | 1.1704 | 0.77697 | -0.40914 | -1.2638 | -1.8554 | 3.6687 | 3.668 | 3.5417 | 3.4146 | 3.1361 | 2.3314 | 2.0308 | 1.7182 | 1.328 | 1.1214 | 0.72166 | -0.44348 | -1.3008 | -1.905
| GLEDFIELD | LW |  |  | 4.1575 | 4.1575 | 4.1293 | 4.1011 | 3.8145 | 3.5227 | 2.4994 | 2.1759 | 1.7243 | 1.6207 | 1.3193 | 0.65916 | 0.11115 | -0.21555 | 3.3996 | 3.3994 | 3.3483 | 3.2967 | 2.989 | 2.3324 | 2.0455 | 1.7387 | 1.3038 | 1.1859 | 0.87678 | 0.23422 | -0.29568 | -0.60345 | 3.6692 | 3.6689 | 3.6127 | 3.5558 | 3.2404 | 2.3764 | 2.0583 | 1.7202 | 1.2541 | 1.1359 | 0.8364 | 0.20942 | -0.32516 | -0.64495
| GLEDFIELD | ST |  |  | 4.1574 | 4.1573 | 4.1385 | 4.1197 | 3.997 | 3.8672 | 3.7427 | 3.6042 | 3.3925 | 3.3339 | 2.4489 | 1.8941 | 1.1438 | 0.76309 | 3.3996 | 3.3994 | 3.3654 | 3.3313 | 3.1933 | 3.0483 | 2.9107 | 2.4139 | 2.2114 | 2.162 | 1.9961 | 1.4206 | 0.67578 | 0.30131 | 3.6693 | 3.6691 | 3.6317 | 3.5941 | 3.4526 | 3.3038 | 3.1581 | 2.4578 | 2.2345 | 2.1642 | 1.9735 | 1.3991 | 0.63757 | 0.24263
| GLEDFIELD | SP |  |  | 4.1573 | 4.1571 | 4.157 | 4.1569 | 4.1569 | 4.1568 | 4.1568 | 4.1568 | 4.1568 | 4.1566 | 4.156 | 4.1555 | 4.1524 | 4.1457 | 3.3996 | 3.3994 | 3.3993 | 3.3991 | 3.399 | 3.3989 | 3.3982 | 3.3975 | 3.3967 | 3.3957 | 3.3927 | 3.3886 | 3.3821 | 3.3722 | 3.6693 | 3.6691 | 3.669 | 3.6688 | 3.6687 | 3.6685 | 3.6674 | 3.6664 | 3.6652 | 3.6638 | 3.6597 | 3.6539 | 3.6457 | 3.6342
FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | 0.10426 | 0.10426 | 0.071982 | 0.039914 | 0.0069529 | -0.032862 | -0.073864 | -0.11606 | -0.15958 | -0.20434 | -0.28425 | -0.41415 | -0.52723 | -0.63639 | 0.10181 | 0.10178 | 0.071144 | 0.040507 | 0.0090974 | -0.028814 | -0.067854 | -0.10802 | -0.14946 | -0.19207 | -0.26822 | -0.39199 | -0.49977 | -0.60382 | 0.10185 | 0.10184 | 0.069388 | 0.036938 | 0.0036702 | -0.036492 | -0.077851 | -0.12041 | -0.16431 | -0.20945 | -0.29009 | -0.42116 | -0.53527 | -0.64542
| GLEN LAOGH | CT |  |  | 0.10426 | 0.10426 | 0.071982 | 0.039914 | 0.0069529 | -0.032862 | -0.073864 | -0.11606 | -0.15958 | -0.20434 | -0.28425 | -0.41415 | -0.52723 | -0.63639 | 0.10181 | 0.10178 | 0.071144 | 0.040507 | 0.0090974 | -0.028814 | -0.067854 | -0.10802 | -0.14946 | -0.19207 | -0.26822 | -0.39199 | -0.49977 | -0.60382 | 0.10185 | 0.10184 | 0.069388 | 0.036938 | 0.0036702 | -0.036492 | -0.077851 | -0.12041 | -0.16431 | -0.20945 | -0.29009 | -0.42116 | -0.53527 | -0.64542
| GLEN LAOGH | LW |  |  | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.099397 | 0.10181 | 0.10178 | 0.10173 | 0.10166 | 0.10165 | 0.10165 | 0.10165 | 0.10165 | 0.10165 | 0.10165 | 0.099445 | 0.098472 | 0.097492 | 0.096522 | 0.10185 | 0.10184 | 0.10182 | 0.10178 | 0.10177 | 0.10177 | 0.10177 | 0.10177 | 0.10177 | 0.10177 | 0.099558 | 0.098607 | 0.097627 | 0.096656
| GLEN LAOGH | ST |  |  | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10182 | 0.1018 | 0.10178 | 0.10175 | 0.10171 | 0.10167 | 0.10165 | 0.10165 | 0.10165 | 0.10165 | 0.10165 | 0.10165 | 0.099784 | 0.099358 | 0.10185 | 0.10185 | 0.10184 | 0.10182 | 0.10181 | 0.10179 | 0.10178 | 0.10177 | 0.10177 | 0.10177 | 0.10177 | 0.10177 | 0.099888 | 0.099474
| GLEN LAOGH | SP |  |  | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10183 | 0.10183 | 0.10183 | 0.10182 | 0.10181 | 0.10179 | 0.10178 | 0.10176 | 0.10174 | 0.10172 | 0.10167 | 0.10165 | 0.10165 | 0.10165 | 0.10186 | 0.10186 | 0.10185 | 0.10185 | 0.10185 | 0.10184 | 0.10183 | 0.10183 | 0.10182 | 0.10181 | 0.10179 | 0.10177 | 0.10177 | 0.10177
KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | 8.7205 | 8.7199 | 8.6567 | 8.5932 | 8.5257 | 8.4443 | 8.3749 | 8.3158 | 8.2543 | 8.1939 | 7.4111 | 7.1051 | 6.8128 | 6.4845 | 8.3411 | 8.3338 | 8.2999 | 8.2518 | 8.1989 | 7.4375 | 7.4015 | 7.3471 | 7.2524 | 7.1571 | 6.9621 | 6.6368 | 6.3206 | 5.9683 | 8.0796 | 8.0733 | 8.0116 | 7.9376 | 7.8584 | 7.423 | 7.3316 | 7.2374 | 7.1402 | 7.0427 | 6.8482 | 6.5238 | 6.211 | 5.8623
| GLENCOE | CT |  |  | 8.7205 | 8.7199 | 8.6567 | 8.5932 | 8.5257 | 8.4443 | 8.3749 | 8.3158 | 8.2543 | 8.1939 | 7.4111 | 7.1051 | 6.8128 | 6.4845 | 8.3411 | 8.3338 | 8.2999 | 8.2518 | 8.1989 | 7.4375 | 7.4015 | 7.3471 | 7.2524 | 7.1571 | 6.9621 | 6.6368 | 6.3206 | 5.9683 | 8.0796 | 8.0733 | 8.0116 | 7.9376 | 7.8584 | 7.423 | 7.3316 | 7.2374 | 7.1402 | 7.0427 | 6.8482 | 6.5238 | 6.211 | 5.8623
| GLENCOE | LW |  |  | 9.2463 | 8.7215 | 8.6938 | 8.6661 | 8.6395 | 8.6138 | 8.5883 | 8.5627 | 8.5374 | 8.5116 | 8.4538 | 8.3739 | 8.311 | 8.2465 | 8.7034 | 8.3458 | 8.3326 | 8.3151 | 8.2969 | 8.2788 | 8.2608 | 8.243 | 8.2254 | 8.2071 | 7.4463 | 7.4055 | 7.3256 | 7.2157 | 8.5272 | 8.0838 | 8.058 | 8.0286 | 7.9985 | 7.9686 | 7.9387 | 7.9089 | 7.8794 | 7.8492 | 7.4285 | 7.324 | 7.2149 | 7.1037
| GLENCOE | ST |  |  | 8.7213 | 8.7212 | 8.7026 | 8.684 | 8.6644 | 8.6444 | 8.6243 | 8.6038 | 8.5832 | 8.5639 | 8.5058 | 8.4078 | 8.3247 | 8.2495 | 8.3438 | 8.3391 | 8.3261 | 8.3074 | 8.2836 | 8.2564 | 8.2341 | 8.2119 | 8.1897 | 8.1654 | 7.4503 | 7.4018 | 7.2498 | 7.1038 | 8.0821 | 8.078 | 8.0572 | 8.0316 | 8.0014 | 7.9683 | 7.9394 | 7.9104 | 7.8815 | 7.8509 | 7.4474 | 7.317 | 7.1701 | 7.0291
| GLENCOE | SP |  |  | 9.2459 | 8.7209 | 8.7207 | 8.7205 | 8.7204 | 8.7204 | 8.7204 | 8.7203 | 8.7203 | 8.72 | 8.7189 | 8.7181 | 8.7129 | 8.7015 | 8.7033 | 8.3474 | 8.3464 | 8.3453 | 8.3409 | 8.3356 | 8.3311 | 8.3266 | 8.321 | 8.3141 | 8.2941 | 8.2637 | 8.2308 | 8.1932 | 8.5275 | 8.0852 | 8.0843 | 8.0833 | 8.0794 | 8.0749 | 8.0711 | 8.0672 | 8.0624 | 8.0565 | 8.0393 | 8.0132 | 7.9843 | 7.9663
DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | 0.027044 | 0.35684 | 0.3335 | 0.31016 | 0.22278 | 0.12563 | 0.023583 | -0.12002 | -0.31142 | -0.37128 | -0.48905 | -1.0097 | -1.3451 | -1.5164 | 0.01852 | 0.34684 | 0.32676 | 0.30351 | 0.21617 | 0.1193 | 0.017611 | -0.12657 | -0.32647 | -0.37855 | -0.49853 | -1.0227 | -1.3623 | -1.5378 | 0.0039244 | 0.33322 | 0.31028 | 0.28627 | 0.19819 | 0.10027 | -0.0025279 | -0.1473 | -0.33986 | -0.401 | -0.5231 | -1.0508 | -1.3932 | -1.5715
| GLENDARUEL | CT |  |  | 0.027044 | 0.35684 | 0.3335 | 0.31016 | 0.22278 | 0.12563 | 0.023583 | -0.12002 | -0.31142 | -0.37128 | -0.48905 | -1.0097 | -1.3451 | -1.5164 | 0.019932 | 0.34946 | 0.32676 | 0.30351 | 0.21617 | 0.1193 | 0.017611 | -0.12657 | -0.31846 | -0.37855 | -0.49853 | -1.0227 | -1.3623 | -1.5378 | 0.0043837 | 0.33407 | 0.31028 | 0.28627 | 0.19819 | 0.10027 | -0.0025279 | -0.1473 | -0.33986 | -0.401 | -0.5231 | -1.0508 | -1.3932 | -1.5715
| GLENDARUEL | LW |  |  | 0.38892 | 0.35731 | 0.35731 | 0.35731 | 0.26106 | 0.16293 | 0.061476 | -0.090867 | -0.31009 | -0.34814 | -0.45717 | -0.70439 | -0.8853 | -0.95026 | 0.36163 | 0.34983 | 0.3493 | 0.34796 | 0.25022 | 0.15064 | 0.047762 | -0.10597 | -0.32647 | -0.36568 | -0.47811 | -0.73082 | -0.91726 | -0.98844 | 0.36486 | 0.3345 | 0.33427 | 0.33372 | 0.23685 | 0.13793 | 0.035174 | -0.11845 | -0.33883 | -0.37792 | -0.48998 | -0.7421 | -0.92925 | -1.003
| GLENDARUEL | ST |  |  | 0.027265 | 0.35725 | 0.35723 | 0.35702 | 0.31145 | 0.26254 | 0.21702 | 0.15286 | 0.049683 | 0.02825 | -0.025065 | -0.23348 | -0.53134 | -0.64051 | 0.01852 | 0.34684 | 0.34461 | 0.3403 | 0.29019 | 0.23581 | 0.18862 | 0.12283 | 0.018064 | -0.0044356 | -0.060976 | -0.27555 | -0.57788 | -0.68115 | 0.0039244 | 0.33322 | 0.33194 | 0.32798 | 0.27835 | 0.22456 | 0.17755 | 0.11193 | 0.0062743 | -0.016866 | -0.07519 | -0.29071 | -0.60038 | -0.7123
| GLENDARUEL | SP |  |  | 0.38883 | 0.71878 | 0.35711 | 0.35706 | 0.35045 | 0.34406 | 0.33751 | 0.33019 | 0.31815 | 0.30518 | 0.25504 | 0.20379 | -0.36997 | -0.55255 | 0.36153 | 0.69116 | 0.34946 | 0.34908 | 0.34085 | 0.3325 | 0.32525 | 0.31724 | 0.30433 | 0.29083 | 0.23912 | 0.1859 | -0.38967 | -0.57397 | 0.36476 | 0.69458 | 0.33423 | 0.33404 | 0.32675 | 0.31955 | 0.31255 | 0.30459 | 0.29176 | 0.27829 | 0.22672 | 0.1737 | -0.40167 | -0.58579
ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | 5.0123 | 5.0116 | 5.0107 | 5.0094 | 5.0049 | 4.9993 | 3.9014 | 3.5993 | 3.2136 | 2.8357 | 1.4146 | -0.43276 | -3.4414 | -4.5729 | 4.9949 | 4.9845 | 4.9691 | 4.9333 | 4.6275 | 3.7328 | 3.3795 | 3.0281 | 2.58 | 2.1396 | 0.48387 | -1.6583 | -5.1669 | -6.4871 | 3.5405 | 3.5397 | 3.5297 | 3.4952 | 3.2012 | 2.8428 | 2.4854 | 2.1298 | 1.6766 | 1.231 | -0.44425 | -2.6114 | -6.1381 | -7.464
| GLENDEVON | CT |  |  | 5.0123 | 5.0116 | 5.0107 | 5.0094 | 5.0049 | 4.9993 | 4.9923 | 4.9841 | 3.9297 | 3.6381 | 2.6226 | 1.2009 | -1.645 | -3.5362 | 4.9949 | 4.9845 | 4.9691 | 4.9333 | 4.7388 | 4.57 | 3.8654 | 3.683 | 3.4178 | 3.0786 | 1.8969 | 0.2501 | -3.0482 | -5.2397 | 3.5405 | 3.5397 | 3.5297 | 3.4952 | 3.3079 | 3.1451 | 2.9772 | 2.7927 | 2.5245 | 2.1813 | 0.98586 | -0.67968 | -4.01 | -6.2103
| GLENDEVON | LW |  |  | 5.0134 | 5.0134 | 5.0134 | 5.0134 | 5.0122 | 5.0096 | 3.9014 | 3.5993 | 3.2136 | 2.8357 | 1.4146 | -0.43276 | -3.4414 | -4.5729 | 5.0047 | 5.0025 | 4.999 | 4.9903 | 4.6275 | 3.7328 | 3.3795 | 3.0281 | 2.58 | 2.1396 | 0.48387 | -1.6583 | -5.1669 | -6.4871 | 3.5416 | 3.5416 | 3.5416 | 3.5416 | 3.2012 | 2.8428 | 2.4854 | 2.1298 | 1.6766 | 1.231 | -0.44425 | -2.6114 | -6.1381 | -7.464
| GLENDEVON | ST |  |  | 5.0132 | 5.013 | 5.0129 | 5.0127 | 5.0109 | 5.0085 | 5.0056 | 5.002 | 4.9967 | 3.7303 | 2.746 | 1.4007 | -0.37463 | -2.4813 | 4.9978 | 4.99 | 4.9798 | 4.9603 | 4.7967 | 4.6362 | 3.9504 | 3.7678 | 3.5097 | 3.1816 | 2.0346 | 0.46961 | -1.5835 | -4.0375 | 3.5414 | 3.5412 | 3.54 | 3.5212 | 3.3639 | 3.2094 | 3.0631 | 2.8783 | 2.6172 | 2.2853 | 1.1247 | -0.45853 | -2.5352 | -5.0037
| GLENDEVON | SP |  |  | 5.0131 | 5.0129 | 5.0127 | 5.0125 | 5.0125 | 5.0124 | 5.0123 | 5.0123 | 5.0121 | 5.0116 | 5.0094 | 3.5054 | 3.0145 | 2.5671 | 5.0051 | 5.0038 | 5.0024 | 5.0009 | 4.958 | 4.9086 | 4.84 | 4.7725 | 4.6827 | 4.5649 | 3.5357 | 2.9173 | 2.351 | 1.8328 | 3.5412 | 3.5411 | 3.5409 | 3.5407 | 3.519 | 3.4716 | 3.4056 | 3.3406 | 3.2543 | 3.1401 | 2.6433 | 2.0177 | 1.4451 | 0.921
FORT AUGUSTUS | GLENDOE PRIMARY | MINIMUM HEADROOM | NH 40060 08894 | YES | 8.0042 | 8.0039 | 7.9997 | 7.9953 | 7.9897 | 7.983 | 7.9758 | 7.9681 | 7.96 | 7.953 | 7.9378 | 7.9095 | 7.4526 | 7.3358 | 7.9284 | 7.9281 | 7.9226 | 7.9168 | 7.9099 | 7.9015 | 7.8926 | 7.8832 | 7.8733 | 7.8643 | 7.8459 | 7.8121 | 7.4441 | 7.3264 | 7.8877 | 7.8874 | 7.8815 | 7.8755 | 7.8682 | 7.8595 | 7.8502 | 7.8403 | 7.83 | 7.8206 | 7.8014 | 7.4578 | 7.3463 | 7.2171
| GLENDOE PRIMARY | CT |  |  | 8.0042 | 8.0039 | 7.9997 | 7.9953 | 7.9897 | 7.983 | 7.9758 | 7.9681 | 7.96 | 7.953 | 7.9378 | 7.9095 | 7.4526 | 7.3358 | 7.9284 | 7.9281 | 7.9226 | 7.9168 | 7.9099 | 7.9015 | 7.8926 | 7.8832 | 7.8733 | 7.8643 | 7.8459 | 7.8121 | 7.4441 | 7.3264 | 7.8877 | 7.8874 | 7.8815 | 7.8755 | 7.8682 | 7.8595 | 7.8502 | 7.8403 | 7.83 | 7.8206 | 7.8014 | 7.4578 | 7.3463 | 7.2171
| GLENDOE PRIMARY | LW |  |  | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 8.0046 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.9288 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881 | 7.8881
| GLENDOE PRIMARY | ST |  |  | 8.0045 | 8.0045 | 8.0044 | 8.0044 | 8.0039 | 8.0033 | 8.0025 | 8.0018 | 8.0009 | 8.0005 | 7.9997 | 7.9982 | 7.9904 | 7.986 | 7.9288 | 7.9287 | 7.9287 | 7.9286 | 7.9281 | 7.9275 | 7.9268 | 7.926 | 7.9251 | 7.9248 | 7.9239 | 7.9224 | 7.9146 | 7.9102 | 7.888 | 7.888 | 7.888 | 7.8879 | 7.8874 | 7.8868 | 7.8861 | 7.8853 | 7.8844 | 7.8841 | 7.8832 | 7.8817 | 7.8739 | 7.8695
| GLENDOE PRIMARY | SP |  |  | 8.0044 | 8.0043 | 8.0042 | 8.0041 | 8.0041 | 8.0041 | 8.0041 | 8.0041 | 8.004 | 8.0039 | 8.0034 | 8.003 | 8.0005 | 7.9951 | 7.9287 | 7.9286 | 7.9285 | 7.9284 | 7.9284 | 7.9283 | 7.9283 | 7.9283 | 7.9283 | 7.9281 | 7.9276 | 7.9272 | 7.9248 | 7.9194 | 7.8879 | 7.8879 | 7.8878 | 7.8877 | 7.8876 | 7.8876 | 7.8876 | 7.8876 | 7.8876 | 7.8874 | 7.8869 | 7.8865 | 7.884 | 7.8786
BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | 23.0084 | 22.907 | 31.5358 | 31.41 | 31.2609 | 31.1108 | 30.9601 | 30.8089 | 30.6446 | 30.5673 | 30.4206 | 22.0403 | 19.9226 | 16.034 | 19.7597 | 19.6681 | 27.8516 | 27.7159 | 27.5747 | 27.4797 | 27.3821 | 27.2821 | 27.1685 | 21.471 | 20.2468 | 17.5002 | 14.9659 | 10.4185 | 20.0996 | 19.9941 | 28.1673 | 28.0296 | 27.8254 | 27.6279 | 27.4303 | 27.2184 | 27.0283 | 21.462 | 19.9797 | 17.1536 | 14.5819 | 9.9952
| GLENEAGLES | CT |  |  | 23.0084 | 22.907 | 31.5358 | 31.41 | 31.2609 | 31.1108 | 30.9601 | 30.8089 | 30.6446 | 30.5673 | 30.4206 | 22.0403 | 19.9226 | 16.034 | 19.7597 | 19.6681 | 27.8516 | 27.7159 | 27.5747 | 27.4797 | 27.3821 | 27.2821 | 27.1685 | 27.119 | 20.2468 | 17.5002 | 14.9659 | 10.4185 | 20.0996 | 19.9941 | 28.1673 | 28.0296 | 27.8254 | 27.6279 | 27.4303 | 27.2184 | 27.0283 | 26.9519 | 19.9797 | 17.1536 | 14.5819 | 9.9952
| GLENEAGLES | LW |  |  | 23.1017 | 23.0935 | 31.8155 | 31.8064 | 31.725 | 31.639 | 31.5471 | 31.4461 | 31.3008 | 31.2626 | 31.1432 | 30.7025 | 22.6364 | 20.5061 | 19.8409 | 19.8289 | 28.0939 | 28.0652 | 27.8035 | 27.7228 | 27.6368 | 27.5421 | 27.4036 | 21.471 | 21.2195 | 19.0184 | 17.9083 | 15.2826 | 20.1956 | 20.1856 | 28.4549 | 28.4389 | 28.2525 | 28.0624 | 27.9193 | 27.8184 | 27.6733 | 21.462 | 21.1988 | 18.9338 | 17.7999 | 15.1488
| GLENEAGLES | ST |  |  | 23.1042 | 23.0983 | 31.8224 | 31.8146 | 31.8029 | 31.7902 | 31.7748 | 31.7581 | 31.7386 | 31.7274 | 31.6893 | 31.5123 | 20.9373 | 18.9093 | 19.8413 | 19.8307 | 28.0981 | 28.077 | 27.9275 | 27.8655 | 27.8541 | 27.8413 | 27.8255 | 27.8179 | 21.6784 | 19.4603 | 15.4833 | 13.0699 | 20.1977 | 20.1899 | 28.4615 | 28.449 | 28.3934 | 28.3379 | 28.277 | 28.2051 | 28.1107 | 28.0996 | 21.6732 | 19.4221 | 15.4341 | 13.0093
| GLENEAGLES | SP |  |  | 23.1003 | 23.0925 | 31.8147 | 31.8068 | 31.7959 | 31.7851 | 31.7744 | 31.7638 | 31.7532 | 31.7421 | 31.7078 | 31.6445 | 31.5154 | 31.4112 | 19.8437 | 19.8366 | 28.1093 | 28.1019 | 28.0565 | 28.0058 | 27.9316 | 27.8585 | 27.8504 | 27.8441 | 27.8239 | 27.7882 | 27.6872 | 21.0652 | 20.1955 | 20.1874 | 28.4592 | 28.451 | 28.4284 | 28.4042 | 28.3728 | 28.3417 | 28.304 | 28.2574 | 28.0806 | 28.0179 | 27.8894 | 21.0096
RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | 0.33258 | 0.33257 | 0.13967 | -0.053185 | -0.25098 | -0.48982 | -0.73578 | -0.98891 | -1.25 | -1.5185 | -1.9979 | -2.7775 | -3.4568 | -4.1138 | 0.32086 | 0.32003 | 0.13534 | -0.049876 | -0.2399 | -0.46891 | -0.70468 | -0.94569 | -1.1943 | -1.4499 | -1.9068 | -2.6497 | -3.2972 | -3.9236 | 0.32329 | 0.32307 | 0.12831 | -0.066905 | -0.26713 | -0.50871 | -0.75747 | -1.0128 | -1.2762 | -1.5469 | -2.0307 | -2.8174 | -3.5028 | -4.1658
| GLENETIVE | CT |  |  | 0.33258 | 0.33257 | 0.13967 | -0.053185 | -0.25098 | -0.48982 | -0.73578 | -0.98891 | -1.25 | -1.5185 | -1.9979 | -2.7775 | -3.4568 | -4.1138 | 0.32086 | 0.32003 | 0.13534 | -0.049876 | -0.2399 | -0.46891 | -0.70468 | -0.94569 | -1.1943 | -1.4499 | -1.9068 | -2.6497 | -3.2972 | -3.9236 | 0.32329 | 0.32307 | 0.12831 | -0.066905 | -0.26713 | -0.50871 | -0.75747 | -1.0128 | -1.2762 | -1.5469 | -2.0307 | -2.8174 | -3.5028 | -4.1658
| GLENETIVE | LW |  |  | 0.33261 | 0.33261 | 0.24669 | 0.16141 | 0.076251 | -0.0093164 | -0.094884 | -0.18082 | -0.26639 | -0.35232 | -0.52513 | -0.81696 | -1.1149 | -1.4202 | 0.32165 | 0.32153 | 0.23893 | 0.15727 | 0.075896 | -0.0057946 | -0.087478 | -0.16951 | -0.25117 | -0.33322 | -0.49851 | -0.77758 | -1.0625 | -1.3544 | 0.32351 | 0.32348 | 0.23673 | 0.15077 | 0.06471 | -0.021694 | -0.10809 | -0.19486 | -0.28126 | -0.36803 | -0.54266 | -0.83754 | -1.1386 | -1.447
| GLENETIVE | ST |  |  | 0.3326 | 0.33259 | 0.27487 | 0.21811 | 0.16115 | 0.10389 | 0.04685 | -0.010457 | -0.067527 | -0.12471 | -0.2975 | -0.58955 | -0.88859 | -1.1945 | 0.32106 | 0.32045 | 0.26504 | 0.20989 | 0.15458 | 0.098783 | 0.044008 | -0.011015 | -0.065801 | -0.12054 | -0.2856 | -0.56432 | -0.84971 | -1.1416 | 0.32335 | 0.32319 | 0.26469 | 0.20722 | 0.1494 | 0.091102 | 0.033732 | -0.024323 | -0.082134 | -0.14003 | -0.31462 | -0.60947 | -0.91137 | -1.2202
| GLENETIVE | SP |  |  | 0.33261 | 0.33261 | 0.30767 | 0.27124 | 0.24206 | 0.21407 | 0.18696 | 0.16032 | 0.13455 | 0.10964 | 0.038914 | -0.066672 | -0.16093 | -0.24524 | 0.32169 | 0.32163 | 0.29153 | 0.26257 | 0.23423 | 0.20713 | 0.18112 | 0.15555 | 0.13082 | 0.10705 | 0.039545 | -0.06125 | -0.15124 | -0.23175 | 0.32352 | 0.32351 | 0.28882 | 0.26157 | 0.23206 | 0.20381 | 0.1764 | 0.14938 | 0.12328 | 0.098125 | 0.026714 | -0.079901 | -0.17508 | -0.26023
FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | 0.13196 | 0.1319 | 0.12574 | 0.11973 | 0.11449 | 0.093889 | 0.083044 | 0.071811 | 0.060195 | 0.048452 | 0.026688 | -0.009449 | -0.042646 | -0.07808 | 0.12517 | 0.12504 | 0.1191 | 0.11561 | 0.099467 | 0.089246 | 0.078693 | 0.067274 | 0.055499 | 0.043557 | 0.020982 | -0.016361 | -0.050991 | -0.08787 | 0.12607 | 0.12588 | 0.11904 | 0.11189 | 0.097028 | 0.087793 | 0.077014 | 0.065682 | 0.053449 | 0.041039 | 0.017699 | -0.020887 | -0.056557 | -0.094604
| GLENUIG | CT |  |  | 0.13196 | 0.1319 | 0.12574 | 0.11973 | 0.11449 | 0.093889 | 0.083044 | 0.071811 | 0.060195 | 0.048452 | 0.026688 | -0.009449 | -0.042646 | -0.07808 | 0.12517 | 0.12504 | 0.1191 | 0.11561 | 0.099467 | 0.089246 | 0.078693 | 0.067274 | 0.055499 | 0.043557 | 0.020982 | -0.016361 | -0.050991 | -0.08787 | 0.12607 | 0.12588 | 0.11904 | 0.11189 | 0.097028 | 0.087793 | 0.077014 | 0.065682 | 0.053449 | 0.041039 | 0.017699 | -0.020887 | -0.056557 | -0.094604
| GLENUIG | LW |  |  | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.12523 | 0.12512 | 0.12496 | 0.12455 | 0.12409 | 0.12373 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12612 | 0.12597 | 0.12591 | 0.12574 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572
| GLENUIG | ST |  |  | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.12527 | 0.12522 | 0.12515 | 0.12502 | 0.12484 | 0.12463 | 0.1236 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.098072 | 0.092165 | 0.12619 | 0.1261 | 0.126 | 0.12593 | 0.12586 | 0.12578 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.098847 | 0.092915
| GLENUIG | SP |  |  | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.13202 | 0.12532 | 0.12531 | 0.12531 | 0.1253 | 0.12525 | 0.12519 | 0.12478 | 0.12438 | 0.12393 | 0.12368 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12627 | 0.12626 | 0.12624 | 0.12623 | 0.12615 | 0.12605 | 0.12584 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572 | 0.12572
BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | 5.7477 | 5.7469 | 5.7443 | 5.7412 | 5.7158 | 5.6819 | 5.6469 | 5.6094 | 5.5554 | 5.5462 | 5.5195 | 5.459 | 5.4058 | 5.3824 | 4.9439 | 4.9394 | 4.9316 | 4.9156 | 4.8956 | 4.868 | 4.8294 | 4.7882 | 4.7307 | 4.7176 | 4.6797 | 4.601 | 3.9127 | 3.6371 | 4.7712 | 4.7694 | 4.7654 | 4.759 | 4.7376 | 4.7028 | 4.6669 | 4.6284 | 4.5736 | 4.5633 | 4.5348 | 4.4743 | 3.7995 | 3.5214
| GOLSPIE | CT |  |  | 5.7477 | 5.7469 | 5.7443 | 5.7412 | 5.735 | 5.7275 | 5.7191 | 5.7097 | 5.6992 | 5.6922 | 5.6725 | 5.6294 | 5.5638 | 5.4423 | 4.9439 | 4.9394 | 4.9316 | 4.9156 | 4.8956 | 4.8745 | 4.8528 | 4.8248 | 4.7962 | 4.7695 | 4.6972 | 4.6563 | 3.9127 | 3.6371 | 4.7712 | 4.7694 | 4.7654 | 4.759 | 4.7503 | 4.7428 | 4.7343 | 4.7249 | 4.7144 | 4.7075 | 4.6877 | 4.6447 | 3.7995 | 3.5214
| GOLSPIE | LW |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.7158 | 5.6819 | 5.6469 | 5.6094 | 5.5554 | 5.5462 | 5.5195 | 5.459 | 5.4058 | 5.3824 | 4.9484 | 4.9475 | 4.9461 | 4.9427 | 4.9056 | 4.868 | 4.8294 | 4.7882 | 4.7307 | 4.7176 | 4.6797 | 4.601 | 4.5295 | 4.488 | 4.7732 | 4.773 | 4.7727 | 4.7718 | 4.7376 | 4.7028 | 4.6669 | 4.6284 | 4.5736 | 4.5633 | 4.5348 | 4.4743 | 4.4211 | 4.3976
| GOLSPIE | ST |  |  | 5.7487 | 5.7485 | 5.7483 | 5.7481 | 5.7462 | 5.744 | 5.7415 | 5.7386 | 5.7353 | 5.7342 | 5.731 | 5.7255 | 5.6974 | 5.6814 | 4.9485 | 4.9479 | 4.9471 | 4.9458 | 4.9425 | 4.9385 | 4.9271 | 4.9155 | 4.9037 | 4.8894 | 4.8477 | 4.7804 | 4.7157 | 4.6997 | 4.7731 | 4.7728 | 4.7724 | 4.7719 | 4.7697 | 4.767 | 4.7623 | 4.7571 | 4.7517 | 4.7495 | 4.7462 | 4.7408 | 4.7126 | 4.6966
| GOLSPIE | SP |  |  | 5.7486 | 5.7483 | 5.7481 | 5.7479 | 5.7479 | 5.7478 | 5.7478 | 5.7477 | 5.7477 | 5.7473 | 5.7462 | 5.7454 | 5.7399 | 5.7279 | 4.9488 | 4.9485 | 4.9482 | 4.9479 | 4.9475 | 4.9469 | 4.9437 | 4.9405 | 4.9363 | 4.9308 | 4.9148 | 4.8906 | 4.8631 | 4.8304 | 4.773 | 4.7728 | 4.7726 | 4.7723 | 4.7722 | 4.772 | 4.7711 | 4.7703 | 4.7692 | 4.7676 | 4.7626 | 4.7606 | 4.7551 | 4.7431
BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | YES | 19.689 | 19.6569 | 19.6248 | 18.8672 | 18.7811 | 17.9138 | 17.2013 | 12.1088 | 12.0181 | 11.7378 | 10.8966 | 9.4609 | 8.4292 | 7.9012 | 15.8242 | 15.7859 | 15.7439 | 14.9245 | 14.7902 | 13.8653 | 11.0661 | 10.3483 | 10.2534 | 9.9676 | 9.1104 | 7.6492 | 6.5922 | 5.4791 | 15.6604 | 15.6268 | 15.5923 | 14.8196 | 14.7218 | 13.8404 | 11.3067 | 10.5899 | 10.496 | 10.2115 | 9.3582 | 7.9032 | 6.6003 | 5.3156
| GOODLYBURN | CT |  |  | 19.7814 | 19.7545 | 19.7272 | 19.7226 | 19.5869 | 19.338 | 19.1079 | 18.8748 | 18.5722 | 18.4201 | 17.9581 | 11.0184 | 9.287 | 8.177 | 15.9073 | 15.8667 | 15.8189 | 15.7653 | 15.577 | 15.2763 | 14.9955 | 14.6894 | 14.3714 | 14.2025 | 13.6908 | 9.1728 | 7.0887 | 5.4791 | 15.7505 | 15.7203 | 15.688 | 15.6715 | 15.5229 | 15.2614 | 15.0238 | 14.7818 | 14.4705 | 14.3089 | 13.819 | 9.0904 | 6.8887 | 5.3156
| GOODLYBURN | LW |  |  | 19.689 | 19.6569 | 19.6248 | 19.6248 | 19.3357 | 18.896 | 18.4403 | 17.9684 | 17.4806 | 17.2926 | 16.7287 | 11.0969 | 9.7205 | 8.8836 | 15.8242 | 15.7859 | 15.7439 | 15.7193 | 15.4029 | 14.9364 | 14.4544 | 13.9569 | 11.3506 | 11.1605 | 10.5901 | 9.3268 | 7.9399 | 7.0925 | 15.6604 | 15.6268 | 15.5923 | 15.5863 | 15.2906 | 14.8443 | 14.3822 | 13.9041 | 13.4101 | 11.4003 | 10.8315 | 9.5707 | 8.1864 | 7.3415
| GOODLYBURN | ST |  |  | 19.8808 | 19.8642 | 19.8476 | 18.8672 | 18.7811 | 17.9138 | 17.2013 | 12.1088 | 12.0181 | 11.7378 | 10.8966 | 9.4609 | 8.4292 | 7.9012 | 16.0059 | 15.9754 | 15.9403 | 14.9245 | 14.7902 | 13.8653 | 11.0661 | 10.3483 | 10.2534 | 9.9676 | 9.1104 | 7.6492 | 6.5922 | 5.9998 | 15.8498 | 15.8298 | 15.8086 | 14.8196 | 14.7218 | 13.8404 | 11.3067 | 10.5899 | 10.496 | 10.2115 | 9.3582 | 7.9032 | 6.6003 | 5.7782
| GOODLYBURN | SP |  |  | 19.9762 | 19.9672 | 19.9581 | 19.4673 | 19.427 | 19.3866 | 19.3463 | 19.3059 | 19.2655 | 19.0421 | 18.3711 | 17.2072 | 12.0377 | 11.7122 | 16.1147 | 16.1037 | 16.0925 | 15.5991 | 15.5454 | 15.4891 | 15.4316 | 15.3743 | 15.312 | 15.0621 | 14.3146 | 11.066 | 10.2663 | 9.9322 | 15.9484 | 15.9389 | 15.9293 | 15.4379 | 15.3943 | 15.35 | 15.3055 | 15.261 | 15.2153 | 14.9854 | 14.2958 | 11.308 | 10.5105 | 10.1785
CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | NO | 8.2916 | 8.29 | 8.2882 | 8.2854 | 8.2552 | 8.2216 | 8.1847 | 8.1447 | 8.0916 | 8.0764 | 6.0675 | 5.2818 | 3.9565 | 2.9698 | 7.5195 | 7.5106 | 7.4989 | 7.4736 | 7.4385 | 7.3957 | 7.3497 | 6.2543 | 6.0672 | 5.8823 | 5.1958 | 4.3074 | 2.6549 | 1.4825 | 7.4889 | 7.4872 | 7.4854 | 7.4827 | 7.4525 | 7.4189 | 7.3819 | 6.2764 | 6.092 | 5.9098 | 5.2334 | 4.3576 | 2.7307 | 1.5613
| GOURDIE | CT |  |  | 8.2916 | 8.29 | 8.2882 | 8.2854 | 8.2552 | 8.2216 | 8.1847 | 8.1447 | 8.0916 | 8.0764 | 6.0902 | 5.2818 | 3.9565 | 2.9698 | 7.5199 | 7.5114 | 7.4992 | 7.4736 | 7.4385 | 7.3957 | 7.3497 | 6.2741 | 6.0867 | 5.903 | 5.2909 | 4.3074 | 2.6549 | 1.4825 | 7.4889 | 7.4872 | 7.4854 | 7.4827 | 7.4525 | 7.4189 | 7.3819 | 6.2938 | 6.1084 | 5.9271 | 5.3234 | 4.3576 | 2.7307 | 1.5613
| GOURDIE | LW |  |  | 8.2939 | 8.2939 | 8.2939 | 8.2939 | 8.2934 | 8.2924 | 8.2908 | 8.2885 | 8.2843 | 8.2834 | 6.0675 | 5.4312 | 4.293 | 3.8137 | 7.5283 | 7.5267 | 7.524 | 7.5174 | 7.4746 | 7.4599 | 7.4449 | 6.2543 | 6.0672 | 5.8823 | 5.1958 | 4.3601 | 2.9094 | 2.3313 | 7.4912 | 7.4912 | 7.4912 | 7.4912 | 7.4907 | 7.4896 | 7.488 | 6.2764 | 6.092 | 5.9098 | 5.2334 | 4.423 | 2.9864 | 2.4101
| GOURDIE | ST |  |  | 8.2934 | 8.2931 | 8.2927 | 8.2923 | 8.2889 | 8.2848 | 8.2799 | 8.2742 | 8.2673 | 8.2651 | 8.2581 | 5.7782 | 5.004 | 4.1987 | 7.5195 | 7.5106 | 7.4989 | 7.4802 | 7.4714 | 7.4563 | 7.4437 | 7.4291 | 6.2615 | 6.1062 | 5.5781 | 4.8355 | 3.8585 | 2.8193 | 7.4907 | 7.4903 | 7.49 | 7.4896 | 7.4862 | 7.482 | 7.4772 | 7.4715 | 6.2832 | 6.1302 | 5.6097 | 4.8816 | 3.9311 | 2.8962
| GOURDIE | SP |  |  | 8.2929 | 8.2924 | 8.2919 | 8.2914 | 8.2913 | 8.2912 | 8.2911 | 8.2909 | 8.2908 | 8.2899 | 8.2868 | 8.284 | 8.2583 | 8.3003 | 7.5273 | 7.5256 | 7.5236 | 7.5216 | 7.5062 | 7.4962 | 7.4794 | 7.4761 | 7.4717 | 7.4659 | 7.4428 | 6.1314 | 5.8563 | 5.6644 | 7.4902 | 7.4897 | 7.4892 | 7.4886 | 7.4886 | 7.4884 | 7.4883 | 7.4882 | 7.488 | 7.4872 | 7.4841 | 6.1552 | 5.8838 | 5.6953
BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | YES | 18.0546 | 17.9544 | 17.8462 | 17.7115 | 17.5717 | 17.4312 | 17.2917 | 17.1531 | 17.0308 | 16.958 | 16.8208 | 14.2776 | 13.6306 | 12.8136 | 16.1861 | 16.0817 | 15.9649 | 15.8081 | 15.6432 | 15.48 | 15.3387 | 15.2377 | 15.1549 | 15.1048 | 15.0019 | 13.2156 | 12.5275 | 11.682 | 16.3907 | 16.2852 | 16.162 | 16.0109 | 15.8547 | 15.6959 | 15.5379 | 15.3808 | 15.2406 | 13.6859 | 13.2871 | 12.6071 | 11.8873 | 11.0099
| GRANTOWN | CT |  |  | 18.0546 | 17.9544 | 17.8462 | 17.7115 | 17.5717 | 17.4312 | 17.2917 | 17.1531 | 17.0308 | 16.958 | 16.8208 | 14.2776 | 13.6306 | 12.8136 | 16.1861 | 16.0817 | 15.9649 | 15.8081 | 15.6432 | 15.48 | 15.3387 | 15.2377 | 15.1549 | 15.1048 | 15.0019 | 13.2156 | 12.5275 | 11.682 | 16.3907 | 16.2852 | 16.162 | 16.0109 | 15.8547 | 15.6959 | 15.5379 | 15.3808 | 15.2406 | 13.6859 | 13.2871 | 12.6071 | 11.8873 | 11.0099
| GRANTOWN | LW |  |  | 18.1468 | 18.1387 | 18.1308 | 18.1217 | 18.1115 | 18.1003 | 18.0881 | 18.075 | 18.0634 | 18.0513 | 18.0132 | 17.9449 | 17.8839 | 17.8187 | 16.284 | 16.2716 | 16.2565 | 16.2285 | 16.2052 | 16.1846 | 16.1634 | 16.1418 | 16.1216 | 16.1001 | 16.0347 | 15.9233 | 15.8307 | 15.7541 | 16.4877 | 16.4791 | 16.4708 | 16.4613 | 16.4505 | 16.4387 | 16.4258 | 16.4121 | 16.3998 | 16.3871 | 16.3469 | 16.2749 | 16.2106 | 16.1419
| GRANTOWN | ST |  |  | 18.1491 | 18.1432 | 18.1372 | 18.1293 | 18.1169 | 18.1036 | 18.0879 | 18.0712 | 18.0539 | 18.0432 | 18.008 | 17.9561 | 17.8411 | 17.7666 | 16.2778 | 16.2612 | 16.2408 | 16.2159 | 16.1847 | 16.1488 | 16.114 | 16.0785 | 16.0428 | 16.005 | 15.8974 | 15.7854 | 15.6609 | 15.5978 | 16.4902 | 16.484 | 16.4777 | 16.4694 | 16.4566 | 16.443 | 16.4268 | 16.4097 | 16.392 | 16.3808 | 16.3442 | 16.2904 | 16.1737 | 16.0977
| GRANTOWN | SP |  |  | 18.1446 | 18.1364 | 18.1283 | 18.12 | 18.1092 | 18.0985 | 18.0879 | 18.0774 | 18.067 | 18.0557 | 18.0218 | 17.9607 | 17.8894 | 17.7924 | 16.2843 | 16.2752 | 16.2658 | 16.2561 | 16.2351 | 16.2121 | 16.1912 | 16.1755 | 16.158 | 16.137 | 16.0754 | 15.9725 | 15.861 | 15.7392 | 16.4855 | 16.4769 | 16.4684 | 16.4598 | 16.4483 | 16.437 | 16.4259 | 16.4148 | 16.4039 | 16.392 | 16.3566 | 16.2924 | 16.2185 | 16.1191
WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | 30.094 | 30.079 | 30.0589 | 30.0204 | 29.9674 | 29.9039 | 29.8039 | 29.7058 | 29.6174 | 29.605 | 29.5688 | 29.5109 | 29.4443 | 30.2208 | 26.0269 | 26.0179 | 26.006 | 25.983 | 25.9512 | 25.9131 | 25.8533 | 25.7944 | 25.7366 | 25.7277 | 25.7019 | 25.6606 | 25.6101 | 26.4028 | 26.5494 | 26.5491 | 26.5487 | 26.5482 | 26.5464 | 26.5443 | 26.5418 | 26.5389 | 26.5356 | 26.5338 | 26.5277 | 26.5134 | 26.4898 | 27.2821
| GREYFRIARS | CT |  |  | 30.1067 | 30.1023 | 30.0959 | 30.081 | 30.0638 | 30.0466 | 30.0294 | 30.0063 | 29.9832 | 29.9599 | 29.8902 | 29.7734 | 29.6464 | 30.3462 | 26.0343 | 26.0316 | 26.0276 | 26.0185 | 26.0076 | 25.9965 | 25.9853 | 25.9704 | 25.9553 | 25.9407 | 25.8968 | 25.8216 | 25.7366 | 26.4681 | 26.5494 | 26.5491 | 26.5487 | 26.5482 | 26.5464 | 26.5443 | 26.5418 | 26.5389 | 26.5356 | 26.5338 | 26.5277 | 26.5134 | 26.4898 | 27.2821
| GREYFRIARS | LW |  |  | 30.1068 | 30.1018 | 30.0939 | 30.0742 | 30.0522 | 30.0307 | 30.0097 | 29.9891 | 29.969 | 29.9472 | 29.8829 | 30.6171 | 30.5127 | 30.4241 | 26.0345 | 26.0316 | 26.0269 | 26.0152 | 26.0021 | 25.9893 | 25.9768 | 25.9646 | 25.9527 | 25.9397 | 25.9015 | 26.6778 | 26.6157 | 26.5543 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 26.5499 | 27.3878 | 27.3878 | 27.3878
| GREYFRIARS | ST |  |  | 30.094 | 30.079 | 30.0589 | 30.0204 | 29.9674 | 29.9039 | 29.8039 | 29.7058 | 29.6174 | 29.605 | 29.5688 | 29.5109 | 29.4443 | 30.2208 | 26.0269 | 26.0179 | 26.006 | 25.983 | 25.9512 | 25.9131 | 25.8533 | 25.7944 | 25.7366 | 25.7277 | 25.7019 | 25.6606 | 25.6101 | 26.4028 | 26.5498 | 26.5497 | 26.5496 | 26.5495 | 26.5487 | 26.5478 | 26.5467 | 26.5455 | 26.544 | 26.5436 | 26.5422 | 26.5398 | 26.5277 | 27.3587
| GREYFRIARS | SP |  |  | 30.1086 | 30.1066 | 30.1043 | 30.1017 | 30.0887 | 30.0732 | 30.0459 | 30.0189 | 29.9841 | 29.9781 | 29.9607 | 29.9344 | 29.9059 | 30.7117 | 26.0355 | 26.0342 | 26.0328 | 26.0312 | 26.0234 | 26.0142 | 25.998 | 25.9819 | 25.9612 | 25.9575 | 25.9468 | 25.9309 | 25.9121 | 26.727 | 26.5496 | 26.5494 | 26.5492 | 26.549 | 26.549 | 26.549 | 26.5489 | 26.5489 | 26.5489 | 26.5486 | 26.5477 | 26.547 | 26.5424 | 27.3705
GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309623 | YES | 23.1105 | 22.937 | 22.7697 | 22.5507 | 22.3392 | 22.1353 | 21.939 | 21.7502 | 21.5714 | 21.4776 | 21.3394 | 21.1098 | 19.3531 | 17.5255 | 21.9448 | 21.8062 | 21.6728 | 21.4979 | 21.3291 | 21.1664 | 21.0097 | 20.859 | 20.7163 | 20.6414 | 20.5311 | 20.3479 | 18.9458 | 17.4872 | 21.9098 | 21.7354 | 21.5674 | 21.3474 | 21.1349 | 20.93 | 20.7328 | 20.5431 | 20.3635 | 20.2693 | 20.1305 | 19.8999 | 18.135 | 16.2991
| GRUDIE BRIDGE | CT |  |  | 23.1105 | 22.937 | 22.7697 | 22.5507 | 22.3392 | 22.1353 | 21.939 | 21.7502 | 21.5714 | 21.4776 | 21.3394 | 21.1098 | 20.882 | 17.9844 | 21.9448 | 21.8062 | 21.6728 | 21.4979 | 21.3291 | 21.1664 | 21.0097 | 20.859 | 20.7163 | 20.6414 | 20.5311 | 20.3479 | 20.1661 | 17.8535 | 21.9098 | 21.7354 | 21.5674 | 21.3474 | 21.1349 | 20.93 | 20.7328 | 20.5431 | 20.3635 | 20.2693 | 20.1305 | 19.8999 | 19.671 | 16.7601
| GRUDIE BRIDGE | LW |  |  | 23.268 | 23.2536 | 23.2396 | 23.2235 | 23.2054 | 23.1855 | 23.1638 | 23.1407 | 23.1166 | 23.0916 | 23.0129 | 22.8717 | 22.7197 | 22.5439 | 22.0704 | 22.0589 | 22.0478 | 22.0349 | 22.0205 | 22.0045 | 21.9873 | 21.9688 | 21.9496 | 21.9296 | 21.8668 | 21.7541 | 21.6328 | 21.4925 | 22.068 | 22.0535 | 22.0395 | 22.0233 | 22.0051 | 21.985 | 21.9633 | 21.9401 | 21.9159 | 21.8907 | 21.8116 | 21.6698 | 21.5171 | 21.3405
| GRUDIE BRIDGE | ST |  |  | 23.2736 | 23.264 | 23.2544 | 23.2415 | 23.2291 | 23.2169 | 23.2021 | 23.1878 | 23.1736 | 23.1597 | 23.1125 | 22.3932 | 20.9587 | 17.8071 | 22.0749 | 22.0672 | 22.0595 | 22.0493 | 22.0393 | 22.0296 | 22.0179 | 22.0064 | 21.995 | 21.984 | 21.9463 | 21.3722 | 20.2273 | 17.7119 | 22.0735 | 22.0639 | 22.0543 | 22.0414 | 22.0288 | 22.0166 | 22.0018 | 21.9873 | 21.9731 | 21.9591 | 21.9117 | 21.1891 | 19.748 | 16.582
| GRUDIE BRIDGE | SP |  |  | 23.2672 | 23.2544 | 23.2416 | 23.2288 | 23.2098 | 23.191 | 23.1726 | 23.1543 | 23.1364 | 23.1187 | 23.067 | 21.1622 | 19.3531 | 17.5255 | 22.0698 | 22.0595 | 22.0493 | 22.0391 | 22.0239 | 22.009 | 21.9942 | 21.9797 | 21.9654 | 21.9512 | 21.91 | 20.3897 | 18.9458 | 17.4872 | 22.0672 | 22.0543 | 22.0414 | 22.0285 | 22.0094 | 21.9906 | 21.9721 | 21.9538 | 21.9357 | 21.9179 | 21.866 | 19.9524 | 18.135 | 16.2991
SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | 3.993 | 3.9869 | 3.978 | 3.9569 | 3.9329 | 3.9088 | 3.8848 | 3.8764 | 3.8679 | 3.8604 | 3.8375 | 3.7956 | 3.7435 | 3.6681 | 4.4847 | 4.4761 | 4.4635 | 4.4507 | 4.4488 | 4.4465 | 4.4438 | 4.4406 | 4.4372 | 4.4352 | 4.4286 | 3.9843 | 3.9226 | 3.8379 | 3.9995 | 3.9991 | 3.9987 | 3.9981 | 3.9963 | 3.9793 | 3.9467 | 3.9362 | 3.9256 | 3.9159 | 3.8863 | 3.8337 | 3.7707 | 3.6846
| GUTCHER | CT |  |  | 3.993 | 3.9869 | 3.978 | 3.9569 | 3.9329 | 3.9088 | 3.8848 | 3.8764 | 3.8679 | 3.8604 | 3.8375 | 3.7956 | 3.7435 | 3.6681 | 4.4847 | 4.4761 | 4.4635 | 4.4507 | 4.4488 | 4.4465 | 4.4438 | 4.4406 | 4.4372 | 4.4352 | 4.4286 | 3.9843 | 3.9226 | 3.8379 | 3.9995 | 3.9991 | 3.9987 | 3.9981 | 3.9963 | 3.9793 | 3.9467 | 3.9362 | 3.9256 | 3.9159 | 3.8863 | 3.8337 | 3.7707 | 3.6846
| GUTCHER | LW |  |  | 3.9998 | 3.9997 | 3.9994 | 3.9987 | 3.9979 | 3.9972 | 3.9964 | 3.9957 | 3.995 | 3.9942 | 3.992 | 3.9883 | 3.9846 | 3.981 | 4.4941 | 4.4939 | 4.4935 | 4.4925 | 4.4914 | 4.4903 | 4.4893 | 4.4882 | 4.4872 | 4.4861 | 4.4829 | 4.4777 | 4.4725 | 4.4673 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| GUTCHER | ST |  |  | 3.9957 | 3.9921 | 3.9873 | 3.9781 | 3.965 | 3.9494 | 3.9448 | 3.9401 | 3.9355 | 3.9314 | 3.9197 | 3.9008 | 3.874 | 3.8516 | 4.4883 | 4.4831 | 4.4763 | 4.4632 | 4.4515 | 4.4508 | 4.4499 | 4.4488 | 4.4477 | 4.4473 | 4.4461 | 4.4442 | 4.4342 | 4.4285 | 3.9999 | 3.9998 | 3.9998 | 3.9997 | 3.999 | 3.9983 | 3.9973 | 3.9963 | 3.9952 | 3.9948 | 3.9936 | 3.969 | 3.9354 | 3.9062
| GUTCHER | SP |  |  | 3.999 | 3.9984 | 3.9977 | 3.9969 | 3.9933 | 3.9891 | 3.9877 | 3.9864 | 3.9847 | 3.983 | 3.9784 | 3.9716 | 3.9627 | 3.9508 | 4.493 | 4.4922 | 4.4912 | 4.4902 | 4.4851 | 4.479 | 4.4771 | 4.4753 | 4.4728 | 4.4705 | 4.4641 | 4.4547 | 4.4478 | 4.4416 | 3.9998 | 3.9997 | 3.9996 | 3.9994 | 3.9994 | 3.9994 | 3.9994 | 3.9994 | 3.9993 | 3.9992 | 3.9986 | 3.9982 | 3.9953 | 3.9891
THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | 4.4627 | 4.4613 | 5.951 | 5.9386 | 5.6329 | 5.3183 | 3.6804 | 3.0369 | 2.0997 | 1.5834 | -0.29021 | -2.9637 | -5.9584 | -7.3941 | 3.9567 | 3.9494 | 5.4323 | 5.4009 | 4.9306 | 3.4244 | 2.6968 | 1.9481 | 0.93533 | 0.34342 | -1.815 | -4.8524 | -8.2933 | -9.9508 | 4.2564 | 4.2535 | 5.741 | 5.7234 | 5.3528 | 3.5832 | 2.8669 | 2.1293 | 1.1307 | 0.5529 | -1.5522 | -4.5509 | -7.9862 | -9.6409
| HALKIRK | CT |  |  | 4.4627 | 4.4613 | 5.951 | 5.9386 | 5.7097 | 5.4778 | 5.2345 | 3.917 | 3.3808 | 3.0546 | 1.7538 | -0.81493 | -3.0327 | -5.3522 | 3.9567 | 3.9494 | 5.4323 | 5.4009 | 5.0589 | 3.9712 | 3.5562 | 3.1056 | 2.4601 | 2.0072 | 0.51011 | -2.3227 | -4.8101 | -7.479 | 4.2564 | 4.2535 | 5.741 | 5.7234 | 5.4613 | 5.1883 | 3.6901 | 3.2404 | 2.5984 | 2.1515 | 0.68358 | -2.1121 | -4.5788 | -7.2552
| HALKIRK | LW |  |  | 4.4646 | 4.4645 | 5.9643 | 5.9639 | 5.6329 | 5.3183 | 3.6804 | 3.0369 | 2.0997 | 1.5834 | -0.29021 | -2.9637 | -5.9584 | -7.3941 | 3.9644 | 3.9635 | 5.4621 | 5.4585 | 4.9306 | 3.4244 | 2.6968 | 1.9481 | 0.93533 | 0.34342 | -1.815 | -4.8524 | -8.2933 | -9.9508 | 4.2597 | 4.2594 | 5.7589 | 5.7577 | 5.3528 | 3.5832 | 2.8669 | 2.1293 | 1.1307 | 0.5529 | -1.5522 | -4.5509 | -7.9862 | -9.6409
| HALKIRK | ST |  |  | 4.4639 | 4.4633 | 5.9626 | 5.9612 | 5.8662 | 5.7724 | 5.628 | 5.464 | 3.9975 | 3.7079 | 2.4419 | 0.36314 | -2.4252 | -5.0876 | 3.96 | 3.9556 | 5.4498 | 5.4387 | 5.2331 | 5.0832 | 4.8775 | 3.6393 | 3.0827 | 2.6485 | 1.1834 | -1.1641 | -4.2987 | -7.3813 | 4.2581 | 4.2566 | 5.7546 | 5.7507 | 5.6279 | 5.5007 | 5.3169 | 3.7962 | 3.2477 | 2.8242 | 1.3963 | -0.90081 | -3.9974 | -7.0747
| HALKIRK | SP |  |  | 4.5493 | 4.5491 | 6.0489 | 6.0487 | 6.0388 | 6.0284 | 6.016 | 6.0029 | 5.9873 | 5.975 | 5.9303 | 5.8898 | 3.1453 | 2.4936 | 4.0341 | 4.0334 | 5.5325 | 5.5316 | 5.4921 | 5.4479 | 5.3863 | 5.3371 | 5.2879 | 5.2255 | 3.7791 | 3.0236 | 1.9173 | 1.1789 | 4.3467 | 4.3464 | 5.846 | 5.8456 | 5.8283 | 5.8095 | 5.7848 | 5.7596 | 5.7239 | 5.6795 | 3.9692 | 3.2338 | 2.1448 | 1.4226
ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | YES | 25.1771 | 25.1467 | 25.1162 | 24.3987 | 24.3185 | 23.5463 | 22.9115 | 22.2757 | 18.3828 | 18.1327 | 17.382 | 15.8715 | 13.7317 | 11.8338 | 23.2041 | 23.1663 | 23.1242 | 22.386 | 22.23 | 21.3798 | 18.2997 | 17.6556 | 16.5931 | 16.3308 | 15.3466 | 12.8749 | 10.5026 | 8.2267 | 22.2236 | 22.1931 | 22.1627 | 21.4451 | 21.365 | 20.5928 | 19.958 | 17.7753 | 16.7108 | 16.3105 | 14.7248 | 12.2705 | 9.9195 | 7.6332
| HARBOUR | CT |  |  | 25.2654 | 25.2405 | 25.2153 | 25.2118 | 25.0859 | 24.8597 | 24.6506 | 24.4388 | 24.1649 | 24.0287 | 23.6158 | 17.7876 | 14.2678 | 11.9367 | 23.2861 | 23.2493 | 23.2061 | 23.1597 | 22.9326 | 22.63 | 22.3482 | 22.0438 | 21.6541 | 21.375 | 20.5008 | 14.7163 | 10.8217 | 8.2267 | 22.3119 | 22.287 | 22.2618 | 22.2583 | 22.1323 | 21.9062 | 21.697 | 21.4853 | 21.2114 | 21.0752 | 17.8319 | 14.1188 | 10.2477 | 7.6332
| HARBOUR | LW |  |  | 25.1771 | 25.1467 | 25.1162 | 25.1162 | 24.8413 | 24.4312 | 24.0051 | 23.5627 | 23.102 | 22.9291 | 22.4086 | 17.2196 | 14.0531 | 12.4567 | 23.2041 | 23.1663 | 23.1242 | 23.0951 | 22.663 | 22.125 | 21.5726 | 21.0055 | 20.3934 | 18.2575 | 16.6589 | 14.0357 | 10.5033 | 8.7476 | 22.2236 | 22.1931 | 22.1627 | 22.1627 | 21.8878 | 21.4777 | 21.0515 | 20.6091 | 18.1483 | 17.6724 | 16.05 | 13.4485 | 9.9217 | 8.1542
| HARBOUR | ST |  |  | 25.3593 | 25.3436 | 25.328 | 24.3987 | 24.3185 | 23.5463 | 22.9115 | 22.2757 | 18.3828 | 18.1327 | 17.382 | 15.8715 | 13.7317 | 11.8338 | 23.3844 | 23.361 | 23.3351 | 22.386 | 22.23 | 21.3798 | 18.2997 | 17.6556 | 16.5931 | 16.3308 | 15.3466 | 12.8749 | 10.5026 | 8.3318 | 22.4057 | 22.3901 | 22.3745 | 21.4451 | 21.365 | 20.5928 | 19.958 | 17.7753 | 16.7108 | 16.3105 | 14.7248 | 12.2705 | 9.9195 | 7.7536
| HARBOUR | SP |  |  | 25.4501 | 25.4418 | 25.4336 | 24.9685 | 24.9304 | 23.8541 | 23.8159 | 23.7777 | 22.7013 | 22.5027 | 19.0653 | 18.031 | 17.3162 | 17.0346 | 23.5437 | 23.4734 | 23.4639 | 22.9975 | 22.939 | 21.8391 | 21.7627 | 21.6869 | 18.099 | 17.8959 | 17.282 | 16.225 | 15.4904 | 14.9641 | 22.4965 | 22.4883 | 22.4801 | 22.015 | 21.9769 | 20.9006 | 20.8624 | 20.8242 | 18.2219 | 18.018 | 17.4009 | 16.1252 | 15.0047 | 14.3428
STORNOWAY | HARRIS GRID | MINIMUM HEADROOM | NG 13495 94249 | YES | 29.97 | 29.8252 | 29.6613 | 29.452 | 29.2261 | 28.9878 | 28.7326 | 28.4527 | 28.123 | 28.0003 | 27.7859 | 26.9313 | 23.7297 | 19.5396 | 29.9843 | 29.8524 | 29.7226 | 29.5564 | 29.3722 | 29.1747 | 28.9589 | 28.716 | 28.4203 | 28.3162 | 28.1282 | 27.3166 | 24.6773 | 21.3051 | 29.9267 | 29.7612 | 29.5965 | 29.386 | 29.1591 | 28.919 | 28.6618 | 28.3793 | 28.0471 | 27.9222 | 27.7031 | 26.8411 | 23.6205 | 19.4058
| HARRIS GRID | CT |  |  | 29.97 | 29.8252 | 29.6613 | 29.452 | 29.2261 | 28.9878 | 28.7326 | 28.4527 | 28.123 | 28.0003 | 27.7859 | 26.9313 | 23.7297 | 19.5396 | 29.9843 | 29.8524 | 29.7226 | 29.5564 | 29.3722 | 29.1747 | 28.9589 | 28.716 | 28.4203 | 28.3162 | 28.1282 | 27.3166 | 24.6773 | 21.3051 | 29.9267 | 29.7612 | 29.5965 | 29.386 | 29.1591 | 28.919 | 28.6618 | 28.3793 | 28.0471 | 27.9222 | 27.7031 | 26.8411 | 23.6205 | 19.4058
| HARRIS GRID | LW |  |  | 30.177 | 30.1644 | 30.1523 | 30.1384 | 30.1177 | 30.0953 | 29.9983 | 29.9512 | 29.8668 | 29.8316 | 29.6988 | 29.3347 | 28.8388 | 27.9935 | 30.1199 | 30.1096 | 30.0995 | 30.0876 | 30.0729 | 30.0578 | 30.0417 | 29.9586 | 29.8747 | 29.84 | 29.709 | 29.3673 | 28.9245 | 28.1075 | 30.0909 | 30.0779 | 30.0653 | 30.0506 | 30.0292 | 29.985 | 29.9583 | 29.9072 | 29.8189 | 29.7796 | 29.6343 | 29.2667 | 28.7691 | 27.9224
| HARRIS GRID | ST |  |  | 30.1818 | 30.1735 | 30.1651 | 30.154 | 30.1409 | 30.1279 | 30.1128 | 30.0866 | 29.9455 | 29.9196 | 29.8307 | 28.8629 | 25.5672 | 22.6615 | 30.1239 | 30.1171 | 30.1102 | 30.1009 | 30.0896 | 30.0791 | 30.0692 | 30.0483 | 29.9504 | 29.923 | 29.83 | 28.9843 | 26.2554 | 23.8999 | 30.0959 | 30.0873 | 30.0786 | 30.067 | 30.0534 | 30.04 | 30.0242 | 29.9756 | 29.9054 | 29.8756 | 29.7742 | 28.7911 | 25.4838 | 22.5635
| HARRIS GRID | SP |  |  | 30.1763 | 30.1651 | 30.154 | 30.1429 | 30.1261 | 30.1095 | 30.0931 | 30.0751 | 29.9788 | 29.9519 | 29.8393 | 27.8803 | 25.066 | 22.7957 | 30.1195 | 30.1104 | 30.1014 | 30.0923 | 30.0798 | 30.0706 | 30.0614 | 30.0506 | 29.9898 | 29.9631 | 29.8509 | 28.259 | 25.7985 | 23.9175 | 30.0903 | 30.0787 | 30.0672 | 30.0557 | 30.0383 | 29.9998 | 29.9842 | 29.9642 | 29.9373 | 29.9072 | 29.7853 | 27.8092 | 24.9861 | 22.7061
THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | 7.735 | 7.5871 | 7.4444 | 7.2584 | 6.831 | 4.5895 | 4.1143 | 3.5097 | 2.5536 | 2.0378 | 0.029807 | -3.5731 | -8.0844 | -14.7249 | 6.9138 | 6.7819 | 6.6441 | 6.4322 | 4.9857 | 4.6222 | 4.1173 | 3.3303 | 2.1138 | 1.4684 | -0.87541 | -4.7214 | -8.6305 | -14.3647 | 7.3395 | 7.1815 | 7.0266 | 6.8167 | 4.7064 | 4.2686 | 3.7008 | 2.9544 | 1.9544 | 1.3804 | -0.92661 | -4.908 | -9.4546 | -16.4764
| HASTIGROW | CT |  |  | 7.735 | 7.5871 | 7.4444 | 7.2584 | 6.831 | 4.5895 | 4.1143 | 3.5097 | 2.5536 | 2.0378 | 0.52145 | -3.4274 | -8.0844 | -14.7249 | 6.9138 | 6.7819 | 6.6441 | 6.4322 | 4.9857 | 4.6222 | 4.1173 | 3.4097 | 2.4426 | 1.884 | 0.18089 | -3.9096 | -8.3879 | -14.3647 | 7.3395 | 7.1815 | 7.0266 | 6.8167 | 4.7064 | 4.2686 | 3.7008 | 2.9544 | 1.9544 | 1.3856 | -0.30933 | -4.5174 | -9.4546 | -16.4764
| HASTIGROW | LW |  |  | 7.8697 | 7.8575 | 7.8457 | 7.8321 | 7.428 | 7.0133 | 4.634 | 3.8115 | 2.6681 | 2.0959 | 0.029807 | -3.5731 | -7.052 | -8.7791 | 7.0356 | 7.024 | 7.0113 | 6.9915 | 6.2664 | 4.7786 | 4.2097 | 3.3303 | 2.1138 | 1.4684 | -0.87541 | -4.7214 | -8.6305 | -10.5507 | 7.4837 | 7.4705 | 7.4574 | 7.4409 | 6.9384 | 4.8082 | 4.0977 | 3.2243 | 2.0169 | 1.3804 | -0.92661 | -4.908 | -8.8416 | -10.7958
| HASTIGROW | ST |  |  | 7.8742 | 7.866 | 7.8578 | 7.8467 | 7.6955 | 7.5147 | 7.3397 | 7.1325 | 4.9191 | 4.5691 | 3.1886 | -0.10523 | -5.6296 | -11.2239 | 7.0367 | 7.0266 | 7.0152 | 6.9969 | 6.684 | 6.3889 | 6.129 | 4.8968 | 4.5439 | 4.1146 | 2.5357 | -0.83853 | -6.2036 | -11.5414 | 7.4879 | 7.4784 | 7.4686 | 7.4548 | 7.2632 | 7.0437 | 6.8259 | 4.9273 | 4.4695 | 4.0075 | 2.4565 | -1.0956 | -6.9918 | -13.0166
| HASTIGROW | SP |  |  | 7.8688 | 7.8578 | 7.8468 | 7.8358 | 7.8016 | 7.7682 | 7.7346 | 7.6973 | 7.6408 | 7.579 | 7.3423 | 2.9916 | -1.4325 | -3.7084 | 7.0364 | 7.0275 | 7.0185 | 7.0095 | 6.9359 | 6.8566 | 6.7462 | 6.6334 | 6.5199 | 6.3934 | 6.094 | 2.9063 | -1.257 | -3.3937 | 7.4831 | 7.4716 | 7.4601 | 7.4485 | 7.4032 | 7.3572 | 7.3034 | 7.2462 | 7.1637 | 7.0686 | 6.6934 | 2.3224 | -2.2231 | -4.5856
STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | 9.8354 | 9.8341 | 9.8326 | 9.8305 | 9.8105 | 9.774 | 9.7245 | 9.6596 | 6.2509 | 6.236 | 6.1845 | 6.1109 | 4.2688 | 2.1648 | 8.6212 | 8.6139 | 8.6032 | 8.5791 | 8.4485 | 8.2453 | 8.1819 | 5.9699 | 5.1422 | 5.1251 | 5.0675 | 4.9844 | 2.8689 | 0.42638 | 9.0047 | 9.0005 | 8.9945 | 8.9817 | 8.92 | 8.8207 | 8.6765 | 5.8615 | 5.0637 | 5.047 | 4.9907 | 4.9097 | 2.8083 | 0.36501
| HATTON | CT |  |  | 9.8354 | 9.8341 | 9.8326 | 9.8305 | 9.8105 | 9.7856 | 9.7554 | 9.7193 | 9.6664 | 9.6515 | 9.606 | 9.1665 | 8.8722 | 6.0467 | 8.6212 | 8.6139 | 8.6032 | 8.5791 | 8.5356 | 8.4874 | 8.4345 | 8.376 | 8.3011 | 8.2625 | 8.1465 | 6.1441 | 5.6317 | 5.171 | 9.0047 | 9.0005 | 8.9945 | 8.9817 | 8.9503 | 8.9141 | 8.8729 | 8.8259 | 8.7623 | 8.7359 | 8.6562 | 6.0191 | 5.4991 | 5.031
| HATTON | LW |  |  | 9.8372 | 9.8372 | 9.8372 | 9.8372 | 9.8113 | 9.774 | 9.7245 | 9.6596 | 9.5532 | 9.5326 | 9.457 | 9.0841 | 8.842 | 8.7448 | 8.6288 | 8.6275 | 8.6255 | 8.6206 | 8.5891 | 8.5464 | 8.4916 | 8.4215 | 8.31 | 8.284 | 8.1922 | 7.8182 | 7.5499 | 6.1378 | 9.0093 | 9.0087 | 9.0077 | 9.0053 | 8.9767 | 8.9368 | 8.8847 | 8.8172 | 8.7084 | 8.6852 | 8.6017 | 8.2114 | 7.9566 | 6.0271
| HATTON | ST |  |  | 9.8368 | 9.8365 | 9.8362 | 9.8359 | 9.8241 | 9.8092 | 9.7927 | 9.7712 | 9.7351 | 9.7261 | 9.6969 | 9.48 | 8.6367 | 6.292 | 8.6271 | 8.6247 | 8.6217 | 8.616 | 8.5969 | 8.5733 | 8.5399 | 8.502 | 8.4498 | 8.425 | 8.3502 | 7.905 | 5.8259 | 5.5642 | 9.0083 | 9.007 | 9.0053 | 9.0024 | 8.987 | 8.968 | 8.9432 | 8.9138 | 8.8699 | 8.8532 | 8.8018 | 8.4462 | 5.6381 | 5.3716
| HATTON | SP |  |  | 9.8364 | 9.836 | 9.8356 | 9.8351 | 9.8339 | 9.8327 | 9.8312 | 9.8294 | 6.2509 | 6.236 | 6.1845 | 6.1109 | 4.2688 | 2.1648 | 8.6289 | 8.6281 | 8.6273 | 8.6265 | 8.4485 | 8.2453 | 8.1819 | 5.9699 | 5.1422 | 5.1251 | 5.0675 | 4.9844 | 2.8689 | 0.42638 | 9.0089 | 9.0084 | 9.0078 | 9.0071 | 8.92 | 8.8207 | 8.6765 | 5.8615 | 5.0637 | 5.047 | 4.9907 | 4.9097 | 2.8083 | 0.36501
PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | 29.5534 | 29.552 | 29.5503 | 29.5479 | 29.5401 | 29.5308 | 29.5199 | 29.5074 | 29.4931 | 29.4852 | 29.4583 | 29.3958 | 29.2932 | 29.0939 | 26.6154 | 26.6097 | 26.6016 | 26.5839 | 26.5598 | 26.5344 | 26.5078 | 26.4561 | 26.4049 | 26.3683 | 26.2564 | 26.056 | 25.814 | 25.4777 | 27.5357 | 27.5334 | 27.5303 | 27.5245 | 27.5132 | 27.5004 | 27.4861 | 27.465 | 27.4424 | 27.4254 | 27.3717 | 27.2658 | 27.1192 | 26.8768
| HAUDAGAIN | CT |  |  | 29.5534 | 29.552 | 29.5503 | 29.5479 | 29.5401 | 29.5308 | 29.5199 | 29.5074 | 29.4931 | 29.4852 | 29.4583 | 29.3958 | 29.2932 | 29.0939 | 26.6154 | 26.6097 | 26.6016 | 26.5839 | 26.5598 | 26.5344 | 26.5078 | 26.4561 | 26.4049 | 26.3683 | 26.2564 | 26.056 | 25.814 | 25.4777 | 27.5357 | 27.5334 | 27.5303 | 27.5245 | 27.5132 | 27.5004 | 27.4861 | 27.465 | 27.4424 | 27.4254 | 27.3717 | 27.2658 | 27.1192 | 26.8768
| HAUDAGAIN | LW |  |  | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 29.5555 | 26.6193 | 26.6164 | 26.6116 | 26.5998 | 26.5866 | 26.5737 | 26.5611 | 26.5488 | 26.5368 | 26.5237 | 26.4851 | 26.4377 | 26.3946 | 26.3518 | 27.5382 | 27.5375 | 27.5365 | 27.5339 | 27.5311 | 27.5283 | 27.5255 | 27.5228 | 27.5202 | 27.5174 | 27.509 | 27.4955 | 27.4819 | 27.4684
| HAUDAGAIN | ST |  |  | 29.5551 | 29.5548 | 29.5545 | 29.5542 | 29.5514 | 29.5482 | 29.5444 | 29.54 | 29.5351 | 29.5335 | 29.5286 | 29.5206 | 29.4785 | 29.4547 | 26.6175 | 26.6136 | 26.6084 | 26.5986 | 26.5831 | 26.5646 | 26.5245 | 26.4846 | 26.4465 | 26.426 | 26.3661 | 26.2697 | 26.1402 | 26.0295 | 27.5375 | 27.5364 | 27.535 | 27.5326 | 27.5271 | 27.5206 | 27.5088 | 27.4967 | 27.4843 | 27.4767 | 27.4545 | 27.4186 | 27.349 | 27.2978
| HAUDAGAIN | SP |  |  | 29.5549 | 29.5546 | 29.5543 | 29.5539 | 29.5539 | 29.5538 | 29.5538 | 29.5537 | 29.5536 | 29.5531 | 29.5515 | 29.5503 | 29.5423 | 29.5248 | 26.621 | 26.6201 | 26.6192 | 26.6183 | 26.6147 | 26.6104 | 26.5987 | 26.5871 | 26.5723 | 26.5611 | 26.5284 | 26.4785 | 26.4349 | 26.3878 | 27.5381 | 27.5377 | 27.5372 | 27.5367 | 27.5359 | 27.5349 | 27.5324 | 27.5298 | 27.5265 | 27.5237 | 27.5153 | 27.5035 | 27.4855 | 27.4587
WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | 26.6072 | 26.5248 | 26.4451 | 26.3451 | 26.2208 | 26.0966 | 25.9727 | 25.8491 | 25.7148 | 25.6566 | 25.5504 | 22.1616 | 21.8914 | 25.4971 | 24.7343 | 24.6608 | 24.5997 | 24.5213 | 24.417 | 24.312 | 24.2064 | 24.0952 | 23.973 | 23.9144 | 23.7878 | 23.4883 | 23.178 | 23.6367 | 24.9208 | 24.8251 | 24.7295 | 24.5995 | 24.4441 | 24.2893 | 24.1357 | 23.9735 | 23.8199 | 23.7427 | 23.5826 | 23.2294 | 20.8869 | 23.2668
| HAYTON | CT |  |  | 26.6072 | 26.5248 | 26.4451 | 26.3451 | 26.2208 | 26.0966 | 25.9727 | 25.8491 | 25.7148 | 25.6566 | 25.5504 | 22.1616 | 21.8914 | 25.4971 | 24.7343 | 24.6608 | 24.5997 | 24.5213 | 24.417 | 24.312 | 24.2064 | 24.0952 | 23.973 | 23.9144 | 23.7878 | 23.4883 | 23.178 | 23.6367 | 24.9208 | 24.8251 | 24.7295 | 24.5995 | 24.4441 | 24.2893 | 24.1357 | 23.9735 | 23.8199 | 23.7427 | 23.5826 | 23.2294 | 20.8869 | 23.2668
| HAYTON | LW |  |  | 26.6829 | 26.6762 | 26.6697 | 26.6622 | 26.6537 | 26.6444 | 26.6344 | 26.6236 | 26.612 | 26.5999 | 26.5619 | 27.3317 | 27.2559 | 27.176 | 24.8012 | 24.7936 | 24.7849 | 24.7705 | 24.7545 | 24.7379 | 24.7267 | 24.716 | 24.7048 | 24.693 | 24.6564 | 25.4306 | 25.3614 | 25.2894 | 25.0077 | 24.9981 | 24.9875 | 24.9705 | 24.9515 | 24.9318 | 24.9115 | 24.8906 | 24.8689 | 24.8461 | 24.776 | 25.4934 | 25.3749 | 25.2713
| HAYTON | ST |  |  | 26.6849 | 26.6801 | 26.6752 | 26.6688 | 26.6593 | 26.6492 | 26.6372 | 26.6247 | 26.6118 | 26.6034 | 26.5759 | 26.5291 | 26.4404 | 27.2118 | 24.7888 | 24.7713 | 24.7533 | 24.7359 | 24.711 | 24.6819 | 24.6553 | 24.6283 | 24.6012 | 24.586 | 24.5394 | 24.4628 | 24.3433 | 25.0849 | 24.9951 | 24.9753 | 24.9507 | 24.9065 | 24.8458 | 24.7754 | 24.7412 | 24.7068 | 24.6726 | 24.6526 | 24.591 | 24.4895 | 24.3466 | 25.0641
| HAYTON | SP |  |  | 26.6814 | 26.6748 | 26.6682 | 26.6615 | 26.6526 | 26.6438 | 26.635 | 26.6264 | 26.6179 | 26.6087 | 26.5814 | 26.5315 | 26.4679 | 27.2259 | 24.7995 | 24.7924 | 24.7852 | 24.7777 | 24.7597 | 24.7399 | 24.7252 | 24.714 | 24.7013 | 24.6911 | 24.6611 | 24.6098 | 24.5458 | 25.3036 | 25.0059 | 24.9971 | 24.9881 | 24.9789 | 24.9578 | 24.9347 | 24.9098 | 24.8853 | 24.8564 | 24.8365 | 24.7781 | 24.6786 | 24.5831 | 25.3215
BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | 4.707 | 4.7058 | 4.7042 | 4.7007 | 4.6955 | 4.6899 | 4.684 | 4.6651 | 4.6573 | 4.655 | 4.6474 | 4.6299 | 4.601 | 4.545 | 4.4122 | 4.4113 | 4.4101 | 4.4076 | 4.4036 | 4.3991 | 4.3943 | 4.3812 | 4.3678 | 4.3554 | 4.3283 | 3.9905 | 3.8626 | 3.7093 | 4.4461 | 4.4453 | 4.4444 | 4.4425 | 4.439 | 4.4351 | 4.4308 | 4.4206 | 4.4101 | 4.4008 | 4.3724 | 4.3432 | 3.935 | 3.7831
| HELMSDALE | CT |  |  | 4.707 | 4.7058 | 4.7042 | 4.7007 | 4.6955 | 4.6899 | 4.684 | 4.6651 | 4.6573 | 4.655 | 4.6474 | 4.6299 | 4.601 | 4.545 | 4.4122 | 4.4113 | 4.4101 | 4.4076 | 4.4036 | 4.3991 | 4.3943 | 4.3812 | 4.3678 | 4.3554 | 4.3283 | 3.9905 | 3.8626 | 3.7093 | 4.4461 | 4.4453 | 4.4444 | 4.4425 | 4.439 | 4.4351 | 4.4308 | 4.4206 | 4.4101 | 4.4008 | 4.3724 | 4.3432 | 3.935 | 3.7831
| HELMSDALE | LW |  |  | 4.7075 | 4.7066 | 4.705 | 4.7011 | 4.6968 | 4.6926 | 4.6885 | 4.6845 | 4.6805 | 4.6763 | 4.6748 | 4.6748 | 4.6748 | 4.6748 | 4.4127 | 4.4121 | 4.4111 | 4.4087 | 4.406 | 4.4034 | 4.4009 | 4.3983 | 4.3959 | 4.3932 | 4.3854 | 4.3727 | 4.36 | 4.3559 | 4.4466 | 4.4462 | 4.4455 | 4.4439 | 4.442 | 4.4402 | 4.4384 | 4.4367 | 4.435 | 4.4331 | 4.4277 | 4.4189 | 4.4101 | 4.4014
| HELMSDALE | ST |  |  | 4.7078 | 4.7073 | 4.7065 | 4.7052 | 4.7026 | 4.6996 | 4.6916 | 4.6835 | 4.6754 | 4.6676 | 4.666 | 4.6634 | 4.6497 | 4.6419 | 4.4128 | 4.4124 | 4.4119 | 4.4111 | 4.4091 | 4.4068 | 4.4014 | 4.3958 | 4.3902 | 4.383 | 4.3619 | 4.3437 | 4.3268 | 3.9651 | 4.4467 | 4.4464 | 4.446 | 4.4454 | 4.4438 | 4.4418 | 4.4377 | 4.4334 | 4.429 | 4.4238 | 4.4087 | 4.3844 | 4.3629 | 4.3552
| HELMSDALE | SP |  |  | 4.7082 | 4.708 | 4.7078 | 4.7076 | 4.7071 | 4.7065 | 4.7039 | 4.7014 | 4.6981 | 4.6936 | 4.6809 | 4.6727 | 4.6694 | 4.6624 | 4.413 | 4.4128 | 4.4127 | 4.4125 | 4.4122 | 4.4118 | 4.4102 | 4.4086 | 4.4065 | 4.4037 | 4.3955 | 4.3832 | 4.3688 | 4.3513 | 4.4468 | 4.4466 | 4.4464 | 4.4463 | 4.4461 | 4.4458 | 4.4447 | 4.4435 | 4.4421 | 4.4401 | 4.4342 | 4.4255 | 4.4145 | 4.4002
INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | 33.3684 | 33.361 | 33.3522 | 33.3396 | 33.2982 | 33.249 | 33.1914 | 33.1249 | 33.0501 | 33.0075 | 32.8651 | 32.535 | 31.9915 | 22.0671 | 28.4732 | 28.4321 | 28.3727 | 28.2395 | 28.0682 | 27.8913 | 27.7079 | 27.538 | 27.3614 | 27.2444 | 26.9958 | 26.496 | 20.9489 | 18.8255 | 27.7788 | 27.7551 | 27.7217 | 27.6505 | 27.546 | 27.4428 | 27.3852 | 27.3188 | 27.2439 | 27.2013 | 27.0589 | 21.9845 | 20.4334 | 18.388
| HILTON | CT |  |  | 33.3684 | 33.361 | 33.3522 | 33.3396 | 33.2982 | 33.249 | 33.1914 | 33.1249 | 33.0501 | 33.0075 | 32.8651 | 32.535 | 31.9915 | 22.0671 | 28.4732 | 28.4321 | 28.3727 | 28.2395 | 28.0682 | 27.8913 | 27.7079 | 27.538 | 27.3614 | 27.2444 | 26.9958 | 26.496 | 20.9489 | 18.8255 | 27.7788 | 27.7551 | 27.7217 | 27.6505 | 27.546 | 27.4428 | 27.3852 | 27.3188 | 27.2439 | 27.2013 | 27.0589 | 21.9845 | 20.4334 | 18.388
| HILTON | LW |  |  | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 33.3795 | 28.5193 | 28.5163 | 28.5116 | 28.4998 | 28.4866 | 28.4738 | 28.4612 | 28.4489 | 28.4369 | 28.4239 | 28.3855 | 28.3236 | 28.2612 | 28.1995 | 27.8069 | 27.8055 | 27.8032 | 27.7975 | 27.7911 | 27.7848 | 27.7787 | 27.7728 | 27.7669 | 27.7606 | 27.7419 | 27.7119 | 27.6816 | 27.6516
| HILTON | ST |  |  | 33.3765 | 33.3745 | 33.3725 | 33.3701 | 33.3504 | 33.3268 | 33.2995 | 33.2682 | 33.2329 | 33.2214 | 33.1866 | 33.1284 | 32.8258 | 32.6542 | 28.493 | 28.4688 | 28.4371 | 28.3776 | 28.2804 | 28.1638 | 28.0629 | 27.9595 | 27.8536 | 27.7694 | 27.5232 | 27.2989 | 26.8865 | 26.6116 | 27.7926 | 27.7798 | 27.7634 | 27.7333 | 27.6759 | 27.6072 | 27.5441 | 27.4778 | 27.4267 | 27.4153 | 27.3804 | 27.3222 | 27.0196 | 22.0658
| HILTON | SP |  |  | 33.3725 | 33.3688 | 33.3649 | 33.361 | 33.3604 | 33.3597 | 33.3589 | 33.3581 | 33.3571 | 33.3515 | 33.3322 | 33.3172 | 33.2209 | 33.0113 | 28.5108 | 28.5042 | 28.497 | 28.4894 | 28.4685 | 28.4437 | 28.4194 | 28.3954 | 28.3646 | 28.3307 | 28.2295 | 28.0864 | 27.8697 | 27.5464 | 27.7992 | 27.7941 | 27.7886 | 27.7829 | 27.7724 | 27.76 | 27.7478 | 27.7357 | 27.7203 | 27.7009 | 27.6419 | 27.5646 | 27.4147 | 27.2051
ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | YES | 30.7998 | 30.6667 | 30.5373 | 30.357 | 30.1585 | 29.9507 | 29.7295 | 29.4863 | 29.1698 | 29.0361 | 28.7747 | 27.8112 | 21.9782 | 18.6345 | 26.9349 | 26.808 | 26.6774 | 26.4755 | 26.251 | 26.0172 | 25.7768 | 25.5961 | 25.3498 | 25.2549 | 25.0566 | 21.685 | 20.3638 | 17.2492 | 28.1428 | 28.0004 | 27.8583 | 27.6508 | 27.4235 | 27.1874 | 26.9386 | 26.6491 | 26.2866 | 26.1052 | 25.705 | 21.8492 | 20.232 | 16.0858
| HUME STREET | CT |  |  | 30.7998 | 30.6667 | 30.5373 | 30.357 | 30.1585 | 29.9507 | 29.7295 | 29.4863 | 29.1698 | 29.0361 | 28.7747 | 27.8112 | 22.9177 | 22.2241 | 26.9349 | 26.808 | 26.6774 | 26.4755 | 26.251 | 26.0172 | 25.7768 | 25.5961 | 25.3498 | 25.2549 | 25.0566 | 21.685 | 20.3638 | 19.0994 | 28.1428 | 28.0004 | 27.8583 | 27.6508 | 27.4235 | 27.1874 | 26.9386 | 26.6491 | 26.2866 | 26.1052 | 25.705 | 21.8492 | 20.4609 | 19.1267
| HUME STREET | LW |  |  | 30.9214 | 30.9097 | 30.8978 | 30.8819 | 30.6986 | 30.5107 | 30.3159 | 30.0929 | 29.755 | 29.6708 | 29.3997 | 28.6755 | 28.0893 | 27.7103 | 27.0453 | 27.0266 | 27.0027 | 26.9546 | 26.7353 | 26.5126 | 26.2839 | 26.028 | 25.6587 | 25.5403 | 25.1687 | 24.4977 | 23.9832 | 21.7696 | 28.2701 | 28.2539 | 28.235 | 28.202 | 27.9994 | 27.7928 | 27.5796 | 27.3385 | 26.9829 | 26.8795 | 26.5515 | 25.7338 | 25.0544 | 21.8068
| HUME STREET | ST |  |  | 30.925 | 30.9168 | 30.9084 | 30.8967 | 30.8806 | 30.8634 | 30.8415 | 30.8119 | 30.7532 | 30.7232 | 30.6244 | 28.9312 | 21.9782 | 18.6345 | 27.0503 | 27.0376 | 27.0229 | 26.9984 | 26.9645 | 26.9259 | 26.8654 | 26.798 | 26.7024 | 26.6132 | 26.3432 | 25.214 | 20.5755 | 17.2492 | 28.2749 | 28.2637 | 28.2514 | 28.2325 | 28.2066 | 28.1779 | 28.1357 | 28.0863 | 28.0081 | 27.9476 | 27.76 | 25.8948 | 20.232 | 16.0858
| HUME STREET | SP |  |  | 30.9202 | 30.9098 | 30.8994 | 30.8889 | 30.874 | 30.8592 | 30.8438 | 30.8275 | 30.8064 | 30.7819 | 30.6877 | 28.2003 | 22.0172 | 20.3709 | 27.0515 | 27.0418 | 27.0319 | 27.0219 | 27.0038 | 26.9846 | 26.958 | 26.9305 | 26.8946 | 26.8481 | 26.6907 | 24.8673 | 21.4693 | 19.8673 | 28.2726 | 28.2616 | 28.2505 | 28.2394 | 28.2215 | 28.2032 | 28.1809 | 28.1577 | 28.128 | 28.0912 | 27.9618 | 25.3685 | 20.6038 | 19.0493
KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | YES | 21.1254 | 21.02 | 20.9772 | 20.8587 | 20.3341 | 19.8334 | 19.1824 | 18.4571 | 17.9989 | 17.8222 | 14.2723 | 11.5366 | 6.8036 | 4.8675 | 17.6399 | 17.5277 | 17.5077 | 17.3937 | 16.8529 | 16.122 | 13.3079 | 12.5873 | 12.4411 | 12.2831 | 10.719 | 7.4815 | 2.7268 | 0.55347 | 18.5805 | 18.4758 | 18.4308 | 18.3151 | 17.8082 | 17.2315 | 13.6607 | 12.9362 | 12.5308 | 12.3573 | 10.8419 | 7.4284 | 2.3339 | 0.13832
| HUNTLY | CT |  |  | 21.1254 | 21.0515 | 20.9772 | 20.8587 | 20.3341 | 19.8334 | 19.3175 | 18.7756 | 17.9989 | 17.8222 | 14.2723 | 11.5366 | 6.8036 | 4.8675 | 17.6399 | 17.5749 | 17.5077 | 17.3937 | 16.8529 | 16.29 | 13.6869 | 13.182 | 12.4411 | 12.2831 | 11.4086 | 7.4815 | 2.7268 | 0.55347 | 18.5805 | 18.5054 | 18.4308 | 18.3151 | 17.8082 | 17.2738 | 16.714 | 13.3015 | 12.5308 | 12.3573 | 11.3765 | 7.4284 | 2.3339 | 0.13832
| HUNTLY | LW |  |  | 21.1906 | 21.1814 | 21.1703 | 21.1324 | 20.455 | 19.8392 | 19.1824 | 18.4571 | 18.419 | 18.1991 | 14.3377 | 12.0722 | 7.6195 | 5.9719 | 17.6961 | 17.6863 | 17.6735 | 17.6303 | 16.8752 | 16.122 | 13.3079 | 12.5873 | 12.5543 | 12.3397 | 10.719 | 7.7745 | 3.2976 | 1.4382 | 18.6476 | 18.6393 | 18.6297 | 18.5961 | 17.9295 | 17.2315 | 13.6607 | 12.9362 | 12.899 | 12.576 | 10.8419 | 7.8831 | 3.0718 | 1.196
| HUNTLY | ST |  |  | 21.194 | 21.1883 | 21.182 | 21.1627 | 20.8344 | 20.4851 | 20.1712 | 19.8349 | 19.2804 | 19.1526 | 18.8275 | 14.3624 | 10.6289 | 8.6142 | 17.6998 | 17.6939 | 17.6872 | 17.6667 | 17.3192 | 16.9511 | 16.5723 | 16.1445 | 13.4038 | 13.2787 | 12.9629 | 10.193 | 6.3954 | 4.1097 | 18.6506 | 18.6453 | 18.6396 | 18.6215 | 18.3075 | 17.9721 | 17.6364 | 17.252 | 13.7584 | 13.631 | 13.1022 | 10.3186 | 6.3548 | 4.0617
| HUNTLY | SP |  |  | 21.1931 | 21.02 | 21.0146 | 21.0061 | 20.8562 | 20.8271 | 20.7973 | 20.7649 | 20.7185 | 20.6675 | 20.4881 | 20.2788 | 18.1333 | 14.1675 | 17.7 | 17.5277 | 17.523 | 17.5152 | 17.1023 | 16.8074 | 16.7597 | 16.7096 | 16.6395 | 16.5581 | 16.2562 | 13.7334 | 11.2093 | 10.084 | 18.649 | 18.4758 | 18.4702 | 18.4617 | 18.2172 | 17.9426 | 17.8947 | 17.8444 | 17.7745 | 17.6939 | 17.3973 | 17.0628 | 11.318 | 10.1834
BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | 3.1148 | 3.0217 | 2.8695 | 2.3875 | 2.0978 | 1.6692 | 1.0311 | 0.39479 | -0.41106 | -1.2011 | -2.5678 | -4.6874 | -6.3907 | -9.5331 | 3.1897 | 3.1402 | 3.0365 | 2.9324 | 2.1896 | 1.4608 | 0.72934 | 0.00098667 | -0.92565 | -1.8364 | -2.7422 | -5.0104 | -7.8202 | -10.3222 | 3.24 | 3.1438 | 2.9839 | 2.4093 | 1.9638 | 1.3876 | 0.63919 | -0.10644 | -1.0501 | -1.978 | -3.4245 | -5.8698 | -8.0625 | -11.4893
| INCHBARE | CT |  |  | 3.1148 | 3.0217 | 2.8695 | 2.3875 | 2.0978 | 1.6955 | 1.2964 | 0.84971 | 0.25672 | -0.42202 | -2.5678 | -4.6874 | -5.746 | -9.5331 | 3.1897 | 3.1402 | 3.0365 | 2.9324 | 2.1896 | 1.805 | 1.4243 | 0.98759 | 0.38117 | -0.34406 | -2.7422 | -5.0104 | -6.0612 | -10.3222 | 3.24 | 3.1438 | 2.9839 | 2.4093 | 1.9638 | 1.5093 | 1.0582 | 0.55067 | -0.12851 | -0.91692 | -3.4245 | -5.8698 | -7.0802 | -11.4893
| INCHBARE | LW |  |  | 3.1987 | 3.1902 | 3.1547 | 3.116 | 2.3096 | 1.6692 | 1.0311 | 0.39479 | -0.41106 | -1.2011 | -1.2788 | -3.0548 | -3.9636 | -6.3867 | 3.2346 | 3.2305 | 3.2017 | 3.1722 | 2.1959 | 1.4608 | 0.72934 | 0.00098667 | -0.92565 | -1.8364 | -1.8815 | -3.8778 | -4.8374 | -7.58 | 3.3262 | 3.3168 | 3.2774 | 3.233 | 2.1395 | 1.3876 | 0.63919 | -0.10644 | -1.0501 | -1.978 | -2.0672 | -4.1337 | -5.1708 | -7.9893
| INCHBARE | ST |  |  | 3.202 | 3.1965 | 3.1731 | 3.1478 | 3.091 | 2.4861 | 2.2424 | 1.9362 | 1.4998 | 0.93181 | -1.0578 | -2.8939 | -6.3907 | -8.4767 | 3.2362 | 3.2334 | 3.2141 | 3.1939 | 3.1733 | 2.3963 | 2.123 | 1.776 | 1.2752 | 0.61785 | -1.6905 | -3.7788 | -7.8202 | -10.1905 | 3.3298 | 3.3239 | 3.2981 | 3.2696 | 3.0076 | 2.3463 | 2.061 | 1.7021 | 1.1901 | 0.52205 | -1.8184 | -3.9668 | -8.0625 | -10.4947
| INCHBARE | SP |  |  | 3.1991 | 3.1922 | 3.1854 | 3.1785 | 3.1552 | 3.146 | 3.1368 | 3.1278 | 2.4874 | 2.2866 | 1.438 | 0.3564 | -0.582 | -1.4805 | 3.2343 | 3.2307 | 3.227 | 3.2233 | 3.2179 | 3.2125 | 3.2072 | 3.2019 | 2.368 | 2.1341 | 1.1413 | -0.11624 | -1.2034 | -2.2412 | 3.3272 | 3.3202 | 3.3131 | 3.3061 | 3.2339 | 3.1531 | 3.0352 | 3.0134 | 2.3505 | 2.1149 | 1.1181 | -0.14933 | -1.2473 | -2.2953
DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | 3.3161 | 3.1746 | 3.0382 | 2.3314 | 2.1438 | 1.9321 | 1.6912 | 1.4362 | 1.109 | 0.97166 | 0.71306 | -0.30379 | -2.7836 | -4.9101 | 2.9913 | 2.9113 | 2.4872 | 2.3045 | 2.1076 | 1.9015 | 1.682 | 1.448 | 1.1442 | 1.0175 | 0.77023 | -0.093185 | -2.1311 | -3.891 | 2.8774 | 2.7467 | 2.3727 | 2.1696 | 1.9395 | 1.6967 | 1.4417 | 1.1736 | 0.83251 | 0.68585 | 0.4077 | -0.62911 | -3.1369 | -5.2716
| INNELLAN | CT |  |  | 3.3161 | 3.1746 | 3.0382 | 2.3314 | 2.1438 | 1.9321 | 1.6912 | 1.4362 | 1.109 | 0.97166 | 0.71306 | -0.16981 | -0.91538 | -1.465 | 2.9913 | 2.9113 | 2.4872 | 2.3045 | 2.1076 | 1.9015 | 1.682 | 1.448 | 1.1442 | 1.0175 | 0.77023 | -0.093185 | -0.79862 | -1.3067 | 2.8774 | 2.7467 | 2.3727 | 2.1696 | 1.9395 | 1.6967 | 1.4417 | 1.1736 | 0.83251 | 0.68585 | 0.4077 | -0.50737 | -1.2701 | -1.8364
| INNELLAN | LW |  |  | 3.4449 | 3.4332 | 3.4218 | 3.4088 | 3.394 | 3.3778 | 3.3602 | 3.3241 | 3.2519 | 3.2156 | 3.079 | 2.1985 | 1.8107 | 1.4919 | 3.0641 | 3.0575 | 3.0511 | 3.0437 | 3.0355 | 3.0263 | 3.0164 | 2.9885 | 2.9262 | 2.9002 | 2.4575 | 2.0934 | 1.7101 | 1.4162 | 2.9962 | 2.9853 | 2.9746 | 2.9617 | 2.9473 | 2.9315 | 2.9145 | 2.879 | 2.8078 | 2.7725 | 2.3933 | 2.0116 | 1.5919 | 1.2553
| INNELLAN | ST |  |  | 3.4493 | 3.4415 | 3.4336 | 3.4231 | 3.4123 | 3.4017 | 3.3888 | 3.3677 | 3.3145 | 3.2917 | 3.2129 | 1.737 | -0.51455 | -3.4446 | 3.0665 | 3.0621 | 3.0576 | 3.0517 | 3.0453 | 3.039 | 3.0314 | 3.0154 | 2.9673 | 2.9496 | 2.8878 | 1.6594 | -0.31098 | -2.7443 | 3.0002 | 2.9926 | 2.9849 | 2.9746 | 2.9641 | 2.9537 | 2.9412 | 2.9204 | 2.8674 | 2.845 | 2.4686 | 1.4907 | -0.85412 | -3.8446
| INNELLAN | SP |  |  | 3.444 | 3.4334 | 3.4229 | 3.4123 | 3.3969 | 3.3816 | 3.3666 | 3.3503 | 3.3291 | 3.3056 | 3.2107 | -0.30379 | -2.7836 | -4.9101 | 3.0635 | 3.0574 | 3.0515 | 3.0454 | 3.0367 | 3.0282 | 3.0197 | 3.0099 | 2.9951 | 2.9778 | 2.9013 | 0.035725 | -2.1311 | -3.891 | 2.9955 | 2.9857 | 2.976 | 2.9662 | 2.9515 | 2.937 | 2.9225 | 2.9068 | 2.8859 | 2.8629 | 2.7694 | -0.62911 | -3.1369 | -5.2716
KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | YES | 16.1713 | 23.4434 | 23.4401 | 23.4181 | 23.3488 | 23.2513 | 23.1378 | 23.0025 | 22.8013 | 22.7428 | 22.5248 | 21.3172 | 20.554 | 20.078 | 12.4313 | 19.3047 | 19.2657 | 19.1586 | 18.9979 | 18.7435 | 18.5782 | 18.4955 | 18.3145 | 18.2066 | 17.8967 | 16.768 | 13.0107 | 12.1168 | 14.0153 | 20.9031 | 20.8858 | 20.8303 | 20.7251 | 20.6087 | 20.4814 | 20.2922 | 20.2106 | 20.1354 | 19.8797 | 18.2667 | 13.4325 | 12.5336
| INSCH | CT |  |  | 16.1713 | 23.4434 | 23.4401 | 23.4181 | 23.3488 | 23.2678 | 23.1772 | 23.0753 | 22.944 | 22.8899 | 22.6984 | 21.3172 | 20.554 | 20.078 | 12.4313 | 19.3047 | 19.2657 | 19.1586 | 18.9979 | 18.8269 | 18.6479 | 18.4955 | 18.3145 | 18.2066 | 17.8967 | 16.768 | 13.0107 | 12.1168 | 14.0153 | 20.9031 | 20.8858 | 20.8303 | 20.7251 | 20.6087 | 20.4833 | 20.3615 | 20.2106 | 20.1354 | 19.8797 | 18.2667 | 13.4325 | 12.5336
| INSCH | LW |  |  | 16.1754 | 23.4504 | 23.4504 | 23.431 | 23.3488 | 23.2513 | 23.1378 | 23.0025 | 22.8013 | 22.7428 | 22.5248 | 21.3399 | 20.7218 | 20.5377 | 12.4591 | 19.3562 | 19.3515 | 19.3205 | 19.2254 | 19.1152 | 18.9893 | 18.8419 | 18.6288 | 18.5575 | 18.3087 | 17.2024 | 16.5668 | 16.138 | 14.0288 | 20.9277 | 20.9258 | 20.9018 | 20.8146 | 20.7121 | 20.5937 | 20.4537 | 20.2478 | 20.1842 | 19.95 | 18.7146 | 18.0641 | 17.7455
| INSCH | ST |  |  | 16.1744 | 23.4488 | 23.4481 | 23.4366 | 23.3945 | 23.3467 | 23.2967 | 23.2385 | 23.1523 | 23.1226 | 23.031 | 22.3922 | 21.7718 | 21.6122 | 12.445 | 19.3308 | 19.3119 | 19.2652 | 19.1755 | 19.0705 | 18.9739 | 18.87 | 18.7391 | 18.6738 | 18.4826 | 17.7195 | 17.132 | 16.9588 | 14.0226 | 20.9167 | 20.9088 | 20.8835 | 20.8227 | 20.7524 | 20.684 | 20.6078 | 20.504 | 20.4604 | 20.3274 | 19.5066 | 18.8175 | 18.5936
| INSCH | SP |  |  | 16.1732 | 23.447 | 23.4458 | 23.4413 | 23.4345 | 23.4277 | 23.4206 | 23.4127 | 23.4027 | 23.3892 | 23.3436 | 23.2877 | 22.6388 | 22.4026 | 12.457 | 19.354 | 19.3505 | 19.3435 | 19.0633 | 18.7435 | 18.5782 | 18.5319 | 18.5203 | 18.5057 | 18.4567 | 18.3956 | 17.7418 | 13.5485 | 14.0266 | 20.9247 | 20.9226 | 20.9171 | 20.8028 | 20.6728 | 20.4814 | 20.2922 | 20.2747 | 20.2557 | 20.1944 | 20.1138 | 19.4417 | 19.02
BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | 23.6867 | 23.6867 | 23.6154 | 23.6154 | 23.6154 | 23.6154 | 23.6154 | 23.6154 | 23.5475 | 23.4754 | 23.6867 | 23.6154 | 23.4754 | 23.6867 | 22.3699 | 22.3691 | 22.298 | 22.2975 | 22.2968 | 22.2959 | 22.2952 | 22.2945 | 22.226 | 22.1535 | 22.3705 | 22.2968 | 22.1535 | 22.3691 | 22.4621 | 22.4613 | 22.3902 | 22.3896 | 22.389 | 22.3881 | 22.3874 | 22.3867 | 22.3183 | 22.2458 | 22.4627 | 22.389 | 22.2458 | 22.4613
| INVERALMOND | CT |  |  | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 22.3699 | 22.3691 | 22.368 | 22.3671 | 22.366 | 22.3649 | 22.3639 | 22.3631 | 22.3623 | 22.3616 | 22.3705 | 22.366 | 22.3616 | 22.3691 | 22.4621 | 22.4613 | 22.4602 | 22.4593 | 22.4583 | 22.4571 | 22.4562 | 22.4554 | 22.4547 | 22.454 | 22.4627 | 22.4583 | 22.454 | 22.4613
| INVERALMOND | LW |  |  | 23.6867 | 23.6867 | 23.6154 | 23.6154 | 23.6154 | 23.6154 | 23.6154 | 23.6154 | 23.5475 | 23.4754 | 23.6867 | 23.6154 | 23.4754 | 23.6867 | 22.3703 | 22.3699 | 22.298 | 22.2975 | 22.2968 | 22.2959 | 22.2952 | 22.2945 | 22.226 | 22.1535 | 22.3706 | 22.2968 | 22.1535 | 22.3699 | 22.4624 | 22.462 | 22.3902 | 22.3896 | 22.389 | 22.3881 | 22.3874 | 22.3867 | 22.3183 | 22.2458 | 22.4628 | 22.389 | 22.2458 | 22.462
| INVERALMOND | ST |  |  | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 22.3703 | 22.3699 | 22.3694 | 22.3688 | 22.3682 | 22.3671 | 22.3661 | 22.3559 | 22.3458 | 22.3359 | 22.3706 | 22.3682 | 22.3359 | 22.3699 | 22.4624 | 22.462 | 22.4615 | 22.461 | 22.4604 | 22.4593 | 22.4583 | 22.4484 | 22.4386 | 22.4289 | 22.4628 | 22.4604 | 22.4289 | 22.462
| INVERALMOND | SP |  |  | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 23.6867 | 22.3704 | 22.3702 | 22.37 | 22.3698 | 22.3697 | 22.3694 | 22.3692 | 22.3668 | 22.364 | 22.3607 | 22.4006 | 22.3697 | 22.3607 | 22.3702 | 22.4626 | 22.4623 | 22.4621 | 22.462 | 22.4618 | 22.4616 | 22.4613 | 22.4591 | 22.4563 | 22.4531 | 22.4817 | 22.4618 | 22.4531 | 22.4623
CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | 2.7843 | 2.7227 | 2.4103 | 2.3002 | 2.1922 | 2.0821 | 1.9729 | 1.8615 | 1.7498 | 1.6713 | 1.5422 | 1.3333 | 1.136 | 0.93657 | 2.7043 | 2.4392 | 2.3573 | 2.2607 | 2.1656 | 2.0668 | 1.9693 | 1.8728 | 1.7759 | 1.7051 | 1.5868 | 1.3952 | 1.2155 | 1.0347 | 2.4598 | 2.353 | 2.2619 | 2.1523 | 2.0449 | 1.9351 | 1.822 | 1.7089 | 1.5956 | 1.5158 | 1.3838 | 1.1701 | 0.96807 | 0.76399
| INVERARAY | CT |  |  | 2.7843 | 2.7227 | 2.4103 | 2.3002 | 2.1922 | 2.0821 | 1.9729 | 1.8615 | 1.7498 | 1.6713 | 1.5422 | 1.3333 | 1.136 | 0.93657 | 2.7043 | 2.4392 | 2.3573 | 2.2607 | 2.1656 | 2.0668 | 1.9693 | 1.8728 | 1.7759 | 1.7051 | 1.5868 | 1.3952 | 1.2155 | 1.0347 | 2.4598 | 2.353 | 2.2619 | 2.1523 | 2.0449 | 1.9351 | 1.822 | 1.7089 | 1.5956 | 1.5158 | 1.3838 | 1.1701 | 0.96807 | 0.76399
| INVERARAY | LW |  |  | 2.8403 | 2.8351 | 2.8302 | 2.8245 | 2.818 | 2.8109 | 2.8033 | 2.7951 | 2.7861 | 2.7769 | 2.7477 | 2.4499 | 2.3768 | 2.2983 | 2.7319 | 2.7294 | 2.7269 | 2.7241 | 2.7209 | 2.4996 | 2.4941 | 2.4883 | 2.4821 | 2.4757 | 2.4448 | 2.3843 | 2.3177 | 2.2465 | 2.6152 | 2.4777 | 2.4714 | 2.4632 | 2.4539 | 2.4439 | 2.4333 | 2.4222 | 2.4103 | 2.3979 | 2.3593 | 2.2911 | 2.2158 | 2.1353
| INVERARAY | ST |  |  | 2.8422 | 2.8388 | 2.8354 | 2.8309 | 2.8264 | 2.8221 | 2.8169 | 2.8118 | 2.8069 | 2.8021 | 2.7859 | 2.7583 | 2.4999 | 2.4659 | 2.7329 | 2.7312 | 2.7295 | 2.7273 | 2.7251 | 2.7229 | 2.7204 | 2.7178 | 2.4981 | 2.4947 | 2.4835 | 2.4611 | 2.4315 | 2.4001 | 2.6171 | 2.6139 | 2.4781 | 2.4725 | 2.4667 | 2.461 | 2.4542 | 2.4476 | 2.4413 | 2.4348 | 2.4133 | 2.377 | 2.3438 | 2.3085
| INVERARAY | SP |  |  | 2.84 | 2.8354 | 2.8309 | 2.8263 | 2.8196 | 2.8129 | 2.8064 | 2.7999 | 2.7935 | 2.7872 | 2.7689 | 2.7328 | 2.4677 | 2.4276 | 2.7317 | 2.7295 | 2.7273 | 2.725 | 2.7217 | 2.7184 | 2.7152 | 2.4961 | 2.4922 | 2.4882 | 2.4767 | 2.4456 | 2.4104 | 2.3755 | 2.615 | 2.6107 | 2.4738 | 2.4687 | 2.461 | 2.4534 | 2.4458 | 2.4383 | 2.4308 | 2.4233 | 2.4015 | 2.3592 | 2.317 | 2.277
LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | NO | 3.1378 | 3.0722 | 2.4554 | 2.3732 | 2.1591 | 1.6104 | 1.033 | 0.45587 | -0.287 | -0.98658 | -1.6456 | -4.0521 | -5.9838 | -8.2218 | 3.0015 | 2.9608 | 2.9211 | 2.8662 | 2.2557 | 1.5807 | 0.90832 | 0.23722 | -0.62508 | -1.4441 | -1.9401 | -4.4643 | -7.1697 | -9.3058 | 2.8973 | 2.8318 | 2.4337 | 2.3398 | 1.9372 | 1.2691 | 0.60338 | -0.061278 | -0.91526 | -1.726 | -2.3818 | -5.0397 | -7.46 | -9.8239
| INVERARITY | CT |  |  | 3.1378 | 3.0722 | 2.4554 | 2.3732 | 2.1591 | 1.8587 | 1.5619 | 1.2165 | 0.72837 | 0.1815 | -1.6456 | -4.0521 | -4.9411 | -8.2218 | 3.0015 | 2.9608 | 2.9211 | 2.8662 | 2.3571 | 2.039 | 1.7241 | 1.351 | 0.81374 | 0.18703 | -1.9401 | -4.4643 | -5.4433 | -9.2531 | 2.8973 | 2.8318 | 2.4337 | 2.3398 | 1.9581 | 1.625 | 1.2957 | 0.90971 | 0.36024 | -0.26813 | -2.3818 | -5.0397 | -6.0351 | -9.8239
| INVERARITY | LW |  |  | 3.1974 | 3.1919 | 3.1867 | 3.1806 | 2.1892 | 1.6104 | 1.033 | 0.45587 | -0.287 | -0.98658 | -1.072 | -3.2597 | -4.0324 | -6.1566 | 3.0379 | 3.0337 | 3.0291 | 3.022 | 2.2557 | 1.5807 | 0.90832 | 0.23722 | -0.62508 | -1.4441 | -1.5244 | -3.8152 | -4.6758 | -7.1361 | 2.9568 | 2.9513 | 2.9461 | 2.94 | 1.9372 | 1.2691 | 0.60338 | -0.061278 | -0.91526 | -1.726 | -1.8139 | -4.2306 | -5.099 | -7.5485
| INVERARITY | ST |  |  | 3.1995 | 3.1958 | 3.1921 | 3.1872 | 3.1721 | 2.3401 | 2.1244 | 1.8505 | 1.4505 | 0.94518 | -0.82872 | -2.7694 | -5.9838 | -7.8157 | 3.0395 | 3.0368 | 3.034 | 3.0299 | 2.9403 | 2.4316 | 2.1815 | 1.8631 | 1.3977 | 0.80472 | -1.2776 | -3.4172 | -7.1697 | -9.3058 | 2.9588 | 2.9552 | 2.9515 | 2.9466 | 2.3593 | 2.1118 | 1.8636 | 1.548 | 1.0872 | 0.50076 | -1.5584 | -3.7483 | -7.46 | -9.5769
| INVERARITY | SP |  |  | 3.197 | 3.1922 | 3.1873 | 3.1824 | 3.1738 | 3.1653 | 3.1568 | 2.4321 | 2.2945 | 2.1098 | 1.3297 | 0.34214 | -0.67421 | -1.5269 | 3.0384 | 3.0353 | 3.0323 | 3.0292 | 2.981 | 2.9401 | 2.9348 | 2.9294 | 2.3882 | 2.1736 | 1.2637 | 0.11681 | -1.0345 | -2.0137 | 2.9564 | 2.9515 | 2.9467 | 2.9418 | 2.9332 | 2.4629 | 2.3408 | 2.2204 | 2.0619 | 1.8485 | 0.94598 | -0.19485 | -1.3426 | -2.3185
INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | NO | 2.8695 | 2.4482 | 2.3522 | 2.2316 | 2.1136 | 1.9991 | 1.8881 | 1.7789 | 1.6716 | 1.6091 | 1.5006 | 1.3202 | 1.1539 | 0.9633 | 2.7216 | 2.4351 | 2.3471 | 2.2354 | 2.126 | 2.0197 | 1.9168 | 1.8093 | 1.72 | 1.6665 | 1.5679 | 1.4053 | 1.2525 | 1.0763 | 2.7624 | 2.6573 | 2.4797 | 2.3436 | 2.2061 | 2.0722 | 1.9425 | 1.8098 | 1.6998 | 1.6347 | 1.5194 | 1.3301 | 1.1552 | 0.95205
| INVERARNIE | CT |  |  | 2.8695 | 2.4482 | 2.3522 | 2.2316 | 2.1136 | 1.9991 | 1.8881 | 1.7789 | 1.6716 | 1.6091 | 1.5006 | 1.3202 | 1.1539 | 0.9633 | 2.7216 | 2.4351 | 2.3471 | 2.2354 | 2.126 | 2.0197 | 1.9168 | 1.8093 | 1.72 | 1.6665 | 1.5679 | 1.4053 | 1.2525 | 1.0763 | 2.7624 | 2.6573 | 2.4797 | 2.3436 | 2.2061 | 2.0722 | 1.9425 | 1.8098 | 1.6998 | 1.6347 | 1.5194 | 1.3301 | 1.1552 | 0.95205
| INVERARNIE | LW |  |  | 2.9624 | 2.9539 | 2.9457 | 2.9363 | 2.9256 | 2.9139 | 2.9012 | 2.8877 | 2.8757 | 2.8632 | 2.824 | 2.4353 | 2.3766 | 2.3145 | 2.7751 | 2.7703 | 2.7656 | 2.7601 | 2.754 | 2.7473 | 2.74 | 2.7322 | 2.7254 | 2.497 | 2.4542 | 2.379 | 2.3112 | 2.2403 | 2.8577 | 2.8488 | 2.8401 | 2.8298 | 2.8181 | 2.8053 | 2.7915 | 2.7768 | 2.7638 | 2.7503 | 2.7089 | 2.6354 | 2.4598 | 2.3757
| INVERARNIE | ST |  |  | 2.9656 | 2.96 | 2.9543 | 2.9468 | 2.9393 | 2.932 | 2.9231 | 2.9144 | 2.9061 | 2.8982 | 2.8712 | 2.8336 | 2.444 | 2.3845 | 2.777 | 2.7737 | 2.7705 | 2.7661 | 2.7618 | 2.7575 | 2.7523 | 2.7472 | 2.4891 | 2.4753 | 2.4317 | 2.3667 | 2.3032 | 2.2457 | 2.8603 | 2.8538 | 2.8471 | 2.8374 | 2.8272 | 2.817 | 2.8064 | 2.7961 | 2.7861 | 2.7776 | 2.7509 | 2.7139 | 2.4738 | 2.4089
| INVERARNIE | SP |  |  | 2.9619 | 2.9544 | 2.9469 | 2.9393 | 2.9282 | 2.9172 | 2.9063 | 2.8956 | 2.8851 | 2.8747 | 2.8444 | 2.4647 | 2.4183 | 2.3742 | 2.7748 | 2.7705 | 2.7662 | 2.7619 | 2.7555 | 2.7492 | 2.743 | 2.7368 | 2.7308 | 2.7248 | 2.4744 | 2.4105 | 2.3565 | 2.3054 | 2.8573 | 2.8494 | 2.8416 | 2.8337 | 2.8216 | 2.8094 | 2.7975 | 2.7857 | 2.7738 | 2.7625 | 2.73 | 2.6675 | 2.6172 | 2.4537
FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | YES | 5.9564 | 5.9558 | 5.9552 | 5.9542 | 5.9506 | 5.9462 | 5.9407 | 5.9341 | 5.8314 | 5.5116 | 4.3123 | 2.7133 | -1.0241 | -2.0467 | 5.9587 | 5.9582 | 5.9575 | 5.9565 | 5.9376 | 5.6096 | 5.2836 | 4.9595 | 4.5479 | 4.1428 | 2.6243 | 0.65433 | -3.3467 | -4.5621 | 5.4579 | 5.4574 | 5.4567 | 5.4557 | 5.4041 | 5.0963 | 4.7904 | 4.4862 | 4.0942 | 3.695 | 2.1637 | 0.1708 | -4.0976 | -5.3272
| INVERBERVIE | CT |  |  | 5.9564 | 5.9558 | 5.9552 | 5.9542 | 5.9506 | 5.9462 | 5.9407 | 5.9341 | 5.9255 | 5.9215 | 5.4043 | 4.2038 | 0.67882 | -0.99564 | 5.9587 | 5.9582 | 5.9575 | 5.9565 | 5.953 | 5.9485 | 5.817 | 5.6487 | 5.4056 | 5.0948 | 4.0135 | 2.5061 | -1.3033 | -3.2805 | 5.4579 | 5.4574 | 5.4567 | 5.4557 | 5.4521 | 5.4187 | 5.29 | 5.1318 | 4.9033 | 4.6116 | 3.5672 | 2.045 | -2.0291 | -4.0286
| INVERBERVIE | LW |  |  | 5.9572 | 5.9572 | 5.9572 | 5.9572 | 5.9561 | 5.9537 | 5.9501 | 5.9449 | 5.8314 | 5.5116 | 4.3123 | 2.7133 | -1.0241 | -2.0467 | 5.9596 | 5.9596 | 5.9596 | 5.9596 | 5.9376 | 5.6096 | 5.2836 | 4.9595 | 4.5479 | 4.1428 | 2.6243 | 0.65433 | -3.3467 | -4.5621 | 5.4588 | 5.4588 | 5.4588 | 5.4588 | 5.4041 | 5.0963 | 4.7904 | 4.4862 | 4.0942 | 3.695 | 2.1637 | 0.1708 | -4.0976 | -5.3272
| INVERBERVIE | ST |  |  | 5.957 | 5.9569 | 5.9567 | 5.9565 | 5.9548 | 5.9526 | 5.9499 | 5.9465 | 5.9416 | 5.9401 | 5.5095 | 3.5569 | 1.0222 | -0.85018 | 5.9594 | 5.9592 | 5.9591 | 5.9589 | 5.9572 | 5.9549 | 5.881 | 5.7188 | 5.488 | 5.1878 | 4.1398 | 2.0729 | -0.57839 | -2.8036 | 5.4585 | 5.4584 | 5.4582 | 5.458 | 5.4563 | 5.4541 | 5.3506 | 5.1983 | 4.9815 | 4.6999 | 3.6921 | 1.4336 | -1.4592 | -3.7104
| INVERBERVIE | SP |  |  | 5.9568 | 5.9565 | 5.9563 | 5.956 | 5.956 | 5.9559 | 5.9558 | 5.9557 | 5.9555 | 5.955 | 5.9526 | 5.9499 | 5.6894 | 5.3071 | 5.9591 | 5.9589 | 5.9586 | 5.9584 | 5.9583 | 5.9582 | 5.9582 | 5.9581 | 5.9579 | 5.9085 | 5.4597 | 4.8937 | 4.3734 | 3.895 | 5.4583 | 5.458 | 5.4578 | 5.4575 | 5.4575 | 5.4574 | 5.4573 | 5.4572 | 5.457 | 5.3767 | 4.9556 | 4.4247 | 3.9219 | 3.4499
GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | 0.29161 | 0.40658 | 0.40656 | 0.40651 | 0.40637 | 0.40619 | 0.40599 | 0.40574 | 0.40548 | 0.40534 | 0.40482 | 0.40364 | 0.40172 | 0.39796 | 0.24929 | 0.36421 | 0.36412 | 0.3639 | 0.36359 | 0.36324 | 0.36287 | 0.3615 | 0.36024 | 0.35913 | 0.35749 | 0.35631 | 0.35438 | 0.30797 | 0.24725 | 0.3622 | 0.36215 | 0.36203 | 0.36183 | 0.36158 | 0.36131 | 0.36062 | 0.35992 | 0.35942 | 0.35826 | 0.35708 | 0.35516 | 0.30816
| INVERBROOM | CT |  |  | 0.29161 | 0.40658 | 0.40656 | 0.40651 | 0.40637 | 0.40619 | 0.40599 | 0.40574 | 0.40548 | 0.40534 | 0.40482 | 0.40364 | 0.40172 | 0.39796 | 0.24929 | 0.36421 | 0.36412 | 0.3639 | 0.36359 | 0.36324 | 0.36287 | 0.3615 | 0.36024 | 0.35913 | 0.35749 | 0.35631 | 0.35438 | 0.30797 | 0.24725 | 0.3622 | 0.36215 | 0.36203 | 0.36183 | 0.36158 | 0.36131 | 0.36062 | 0.35992 | 0.35942 | 0.35826 | 0.35708 | 0.35516 | 0.30816
| INVERBROOM | LW |  |  | 0.29165 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.24933 | 0.36427 | 0.36418 | 0.36395 | 0.3637 | 0.36346 | 0.36322 | 0.36298 | 0.36275 | 0.3625 | 0.3618 | 0.36084 | 0.36003 | 0.35953 | 0.24729 | 0.36227 | 0.36223 | 0.36214 | 0.36204 | 0.36195 | 0.36185 | 0.36176 | 0.36167 | 0.36157 | 0.36128 | 0.36086 | 0.36056 | 0.36026
| INVERBROOM | ST |  |  | 0.29165 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.24935 | 0.36432 | 0.36429 | 0.36421 | 0.36412 | 0.364 | 0.36289 | 0.36181 | 0.36093 | 0.3603 | 0.3594 | 0.35932 | 0.35932 | 0.35932 | 0.2473 | 0.36229 | 0.36227 | 0.36224 | 0.36221 | 0.36216 | 0.36172 | 0.36129 | 0.36089 | 0.36069 | 0.3601 | 0.36009 | 0.36009 | 0.36009
| INVERBROOM | SP |  |  | 0.29165 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.40665 | 0.24938 | 0.36437 | 0.36437 | 0.36436 | 0.36434 | 0.36431 | 0.36395 | 0.36359 | 0.36311 | 0.36279 | 0.36194 | 0.36084 | 0.35998 | 0.35945 | 0.24731 | 0.36231 | 0.3623 | 0.3623 | 0.36229 | 0.36228 | 0.36214 | 0.362 | 0.36181 | 0.36168 | 0.36135 | 0.36086 | 0.36053 | 0.36021
FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | 1.2428 | 1.2427 | 1.1883 | 1.1388 | 1.097 | 0.98509 | 0.91931 | 0.85086 | 0.78023 | 0.70607 | 0.569 | 0.34534 | 0.1481 | -0.047055 | 1.1041 | 1.1037 | 1.0762 | 0.99638 | 0.94253 | 0.87748 | 0.81047 | 0.74031 | 0.66796 | 0.59377 | 0.45846 | 0.23768 | 0.041955 | -0.1519 | 1.1057 | 1.1055 | 1.0549 | 0.98934 | 0.93383 | 0.86704 | 0.79744 | 0.72495 | 0.64951 | 0.572 | 0.43096 | 0.20084 | -0.0028918 | -0.20446
| INVERGARRY | CT |  |  | 1.2428 | 1.2427 | 1.1883 | 1.1388 | 1.097 | 0.98509 | 0.91931 | 0.85086 | 0.78023 | 0.70607 | 0.569 | 0.34534 | 0.1481 | -0.047055 | 1.1041 | 1.1037 | 1.0762 | 0.99638 | 0.94253 | 0.87748 | 0.81047 | 0.74031 | 0.66796 | 0.59377 | 0.45846 | 0.23768 | 0.041955 | -0.1519 | 1.1057 | 1.1055 | 1.0549 | 0.98934 | 0.93383 | 0.86704 | 0.79744 | 0.72495 | 0.64951 | 0.572 | 0.43096 | 0.20084 | -0.0028918 | -0.20446
| INVERGARRY | LW |  |  | 1.2429 | 1.2429 | 1.2188 | 1.1947 | 1.1706 | 1.1465 | 1.124 | 1.1056 | 1.0884 | 1.0732 | 0.97233 | 0.89253 | 0.8111 | 0.72776 | 1.1042 | 1.1038 | 1.0868 | 1.076 | 1.0651 | 1.0541 | 0.98255 | 0.95864 | 0.93484 | 0.91087 | 0.86178 | 0.7791 | 0.69475 | 0.60848 | 1.1058 | 1.1056 | 1.0814 | 1.0574 | 1.0359 | 0.99829 | 0.97424 | 0.9498 | 0.92526 | 0.90053 | 0.84976 | 0.76427 | 0.67706 | 0.58789
| INVERGARRY | ST |  |  | 1.2429 | 1.2429 | 1.2268 | 1.2107 | 1.1947 | 1.1786 | 1.1626 | 1.1464 | 1.1303 | 1.1174 | 1.0828 | 0.95187 | 0.86964 | 0.78548 | 1.1043 | 1.1041 | 1.0907 | 1.0843 | 1.0777 | 1.0708 | 1.062 | 1.0531 | 0.98943 | 0.97283 | 0.92287 | 0.83879 | 0.75315 | 0.66555 | 1.1058 | 1.1057 | 1.0896 | 1.0734 | 1.0591 | 1.0452 | 1.0293 | 0.99764 | 0.98073 | 0.96368 | 0.91239 | 0.82525 | 0.73651 | 0.64577
| INVERGARRY | SP |  |  | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.2429 | 1.1045 | 1.1045 | 1.1044 | 1.1044 | 1.1042 | 1.104 | 1.1033 | 1.1027 | 1.1018 | 1.101 | 1.0988 | 1.0959 | 1.0943 | 1.0938 | 1.1059 | 1.1059 | 1.1059 | 1.1058 | 1.1058 | 1.1057 | 1.1054 | 1.1052 | 1.1048 | 1.1045 | 1.1036 | 1.1024 | 1.1015 | 1.1009
ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | YES | 17.5019 | 17.4996 | 17.4951 | 17.4894 | 17.4745 | 17.4567 | 17.4359 | 14.4054 | 14.1773 | 13.953 | 13.1173 | 11.9951 | 9.9495 | 8.3194 | 19.8546 | 19.8523 | 19.849 | 19.8444 | 19.8306 | 19.8142 | 19.7948 | 19.7724 | 19.7465 | 19.7321 | 19.6848 | 13.5807 | 11.6026 | 9.8218 | 11.2682 | 11.2588 | 11.2441 | 11.2136 | 11.1415 | 11.0723 | 11.0008 | 10.9098 | 10.6466 | 10.3869 | 9.4198 | 8.1576 | 5.8227 | 3.9875
| INVERGORDON | CT |  |  | 17.5019 | 17.4996 | 17.4951 | 17.4894 | 17.4745 | 17.4567 | 17.4359 | 14.4239 | 14.2172 | 13.9786 | 13.183 | 11.9951 | 9.9495 | 8.3194 | 19.8546 | 19.8523 | 19.849 | 19.8444 | 19.8306 | 19.8142 | 19.7948 | 19.7724 | 19.7465 | 19.7321 | 19.6848 | 13.5807 | 11.6026 | 9.8218 | 11.2682 | 11.2588 | 11.2441 | 11.2136 | 11.1415 | 11.0723 | 11.0008 | 10.9181 | 10.7076 | 10.4335 | 9.5192 | 8.1626 | 5.8227 | 3.9875
| INVERGORDON | LW |  |  | 17.5053 | 17.5053 | 17.5053 | 17.5053 | 17.5046 | 17.5031 | 17.5009 | 14.4054 | 14.1773 | 13.953 | 13.1173 | 12.025 | 10.2789 | 9.5923 | 19.858 | 19.858 | 19.858 | 19.858 | 19.8573 | 19.8558 | 19.8536 | 19.8504 | 19.8443 | 19.843 | 19.8374 | 13.6509 | 11.9115 | 11.1451 | 11.278 | 11.2766 | 11.2743 | 11.2688 | 11.1917 | 11.1148 | 11.0379 | 10.9098 | 10.6466 | 10.3869 | 9.4198 | 8.1576 | 6.1385 | 5.3447
| INVERGORDON | ST |  |  | 17.5046 | 17.5041 | 17.5036 | 17.503 | 17.498 | 17.4919 | 17.4847 | 17.4764 | 17.4663 | 14.401 | 13.7191 | 12.7572 | 11.5068 | 10.0983 | 19.8573 | 19.8568 | 19.8563 | 19.8557 | 19.8507 | 19.8446 | 19.8374 | 19.8291 | 19.819 | 19.8158 | 19.8055 | 19.7799 | 13.1941 | 11.7295 | 11.2769 | 11.2749 | 11.2723 | 11.2679 | 11.2308 | 11.1931 | 11.1479 | 11.0945 | 11.0247 | 10.9102 | 10.122 | 9.0118 | 7.5792 | 5.956
| INVERGORDON | SP |  |  | 17.5038 | 17.5029 | 17.5021 | 17.5012 | 17.5011 | 17.5009 | 17.5007 | 17.5005 | 17.5002 | 17.4988 | 17.4939 | 14.2415 | 13.878 | 13.5208 | 19.8565 | 19.8556 | 19.8548 | 19.8539 | 19.8537 | 19.8536 | 19.8534 | 19.8532 | 19.8529 | 19.8515 | 19.8465 | 19.8421 | 19.8026 | 19.7495 | 11.2775 | 11.2765 | 11.2753 | 11.2742 | 11.2655 | 11.2555 | 11.2386 | 11.2219 | 11.2 | 11.1688 | 11.0462 | 10.7213 | 10.3065 | 9.9011
FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | YES | 20.458 | 20.4488 | 20.2442 | 20.0241 | 19.7886 | 19.5105 | 19.2231 | 18.8738 | 18.5157 | 14.427 | 14.0191 | 13.3257 | 12.6427 | 11.3119 | 17.4135 | 17.4024 | 17.286 | 17.1501 | 17.0005 | 16.8278 | 16.6494 | 16.3976 | 16.141 | 13.4905 | 12.7121 | 11.3202 | 9.9692 | 8.4963 | 18.0477 | 18.0433 | 17.7521 | 17.4553 | 17.1418 | 16.7876 | 13.7785 | 13.4784 | 13.1671 | 12.8574 | 12.2841 | 11.3218 | 10.4047 | 9.1402
| INVERLOCHY | CT |  |  | 20.458 | 20.4488 | 20.2442 | 20.0241 | 19.7886 | 19.5105 | 19.2231 | 18.8738 | 18.5157 | 14.427 | 14.0191 | 13.3257 | 12.6427 | 11.3119 | 17.4135 | 17.4024 | 17.286 | 17.1501 | 17.0005 | 16.8278 | 16.6494 | 16.3976 | 16.141 | 13.4905 | 12.7121 | 11.3202 | 9.9692 | 8.4963 | 18.0477 | 18.0433 | 17.7521 | 17.4553 | 17.1418 | 16.7876 | 13.7785 | 13.4784 | 13.1671 | 12.8574 | 12.2841 | 11.3218 | 10.4047 | 9.1402
| INVERLOCHY | LW |  |  | 20.4637 | 20.4581 | 20.3643 | 20.2573 | 20.1482 | 20.0392 | 19.9308 | 19.8226 | 19.7152 | 19.6056 | 19.3624 | 18.9572 | 18.5453 | 18.1271 | 17.4198 | 17.4127 | 17.3568 | 17.2839 | 17.2081 | 17.1328 | 17.0581 | 16.9839 | 16.9105 | 16.8347 | 16.6526 | 16.3524 | 16.048 | 13.6873 | 18.0518 | 18.0501 | 17.9208 | 17.7874 | 17.6538 | 17.5199 | 17.3861 | 17.2519 | 17.1184 | 16.9838 | 16.7061 | 13.7465 | 13.4173 | 13.0801
| INVERLOCHY | ST |  |  | 20.4636 | 20.459 | 20.3964 | 20.3285 | 20.2536 | 20.1748 | 20.0785 | 19.9819 | 19.8855 | 19.7721 | 19.436 | 18.9546 | 18.4244 | 17.9108 | 17.4199 | 17.4142 | 17.3769 | 17.3329 | 17.2807 | 17.224 | 17.1449 | 17.0659 | 16.9872 | 16.8853 | 16.5858 | 16.0972 | 15.5576 | 13.5303 | 18.0514 | 18.0497 | 17.9632 | 17.8749 | 17.7824 | 17.6878 | 17.5872 | 17.4858 | 17.3841 | 17.2803 | 16.969 | 16.4476 | 13.5542 | 13.1812
| INVERLOCHY | SP |  |  | 20.4673 | 20.4662 | 20.4348 | 20.4034 | 20.3699 | 20.337 | 20.2985 | 20.2605 | 20.2202 | 20.1735 | 20.0396 | 19.8368 | 19.6505 | 19.489 | 17.4248 | 17.4235 | 17.4063 | 17.389 | 17.3683 | 17.3473 | 17.3183 | 17.2897 | 17.2575 | 17.2165 | 17.0984 | 16.918 | 16.7406 | 16.5599 | 18.0523 | 18.0516 | 18.006 | 17.9602 | 17.9153 | 17.8722 | 17.8283 | 17.7851 | 17.7424 | 17.6982 | 17.5722 | 17.3846 | 17.2047 | 17.0261
PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | 3.162 | 6.9617 | 6.9598 | 6.9577 | 6.9462 | 6.1747 | 5.8898 | 5.5958 | 5.1979 | 4.9752 | 4.1716 | 3.0282 | 1.384 | 0.76264 | 3.0448 | 6.8401 | 6.8315 | 6.295 | 6.1458 | 5.9682 | 5.6574 | 5.3379 | 4.9077 | 4.6526 | 3.7278 | 2.4287 | 0.53125 | -0.18641 | 3.0058 | 6.8006 | 6.7903 | 6.7695 | 6.6963 | 6.1989 | 5.8908 | 5.5734 | 5.1431 | 4.888 | 3.9629 | 2.6635 | 0.76545 | 0.047577
| INVERNEIL | CT |  |  | 3.162 | 6.9617 | 6.9598 | 6.9577 | 6.9542 | 6.291 | 6.1225 | 5.9428 | 5.6871 | 5.5168 | 4.9614 | 3.8835 | 2.2757 | 1.2928 | 3.0448 | 6.8401 | 6.8315 | 6.295 | 6.1972 | 6.1117 | 5.9326 | 5.7412 | 5.4681 | 5.2746 | 4.6359 | 3.4455 | 1.606 | 0.47496 | 3.0058 | 6.8006 | 6.7903 | 6.7695 | 6.6963 | 6.691 | 6.1476 | 5.9632 | 5.6899 | 5.4967 | 4.8548 | 3.6585 | 1.8137 | 0.6777
| INVERNEIL | LW |  |  | 3.1624 | 6.9624 | 6.9624 | 6.9624 | 6.9618 | 6.1747 | 5.8898 | 5.5958 | 5.1979 | 4.9752 | 4.1716 | 3.0282 | 1.384 | 0.76264 | 3.0487 | 6.8474 | 6.8452 | 6.8398 | 6.1458 | 5.9682 | 5.6574 | 5.3379 | 4.9077 | 4.6526 | 3.7278 | 2.4287 | 0.53125 | -0.18641 | 3.0103 | 6.8087 | 6.8062 | 6.8 | 6.7062 | 6.1989 | 5.8908 | 5.5734 | 5.1431 | 4.888 | 3.9629 | 2.6635 | 0.76545 | 0.047577
| INVERNEIL | ST |  |  | 3.1623 | 6.9623 | 6.9622 | 6.9621 | 6.9462 | 6.929 | 6.2348 | 6.1418 | 6.0063 | 5.8616 | 5.3626 | 4.6427 | 3.6832 | 2.6219 | 3.047 | 6.8444 | 6.8409 | 6.8343 | 6.2251 | 6.1332 | 6.0472 | 5.9413 | 5.7875 | 5.6188 | 5.0358 | 4.2025 | 3.0972 | 1.8592 | 3.0083 | 6.8053 | 6.8013 | 6.7937 | 6.7066 | 6.6734 | 6.2617 | 6.1689 | 6.0197 | 5.8532 | 5.2712 | 4.4376 | 3.332 | 2.0936
| INVERNEIL | SP |  |  | 3.1622 | 6.9621 | 6.9619 | 6.9618 | 6.9618 | 6.9618 | 6.9617 | 6.9617 | 6.9616 | 6.9613 | 6.1004 | 5.8385 | 5.5955 | 5.3728 | 3.0493 | 6.8488 | 6.8483 | 6.8477 | 6.8313 | 6.2908 | 6.2579 | 6.2255 | 6.1824 | 6.1246 | 5.881 | 5.5738 | 5.2918 | 5.0325 | 3.011 | 6.8105 | 6.8099 | 6.8092 | 6.7903 | 6.7686 | 6.7381 | 6.708 | 6.706 | 6.7057 | 6.1133 | 5.8093 | 5.5272 | 5.2679
INVERNESS | INVERNESS 11 kV | MINIMUM HEADROOM | NH 65302 42625 | NO | 14.9161 | 19.4633 | 19.4596 | 19.4546 | 19.4394 | 19.4213 | 19.4002 | 19.376 | 19.3487 | 19.3328 | 19.2812 | 19.1623 | 19.1623 | 18.7887 | 14.0347 | 17.8235 | 17.8074 | 17.7726 | 17.7253 | 17.6756 | 17.6236 | 17.5524 | 17.4788 | 17.413 | 17.2129 | 16.8533 | 16.6103 | 13.6669 | 13.3921 | 17.1867 | 17.1791 | 17.1647 | 17.1393 | 17.1112 | 17.0804 | 17.0413 | 16.9994 | 16.9678 | 16.8693 | 16.6745 | 16.6076 | 13.4577
| INVERNESS 11 kV | CT |  |  | 14.9161 | 19.4633 | 19.4596 | 19.4546 | 19.4394 | 19.4213 | 19.4002 | 19.376 | 19.3487 | 19.3328 | 19.2812 | 19.1623 | 19.1623 | 18.7887 | 14.0347 | 17.8235 | 17.8074 | 17.7726 | 17.7253 | 17.6756 | 17.6236 | 17.5524 | 17.4788 | 17.413 | 17.2129 | 16.8533 | 16.6103 | 13.6669 | 13.3921 | 17.1867 | 17.1791 | 17.1647 | 17.1393 | 17.1112 | 17.0804 | 17.0413 | 16.9994 | 16.9678 | 16.8693 | 16.6745 | 16.6076 | 13.4577
| INVERNESS 11 kV | LW |  |  | 14.9199 | 19.4699 | 19.4699 | 19.4699 | 19.4699 | 19.4699 | 19.4699 | 19.4699 | 19.4699 | 19.4699 | 19.4699 | 19.6635 | 19.6635 | 19.6635 | 14.0449 | 17.8419 | 17.8372 | 17.8253 | 17.8121 | 17.7992 | 17.7866 | 17.7743 | 17.7622 | 17.7491 | 17.7105 | 17.8419 | 17.7792 | 17.7172 | 13.398 | 17.197 | 17.1955 | 17.1918 | 17.1876 | 17.1836 | 17.1796 | 17.1757 | 17.1719 | 17.1678 | 17.1556 | 17.3297 | 17.3099 | 17.2903
| INVERNESS 11 kV | ST |  |  | 14.9189 | 19.4683 | 19.4677 | 19.4669 | 19.4608 | 19.4535 | 19.4449 | 19.4352 | 19.4242 | 19.4206 | 19.4097 | 19.3916 | 19.4911 | 19.4376 | 14.0389 | 17.8313 | 17.8215 | 17.803 | 17.7728 | 17.7367 | 17.6967 | 17.6562 | 17.6151 | 17.5785 | 17.4715 | 17.2992 | 17.2459 | 17.0402 | 13.3954 | 17.1926 | 17.1891 | 17.1827 | 17.169 | 17.1526 | 17.1342 | 17.1147 | 17.0943 | 17.0803 | 17.0391 | 16.9724 | 17.0237 | 16.9222
| INVERNESS 11 kV | SP |  |  | 14.9972 | 19.5461 | 19.545 | 19.5439 | 19.5438 | 19.5436 | 19.5434 | 19.5431 | 19.5429 | 19.5413 | 19.5359 | 19.5317 | 19.5047 | 19.6396 | 14.118 | 17.9162 | 17.9141 | 17.912 | 17.9061 | 17.899 | 17.8884 | 17.8779 | 17.8645 | 17.85 | 17.8073 | 17.7446 | 17.6626 | 17.7458 | 13.4765 | 17.2752 | 17.2738 | 17.2724 | 17.2704 | 17.268 | 17.2645 | 17.2611 | 17.2567 | 17.251 | 17.2338 | 17.2112 | 17.1668 | 17.2855
KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | YES | 44.6491 | 44.6433 | 44.6363 | 44.6262 | 44.4852 | 44.329 | 44.1589 | 43.9752 | 43.7281 | 43.6629 | 43.4818 | 41.5017 | 30.345 | 25.2497 | 38.4272 | 38.3699 | 38.286 | 38.0919 | 37.5282 | 36.9911 | 36.4968 | 36.0097 | 35.395 | 35.0163 | 28.5492 | 24.804 | 22.1613 | 16.3097 | 40.4591 | 40.4286 | 40.3849 | 40.3002 | 40.0175 | 39.7336 | 39.4375 | 39.1343 | 38.7283 | 38.5153 | 37.8904 | 26.0304 | 23.454 | 17.6629
| INVERURIE | CT |  |  | 44.6491 | 44.6433 | 44.6363 | 44.6262 | 44.4852 | 44.329 | 44.1589 | 43.9752 | 43.7281 | 43.6629 | 43.4818 | 41.5017 | 30.345 | 25.2497 | 38.4272 | 38.3699 | 38.286 | 38.0919 | 37.5282 | 36.9911 | 36.4968 | 36.0097 | 35.395 | 35.0163 | 28.5492 | 24.804 | 22.1613 | 16.3097 | 40.4591 | 40.4286 | 40.3849 | 40.3002 | 40.0175 | 39.7336 | 39.4375 | 39.1343 | 38.7283 | 38.5153 | 37.8904 | 26.0304 | 23.454 | 17.6629
| INVERURIE | LW |  |  | 44.6578 | 44.6578 | 44.6578 | 44.6578 | 44.6552 | 44.6498 | 44.6416 | 44.6298 | 44.6076 | 44.6029 | 44.5826 | 43.3404 | 43.0709 | 43.0353 | 38.4858 | 38.4779 | 38.4654 | 38.4341 | 37.8796 | 37.3283 | 36.8533 | 36.3862 | 36.0015 | 35.6453 | 35.5718 | 28.4253 | 27.2224 | 24.3865 | 40.4917 | 40.4879 | 40.4819 | 40.4669 | 40.2483 | 40.0599 | 39.8705 | 39.6795 | 39.4769 | 39.3257 | 39.2832 | 37.6972 | 28.3587 | 25.6831
| INVERURIE | ST |  |  | 44.6557 | 44.6542 | 44.6528 | 44.6511 | 44.6365 | 44.6188 | 44.5979 | 44.5733 | 44.5431 | 44.5334 | 44.5026 | 43.8347 | 43.434 | 29.5364 | 38.4586 | 38.4295 | 38.3911 | 38.3182 | 38.0079 | 37.6881 | 37.3923 | 37.066 | 36.6652 | 36.2121 | 35.1904 | 28.4275 | 23.5153 | 20.5319 | 40.4776 | 40.4628 | 40.4437 | 40.408 | 40.2789 | 40.1599 | 40.0468 | 39.9128 | 39.7368 | 39.5412 | 39.0776 | 38.1414 | 24.9977 | 22.0546
| INVERURIE | SP |  |  | 44.6535 | 44.6512 | 44.6488 | 44.6463 | 44.6459 | 44.6455 | 44.6449 | 44.6443 | 44.6434 | 44.6396 | 44.6251 | 44.6119 | 44.4862 | 44.3332 | 38.4832 | 38.4767 | 38.4694 | 38.4615 | 38.3798 | 38.2851 | 38.1638 | 38.0443 | 37.8864 | 37.6837 | 36.9229 | 36.1461 | 35.5497 | 34.9551 | 40.4882 | 40.4839 | 40.4791 | 40.4741 | 40.4347 | 40.3892 | 40.3367 | 40.2963 | 40.2428 | 40.1722 | 39.8879 | 39.5397 | 39.2178 | 38.8808
DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | 2.8052 | 2.8037 | 2.8016 | 2.796 | 2.7401 | 2.6896 | 2.4753 | 2.4128 | 2.326 | 2.3051 | 2.2447 | 2.1212 | 2.0217 | 1.9651 | 2.6724 | 2.6717 | 2.6707 | 2.6688 | 2.6181 | 2.4567 | 2.3968 | 2.3333 | 2.2454 | 2.2235 | 2.1599 | 2.0312 | 1.9265 | 1.8648 | 2.7302 | 2.7299 | 2.7295 | 2.7289 | 2.6812 | 2.4705 | 2.4108 | 2.3472 | 2.2592 | 2.2371 | 2.1731 | 2.0437 | 1.9384 | 1.8759
| KAMES | CT |  |  | 2.8052 | 2.8037 | 2.8016 | 2.7967 | 2.7904 | 2.7838 | 2.7811 | 2.7781 | 2.7748 | 2.773 | 2.7666 | 2.4261 | 2.3232 | 2.1987 | 2.6724 | 2.6717 | 2.6707 | 2.6688 | 2.6654 | 2.6618 | 2.6577 | 2.6501 | 2.6422 | 2.4889 | 2.427 | 2.3223 | 2.2073 | 2.0708 | 2.7302 | 2.7299 | 2.7295 | 2.7289 | 2.7271 | 2.7249 | 2.7223 | 2.7194 | 2.7161 | 2.7142 | 2.4393 | 2.333 | 2.2164 | 2.0784
| KAMES | LW |  |  | 2.8056 | 2.8041 | 2.8018 | 2.796 | 2.7401 | 2.6896 | 2.4753 | 2.4128 | 2.326 | 2.3051 | 2.2447 | 2.1212 | 2.0217 | 1.9651 | 2.6729 | 2.6724 | 2.6716 | 2.6697 | 2.6181 | 2.4567 | 2.3968 | 2.3333 | 2.2454 | 2.2235 | 2.1599 | 2.0312 | 1.9265 | 1.8648 | 2.7307 | 2.7307 | 2.7307 | 2.7307 | 2.6812 | 2.4705 | 2.4108 | 2.3472 | 2.2592 | 2.2371 | 2.1731 | 2.0437 | 1.9384 | 1.8759
| KAMES | ST |  |  | 2.8062 | 2.8054 | 2.8044 | 2.8025 | 2.7997 | 2.7963 | 2.788 | 2.7875 | 2.7868 | 2.7866 | 2.786 | 2.785 | 2.4709 | 2.4186 | 2.673 | 2.6728 | 2.6724 | 2.6718 | 2.6706 | 2.6692 | 2.6658 | 2.6624 | 2.6591 | 2.6556 | 2.4906 | 2.432 | 2.3697 | 2.3098 | 2.7306 | 2.7306 | 2.7306 | 2.7305 | 2.7302 | 2.7297 | 2.7293 | 2.7287 | 2.7281 | 2.7279 | 2.7273 | 2.4441 | 2.3808 | 2.3199
| KAMES | SP |  |  | 2.8068 | 2.8067 | 2.8065 | 2.8064 | 2.8034 | 2.8004 | 2.7952 | 2.7899 | 2.7821 | 2.7738 | 2.7555 | 2.7416 | 2.389 | 2.321 | 2.6732 | 2.6732 | 2.6731 | 2.673 | 2.6705 | 2.668 | 2.6648 | 2.6614 | 2.656 | 2.6503 | 2.6307 | 2.4834 | 2.3054 | 2.2348 | 2.7306 | 2.7305 | 2.7305 | 2.7305 | 2.7282 | 2.726 | 2.7238 | 2.7213 | 2.7171 | 2.7127 | 2.6968 | 2.4971 | 2.3188 | 2.2478
KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | YES | 21.6417 | 21.5524 | 21.466 | 21.355 | 21.1305 | 20.8985 | 20.6601 | 20.416 | 20.1094 | 13.6186 | 11.7817 | 7.7224 | 4.1996 | -1.4207 | 19.0048 | 18.9411 | 18.8835 | 18.7982 | 18.4055 | 18.0615 | 17.7375 | 13.4396 | 11.8692 | 10.5449 | 8.4428 | 3.7787 | -0.35485 | -6.4151 | 19.0755 | 18.98 | 18.8855 | 18.7579 | 18.4088 | 18.0709 | 17.7278 | 12.8384 | 11.2436 | 9.8949 | 7.7517 | 3.057 | -1.0635 | -7.3851
| KEITH | CT |  |  | 21.6417 | 21.5524 | 21.466 | 21.355 | 21.1305 | 20.8985 | 20.6601 | 20.416 | 20.1094 | 20.0157 | 12.3821 | 8.1942 | 4.3938 | -1.4207 | 19.0048 | 18.9411 | 18.8835 | 18.7982 | 18.4055 | 18.0615 | 17.7375 | 17.5209 | 17.2545 | 13.0282 | 9.4248 | 4.7534 | 0.33791 | -6.4151 | 19.0755 | 18.98 | 18.8855 | 18.7579 | 18.4088 | 18.0709 | 17.7278 | 17.4121 | 13.3824 | 12.2814 | 8.6047 | 3.8178 | -0.59696 | -7.3851
| KEITH | LW |  |  | 21.7238 | 21.7165 | 21.7095 | 21.7014 | 21.5223 | 21.3351 | 21.1373 | 20.921 | 20.606 | 13.6186 | 11.7817 | 7.7224 | 4.1996 | 0.69255 | 19.0774 | 19.0659 | 19.0509 | 19.0205 | 18.4056 | 18.1377 | 17.9444 | 13.4396 | 11.8692 | 10.5449 | 8.4428 | 3.7787 | -0.35485 | -4.4065 | 19.1624 | 19.1535 | 19.1438 | 19.1294 | 18.6968 | 18.3236 | 18.1259 | 12.8384 | 11.2436 | 9.8949 | 7.7517 | 3.057 | -1.0635 | -5.1408
| KEITH | ST |  |  | 21.726 | 21.7207 | 21.7155 | 21.7085 | 21.6762 | 21.5827 | 21.4906 | 21.3865 | 21.2239 | 21.1837 | 14.0842 | 10.518 | 4.2444 | -0.25714 | 19.0814 | 19.0743 | 19.0663 | 19.0534 | 18.8296 | 18.5757 | 18.3394 | 18.1885 | 18.0289 | 17.9916 | 10.9959 | 6.9156 | -0.2026 | -5.4356 | 19.1654 | 19.1592 | 19.1528 | 19.1438 | 19.0138 | 18.8283 | 18.638 | 18.4104 | 18.2124 | 18.1723 | 10.3469 | 6.2016 | -1.0146 | -6.2594
| KEITH | SP |  |  | 21.7228 | 21.7161 | 21.7094 | 21.7026 | 21.6898 | 21.6772 | 21.6646 | 21.6516 | 21.6363 | 21.6202 | 21.5668 | 21.4894 | 21.1134 | 13.3049 | 19.082 | 19.0765 | 19.071 | 19.0654 | 18.9826 | 18.9223 | 18.8307 | 18.7401 | 18.62 | 18.4876 | 18.3947 | 13.6893 | 11.7685 | 10.1487 | 19.1629 | 19.1558 | 19.1488 | 19.1418 | 19.1031 | 19.0609 | 19.0012 | 18.9419 | 18.865 | 18.7648 | 18.5559 | 13.0661 | 11.1087 | 9.4544
KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | YES | 18.6443 | 18.6424 | 18.6402 | 18.637 | 18.626 | 18.6129 | 18.5972 | 18.579 | 18.5574 | 18.5459 | 18.5074 | 13.4835 | 11.2514 | 9.9865 | 16.4684 | 16.4593 | 16.4465 | 16.4177 | 16.3001 | 16.1319 | 15.9749 | 15.8455 | 15.7688 | 15.7213 | 12.5685 | 10.9333 | 8.2796 | 6.8894 | 16.7631 | 16.7584 | 16.752 | 16.7387 | 16.6892 | 16.6306 | 16.5629 | 16.4945 | 16.4327 | 16.3783 | 12.699 | 11.0875 | 8.4724 | 7.0919
| KEMNAY | CT |  |  | 18.6443 | 18.6424 | 18.6402 | 18.637 | 18.626 | 18.6129 | 18.5972 | 18.579 | 18.5574 | 18.5459 | 18.5074 | 14.1223 | 11.7459 | 9.9865 | 16.4684 | 16.4593 | 16.4465 | 16.4177 | 16.3089 | 16.2106 | 16.1107 | 15.9866 | 15.8437 | 15.7213 | 13.2441 | 11.732 | 8.9319 | 6.8894 | 16.7631 | 16.7584 | 16.752 | 16.7387 | 16.6892 | 16.6426 | 16.5938 | 16.5339 | 16.4561 | 16.3824 | 13.3631 | 11.8715 | 9.1103 | 7.0919
| KEMNAY | LW |  |  | 18.6472 | 18.6472 | 18.6472 | 18.6472 | 18.6462 | 18.6442 | 18.6412 | 18.6369 | 18.6287 | 18.627 | 18.6195 | 13.4835 | 11.2514 | 10.4059 | 16.4779 | 16.4765 | 16.4744 | 16.469 | 16.3001 | 16.1319 | 15.9749 | 15.8455 | 15.7688 | 15.7499 | 12.5685 | 10.9333 | 8.2796 | 7.2748 | 16.7686 | 16.768 | 16.7672 | 16.7651 | 16.698 | 16.6306 | 16.5629 | 16.4945 | 16.4327 | 16.3783 | 12.699 | 11.0875 | 8.4724 | 7.4748
| KEMNAY | ST |  |  | 18.6465 | 18.646 | 18.6456 | 18.6451 | 18.6405 | 18.6349 | 18.6283 | 18.6205 | 18.6108 | 18.6077 | 18.5977 | 14.536 | 13.0636 | 11.3713 | 16.4713 | 16.4648 | 16.4563 | 16.4401 | 16.352 | 16.2625 | 16.1781 | 16.0761 | 15.9476 | 15.8151 | 13.5182 | 12.1918 | 10.4568 | 8.4505 | 16.7656 | 16.7627 | 16.7591 | 16.7524 | 16.715 | 16.6764 | 16.6391 | 16.5943 | 16.534 | 16.4642 | 13.6344 | 12.3271 | 10.6162 | 8.6386
| KEMNAY | SP |  |  | 18.6458 | 18.6451 | 18.6444 | 18.6437 | 18.6435 | 18.6434 | 18.6432 | 18.643 | 18.6427 | 18.6415 | 18.637 | 18.6327 | 18.5902 | 18.542 | 16.4767 | 16.4751 | 16.4734 | 16.4715 | 16.449 | 16.423 | 16.3879 | 16.3532 | 16.3074 | 16.2455 | 15.9975 | 15.7894 | 15.7143 | 13.3484 | 16.7673 | 16.7662 | 16.7651 | 16.7639 | 16.755 | 16.7447 | 16.7307 | 16.717 | 16.6988 | 16.6737 | 16.5717 | 16.458 | 16.3452 | 13.4663
TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | 0.6146 | 0.61452 | 0.5991 | 0.58426 | 0.56875 | 0.5532 | 0.49075 | 0.46304 | 0.4344 | 0.40525 | 0.35262 | 0.26534 | 0.18636 | 0.10521 | 0.58055 | 0.58029 | 0.56425 | 0.55531 | 0.5463 | 0.49082 | 0.46475 | 0.43707 | 0.40853 | 0.37941 | 0.32532 | 0.23651 | 0.15599 | 0.073252 | 0.58926 | 0.58889 | 0.57188 | 0.55422 | 0.5358 | 0.48805 | 0.46485 | 0.43731 | 0.40884 | 0.3791 | 0.32296 | 0.23082 | 0.14746 | 0.062007
| KENMORE | CT |  |  | 0.6146 | 0.61452 | 0.5991 | 0.58426 | 0.56875 | 0.5532 | 0.49075 | 0.46304 | 0.4344 | 0.40525 | 0.35262 | 0.26534 | 0.18636 | 0.10521 | 0.58055 | 0.58029 | 0.56425 | 0.55531 | 0.5463 | 0.49082 | 0.46475 | 0.43707 | 0.40853 | 0.37941 | 0.32532 | 0.23651 | 0.15599 | 0.073252 | 0.58926 | 0.58889 | 0.57188 | 0.55422 | 0.5358 | 0.48805 | 0.46485 | 0.43731 | 0.40884 | 0.3791 | 0.32296 | 0.23082 | 0.14746 | 0.062007
| KENMORE | LW |  |  | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.6147 | 0.58064 | 0.58041 | 0.58005 | 0.57914 | 0.57814 | 0.57716 | 0.57635 | 0.57559 | 0.57485 | 0.57476 | 0.57476 | 0.57476 | 0.57476 | 0.57476 | 0.58934 | 0.58897 | 0.58859 | 0.58823 | 0.58784 | 0.58779 | 0.58779 | 0.58779 | 0.58779 | 0.58779 | 0.58779 | 0.58779 | 0.58779 | 0.58779
| KENMORE | ST |  |  | 0.61467 | 0.61465 | 0.61463 | 0.61461 | 0.61443 | 0.61419 | 0.61393 | 0.61362 | 0.61328 | 0.61317 | 0.61284 | 0.61227 | 0.60933 | 0.60767 | 0.5807 | 0.58056 | 0.58039 | 0.58009 | 0.57952 | 0.57882 | 0.5778 | 0.57673 | 0.57565 | 0.57441 | 0.57289 | 0.57232 | 0.56939 | 0.56772 | 0.58946 | 0.58926 | 0.589 | 0.58855 | 0.58822 | 0.58779 | 0.58724 | 0.5867 | 0.58637 | 0.58625 | 0.58592 | 0.58536 | 0.58242 | 0.58076
| KENMORE | SP |  |  | 0.61466 | 0.61463 | 0.61461 | 0.61458 | 0.61458 | 0.61457 | 0.61457 | 0.61456 | 0.61456 | 0.61452 | 0.61439 | 0.61429 | 0.61366 | 0.61229 | 0.58079 | 0.58075 | 0.58071 | 0.58066 | 0.58055 | 0.58042 | 0.58015 | 0.57989 | 0.57956 | 0.57897 | 0.57728 | 0.57507 | 0.57372 | 0.57235 | 0.58962 | 0.58957 | 0.58951 | 0.58946 | 0.58928 | 0.58907 | 0.58864 | 0.58844 | 0.58831 | 0.58805 | 0.58748 | 0.58738 | 0.58675 | 0.58538
STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | YES | 8.2239 | 9.5226 | 9.521 | 9.5187 | 9.5112 | 9.5024 | 9.492 | 9.48 | 9.4665 | 9.4588 | 9.4331 | 9.4553 | 9.4157 | 9.5072 | 6.8384 | 8.1347 | 8.1295 | 8.1187 | 8.102 | 8.0842 | 8.065 | 8.0329 | 8.0045 | 7.9806 | 7.9069 | 7.9261 | 7.837 | 6.1893 | 7.8163 | 9.1142 | 9.1114 | 9.1064 | 9.0961 | 9.0844 | 9.0713 | 9.0529 | 9.0331 | 9.0187 | 8.973 | 8.9895 | 8.9293 | 8.9473
| KEPCULLOCH | CT |  |  | 8.2239 | 9.5226 | 9.521 | 9.5187 | 9.5112 | 9.5024 | 9.492 | 9.48 | 9.4665 | 9.4588 | 9.4331 | 9.7195 | 9.6214 | 9.5072 | 6.8384 | 8.1347 | 8.1295 | 8.1187 | 8.102 | 8.0842 | 8.065 | 8.0329 | 8.0045 | 7.9806 | 7.9069 | 8.1314 | 7.9546 | 6.1893 | 7.8163 | 9.1142 | 9.1114 | 9.1064 | 9.0961 | 9.0844 | 9.0713 | 9.0529 | 9.0331 | 9.0187 | 8.973 | 9.2247 | 9.0939 | 8.9473
| KEPCULLOCH | LW |  |  | 8.2259 | 9.5259 | 9.5259 | 9.5259 | 9.5259 | 9.5259 | 9.5259 | 9.5259 | 9.5259 | 9.5259 | 9.5259 | 9.9475 | 9.9475 | 9.9475 | 6.8419 | 8.1408 | 8.1389 | 8.1343 | 8.1291 | 8.1241 | 8.1191 | 8.1143 | 8.1096 | 8.1045 | 8.0894 | 8.5062 | 8.4877 | 8.4693 | 7.8187 | 9.1184 | 9.1178 | 9.1163 | 9.1147 | 9.1131 | 9.1115 | 9.11 | 9.1085 | 9.1069 | 9.1022 | 9.5139 | 9.5062 | 9.4986
| KEPCULLOCH | ST |  |  | 8.2255 | 9.5252 | 9.525 | 9.5247 | 9.5221 | 9.519 | 9.5154 | 9.5113 | 9.5067 | 9.5052 | 9.5006 | 9.4553 | 9.4157 | 9.89 | 6.8411 | 8.1395 | 8.1376 | 8.1339 | 8.1268 | 8.1184 | 8.0996 | 8.0806 | 8.0614 | 8.0489 | 8.0132 | 7.9261 | 7.837 | 8.262 | 7.8182 | 9.1175 | 9.1167 | 9.1153 | 9.1113 | 9.1066 | 9.0982 | 9.0894 | 9.0802 | 9.0742 | 9.0567 | 8.9895 | 8.9293 | 9.383
| KEPCULLOCH | SP |  |  | 8.2251 | 9.5247 | 9.5243 | 9.5239 | 9.5239 | 9.5238 | 9.5237 | 9.5236 | 9.5235 | 9.5229 | 9.5209 | 9.5193 | 9.509 | 9.5625 | 6.8421 | 8.1415 | 8.1408 | 8.1402 | 8.1388 | 8.1372 | 8.1322 | 8.1273 | 8.121 | 8.1149 | 8.0969 | 8.0708 | 8.0428 | 8.0796 | 7.8183 | 9.1178 | 9.1173 | 9.1168 | 9.1163 | 9.1158 | 9.1142 | 9.1125 | 9.1105 | 9.1082 | 9.1011 | 9.0916 | 9.0739 | 9.1204
TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351
| KERRERA | CT |  |  | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351
| KERRERA | LW |  |  | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351
| KERRERA | ST |  |  | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351
| KERRERA | SP |  |  | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.34488 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.3351
GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | 5.0992 | 5.0986 | 5.0404 | 4.982 | 4.9197 | 4.8446 | 4.7666 | 4.6265 | 4.4794 | 4.3307 | 4.0516 | 3.5896 | 3.1614 | 2.7027 | 4.7528 | 4.7521 | 4.7262 | 4.6999 | 4.6706 | 4.5622 | 4.4299 | 4.286 | 4.133 | 3.9781 | 3.6827 | 3.1945 | 2.7346 | 2.2432 | 4.4483 | 4.4476 | 4.3558 | 4.2484 | 4.1356 | 4.0004 | 3.8606 | 3.707 | 3.5486 | 3.3881 | 3.0805 | 2.5722 | 2.0995 | 1.5974
| KERRY FALLS | CT |  |  | 5.0992 | 5.0986 | 5.0404 | 4.982 | 4.9197 | 4.8446 | 4.7666 | 4.6265 | 4.4794 | 4.3307 | 4.0516 | 3.5896 | 3.1614 | 2.7027 | 4.7528 | 4.7521 | 4.7262 | 4.6999 | 4.6706 | 4.5622 | 4.4299 | 4.286 | 4.133 | 3.9781 | 3.6827 | 3.1945 | 2.7346 | 2.2432 | 4.4483 | 4.4476 | 4.3558 | 4.2484 | 4.1356 | 4.0004 | 3.8606 | 3.707 | 3.5486 | 3.3881 | 3.0805 | 2.5722 | 2.0995 | 1.5974
| KERRY FALLS | LW |  |  | 5.1001 | 5.1001 | 5.0747 | 5.0492 | 5.0239 | 4.9984 | 4.973 | 4.9474 | 4.922 | 4.8964 | 4.845 | 4.7154 | 4.5508 | 4.3825 | 4.7537 | 4.7537 | 4.7425 | 4.7313 | 4.7202 | 4.709 | 4.6978 | 4.6866 | 4.6536 | 4.6094 | 4.5152 | 4.3529 | 4.1855 | 4.0067 | 4.4492 | 4.4492 | 4.4151 | 4.3652 | 4.315 | 4.2648 | 4.2146 | 4.1643 | 4.1143 | 4.0638 | 3.9581 | 3.7805 | 3.5996 | 3.4149
| KERRY FALLS | ST |  |  | 5.1 | 5.1 | 5.0829 | 5.0659 | 5.0484 | 5.0307 | 5.0128 | 4.9948 | 4.9767 | 4.9593 | 4.9068 | 4.7918 | 4.5984 | 4.4038 | 4.7536 | 4.7535 | 4.746 | 4.7385 | 4.7304 | 4.7222 | 4.7139 | 4.7054 | 4.6968 | 4.689 | 4.5939 | 4.4018 | 4.1997 | 3.9986 | 4.4491 | 4.449 | 4.4264 | 4.4001 | 4.3673 | 4.3339 | 4.2961 | 4.2582 | 4.2205 | 4.1808 | 4.0598 | 3.8527 | 3.6231 | 3.3947
| KERRY FALLS | SP |  |  | 5.1 | 5.0999 | 5.0999 | 5.0998 | 5.0998 | 5.0998 | 5.0997 | 5.0997 | 5.0997 | 5.0996 | 5.0992 | 5.0989 | 5.0971 | 5.0932 | 4.7535 | 4.7535 | 4.7534 | 4.7533 | 4.7533 | 4.7533 | 4.7533 | 4.7533 | 4.7532 | 4.7531 | 4.7528 | 4.7525 | 4.7507 | 4.7467 | 4.4491 | 4.449 | 4.4489 | 4.4488 | 4.4488 | 4.4488 | 4.4488 | 4.4488 | 4.4456 | 4.4396 | 4.4225 | 4.3932 | 4.3625 | 4.3304
TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | 1.6029 | 1.6004 | 1.5686 | 1.5319 | 0.97067 | 0.92543 | 0.87946 | 0.83468 | 0.78869 | 0.74161 | 0.64209 | 0.47839 | 0.32233 | 0.15863 | 1.5176 | 1.5162 | 1.4814 | 1.444 | 1.4048 | 1.3586 | 1.311 | 1.2812 | 1.2512 | 1.2213 | 0.90416 | 0.73711 | 0.58249 | 0.42093 | 1.5451 | 1.545 | 1.5096 | 1.4742 | 1.4372 | 1.3926 | 1.3466 | 0.96195 | 0.91017 | 0.85704 | 0.7449 | 0.56072 | 0.3858 | 0.20373
| KILCHRENAN | CT |  |  | 1.6029 | 1.6004 | 1.5686 | 1.5319 | 0.97067 | 0.92543 | 0.87946 | 0.83468 | 0.78869 | 0.74161 | 0.64209 | 0.47839 | 0.32233 | 0.15863 | 1.5176 | 1.5162 | 1.4814 | 1.444 | 1.4048 | 1.3586 | 1.311 | 1.2812 | 1.2512 | 1.2213 | 0.90416 | 0.73711 | 0.58249 | 0.42093 | 1.5451 | 1.545 | 1.5096 | 1.4742 | 1.4372 | 1.3926 | 1.3466 | 0.96195 | 0.91017 | 0.85704 | 0.7449 | 0.56072 | 0.3858 | 0.20373
| KILCHRENAN | LW |  |  | 1.6045 | 1.6032 | 1.6012 | 1.5961 | 1.5904 | 1.5848 | 1.5794 | 1.574 | 1.5688 | 1.5632 | 0.98877 | 0.94407 | 0.89908 | 0.85452 | 1.5186 | 1.5179 | 1.5168 | 1.5142 | 1.5112 | 1.5083 | 1.5055 | 1.5027 | 1.5 | 1.497 | 1.4884 | 1.4744 | 1.4603 | 1.4463 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 0.98368
| KILCHRENAN | ST |  |  | 1.605 | 1.6044 | 1.6036 | 1.6019 | 1.5998 | 1.5972 | 1.5914 | 1.5858 | 1.5803 | 1.5757 | 1.5625 | 0.97984 | 0.945 | 0.91021 | 1.5189 | 1.5185 | 1.5181 | 1.5172 | 1.5161 | 1.5147 | 1.5118 | 1.5088 | 1.506 | 1.5036 | 1.4966 | 1.4856 | 1.4747 | 1.4638 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454
| KILCHRENAN | SP |  |  | 1.6056 | 1.6056 | 1.6055 | 1.6053 | 1.6047 | 1.604 | 1.6022 | 1.6004 | 1.5981 | 1.5963 | 1.591 | 1.5828 | 1.5752 | 1.568 | 1.5192 | 1.5191 | 1.5191 | 1.519 | 1.5187 | 1.5183 | 1.5174 | 1.5164 | 1.5152 | 1.5143 | 1.5115 | 1.5073 | 1.5033 | 1.4995 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454 | 1.5454
STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | 7.1044 | 7.1032 | 7.1018 | 7.0998 | 7.0926 | 7.0839 | 7.0734 | 7.061 | 4.7234 | 4.36 | 2.9463 | 1.0919 | -2.0016 | -3.1647 | 6.3974 | 6.3901 | 6.3795 | 6.3556 | 6.2602 | 6.1206 | 4.8612 | 4.4999 | 4.0392 | 3.5864 | 1.8839 | -0.34661 | -3.9814 | -5.3484 | 6.7608 | 6.7597 | 6.7583 | 6.7562 | 6.7491 | 6.7403 | 6.7298 | 4.6707 | 4.2109 | 3.759 | 2.0599 | -0.13835 | -3.7441 | -5.1071
| KILLEARN | CT |  |  | 7.1044 | 7.1032 | 7.1018 | 7.0998 | 7.0926 | 7.0839 | 7.0734 | 7.061 | 7.0455 | 4.9908 | 3.9832 | 2.4966 | -0.46235 | -2.5069 | 6.3974 | 6.3901 | 6.3795 | 6.3556 | 6.2663 | 6.1858 | 6.1045 | 6.0515 | 4.7438 | 4.3834 | 3.1328 | 1.373 | -2.1352 | -4.51 | 6.7608 | 6.7597 | 6.7583 | 6.7562 | 6.7491 | 6.7403 | 6.7298 | 6.7174 | 4.914 | 4.5544 | 3.3062 | 1.5528 | -1.9032 | -4.2723
| KILLEARN | LW |  |  | 7.1062 | 7.1062 | 7.1062 | 7.1062 | 7.1049 | 7.1022 | 7.0981 | 7.0923 | 4.7234 | 4.36 | 2.9463 | 1.0919 | -2.0016 | -3.1647 | 6.4053 | 6.4045 | 6.4032 | 6.3999 | 6.2602 | 6.1206 | 4.8612 | 4.4999 | 4.0392 | 3.5864 | 1.8839 | -0.34661 | -3.9814 | -5.3484 | 6.7627 | 6.7627 | 6.7627 | 6.7627 | 6.7613 | 6.7587 | 6.7546 | 4.6707 | 4.2109 | 3.759 | 2.0599 | -0.13835 | -3.7441 | -5.1071
| KILLEARN | ST |  |  | 7.1058 | 7.1055 | 7.1053 | 7.1049 | 7.1019 | 7.0981 | 7.0936 | 7.0881 | 7.0806 | 7.0783 | 4.1578 | 2.7839 | 0.95883 | -1.2414 | 6.3996 | 6.394 | 6.3868 | 6.3729 | 6.2997 | 6.2254 | 6.1626 | 6.0874 | 4.8796 | 4.5354 | 3.3363 | 1.6953 | -0.48977 | -3.0713 | 6.7622 | 6.762 | 6.7617 | 6.7614 | 6.7583 | 6.7546 | 6.75 | 6.7445 | 6.7371 | 4.7061 | 3.5094 | 1.8719 | -0.28051 | -2.8371
| KILLEARN | SP |  |  | 7.1054 | 7.1049 | 7.1045 | 7.104 | 7.1039 | 7.1038 | 7.1037 | 7.1035 | 7.1033 | 7.1024 | 7.0988 | 4.9685 | 4.4794 | 4.0255 | 6.4043 | 6.4032 | 6.402 | 6.4007 | 6.3825 | 6.3615 | 6.3343 | 6.3076 | 6.2721 | 6.2254 | 4.9891 | 4.3415 | 3.7424 | 3.1853 | 6.7618 | 6.7614 | 6.7609 | 6.7604 | 6.7603 | 6.7602 | 6.7601 | 6.7599 | 6.7597 | 6.7588 | 6.7552 | 4.5126 | 3.9146 | 3.3586
KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | 3.6769 | 3.6764 | 3.609 | 3.5413 | 3.4701 | 3.3841 | 3.2952 | 2.3355 | 2.1519 | 1.9652 | 1.6276 | 1.0724 | 0.57257 | 0.055895 | 3.0415 | 3.0398 | 2.9328 | 2.8781 | 2.8199 | 2.4144 | 2.2628 | 2.0852 | 1.9021 | 1.7155 | 1.3683 | 0.79768 | 0.27882 | -0.25699 | 3.195 | 3.1926 | 3.0839 | 2.9709 | 2.8529 | 2.4813 | 2.3454 | 2.1621 | 1.9732 | 1.7807 | 1.421 | 0.83013 | 0.29261 | -0.26135
| KILLIN TOWN | CT |  |  | 3.6769 | 3.6764 | 3.609 | 3.5413 | 3.4701 | 3.3841 | 3.2952 | 2.3355 | 2.1519 | 1.9652 | 1.6276 | 1.0724 | 0.57257 | 0.055895 | 3.0415 | 3.0398 | 2.9328 | 2.8781 | 2.8199 | 2.4144 | 2.2628 | 2.0852 | 1.9021 | 1.7155 | 1.3683 | 0.79768 | 0.27882 | -0.25699 | 3.195 | 3.1926 | 3.0839 | 2.9709 | 2.8529 | 2.4813 | 2.3454 | 2.1621 | 1.9732 | 1.7807 | 1.421 | 0.83013 | 0.29261 | -0.26135
| KILLIN TOWN | LW |  |  | 3.6776 | 3.6776 | 3.6479 | 3.6182 | 3.5887 | 3.559 | 3.5294 | 3.4996 | 3.4699 | 3.4401 | 3.3802 | 2.4694 | 2.2652 | 2.0559 | 3.0421 | 3.0406 | 2.9881 | 2.932 | 2.8969 | 2.8655 | 2.8411 | 2.8248 | 2.8099 | 2.4643 | 2.3486 | 2.1509 | 1.9495 | 1.7303 | 3.1955 | 3.1932 | 3.1427 | 3.0865 | 3.0295 | 2.9725 | 2.9158 | 2.862 | 2.8197 | 2.7773 | 2.4235 | 2.2138 | 2.0005 | 1.7836
| KILLIN TOWN | ST |  |  | 3.6774 | 3.6773 | 3.6574 | 3.6375 | 3.6168 | 3.5958 | 3.5745 | 3.553 | 3.5314 | 3.5109 | 3.4492 | 3.3449 | 2.3895 | 2.1672 | 3.0426 | 3.0417 | 3.0072 | 2.9718 | 2.9349 | 2.914 | 2.8885 | 2.863 | 2.8411 | 2.826 | 2.4653 | 2.2613 | 2.0335 | 1.8086 | 3.1964 | 3.1951 | 3.1623 | 3.128 | 3.0919 | 3.0547 | 3.0123 | 2.9698 | 2.9275 | 2.8817 | 2.7945 | 2.318 | 2.073 | 1.831
| KILLIN TOWN | SP |  |  | 3.6773 | 3.6771 | 3.6769 | 3.6768 | 3.6768 | 3.6767 | 3.6767 | 3.6767 | 3.6766 | 3.6764 | 3.6756 | 3.6749 | 3.6708 | 3.6619 | 3.0432 | 3.0429 | 3.0426 | 3.0423 | 3.0416 | 3.0407 | 3.0383 | 3.036 | 3.033 | 3.0292 | 3.0185 | 3.0137 | 3.0056 | 2.993 | 3.1973 | 3.197 | 3.1967 | 3.1963 | 3.1951 | 3.1938 | 3.19 | 3.1863 | 3.1816 | 3.1758 | 3.1716 | 3.171 | 3.1669 | 3.158
TAYNUILT | KILMELFORD PS | MINIMUM HEADROOM | NM 84056 14437 | YES | 4.6417 | 4.6411 | 4.6404 | 4.6392 | 4.6324 | 4.6246 | 4.6158 | 4.6061 | 4.594 | 4.5894 | 3.8997 | 2.2402 | 2.0957 | 1.9223 | 4.6437 | 4.643 | 4.6423 | 4.6412 | 4.6343 | 4.6265 | 4.6177 | 4.608 | 4.5959 | 4.5914 | 4.2561 | 2.1582 | 2.0042 | 1.8092 | 4.5536 | 4.546 | 4.5349 | 4.5088 | 4.4751 | 4.441 | 4.4063 | 4.3854 | 4.3624 | 4.346 | 2.1989 | 1.5381 | 1.4751 | 1.382
| KILMELFORD PS | CT |  |  | 4.6417 | 4.6411 | 4.6404 | 4.6392 | 4.6324 | 4.6246 | 4.6158 | 4.6061 | 4.594 | 4.5894 | 3.8997 | 2.2402 | 2.0957 | 1.9223 | 4.6437 | 4.643 | 4.6423 | 4.6412 | 4.6343 | 4.6265 | 4.6177 | 4.608 | 4.5959 | 4.5914 | 4.2561 | 2.1582 | 2.0042 | 1.8092 | 4.5536 | 4.546 | 4.5349 | 4.5088 | 4.4751 | 4.441 | 4.4063 | 4.3854 | 4.3624 | 4.346 | 2.1989 | 1.5381 | 1.4751 | 1.382
| KILMELFORD PS | LW |  |  | 4.6426 | 4.6426 | 4.6426 | 4.6426 | 4.6373 | 4.6319 | 4.6263 | 4.6203 | 4.6117 | 4.6102 | 3.9302 | 3.2898 | 2.4501 | 2.3957 | 4.6446 | 4.6446 | 4.6446 | 4.6446 | 4.6393 | 4.6339 | 4.6283 | 4.6223 | 4.6136 | 4.6122 | 4.2866 | 2.4234 | 2.3636 | 2.3133 | 4.5607 | 4.559 | 4.5564 | 4.5497 | 4.537 | 4.5244 | 4.5117 | 4.4988 | 4.4834 | 4.4746 | 2.2294 | 1.6086 | 1.5944 | 1.5894
| KILMELFORD PS | ST |  |  | 4.6424 | 4.6422 | 4.6421 | 4.6419 | 4.638 | 4.6335 | 4.6289 | 4.6237 | 4.6164 | 4.6146 | 4.2665 | 2.4824 | 2.3886 | 2.3184 | 4.6444 | 4.6442 | 4.644 | 4.6439 | 4.6399 | 4.6355 | 4.6309 | 4.6256 | 4.6184 | 4.6166 | 4.4509 | 2.3912 | 2.3016 | 2.2331 | 4.557 | 4.5525 | 4.5466 | 4.5353 | 4.5163 | 4.4937 | 4.4803 | 4.4664 | 4.4507 | 4.4411 | 4.0422 | 1.6305 | 1.5876 | 1.5682
| KILMELFORD PS | SP |  |  | 4.6422 | 4.6419 | 4.6416 | 4.6414 | 4.6387 | 4.6361 | 4.6334 | 4.6304 | 4.6256 | 4.62 | 4.6003 | 4.5831 | 4.3934 | 4.3215 | 4.6441 | 4.6439 | 4.6436 | 4.6433 | 4.6406 | 4.638 | 4.6354 | 4.6324 | 4.6275 | 4.622 | 4.6022 | 4.585 | 4.3953 | 4.3234 | 4.561 | 4.5601 | 4.559 | 4.5579 | 4.5508 | 4.5431 | 4.5375 | 4.5316 | 4.5231 | 4.5145 | 4.4858 | 4.4547 | 4.2518 | 4.1677
TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | 4.5026 | 4.5022 | 4.4999 | 4.4974 | 4.4931 | 4.488 | 4.4824 | 4.4761 | 4.4693 | 4.4643 | 3.9498 | 3.9231 | 3.8846 | 2.4184 | 3.6497 | 3.6485 | 3.6452 | 3.6402 | 3.6333 | 3.6256 | 3.6173 | 3.6042 | 3.5917 | 3.5806 | 2.3791 | 2.3571 | 2.3227 | 2.1568 | 4.078 | 4.0776 | 4.0757 | 4.0736 | 4.0698 | 4.0652 | 4.0601 | 4.0544 | 4.0481 | 4.0437 | 2.3569 | 2.2676 | 2.1659 | 1.994
| KILNINVER | CT |  |  | 4.5026 | 4.5022 | 4.4999 | 4.4974 | 4.4931 | 4.488 | 4.4824 | 4.4761 | 4.4693 | 4.4643 | 3.9498 | 3.9231 | 3.8846 | 2.4184 | 3.6497 | 3.6485 | 3.6452 | 3.6402 | 3.6333 | 3.6256 | 3.6173 | 3.6042 | 3.5917 | 3.5806 | 2.3791 | 2.3571 | 2.3227 | 2.1568 | 4.078 | 4.0776 | 4.0757 | 4.0736 | 4.0698 | 4.0652 | 4.0601 | 4.0544 | 4.0481 | 4.0437 | 2.3569 | 2.2676 | 2.1659 | 1.994
| KILNINVER | LW |  |  | 4.5033 | 4.5033 | 4.5033 | 4.5033 | 4.5033 | 4.5033 | 4.5033 | 4.5033 | 4.5033 | 4.5033 | 4.0016 | 4.0016 | 3.9389 | 3.9389 | 3.6503 | 3.6494 | 3.6481 | 3.6446 | 3.6408 | 3.6371 | 3.6337 | 3.6312 | 3.6288 | 3.6262 | 2.417 | 2.417 | 2.3848 | 2.3848 | 4.0787 | 4.0787 | 4.0787 | 4.0787 | 4.0787 | 4.0787 | 4.0787 | 4.0787 | 4.0787 | 4.0787 | 2.4454 | 2.4191 | 2.3271 | 2.3008
| KILNINVER | ST |  |  | 4.5031 | 4.503 | 4.5029 | 4.5028 | 4.5019 | 4.5008 | 4.4995 | 4.498 | 4.4964 | 4.4958 | 4.2434 | 4.2407 | 4.2265 | 4.2184 | 3.6505 | 3.65 | 3.6493 | 3.6481 | 3.6457 | 3.6429 | 3.6376 | 3.6322 | 3.6269 | 3.6223 | 3.4291 | 3.4073 | 3.3743 | 3.3475 | 4.0785 | 4.0784 | 4.0783 | 4.0782 | 4.0773 | 4.0762 | 4.0749 | 4.0734 | 4.0718 | 4.0712 | 3.8526 | 3.8499 | 3.8357 | 3.8277
| KILNINVER | SP |  |  | 4.503 | 4.5029 | 4.5027 | 4.5026 | 4.5026 | 4.5025 | 4.5025 | 4.5025 | 4.5025 | 4.5022 | 4.5015 | 4.501 | 4.4975 | 4.4898 | 3.6508 | 3.6506 | 3.6504 | 3.6502 | 3.6497 | 3.6492 | 3.6479 | 3.6465 | 3.6448 | 3.6423 | 3.6349 | 3.6264 | 3.6161 | 3.6021 | 4.0784 | 4.0783 | 4.0781 | 4.078 | 4.078 | 4.0779 | 4.0779 | 4.0779 | 4.0778 | 4.0776 | 4.0769 | 4.0764 | 4.0729 | 4.0652
BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | 6.9514 | 6.9507 | 6.9396 | 6.9282 | 6.9139 | 6.8967 | 6.8784 | 6.8588 | 6.8385 | 6.8227 | 6.7866 | 6.7189 | 5.8561 | 5.6443 | 6.5442 | 6.5435 | 6.5375 | 6.5317 | 6.5232 | 6.513 | 6.5018 | 6.4897 | 6.4767 | 6.4663 | 5.9357 | 5.7801 | 5.6062 | 5.3881 | 6.7569 | 6.7561 | 6.7448 | 6.7329 | 6.7182 | 6.7006 | 6.6818 | 6.6617 | 6.6406 | 6.6218 | 5.9972 | 5.8358 | 5.6478 | 5.4146
| KILTARLITY | CT |  |  | 6.9514 | 6.9507 | 6.9396 | 6.9282 | 6.9139 | 6.8967 | 6.8784 | 6.8588 | 6.8385 | 6.8227 | 6.7866 | 6.7189 | 5.8561 | 5.6443 | 6.5442 | 6.5435 | 6.5375 | 6.5317 | 6.5232 | 6.513 | 6.5018 | 6.4897 | 6.4767 | 6.4663 | 5.9357 | 5.7801 | 5.6062 | 5.3881 | 6.7569 | 6.7561 | 6.7448 | 6.7329 | 6.7182 | 6.7006 | 6.6818 | 6.6617 | 6.6406 | 6.6218 | 5.9972 | 5.8358 | 5.6478 | 5.4146
| KILTARLITY | LW |  |  | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.9523 | 6.5469 | 6.5465 | 6.5459 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578 | 6.7578
| KILTARLITY | ST |  |  | 6.9522 | 6.9521 | 6.952 | 6.9519 | 6.9509 | 6.9498 | 6.9485 | 6.947 | 6.9453 | 6.9448 | 6.9431 | 6.9404 | 6.9259 | 6.9177 | 6.5457 | 6.545 | 6.5449 | 6.5448 | 6.5438 | 6.5427 | 6.5414 | 6.5399 | 6.5382 | 6.5377 | 6.536 | 6.5332 | 5.9435 | 5.8669 | 6.7577 | 6.7576 | 6.7575 | 6.7574 | 6.7564 | 6.7553 | 6.754 | 6.7525 | 6.7508 | 6.7503 | 6.7486 | 6.7459 | 6.7314 | 6.7232
| KILTARLITY | SP |  |  | 6.952 | 6.9518 | 6.9516 | 6.9514 | 6.9514 | 6.9513 | 6.9513 | 6.9512 | 6.9512 | 6.9509 | 6.9499 | 6.9492 | 7.0706 | 7.06 | 6.5467 | 6.5463 | 6.5459 | 6.5455 | 6.5442 | 6.5442 | 6.5442 | 6.5441 | 6.5441 | 6.5438 | 6.5428 | 6.542 | 6.6635 | 6.6529 | 6.7575 | 6.7573 | 6.7571 | 6.7569 | 6.7569 | 6.7568 | 6.7568 | 6.7567 | 6.7567 | 6.7564 | 6.7554 | 6.7547 | 6.8761 | 6.8655
REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | 20.2198 | 20.1472 | 20.0763 | 19.9851 | 19.8564 | 19.6669 | 19.3019 | 18.888 | 18.1861 | 18.0229 | 17.5467 | 16.541 | 11.6207 | 11.2367 | 17.0621 | 16.9869 | 16.9069 | 16.7833 | 16.6185 | 16.3972 | 16.0566 | 15.606 | 14.8683 | 14.6566 | 14.0394 | 10.9158 | 10.0195 | 9.6498 | 18.1493 | 18.0727 | 17.9967 | 17.8954 | 17.7562 | 17.5603 | 17.2178 | 16.797 | 16.0885 | 15.9164 | 15.4141 | 10.8528 | 9.9457 | 9.5646
| KINCORTH | CT |  |  | 20.2198 | 20.1472 | 20.0763 | 19.9851 | 19.8564 | 19.6709 | 19.495 | 19.3157 | 19.0869 | 18.9784 | 18.7128 | 17.9445 | 17.1089 | 16.4092 | 17.0621 | 16.9869 | 16.9069 | 16.7833 | 16.6185 | 16.3972 | 16.1861 | 15.9466 | 15.6937 | 15.6077 | 15.3856 | 14.6869 | 13.9221 | 10.9871 | 18.1493 | 18.0727 | 17.9967 | 17.8954 | 17.7562 | 17.5603 | 17.3742 | 17.1805 | 16.9376 | 16.8147 | 16.5083 | 15.6736 | 14.771 | 10.9593
| KINCORTH | LW |  |  | 20.2867 | 20.2806 | 20.2746 | 20.267 | 20.2584 | 20.1818 | 20.1046 | 20.0268 | 19.9484 | 19.883 | 19.6853 | 19.115 | 18.4568 | 18.0647 | 17.1307 | 17.1221 | 17.1116 | 17.0918 | 17.0696 | 16.9799 | 16.8899 | 16.7998 | 16.7094 | 16.631 | 16.395 | 15.764 | 15.0455 | 14.5943 | 18.2198 | 18.213 | 18.2059 | 18.1957 | 18.1844 | 18.105 | 18.0251 | 17.9447 | 17.8636 | 17.7954 | 17.5892 | 17.0051 | 16.3328 | 15.9267
| KINCORTH | ST |  |  | 20.2883 | 20.2837 | 20.279 | 20.2724 | 20.1867 | 19.7051 | 19.3019 | 18.888 | 18.1861 | 18.0229 | 17.5467 | 16.541 | 11.6207 | 11.2367 | 17.1302 | 17.1219 | 17.1121 | 17.0954 | 16.9957 | 16.4971 | 16.0566 | 15.606 | 14.8683 | 14.6566 | 14.0394 | 10.9158 | 10.0195 | 9.6498 | 18.2211 | 18.2157 | 18.2099 | 18.2012 | 18.1128 | 17.6279 | 17.2178 | 16.797 | 16.0885 | 15.9164 | 15.4141 | 10.8528 | 9.9457 | 9.5646
| KINCORTH | SP |  |  | 20.2857 | 20.28 | 20.2744 | 20.2687 | 20.2606 | 19.6669 | 19.6583 | 19.6498 | 19.0552 | 18.9427 | 18.6057 | 17.9993 | 17.5763 | 17.3889 | 17.1322 | 17.1267 | 17.1211 | 17.1154 | 17.1047 | 16.5074 | 16.4873 | 16.4674 | 15.8581 | 15.7273 | 15.3375 | 14.6496 | 14.1504 | 13.8915 | 18.2192 | 18.2133 | 18.2074 | 18.2014 | 18.1925 | 17.5978 | 17.5867 | 17.5758 | 16.9783 | 16.8622 | 16.5147 | 15.8916 | 15.4531 | 15.2509
FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | 0.13316 | 0.13316 | 0.12135 | 0.097213 | 0.079945 | 0.059095 | 0.037624 | 0.015529 | -0.007262 | -0.030699 | -0.072548 | -0.14057 | -0.19988 | -0.25723 | 0.12615 | 0.12607 | 0.11715 | 0.092767 | 0.076129 | 0.056078 | 0.035437 | 0.014203 | -0.0076904 | -0.030213 | -0.070617 | -0.13628 | -0.19355 | -0.24885 | 0.12709 | 0.12695 | 0.11337 | 0.090883 | 0.073722 | 0.053002 | 0.031664 | 0.0096295 | -0.013488 | -0.037265 | -0.079799 | -0.14893 | -0.20916 | -0.2673
| KINGAIRLOCH | CT |  |  | 0.13316 | 0.13316 | 0.12135 | 0.097213 | 0.079945 | 0.059095 | 0.037624 | 0.015529 | -0.007262 | -0.030699 | -0.072548 | -0.14057 | -0.19988 | -0.25723 | 0.12616 | 0.12609 | 0.11715 | 0.092767 | 0.076129 | 0.056078 | 0.035437 | 0.014203 | -0.0076904 | -0.030213 | -0.070617 | -0.13628 | -0.19355 | -0.24885 | 0.1271 | 0.12699 | 0.11337 | 0.090883 | 0.073722 | 0.053002 | 0.031664 | 0.0096295 | -0.013488 | -0.037265 | -0.079799 | -0.14893 | -0.20916 | -0.2673
| KINGAIRLOCH | LW |  |  | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.12615 | 0.12607 | 0.12593 | 0.12559 | 0.12522 | 0.12488 | 0.12458 | 0.1243 | 0.12426 | 0.12426 | 0.12426 | 0.12426 | 0.12426 | 0.12426 | 0.12709 | 0.12695 | 0.12686 | 0.12673 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664
| KINGAIRLOCH | ST |  |  | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.12619 | 0.12615 | 0.12609 | 0.12598 | 0.12584 | 0.12567 | 0.1255 | 0.12533 | 0.12517 | 0.125 | 0.12459 | 0.12426 | 0.12426 | 0.12426 | 0.12714 | 0.12708 | 0.12699 | 0.12688 | 0.12683 | 0.12676 | 0.12669 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664 | 0.12664
| KINGAIRLOCH | SP |  |  | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.13316 | 0.12623 | 0.12622 | 0.12622 | 0.12621 | 0.12617 | 0.12612 | 0.12606 | 0.12601 | 0.12594 | 0.12587 | 0.12566 | 0.12535 | 0.12505 | 0.12482 | 0.12721 | 0.1272 | 0.12719 | 0.12718 | 0.12711 | 0.12703 | 0.12694 | 0.12689 | 0.12686 | 0.12684 | 0.12676 | 0.12664 | 0.12664 | 0.12664
DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | YES | 7.086 | 7.0835 | 7.0805 | 7.0762 | 7.0615 | 7.0434 | 4.9569 | 4.4699 | 3.8461 | 3.2364 | 2.6679 | 0.0135 | -2.4817 | -5.3883 | 7.0217 | 7.0139 | 7.0037 | 6.9846 | 6.8631 | 4.9942 | 4.3788 | 3.7668 | 2.9845 | 2.2163 | 1.5374 | -1.256 | -4.3696 | -7.5172 | 6.9951 | 6.9848 | 6.9711 | 6.9453 | 4.7841 | 4.2531 | 3.7249 | 3.1991 | 2.4488 | 1.6803 | 1.0012 | -1.9839 | -5.0031 | -8.2469
| KINGSEAT | CT |  |  | 7.086 | 7.0835 | 7.0805 | 7.0762 | 7.0615 | 7.0434 | 7.0219 | 6.9964 | 4.9053 | 4.4088 | 2.6679 | 0.0135 | -1.8287 | -5.3883 | 7.023 | 7.0167 | 7.008 | 6.9901 | 6.8919 | 6.8024 | 6.7102 | 4.8546 | 4.3508 | 3.7202 | 1.5374 | -1.256 | -3.3864 | -7.5172 | 6.998 | 6.9902 | 6.9795 | 6.9567 | 4.9391 | 4.6853 | 4.4307 | 4.1211 | 3.685 | 3.1425 | 1.0012 | -1.9839 | -4.1149 | -8.2469
| KINGSEAT | LW |  |  | 7.0898 | 7.0898 | 7.0898 | 7.0898 | 7.0875 | 7.083 | 4.9569 | 4.4699 | 3.8461 | 3.2364 | 3.1959 | 1.0296 | 0.3896 | -1.5427 | 7.0304 | 7.0298 | 7.0289 | 7.0266 | 6.8631 | 4.9942 | 4.3788 | 3.7668 | 2.9845 | 2.2163 | 2.1697 | -0.10082 | -0.84372 | -3.1179 | 7.0067 | 7.0059 | 7.0046 | 7.0014 | 4.7841 | 4.2531 | 3.7249 | 3.1991 | 2.4488 | 1.6803 | 1.6337 | -0.82841 | -1.5715 | -3.8465
| KINGSEAT | ST |  |  | 7.0888 | 7.0882 | 7.0876 | 7.0868 | 7.0803 | 7.0721 | 7.0624 | 7.0508 | 4.8838 | 4.4096 | 2.7609 | 0.71998 | -2.4817 | -4.3667 | 7.0217 | 7.0139 | 7.0037 | 6.9846 | 6.892 | 6.7968 | 6.7166 | 4.7755 | 4.2971 | 3.6999 | 1.6237 | -0.62308 | -4.3696 | -6.5783 | 6.9951 | 6.9848 | 6.9711 | 6.9453 | 4.8962 | 4.6009 | 4.3586 | 4.0611 | 3.6491 | 3.1367 | 1.0875 | -1.2554 | -5.0031 | -7.2124
| KINGSEAT | SP |  |  | 7.0878 | 7.0868 | 7.0858 | 7.0847 | 7.0845 | 7.0843 | 7.084 | 7.0837 | 7.0832 | 7.0813 | 7.0739 | 4.1914 | 3.3475 | 2.5543 | 7.0278 | 7.0259 | 7.0238 | 7.0216 | 6.9993 | 6.9735 | 6.9409 | 6.9087 | 6.866 | 6.8094 | 4.5373 | 3.4153 | 2.372 | 1.3931 | 7.0038 | 7.0016 | 6.9992 | 6.9966 | 6.9662 | 6.9312 | 6.8868 | 4.9434 | 4.8037 | 4.6215 | 3.8603 | 2.8797 | 1.836 | 0.8569
BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | YES | 8.8887 | 8.8871 | 8.8599 | 8.8318 | 8.7969 | 8.755 | 8.7102 | 8.6626 | 8.6122 | 8.5678 | 8.4742 | 8.3007 | 5.8131 | 5.2293 | 8.1324 | 8.1252 | 8.0724 | 8.0072 | 7.9331 | 7.8488 | 7.7635 | 7.6806 | 7.6013 | 7.5294 | 7.39 | 6.3464 | 5.4168 | 4.8424 | 8.6566 | 8.655 | 8.6058 | 8.5558 | 8.4984 | 8.4293 | 8.3565 | 8.2802 | 8.2 | 8.1251 | 7.977 | 6.2506 | 5.1118 | 4.4667
| KINGUSSIE | CT |  |  | 8.8887 | 8.8871 | 8.8599 | 8.8318 | 8.7969 | 8.755 | 8.7102 | 8.6626 | 8.6122 | 8.5678 | 8.4742 | 8.3007 | 5.8131 | 5.2293 | 8.1324 | 8.1252 | 8.0724 | 8.0072 | 7.9331 | 7.8488 | 7.7635 | 7.6806 | 7.6013 | 7.5294 | 7.39 | 6.3464 | 5.4168 | 4.8424 | 8.6566 | 8.655 | 8.6058 | 8.5558 | 8.4984 | 8.4293 | 8.3565 | 8.2802 | 8.2 | 8.1251 | 7.977 | 6.2506 | 5.1118 | 4.4667
| KINGUSSIE | LW |  |  | 8.8911 | 8.8911 | 8.8798 | 8.8686 | 8.8574 | 8.8462 | 8.8349 | 8.8236 | 8.8124 | 8.8011 | 8.7784 | 8.7401 | 8.1924 | 8.1523 | 8.1385 | 8.1358 | 8.1128 | 8.0836 | 8.0532 | 8.023 | 7.9931 | 7.9633 | 7.9339 | 7.9035 | 7.849 | 7.7661 | 7.3497 | 7.2765 | 8.6589 | 8.6589 | 8.638 | 8.617 | 8.5961 | 8.5751 | 8.5542 | 8.5331 | 8.5121 | 8.491 | 8.4487 | 8.3772 | 7.7588 | 6.4029
| KINGUSSIE | ST |  |  | 8.8905 | 8.8901 | 8.8823 | 8.8743 | 8.8632 | 8.8513 | 8.8387 | 8.8253 | 8.8112 | 8.8016 | 8.7723 | 8.7231 | 8.3732 | 8.301 | 8.1361 | 8.1321 | 8.1142 | 8.0917 | 8.0626 | 8.0303 | 7.9897 | 7.9556 | 7.9298 | 7.9079 | 7.8421 | 7.7439 | 7.4356 | 6.2179 | 8.6584 | 8.658 | 8.6437 | 8.6292 | 8.6116 | 8.5933 | 8.5741 | 8.5542 | 8.5336 | 8.5175 | 8.4686 | 8.3862 | 7.9839 | 6.2369
| KINGUSSIE | SP |  |  | 8.89 | 8.8895 | 8.8889 | 8.8883 | 8.8882 | 8.8881 | 8.888 | 8.8879 | 8.8877 | 8.8869 | 8.8841 | 8.8818 | 8.8676 | 8.8367 | 8.1392 | 8.1381 | 8.137 | 8.1357 | 8.132 | 8.1276 | 8.1199 | 8.1123 | 8.1026 | 8.0922 | 8.0617 | 8.0425 | 8.0175 | 7.9765 | 8.6579 | 8.6574 | 8.6568 | 8.6562 | 8.6561 | 8.656 | 8.6559 | 8.6558 | 8.6556 | 8.6548 | 8.652 | 8.6497 | 8.6355 | 8.6046
TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | 4.2045 | 4.202 | 4.1828 | 4.159 | 4.1331 | 4.1039 | 4.074 | 4.0348 | 3.995 | 3.9544 | 3.8638 | 3.8042 | 3.7431 | 3.6652 | 2.4964 | 2.4931 | 2.4806 | 2.4619 | 2.4413 | 2.4189 | 2.3962 | 2.362 | 2.3277 | 2.2925 | 2.2009 | 2.0488 | 1.8925 | 1.7202 | 3.691 | 3.6908 | 3.6671 | 3.6433 | 3.6179 | 3.5873 | 3.5554 | 3.5225 | 3.4882 | 3.4542 | 3.3911 | 3.285 | 2.3448 | 2.1418
| KINLOCH | CT |  |  | 4.2045 | 4.202 | 4.1828 | 4.159 | 4.1331 | 4.1039 | 4.074 | 4.0348 | 3.995 | 3.9544 | 3.8638 | 3.8042 | 3.7431 | 3.6652 | 2.4964 | 2.4933 | 2.4806 | 2.4619 | 2.4413 | 2.4189 | 2.3962 | 2.362 | 2.3277 | 2.2925 | 2.2009 | 2.0488 | 1.8925 | 1.7202 | 3.691 | 3.6908 | 3.6671 | 3.6433 | 3.6179 | 3.5873 | 3.5554 | 3.5225 | 3.4882 | 3.4542 | 3.3911 | 3.285 | 2.3448 | 2.1418
| KINLOCH | LW |  |  | 4.2047 | 4.202 | 4.1977 | 4.187 | 4.1751 | 4.1635 | 4.1521 | 4.1409 | 4.13 | 4.1183 | 4.0834 | 4.0272 | 4.0254 | 4.0254 | 2.4966 | 2.4931 | 2.4876 | 2.4738 | 2.4585 | 2.4435 | 2.4288 | 2.4145 | 2.4005 | 2.3853 | 2.3404 | 2.2681 | 2.1954 | 2.1233 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914 | 3.6914
| KINLOCH | ST |  |  | 4.2057 | 4.2044 | 4.2026 | 4.1992 | 4.1944 | 4.1886 | 4.1781 | 4.1678 | 4.1576 | 4.1459 | 4.1122 | 4.0583 | 4.018 | 4.0158 | 2.4979 | 2.4962 | 2.4939 | 2.4895 | 2.4834 | 2.4761 | 2.4627 | 2.4495 | 2.4365 | 2.4215 | 2.3783 | 2.3091 | 2.2376 | 2.168 | 3.6914 | 3.6914 | 3.6913 | 3.6913 | 3.6911 | 3.6907 | 3.6904 | 3.69 | 3.6895 | 3.6893 | 3.6889 | 3.6881 | 3.6841 | 3.6819
| KINLOCH | SP |  |  | 4.207 | 4.2067 | 4.2064 | 4.2062 | 4.2049 | 4.2033 | 4.1999 | 4.1966 | 4.1923 | 4.1877 | 4.1742 | 4.1535 | 4.1328 | 4.1116 | 2.4995 | 2.4992 | 2.4989 | 2.4985 | 2.4969 | 2.4949 | 2.4906 | 2.4863 | 2.4807 | 2.4748 | 2.4576 | 2.431 | 2.4048 | 2.3784 | 3.6913 | 3.6913 | 3.6912 | 3.6912 | 3.6911 | 3.6911 | 3.6911 | 3.6911 | 3.6911 | 3.691 | 3.6907 | 3.6905 | 3.689 | 3.6857
TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | 1.1665 | 1.1663 | 1.1643 | 1.1622 | 1.1593 | 1.1559 | 1.1521 | 1.148 | 1.1436 | 1.1401 | 1.132 | 1.116 | 1.0952 | 1.0607 | 2.1354 | 2.1329 | 2.1286 | 2.1187 | 2.1074 | 2.0963 | 2.0855 | 2.0714 | 2.0546 | 2.0376 | 1.9886 | 1.9066 | 1.8188 | 1.7181 | 1.558 | 1.5556 | 1.5498 | 1.5396 | 1.5279 | 1.5157 | 1.5033 | 1.4848 | 1.4662 | 1.4473 | 1.3954 | 1.3085 | 1.2167 | 1.1121
| KINLOCH RANNOCH | CT |  |  | 1.1665 | 1.1663 | 1.1643 | 1.1622 | 1.1593 | 1.1559 | 1.1521 | 1.148 | 1.1436 | 1.1401 | 1.132 | 1.116 | 1.0952 | 1.0607 | 2.1354 | 2.1331 | 2.1286 | 2.1197 | 2.1094 | 2.0989 | 2.0882 | 2.0714 | 2.0546 | 2.0376 | 1.9886 | 1.9066 | 1.8188 | 1.7181 | 1.558 | 1.5558 | 1.5498 | 1.5396 | 1.5279 | 1.5157 | 1.5033 | 1.4848 | 1.4662 | 1.4473 | 1.3954 | 1.3085 | 1.2167 | 1.1121
| KINLOCH RANNOCH | LW |  |  | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 1.1668 | 2.1355 | 2.1329 | 2.1289 | 2.1187 | 2.1074 | 2.0963 | 2.0855 | 2.0749 | 2.0645 | 2.0533 | 2.0201 | 1.9667 | 1.913 | 1.8598 | 1.5582 | 1.5556 | 1.5516 | 1.5416 | 1.5305 | 1.5196 | 1.509 | 1.4985 | 1.4884 | 1.4773 | 1.4447 | 1.3922 | 1.3394 | 1.287
| KINLOCH RANNOCH | ST |  |  | 1.1667 | 1.1667 | 1.1667 | 1.1666 | 1.1663 | 1.166 | 1.1656 | 1.1651 | 1.1646 | 1.1645 | 1.1639 | 1.1631 | 1.1587 | 1.1562 | 2.1365 | 2.1352 | 2.1335 | 2.1303 | 2.1256 | 2.1201 | 2.1127 | 2.1054 | 2.0982 | 2.0886 | 2.0607 | 2.0162 | 1.9687 | 1.9232 | 1.5591 | 1.5579 | 1.5562 | 1.553 | 1.5484 | 1.543 | 1.5357 | 1.5285 | 1.5214 | 1.512 | 1.4846 | 1.4408 | 1.394 | 1.3492
| KINLOCH RANNOCH | SP |  |  | 1.1667 | 1.1666 | 1.1666 | 1.1665 | 1.1665 | 1.1665 | 1.1665 | 1.1665 | 1.1665 | 1.1664 | 1.1661 | 1.166 | 1.1647 | 1.162 | 2.1377 | 2.1375 | 2.1372 | 2.1369 | 2.1357 | 2.1342 | 2.1319 | 2.1295 | 2.1266 | 2.1227 | 2.1116 | 2.0946 | 2.0775 | 2.0601 | 1.5603 | 1.5601 | 1.5598 | 1.5596 | 1.5584 | 1.5569 | 1.5546 | 1.5523 | 1.5494 | 1.5456 | 1.5347 | 1.5179 | 1.5011 | 1.4839
GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | 0.72079 | 0.72062 | 0.56297 | 0.31254 | 0.055205 | -0.26401 | -0.59773 | -0.94128 | -1.2958 | -1.6597 | -2.3153 | -3.3906 | -4.332 | -5.2518 | 0.63417 | 0.63401 | 0.48048 | 0.26106 | 0.035418 | -0.23649 | -0.51649 | -0.80874 | -1.1333 | -1.4881 | -2.1275 | -3.1689 | -4.0833 | -4.9774 | 0.63021 | 0.63004 | 0.44249 | 0.23693 | -0.0057599 | -0.30396 | -0.61113 | -0.92817 | -1.2553 | -1.6201 | -2.2888 | -3.3777 | -4.3333 | -5.268
| KINLOCHEWE | CT |  |  | 0.72079 | 0.72062 | 0.56297 | 0.31254 | 0.055205 | -0.26401 | -0.59773 | -0.94128 | -1.2958 | -1.6597 | -2.3153 | -3.3906 | -4.332 | -5.2518 | 0.63417 | 0.63401 | 0.48048 | 0.26106 | 0.035418 | -0.23649 | -0.51649 | -0.80874 | -1.1333 | -1.4881 | -2.1275 | -3.1689 | -4.0833 | -4.9774 | 0.63021 | 0.63004 | 0.44249 | 0.23693 | -0.0057599 | -0.30396 | -0.61113 | -0.92817 | -1.2553 | -1.6201 | -2.2888 | -3.3777 | -4.3333 | -5.268
| KINLOCHEWE | LW |  |  | 0.72101 | 0.72101 | 0.65758 | 0.59171 | 0.48115 | 0.37015 | 0.25915 | 0.14767 | 0.036672 | -0.075703 | -0.30945 | -0.70422 | -1.1073 | -1.5202 | 0.6344 | 0.6344 | 0.60125 | 0.50196 | 0.4027 | 0.30314 | 0.20364 | 0.10381 | 0.0044541 | -0.095565 | -0.29986 | -0.6441 | -0.99535 | -1.3836 | 0.63043 | 0.63043 | 0.54729 | 0.46416 | 0.37907 | 0.2888 | 0.18616 | 0.080477 | -0.026494 | -0.13397 | -0.35074 | -0.71666 | -1.0902 | -1.507
| KINLOCHEWE | ST |  |  | 0.72099 | 0.72097 | 0.67866 | 0.63636 | 0.59173 | 0.51751 | 0.44326 | 0.36864 | 0.29431 | 0.21988 | -0.0046072 | -0.39774 | -0.80364 | -1.2182 | 0.63437 | 0.63435 | 0.61587 | 0.56954 | 0.50414 | 0.43819 | 0.3702 | 0.302 | 0.2341 | 0.16513 | -0.042416 | -0.39182 | -0.75012 | -1.1154 | 0.63041 | 0.63039 | 0.57494 | 0.5195 | 0.46411 | 0.40824 | 0.34811 | 0.28737 | 0.21882 | 0.14906 | -0.068303 | -0.4357 | -0.81296 | -1.2072
| KINLOCHEWE | SP |  |  | 0.72097 | 0.72095 | 0.69841 | 0.67588 | 0.65403 | 0.63321 | 0.61304 | 0.59017 | 0.55666 | 0.52431 | 0.43246 | 0.2954 | 0.17259 | 0.062054 | 0.63436 | 0.63434 | 0.62448 | 0.61463 | 0.59804 | 0.56601 | 0.53422 | 0.50299 | 0.47243 | 0.44263 | 0.35793 | 0.23122 | 0.11726 | 0.014351 | 0.63039 | 0.63037 | 0.60084 | 0.5713 | 0.54267 | 0.51539 | 0.48895 | 0.46297 | 0.43788 | 0.41364 | 0.33941 | 0.21952 | 0.10269 | -0.0046506
KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | YES | 1.0617 | 1.0612 | 1.0608 | 1.0601 | 1.0578 | 1.0551 | 1.0519 | 1.0483 | 1.0442 | 1.0418 | 1.034 | 0.98582 | 0.8838 | 0.75485 | 0.81353 | 0.8131 | 0.81265 | 0.81196 | 0.80966 | 0.80699 | 0.80381 | 0.80014 | 0.79607 | 0.79367 | 0.78588 | 0.71242 | 0.59129 | 0.44353 | 0.96936 | 0.96892 | 0.96847 | 0.96778 | 0.96548 | 0.96281 | 0.95963 | 0.94026 | 0.91886 | 0.89768 | 0.83432 | 0.726 | 0.60504 | 0.45745
| KINLOCHLEVEN | CT |  |  | 1.0617 | 1.0612 | 1.0608 | 1.0601 | 1.0578 | 1.0551 | 1.0519 | 1.0483 | 1.0442 | 1.0418 | 1.034 | 0.98582 | 0.8838 | 0.75485 | 0.81353 | 0.8131 | 0.81265 | 0.81196 | 0.80966 | 0.80699 | 0.80381 | 0.80014 | 0.79607 | 0.79367 | 0.78588 | 0.71242 | 0.59129 | 0.44353 | 0.96936 | 0.96892 | 0.96847 | 0.96778 | 0.96548 | 0.96281 | 0.95963 | 0.94026 | 0.91886 | 0.89768 | 0.83432 | 0.726 | 0.60504 | 0.45745
| KINLOCHLEVEN | LW |  |  | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 1.0623 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.81413 | 0.96996 | 0.96996 | 0.96996 | 0.96996 | 0.96996 | 0.96996 | 0.96996 | 0.96871 | 0.96481 | 0.96058 | 0.94809 | 0.92796 | 0.9077 | 0.88764
| KINLOCHLEVEN | ST |  |  | 1.0622 | 1.0621 | 1.062 | 1.0619 | 1.0611 | 1.0603 | 1.0592 | 1.058 | 1.0567 | 1.0562 | 1.0549 | 1.0526 | 1.0367 | 0.98491 | 0.81402 | 0.81394 | 0.81385 | 0.81377 | 0.81301 | 0.81212 | 0.81106 | 0.80987 | 0.80851 | 0.80808 | 0.80673 | 0.8045 | 0.77012 | 0.70637 | 0.96984 | 0.96977 | 0.96967 | 0.96959 | 0.96883 | 0.96794 | 0.96688 | 0.96569 | 0.96245 | 0.94966 | 0.91237 | 0.85241 | 0.78364 | 0.71999
| KINLOCHLEVEN | SP |  |  | 1.062 | 1.0619 | 1.0618 | 1.0616 | 1.0616 | 1.0616 | 1.0615 | 1.0615 | 1.0615 | 1.0613 | 1.0606 | 1.0601 | 1.0566 | 1.0492 | 0.81388 | 0.81375 | 0.81361 | 0.81347 | 0.81345 | 0.81343 | 0.8134 | 0.81337 | 0.81334 | 0.81313 | 0.81245 | 0.81191 | 0.80848 | 0.80102 | 0.9697 | 0.96957 | 0.96944 | 0.9693 | 0.96927 | 0.96925 | 0.96922 | 0.96919 | 0.96916 | 0.96896 | 0.9643 | 0.94193 | 0.91795 | 0.89113
FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | 2.0286 | 2.0286 | 2.0258 | 2.0231 | 2.0204 | 2.0172 | 2.0145 | 2.0121 | 1.9969 | 1.9918 | 1.9828 | 1.9682 | 1.9554 | 1.9429 | 2.0226 | 2.0225 | 2.0194 | 2.0172 | 2.0156 | 2.0137 | 2.0118 | 1.9973 | 1.9925 | 1.9875 | 1.9784 | 1.9636 | 1.9507 | 1.9381 | 2.0234 | 2.0233 | 2.0203 | 2.0171 | 2.0139 | 2.01 | 1.9995 | 1.9957 | 1.9914 | 1.9864 | 1.9773 | 1.9619 | 1.9484 | 1.9354
| KINLOCHMOIDART | CT |  |  | 2.0286 | 2.0286 | 2.0258 | 2.0231 | 2.0204 | 2.0172 | 2.0145 | 2.0121 | 1.9969 | 1.9918 | 1.9828 | 1.9682 | 1.9554 | 1.9429 | 2.0226 | 2.0225 | 2.0194 | 2.0172 | 2.0156 | 2.0137 | 2.0118 | 1.9973 | 1.9925 | 1.9875 | 1.9784 | 1.9636 | 1.9507 | 1.9381 | 2.0234 | 2.0233 | 2.0203 | 2.0171 | 2.0139 | 2.01 | 1.9995 | 1.9957 | 1.9914 | 1.9864 | 1.9773 | 1.9619 | 1.9484 | 1.9354
| KINLOCHMOIDART | LW |  |  | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0226 | 2.0225 | 2.0224 | 2.0222 | 2.0219 | 2.0217 | 2.0215 | 2.0213 | 2.0211 | 2.0209 | 2.0209 | 2.0209 | 2.0209 | 2.0209 | 2.0234 | 2.0233 | 2.0232 | 2.0231 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023
| KINLOCHMOIDART | ST |  |  | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0226 | 2.0226 | 2.0225 | 2.0224 | 2.0224 | 2.0222 | 2.0218 | 2.0214 | 2.0211 | 2.0209 | 2.0209 | 2.0209 | 2.0209 | 2.0209 | 2.0234 | 2.0234 | 2.0233 | 2.0232 | 2.0232 | 2.0231 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023
| KINLOCHMOIDART | SP |  |  | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0286 | 2.0226 | 2.0226 | 2.0226 | 2.0226 | 2.0226 | 2.0225 | 2.0224 | 2.0222 | 2.0221 | 2.022 | 2.0218 | 2.0215 | 2.0212 | 2.021 | 2.0235 | 2.0235 | 2.0234 | 2.0234 | 2.0234 | 2.0233 | 2.0232 | 2.0231 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023 | 2.023
ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | YES | 16.5731 | 16.5717 | 16.5701 | 16.5674 | 16.5524 | 16.5341 | 16.5137 | 14.5153 | 14.2947 | 14.0785 | 13.2701 | 12.1605 | 9.4628 | 8.7486 | 14.5048 | 14.5015 | 14.4971 | 14.4876 | 13.6623 | 13.4363 | 13.212 | 12.989 | 12.7069 | 12.4289 | 11.39 | 10.0385 | 7.2034 | 6.3619 | 15.1418 | 15.1406 | 15.1393 | 15.1373 | 13.6422 | 13.4228 | 13.2049 | 12.9883 | 12.7143 | 12.4444 | 11.4357 | 10.1231 | 7.1181 | 6.301
| KINLOSS | CT |  |  | 16.5731 | 16.5717 | 16.5701 | 16.5674 | 16.5524 | 16.5374 | 16.5209 | 16.4984 | 16.4698 | 14.5099 | 13.8557 | 12.9059 | 10.1504 | 8.8 | 14.5048 | 14.5015 | 14.4971 | 14.4876 | 13.7762 | 13.6859 | 13.5911 | 13.4422 | 13.2423 | 12.9976 | 12.1622 | 10.9639 | 8.0756 | 6.4857 | 15.1418 | 15.1406 | 15.1393 | 15.1373 | 13.7562 | 13.6646 | 13.5723 | 13.4273 | 13.2329 | 12.9951 | 12.1834 | 11.0181 | 7.9592 | 6.4108
| KINLOSS | LW |  |  | 16.5748 | 16.5745 | 16.5741 | 16.5731 | 16.5539 | 16.5341 | 16.5137 | 14.5153 | 14.2947 | 14.0785 | 13.2701 | 12.1605 | 9.4628 | 8.7486 | 14.5064 | 14.5038 | 14.4996 | 14.4893 | 13.6623 | 13.4363 | 13.212 | 12.989 | 12.7069 | 12.4289 | 11.39 | 10.0385 | 7.2034 | 6.3619 | 15.1435 | 15.1435 | 15.1435 | 15.1435 | 13.6422 | 13.4228 | 13.2049 | 12.9883 | 12.7143 | 12.4444 | 11.4357 | 10.1231 | 7.1181 | 6.301
| KINLOSS | ST |  |  | 16.5744 | 16.5739 | 16.5733 | 16.5723 | 16.5625 | 16.5525 | 16.5415 | 16.5282 | 16.51 | 16.4904 | 13.9898 | 13.1597 | 11.5727 | 10.2409 | 14.5051 | 14.5019 | 14.4977 | 14.4897 | 13.7895 | 13.6995 | 13.5994 | 13.4771 | 13.3085 | 13.0851 | 12.317 | 11.2536 | 9.5503 | 7.9457 | 15.1432 | 15.143 | 15.1428 | 15.1425 | 13.7699 | 13.6782 | 13.5809 | 13.4621 | 13.2983 | 13.0813 | 12.3356 | 11.3027 | 9.5215 | 7.963
| KINLOSS | SP |  |  | 16.5745 | 16.5741 | 16.5738 | 16.5735 | 16.5714 | 16.569 | 16.5654 | 16.5617 | 16.5569 | 16.55 | 16.5215 | 14.436 | 14.1294 | 13.8443 | 14.5078 | 14.5072 | 14.5064 | 14.5056 | 14.4849 | 14.4611 | 14.4246 | 13.7676 | 13.7109 | 13.631 | 13.3046 | 12.8864 | 12.4994 | 12.1387 | 15.143 | 15.1427 | 15.1424 | 15.1421 | 15.1421 | 15.142 | 13.7874 | 13.7453 | 13.6894 | 13.6117 | 13.2949 | 12.8888 | 12.5123 | 12.1616
BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | 10.7834 | 10.7812 | 10.7788 | 10.775 | 10.7579 | 10.7379 | 10.7153 | 10.6898 | 10.6593 | 10.6456 | 10.6017 | 10.4087 | 10.2315 | 9.9223 | 9.4226 | 9.4194 | 9.4154 | 9.4079 | 9.3867 | 9.3627 | 9.3362 | 9.3081 | 9.275 | 9.2586 | 9.2065 | 6.9579 | 6.5152 | 5.9449 | 9.8806 | 9.8735 | 9.8636 | 9.8466 | 9.8294 | 9.8094 | 9.7868 | 9.7614 | 9.7308 | 9.7171 | 9.6732 | 9.4763 | 9.2991 | 7.037
| KIPPEN | CT |  |  | 10.7834 | 10.7812 | 10.7788 | 10.775 | 10.7579 | 10.7379 | 10.7153 | 10.6898 | 10.6593 | 10.6456 | 10.6017 | 10.4087 | 10.2315 | 9.9223 | 9.4226 | 9.4194 | 9.4154 | 9.4079 | 9.3867 | 9.3627 | 9.3362 | 9.3081 | 9.275 | 9.2586 | 9.2065 | 6.9579 | 6.5152 | 5.9449 | 9.8806 | 9.8735 | 9.8636 | 9.8466 | 9.8294 | 9.8094 | 9.7868 | 9.7614 | 9.7308 | 9.7171 | 9.6732 | 9.4763 | 9.2991 | 7.037
| KIPPEN | LW |  |  | 10.7865 | 10.7865 | 10.7865 | 10.7865 | 10.7782 | 10.7698 | 10.761 | 10.7517 | 10.7382 | 10.7358 | 10.7292 | 10.6397 | 10.6205 | 10.6127 | 9.4268 | 9.4267 | 9.4265 | 9.426 | 9.4171 | 9.4081 | 9.3988 | 9.3889 | 9.3749 | 9.372 | 9.3637 | 9.3 | 9.2782 | 9.2677 | 9.8888 | 9.8882 | 9.8872 | 9.8848 | 9.8738 | 9.8628 | 9.8515 | 9.8396 | 9.8237 | 9.8187 | 9.8042 | 9.7072 | 9.6881 | 9.6803
| KIPPEN | ST |  |  | 10.7857 | 10.7851 | 10.7845 | 10.7838 | 10.7743 | 10.7635 | 10.7518 | 10.7383 | 10.7211 | 10.7163 | 10.7027 | 10.6346 | 10.5187 | 10.4596 | 9.4253 | 9.424 | 9.4225 | 9.42 | 9.4081 | 9.3944 | 9.3806 | 9.3652 | 9.346 | 9.3394 | 9.3205 | 9.2581 | 7.2446 | 7.0196 | 9.8846 | 9.8808 | 9.8759 | 9.8667 | 9.8459 | 9.835 | 9.8233 | 9.8099 | 9.7927 | 9.7879 | 9.7742 | 9.7041 | 9.5883 | 9.5292
| KIPPEN | SP |  |  | 10.7846 | 10.7836 | 10.7826 | 10.7815 | 10.7808 | 10.7801 | 10.7793 | 10.7784 | 10.7771 | 10.7745 | 10.7654 | 10.7578 | 10.6924 | 10.6235 | 9.4249 | 9.4238 | 9.4227 | 9.4215 | 9.4201 | 9.4186 | 9.4171 | 9.4156 | 9.4135 | 9.4101 | 9.3989 | 9.3882 | 9.3197 | 9.2479 | 9.8868 | 9.8854 | 9.8838 | 9.8822 | 9.8783 | 9.8738 | 9.8699 | 9.866 | 9.8607 | 9.8548 | 9.8369 | 9.8293 | 9.7639 | 9.695
THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | YES | 33.555 | 33.5076 | 33.4538 | 33.3926 | 32.885 | 32.2594 | 31.6127 | 30.9396 | 30.2251 | 29.9957 | 29.2482 | 21.6846 | 19.7501 | 18.2549 | 29.3129 | 29.2638 | 29.2072 | 29.1391 | 28.6238 | 27.9906 | 27.3366 | 26.6564 | 25.8451 | 25.4482 | 24.3109 | 18.7474 | 15.7392 | 13.2524 | 27.7636 | 27.7144 | 27.6577 | 27.6048 | 27.1325 | 26.5413 | 25.9284 | 25.2884 | 21.8584 | 21.6335 | 20.9383 | 16.7614 | 13.8201 | 11.3991
| KIRKWALL | CT |  |  | 33.642 | 33.5863 | 33.5185 | 33.4121 | 33.0723 | 32.6968 | 32.348 | 31.979 | 31.5231 | 31.3143 | 30.7016 | 21.6846 | 19.7501 | 18.2549 | 29.3976 | 29.3382 | 29.265 | 29.1455 | 28.7917 | 28.3459 | 27.9074 | 27.3488 | 26.7069 | 26.3791 | 25.7869 | 18.7474 | 15.7392 | 13.2524 | 27.8482 | 27.7887 | 27.7311 | 27.6845 | 27.4088 | 27.0397 | 26.6766 | 26.2772 | 25.7915 | 25.5504 | 21.9063 | 16.7614 | 13.8201 | 11.3991
| KIRKWALL | LW |  |  | 33.555 | 33.5076 | 33.4538 | 33.3926 | 32.885 | 32.2594 | 31.6127 | 30.9396 | 30.2251 | 29.9957 | 29.3194 | 21.9483 | 20.6635 | 19.868 | 29.3129 | 29.2638 | 29.2072 | 29.1391 | 28.6238 | 27.9906 | 27.3366 | 26.6564 | 25.901 | 25.6209 | 24.7947 | 20.443 | 19.1583 | 18.3628 | 27.7636 | 27.7144 | 27.6577 | 27.6048 | 27.1325 | 26.5413 | 25.9284 | 25.2884 | 21.8584 | 21.6335 | 20.9708 | 18.6295 | 17.2426 | 16.2185
| KIRKWALL | ST |  |  | 34.5655 | 33.7373 | 33.7017 | 33.6592 | 33.4557 | 32.6699 | 31.9613 | 31.2992 | 30.279 | 30.015 | 29.2482 | 22.4193 | 21.2467 | 20.6765 | 30.0984 | 29.4927 | 29.4545 | 29.407 | 29.1967 | 28.4029 | 27.6807 | 26.9516 | 25.8451 | 25.4482 | 24.3109 | 20.5387 | 18.6919 | 17.4508 | 28.7867 | 27.9433 | 27.905 | 27.8653 | 27.6929 | 26.9443 | 26.2978 | 25.6427 | 21.9222 | 21.6702 | 20.9383 | 18.543 | 16.7861 | 15.6098
| KIRKWALL | SP |  |  | 34.6853 | 34.6727 | 34.5629 | 33.9988 | 33.9378 | 33.0218 | 32.9454 | 32.8691 | 31.9338 | 31.7114 | 31.059 | 30.1593 | 29.5189 | 29.1881 | 30.22 | 30.2072 | 30.0971 | 29.5326 | 29.4696 | 28.5513 | 28.4705 | 28.3899 | 27.449 | 27.2188 | 26.5401 | 25.4055 | 22.0456 | 21.7336 | 28.9086 | 28.8957 | 28.7856 | 28.2211 | 28.1578 | 27.2392 | 27.1578 | 27.0767 | 26.1351 | 25.9039 | 25.3467 | 21.7831 | 21.1627 | 20.8507
BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | 2.7934 | 2.7918 | 2.7297 | 2.6653 | 2.5971 | 2.5155 | 1.9843 | 1.8748 | 1.7619 | 1.6478 | 1.4286 | 1.0649 | 0.7224 | 0.33281 | 2.3527 | 2.3521 | 2.3153 | 2.2783 | 2.2381 | 1.9613 | 1.8596 | 1.7345 | 1.6055 | 1.475 | 1.2262 | 0.81448 | 0.42766 | 0.0093026 | 2.7942 | 2.7933 | 2.7117 | 2.6292 | 2.5425 | 1.984 | 1.8897 | 1.7667 | 1.6329 | 1.4973 | 1.2406 | 0.81586 | 0.41965 | -0.0078434
| KISHORNHILL | CT |  |  | 2.7934 | 2.7918 | 2.7297 | 2.6653 | 2.5971 | 2.5155 | 1.9843 | 1.8748 | 1.7619 | 1.6478 | 1.4286 | 1.0649 | 0.7224 | 0.33281 | 2.3527 | 2.3521 | 2.3153 | 2.2783 | 2.2381 | 1.9613 | 1.8596 | 1.7345 | 1.6055 | 1.475 | 1.2262 | 0.81448 | 0.42766 | 0.0093026 | 2.7942 | 2.7933 | 2.7117 | 2.6292 | 2.5425 | 1.984 | 1.8897 | 1.7667 | 1.6329 | 1.4973 | 1.2406 | 0.81586 | 0.41965 | -0.0078434
| KISHORNHILL | LW |  |  | 2.7941 | 2.7929 | 2.7644 | 2.7329 | 2.7011 | 2.6692 | 2.6375 | 2.6057 | 2.5742 | 2.5422 | 2.4726 | 1.9373 | 1.812 | 1.6841 | 2.3535 | 2.3535 | 2.3351 | 2.3168 | 2.2986 | 2.2802 | 2.2619 | 2.2435 | 2.2291 | 2.2197 | 1.929 | 1.8002 | 1.6639 | 1.5172 | 2.795 | 2.7946 | 2.7583 | 2.7212 | 2.6841 | 2.6468 | 2.6096 | 2.5723 | 2.5351 | 2.4977 | 1.9681 | 1.8291 | 1.6876 | 1.5438
| KISHORNHILL | ST |  |  | 2.7945 | 2.7939 | 2.7753 | 2.756 | 2.7356 | 2.7147 | 2.6854 | 2.6562 | 2.6272 | 2.5966 | 2.5059 | 1.9855 | 1.8357 | 1.6874 | 2.3534 | 2.3533 | 2.3413 | 2.3299 | 2.3174 | 2.3042 | 2.2899 | 2.2767 | 2.2634 | 2.2508 | 1.9881 | 1.8352 | 1.6728 | 1.5119 | 2.795 | 2.7948 | 2.7707 | 2.7464 | 2.7214 | 2.6962 | 2.6684 | 2.6405 | 2.6126 | 2.5848 | 2.5011 | 1.8262 | 1.6363 | 1.4482
| KISHORNHILL | SP |  |  | 2.7951 | 2.7949 | 2.7947 | 2.7946 | 2.794 | 2.7933 | 2.7896 | 2.7861 | 2.7815 | 2.7765 | 2.7622 | 2.74 | 2.7176 | 2.6943 | 2.3533 | 2.3533 | 2.3532 | 2.3531 | 2.3531 | 2.3531 | 2.3531 | 2.3531 | 2.3531 | 2.353 | 2.3526 | 2.3523 | 2.3505 | 2.3466 | 2.7952 | 2.7951 | 2.795 | 2.7949 | 2.7947 | 2.7945 | 2.7934 | 2.7924 | 2.791 | 2.7895 | 2.7851 | 2.7785 | 2.7707 | 2.7612
BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | YES | 6.5927 | 6.4715 | 6.3547 | 5.2045 | 5.057 | 4.914 | 4.7753 | 4.641 | 3.9088 | 3.8503 | 3.6693 | 3.3651 | 3.0559 | 2.6972 | 5.8305 | 5.7761 | 5.727 | 4.6636 | 4.5998 | 4.5374 | 4.4765 | 3.8649 | 3.7339 | 3.6499 | 3.4755 | 3.1833 | 2.8836 | 2.5337 | 5.8353 | 5.7313 | 5.631 | 4.5021 | 4.3751 | 3.8733 | 3.7172 | 3.5437 | 3.3882 | 3.2904 | 3.0922 | 2.7614 | 2.426 | 2.041
| KYLE | CT |  |  | 6.5927 | 6.4715 | 6.3547 | 5.2045 | 5.057 | 4.914 | 4.7753 | 4.641 | 3.9088 | 3.8503 | 3.6693 | 3.3651 | 3.0559 | 2.6972 | 5.8305 | 5.7761 | 5.727 | 4.6636 | 4.5998 | 4.5374 | 4.4765 | 3.8649 | 3.7339 | 3.6499 | 3.4755 | 3.1833 | 2.8836 | 2.5337 | 5.8353 | 5.7313 | 5.631 | 4.5021 | 4.3751 | 3.8733 | 3.7172 | 3.5437 | 3.3882 | 3.2904 | 3.0922 | 2.7614 | 2.426 | 2.041
| KYLE | LW |  |  | 6.7029 | 6.6928 | 6.6832 | 5.672 | 5.6594 | 5.6456 | 5.6305 | 5.6145 | 5.5992 | 5.5833 | 5.5333 | 5.4435 | 5.3561 | 5.2589 | 5.9203 | 5.9109 | 5.9011 | 4.8872 | 4.8716 | 4.8551 | 4.8417 | 4.8338 | 4.827 | 4.8199 | 4.7975 | 4.7578 | 4.719 | 4.6762 | 5.93 | 5.9214 | 5.9131 | 4.9035 | 4.8927 | 4.8808 | 4.868 | 4.8542 | 4.8411 | 4.8274 | 4.7845 | 4.7076 | 4.6326 | 4.5492
| KYLE | ST |  |  | 6.7066 | 6.6998 | 6.6931 | 5.684 | 5.6745 | 5.665 | 5.6535 | 5.642 | 5.6307 | 5.6208 | 5.587 | 5.537 | 5.4796 | 5.4311 | 5.9238 | 5.9177 | 5.9114 | 4.9025 | 4.8925 | 4.8821 | 4.8662 | 4.8507 | 4.839 | 4.8315 | 4.8137 | 4.7874 | 4.7531 | 4.7261 | 5.9331 | 5.9273 | 5.9215 | 4.9138 | 4.9054 | 4.8971 | 4.8871 | 4.8771 | 4.8672 | 4.8585 | 4.8294 | 4.7861 | 4.7349 | 4.6922
| KYLE | SP |  |  | 6.702 | 6.693 | 6.684 | 5.675 | 5.6618 | 5.6378 | 5.6137 | 5.5884 | 5.5552 | 5.5206 | 5.4049 | 5.2642 | 3.7437 | 3.4351 | 5.9207 | 5.9132 | 5.9058 | 4.8983 | 4.8869 | 4.8647 | 4.8408 | 4.8159 | 4.7823 | 4.7505 | 4.6547 | 4.5535 | 3.4678 | 3.133 | 5.9292 | 5.9215 | 5.9137 | 4.906 | 4.8946 | 4.8725 | 4.8502 | 4.8268 | 4.7953 | 4.7624 | 4.6519 | 4.5212 | 3.3193 | 2.9702
LAIRG | LAIRG GRID | MINIMUM HEADROOM | NC 58798 07111 | YES | 3.8217 | 3.7091 | 3.5403 | 3.341 | 2.4462 | 1.9279 | 1.3587 | 0.77637 | 0.063753 | -0.18849 | -0.68073 | -2.7624 | -4.1447 | -4.8519 | 3.0993 | 3.0279 | 2.4494 | 2.2819 | 1.9637 | 1.4809 | 0.9824 | 0.46558 | -0.1857 | -0.4174 | -0.88702 | -2.936 | -4.3155 | -5.0189 | 3.1746 | 3.054 | 2.4994 | 2.3077 | 1.9499 | 1.3882 | 0.81218 | 0.22424 | -0.49197 | -0.74469 | -1.2505 | -3.3541 | -4.765 | -5.5055
| LAIRG GRID | CT |  |  | 3.8217 | 3.7091 | 3.5403 | 3.341 | 2.4462 | 1.9279 | 1.3587 | 0.77637 | 0.063753 | -0.18849 | -0.68073 | -2.7624 | -4.1447 | -4.8519 | 3.0993 | 3.0279 | 2.4494 | 2.2819 | 1.9637 | 1.4809 | 0.9824 | 0.46558 | -0.1857 | -0.4174 | -0.88702 | -2.936 | -4.3155 | -5.0189 | 3.1746 | 3.054 | 2.4994 | 2.3077 | 1.9499 | 1.3882 | 0.81218 | 0.22424 | -0.49197 | -0.74469 | -1.2505 | -3.3541 | -4.765 | -5.5055
| LAIRG GRID | LW |  |  | 3.924 | 3.9147 | 3.8789 | 3.8418 | 3.3548 | 2.2822 | 1.7765 | 1.2355 | 0.47304 | 0.31394 | -0.17004 | -1.3287 | -2.2793 | -2.7654 | 3.174 | 3.1667 | 3.1252 | 3.0893 | 2.2323 | 1.7433 | 1.238 | 0.69765 | -0.064146 | -0.22302 | -0.71181 | -1.8247 | -2.7131 | -3.1631 | 3.2841 | 3.2739 | 3.2272 | 3.1806 | 2.2971 | 1.8019 | 1.2901 | 0.74205 | -0.02756 | -0.19378 | -0.69143 | -1.8357 | -2.7975 | -3.2949
| LAIRG GRID | ST |  |  | 3.9275 | 3.9212 | 3.8971 | 3.8709 | 3.715 | 3.5502 | 3.3906 | 3.2135 | 2.375 | 2.3039 | 2.0992 | 1.4135 | 0.3907 | -0.058572 | 3.1768 | 3.1719 | 3.1442 | 3.1154 | 2.9614 | 2.4182 | 2.2719 | 2.095 | 1.8271 | 1.7481 | 1.5212 | 0.8101 | -0.17697 | -0.58927 | 3.2879 | 3.2811 | 3.2498 | 3.216 | 3.0539 | 2.4917 | 2.3334 | 2.1575 | 1.8904 | 1.815 | 1.596 | 0.87503 | -0.17091 | -0.64258
| LAIRG GRID | SP |  |  | 3.9233 | 3.9148 | 3.9065 | 3.898 | 3.8698 | 3.8422 | 3.8144 | 3.7849 | 3.7441 | 3.7013 | 3.556 | 3.3888 | 1.3943 | 0.91036 | 3.1739 | 3.1675 | 3.1613 | 3.1549 | 3.1296 | 3.1049 | 3.0793 | 3.0519 | 3.0152 | 2.9763 | 2.3915 | 2.2103 | 0.80588 | 0.30805 | 3.2836 | 3.2746 | 3.2657 | 3.2567 | 3.2275 | 3.199 | 3.1698 | 3.139 | 3.0968 | 3.0527 | 2.9041 | 2.3387 | 0.95197 | 0.47085
MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | 5.509 | 5.3519 | 5.1816 | 3.9543 | 3.3126 | 2.5695 | 1.6976 | 0.76802 | -0.5101 | -1.012 | -2.3497 | -6.5141 | -10.8847 | -16.5669 | 4.7334 | 4.5989 | 4.4542 | 3.9683 | 3.1944 | 2.3928 | 1.5482 | 0.64387 | -0.61576 | -1.1178 | -2.5453 | -6.8072 | -11.4135 | -16.5149 | 5.0658 | 4.9006 | 4.7212 | 3.8535 | 3.1284 | 2.2778 | 1.3855 | 0.43465 | -0.86946 | -1.3994 | -2.8672 | -7.2135 | -11.9326 | -17.8926
| LATHERON | CT |  |  | 5.509 | 5.3519 | 5.1816 | 3.9543 | 3.3126 | 2.5695 | 1.6976 | 0.76802 | -0.5101 | -1.012 | -2.3497 | -6.5141 | -10.8847 | -16.5669 | 4.7334 | 4.5989 | 4.4542 | 3.9683 | 3.1944 | 2.3928 | 1.5482 | 0.64387 | -0.61576 | -1.1178 | -2.5453 | -6.8072 | -11.4135 | -16.5149 | 5.0658 | 4.9006 | 4.7212 | 3.8535 | 3.1284 | 2.2778 | 1.3855 | 0.43465 | -0.86946 | -1.3994 | -2.8672 | -7.2135 | -11.9326 | -17.8926
| LATHERON | LW |  |  | 5.6518 | 5.6388 | 5.6262 | 5.6118 | 3.9043 | 3.1202 | 2.1912 | 1.1909 | 0.87071 | 0.35052 | -1.4496 | -4.5674 | -8.4357 | -9.9025 | 4.8562 | 4.8446 | 4.8328 | 4.8171 | 3.6064 | 2.711 | 1.7469 | 0.71196 | 0.34687 | -0.2181 | -2.1895 | -5.5038 | -9.7094 | -11.2946 | 5.2161 | 5.2022 | 5.1886 | 5.1721 | 3.7771 | 2.8583 | 1.9063 | 0.87841 | 0.51308 | -0.052346 | -2.022 | -5.3631 | -9.6633 | -11.2883
| LATHERON | ST |  |  | 6.0357 | 6.027 | 6.0182 | 6.0066 | 5.8824 | 5.6612 | 5.4479 | 5.1969 | 3.4812 | 3.1473 | 2.0603 | -0.80937 | -5.7975 | -11.0095 | 5.1671 | 5.1579 | 5.148 | 5.1331 | 4.9384 | 4.6493 | 3.9163 | 3.5487 | 2.9422 | 2.6049 | 1.3943 | -1.5096 | -6.306 | -11.1345 | 5.613 | 5.6031 | 5.593 | 5.5788 | 5.4257 | 5.1796 | 4.9658 | 3.8547 | 3.2232 | 2.8673 | 1.66 | -1.3952 | -6.6418 | -12.1429
| LATHERON | SP |  |  | 6.0301 | 6.0185 | 6.0069 | 5.9954 | 5.9615 | 5.9285 | 5.8952 | 5.8584 | 5.803 | 5.7425 | 5.5103 | 1.7732 | -2.636 | -5.6481 | 5.1645 | 5.1548 | 5.145 | 5.1351 | 5.0851 | 5.0329 | 4.969 | 4.902 | 4.8056 | 4.7135 | 3.7012 | 1.5763 | -2.5552 | -5.2324 | 5.6079 | 5.5958 | 5.5837 | 5.5715 | 5.5295 | 5.4871 | 5.4399 | 5.3895 | 5.3189 | 5.2579 | 3.941 | 1.3953 | -3.1087 | -6.1829
FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | YES | 8.6953 | 8.6931 | 8.6904 | 8.6685 | 8.627 | 8.5767 | 8.5119 | 8.4277 | 8.2986 | 8.2512 | 8.1009 | 7.5095 | 3.9553 | 1.8301 | 7.2837 | 7.2599 | 7.2248 | 7.1254 | 6.9372 | 6.8683 | 4.9894 | 4.3855 | 3.5827 | 3.5568 | 3.4806 | 3.3583 | 2.1321 | -0.32594 | 7.0726 | 7.0705 | 7.0678 | 7.0459 | 7.0044 | 4.9785 | 4.3903 | 3.7591 | 2.9199 | 2.8931 | 2.8146 | 2.6886 | 1.4309 | -0.99552
| LAURENCEKIRK | CT |  |  | 8.6953 | 8.6931 | 8.6904 | 8.6685 | 8.627 | 8.5767 | 8.5195 | 8.4537 | 8.3719 | 8.3272 | 8.1962 | 7.5095 | 4.0147 | 3.4119 | 7.2837 | 7.2599 | 7.2248 | 7.1254 | 7.0006 | 6.8683 | 6.7653 | 6.6863 | 6.6045 | 6.5598 | 6.4288 | 3.6397 | 2.5156 | 1.8353 | 7.0726 | 7.0705 | 7.0678 | 7.0459 | 7.0044 | 6.9541 | 6.8969 | 6.8311 | 4.8873 | 4.7851 | 4.4767 | 3.0048 | 1.7759 | 1.0803
| LAURENCEKIRK | LW |  |  | 8.6986 | 8.6986 | 8.6986 | 8.6782 | 8.6353 | 8.5799 | 8.5119 | 8.4277 | 8.2986 | 8.2512 | 8.1009 | 7.5779 | 4.3256 | 4.1329 | 7.3069 | 7.3024 | 7.2953 | 7.2572 | 7.1945 | 7.1198 | 7.0329 | 6.9303 | 6.7831 | 6.7161 | 6.508 | 5.9238 | 4.2019 | 3.4086 | 7.076 | 7.076 | 7.076 | 7.0556 | 7.0127 | 6.9573 | 6.8893 | 6.8051 | 6.676 | 6.6286 | 4.8758 | 4.2687 | 3.3874 | 2.6786
| LAURENCEKIRK | ST |  |  | 8.6977 | 8.6971 | 8.6965 | 8.6846 | 8.6606 | 8.6325 | 8.6017 | 8.5659 | 8.5152 | 8.4923 | 8.4363 | 7.6905 | 4.6122 | 4.5284 | 7.293 | 7.2777 | 7.2575 | 7.2077 | 7.1324 | 7.0428 | 6.9645 | 6.8821 | 6.7858 | 6.7415 | 6.6689 | 4.2793 | 3.4869 | 3.1907 | 7.0751 | 7.0745 | 7.0739 | 7.062 | 7.038 | 7.0099 | 6.9791 | 6.9433 | 6.8926 | 6.8696 | 4.9569 | 3.5701 | 2.7312 | 2.4253
| LAURENCEKIRK | SP |  |  | 8.6968 | 8.6958 | 8.6949 | 8.6905 | 8.6862 | 8.6818 | 8.6773 | 8.6723 | 8.6673 | 8.6594 | 8.6353 | 8.595 | 3.9553 | 1.8301 | 7.3064 | 7.3033 | 7.2998 | 7.2927 | 6.9372 | 6.9145 | 4.9894 | 4.3855 | 3.5827 | 3.5568 | 3.4806 | 3.3583 | 2.1321 | -0.32594 | 7.0742 | 7.0732 | 7.0723 | 7.0678 | 7.0636 | 4.9785 | 4.3903 | 3.7591 | 2.9199 | 2.8931 | 2.8146 | 2.6886 | 1.4309 | -0.99552
STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | 3.8074 | 3.6932 | 3.5668 | 3.4127 | 2.3769 | 2.2404 | 2.107 | 1.9767 | 1.8661 | 1.8018 | 1.6931 | 1.3345 | 0.93213 | 0.51238 | 3.3758 | 3.2772 | 3.1653 | 3.0412 | 2.4992 | 2.3552 | 2.2054 | 2.0569 | 1.9267 | 1.8351 | 1.6338 | 1.2978 | 0.91998 | 0.51523 | 3.3741 | 3.2561 | 3.126 | 2.3772 | 2.248 | 2.1195 | 1.9626 | 1.7789 | 1.6187 | 1.509 | 1.2852 | 0.90329 | 0.47655 | 0.033061
| LAXAY | CT |  |  | 3.8074 | 3.6932 | 3.5668 | 3.4127 | 2.3769 | 2.2404 | 2.107 | 1.9767 | 1.8661 | 1.8018 | 1.6931 | 1.3345 | 0.93213 | 0.51238 | 3.3758 | 3.2772 | 3.1653 | 3.0412 | 2.4992 | 2.3552 | 2.2054 | 2.0569 | 1.9267 | 1.8351 | 1.6338 | 1.2978 | 0.91998 | 0.51523 | 3.3741 | 3.2561 | 3.126 | 2.3772 | 2.248 | 2.1195 | 1.9626 | 1.7789 | 1.6187 | 1.509 | 1.2852 | 0.90329 | 0.47655 | 0.033061
| LAXAY | LW |  |  | 3.9115 | 3.902 | 3.8929 | 3.8824 | 3.8706 | 3.8576 | 3.8435 | 3.8284 | 3.8149 | 3.8008 | 3.7566 | 3.6774 | 3.5642 | 3.4913 | 3.4661 | 3.4577 | 3.4491 | 3.4375 | 3.4245 | 3.4106 | 3.3958 | 3.3804 | 3.3663 | 3.3515 | 3.3056 | 3.2251 | 3.1292 | 3.0884 | 3.4815 | 3.4718 | 3.4624 | 3.4515 | 3.4393 | 3.4259 | 3.4113 | 3.3957 | 3.3818 | 3.3672 | 3.3216 | 3.2397 | 3.1227 | 2.4407
| LAXAY | ST |  |  | 3.915 | 3.9086 | 3.9023 | 3.8938 | 3.8848 | 3.8758 | 3.865 | 3.8543 | 3.8439 | 3.8348 | 3.8039 | 3.7595 | 3.6882 | 3.6491 | 3.4693 | 3.4637 | 3.458 | 3.4501 | 3.4414 | 3.4323 | 3.4112 | 3.3903 | 3.3699 | 3.3475 | 3.279 | 3.2335 | 3.1879 | 2.4108 | 3.4851 | 3.4786 | 3.472 | 3.4633 | 3.454 | 3.4448 | 3.4336 | 3.4226 | 3.4119 | 3.4025 | 3.3706 | 3.3249 | 3.2517 | 2.3984
| LAXAY | SP |  |  | 3.9107 | 3.9022 | 3.8938 | 3.8852 | 3.8728 | 3.8606 | 3.8485 | 3.8366 | 3.8248 | 3.8131 | 3.7788 | 3.7119 | 3.653 | 3.5933 | 3.4658 | 3.4586 | 3.4514 | 3.4441 | 3.4321 | 3.4199 | 3.406 | 3.3923 | 3.3777 | 3.3623 | 3.3176 | 3.2371 | 3.1766 | 3.1402 | 3.4808 | 3.472 | 3.4632 | 3.4545 | 3.4416 | 3.429 | 3.4165 | 3.4042 | 3.3921 | 3.38 | 3.3445 | 3.2754 | 3.2147 | 3.1532
COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | 8.1638 | 6.2221 | 6.1126 | 5.9727 | 5.8164 | 5.6223 | 5.1777 | 4.691 | 4.0229 | 3.3456 | 1.307 | -3.2801 | -7.9468 | -15.6325 | 6.207 | 6.0842 | 5.9565 | 5.7646 | 5.2928 | 4.8558 | 4.4074 | 3.7155 | 2.7871 | 1.9066 | 0.12712 | -4.1719 | -8.3637 | -15.581 | 5.7767 | 5.6251 | 5.4686 | 5.2365 | 4.6953 | 4.1952 | 3.6852 | 3.0983 | 2.1831 | 1.3154 | -0.82966 | -5.7204 | -10.5231 | -18.7954
| LEOCH | CT |  |  | 8.1638 | 6.2221 | 6.1126 | 5.9727 | 5.8164 | 5.6223 | 5.1777 | 4.691 | 4.0229 | 3.3969 | 1.307 | -3.2801 | -7.9468 | -15.6325 | 6.207 | 6.0842 | 5.9565 | 5.7646 | 5.2928 | 4.8558 | 4.4074 | 3.9137 | 3.2202 | 2.5126 | 0.12712 | -4.1719 | -8.2768 | -15.581 | 5.7767 | 5.6251 | 5.4686 | 5.2365 | 4.6953 | 4.1952 | 3.6852 | 3.1279 | 2.3605 | 1.6103 | -0.82966 | -5.7204 | -10.5231 | -18.7954
| LEOCH | LW |  |  | 8.2779 | 8.2676 | 8.2575 | 8.2453 | 8.1986 | 5.9717 | 5.4098 | 4.8331 | 4.0738 | 3.3456 | 3.1797 | 0.13629 | -1.5958 | -3.9751 | 6.9665 | 6.9621 | 6.2955 | 6.2781 | 5.6594 | 5.0432 | 4.4252 | 3.7155 | 2.7871 | 1.9066 | 1.7517 | -1.1998 | -2.824 | -5.5383 | 5.9165 | 5.903 | 5.8882 | 5.8653 | 5.1734 | 4.4844 | 3.7982 | 3.0983 | 2.1831 | 1.3154 | 1.1429 | -2.1706 | -4.0269 | -6.7538
| LEOCH | ST |  |  | 8.2799 | 8.2716 | 8.2628 | 8.2501 | 8.2114 | 8.1973 | 6.2897 | 5.9845 | 5.5335 | 5 | 3.1056 | -0.85996 | -7.2149 | -12.0052 | 6.9677 | 6.2904 | 6.2664 | 6.2237 | 5.9362 | 5.653 | 5.3913 | 5.0596 | 4.5704 | 3.9319 | 1.6193 | -2.1212 | -8.3637 | -12.8631 | 5.9052 | 5.8826 | 5.855 | 5.8064 | 5.4848 | 5.1683 | 4.8757 | 4.5061 | 3.9643 | 3.3133 | 1.0403 | -3.2484 | -10.1932 | -15.3372
| LEOCH | SP |  |  | 8.2763 | 8.2666 | 8.2569 | 8.2472 | 8.227 | 8.2058 | 8.1819 | 8.1608 | 8.1418 | 8.12 | 5.4889 | 1.6842 | -1.492 | -4.1738 | 6.9653 | 6.2999 | 6.2947 | 6.2867 | 6.2024 | 6.1064 | 5.9793 | 5.8528 | 5.6843 | 5.4651 | 4.5402 | 1.0665 | -1.9204 | -4.3772 | 5.9144 | 5.9022 | 5.8895 | 5.8765 | 5.78 | 5.6712 | 5.5278 | 5.3852 | 5.1963 | 4.9512 | 3.9206 | -0.17588 | -3.499 | -6.318
NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | 4.2688 | 3.6304 | 3.5888 | 3.545 | 1.7822 | 0.52498 | -0.74767 | -2.0583 | -2.9792 | -3.1792 | -4.8253 | -7.2443 | -9.628 | -14.2474 | 3.4927 | 3.1014 | 3.0688 | 3.0354 | 1.2325 | -0.1113 | -1.4744 | -2.8776 | -3.7823 | -3.966 | -5.5537 | -7.8409 | -10.2243 | -15.3851 | 3.7836 | 2.4974 | 2.4593 | 2.4202 | 1.3407 | -0.038642 | -1.4322 | -2.8626 | -3.7884 | -3.9935 | -6.0297 | -8.5322 | -11.0991 | -16.432
| LETHEN | CT |  |  | 4.2688 | 4.2678 | 4.0883 | 3.884 | 3.2525 | 1.758 | 0.90412 | -0.032677 | -1.2794 | -2.1571 | -4.8253 | -7.2443 | -9.628 | -14.2474 | 3.4927 | 3.4924 | 3.3626 | 3.2184 | 2.0569 | 1.2676 | 0.46108 | -0.44062 | -1.6924 | -2.6072 | -5.5537 | -7.8409 | -10.2243 | -15.3851 | 3.7836 | 3.7823 | 3.5716 | 3.333 | 2.1704 | 1.3079 | 0.39689 | -0.60864 | -1.9519 | -2.953 | -6.0297 | -8.5322 | -11.0991 | -16.432
| LETHEN | LW |  |  | 4.3538 | 3.6304 | 3.5888 | 3.545 | 1.7822 | 0.52498 | -0.74767 | -2.0583 | -2.9792 | -3.1792 | -3.7388 | -6.7405 | -8.5682 | -11.5542 | 3.5449 | 3.1014 | 3.0688 | 3.0354 | 1.2325 | -0.1113 | -1.4744 | -2.8776 | -3.7823 | -3.966 | -4.4904 | -7.7289 | -9.6187 | -12.9733 | 3.878 | 2.4974 | 2.4593 | 2.4202 | 1.3407 | -0.038642 | -1.4322 | -2.8626 | -3.7884 | -3.9935 | -4.5643 | -7.8828 | -9.8511 | -13.2819
| LETHEN | ST |  |  | 4.3566 | 3.6358 | 3.6078 | 3.5775 | 3.2874 | 2.117 | 1.648 | 1.0837 | 0.24353 | -0.47539 | -2.9192 | -4.0319 | -6.0731 | -8.8054 | 3.5466 | 3.1047 | 3.0828 | 3.0598 | 2.0633 | 1.5777 | 1.0955 | 0.49082 | -0.41318 | -1.2203 | -4.0043 | -5.0958 | -7.1938 | -10.2549 | 3.8811 | 3.0803 | 2.477 | 2.4497 | 2.1794 | 1.7009 | 1.1909 | 0.56745 | -0.35705 | -1.1867 | -4.0183 | -5.1813 | -7.3512 | -10.4784
| LETHEN | SP |  |  | 4.3536 | 4.3467 | 3.6245 | 3.6175 | 3.5595 | 3.4996 | 3.4262 | 3.3503 | 2.3307 | 2.0473 | 0.88855 | -0.51566 | -3.6762 | -5.3789 | 3.5445 | 3.5403 | 3.0973 | 3.0931 | 2.4632 | 2.3403 | 2.1691 | 1.9969 | 1.7615 | 1.4578 | 0.15567 | -1.4277 | -4.7516 | -6.6074 | 3.8779 | 3.8701 | 2.4911 | 2.4846 | 2.4477 | 2.4119 | 2.3126 | 2.1488 | 1.921 | 1.6029 | 0.28096 | -1.3279 | -4.6639 | -6.5313
GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | 0.10458 | 0.10458 | 0.047288 | -0.0099347 | -0.068634 | -0.13951 | -0.21249 | -0.2876 | -0.36508 | -0.44474 | -0.587 | -0.81824 | -1.0195 | -1.2138 | 0.10246 | 0.10245 | 0.047935 | -0.0065276 | -0.062362 | -0.12977 | -0.19919 | -0.27063 | -0.34431 | -0.42008 | -0.5554 | -0.77536 | -0.96685 | -1.1517 | 0.10236 | 0.10236 | 0.044608 | -0.013126 | -0.072313 | -0.14377 | -0.21737 | -0.29309 | -0.37121 | -0.45154 | -0.59498 | -0.82814 | -1.0311 | -1.227
| LETTEREWE | CT |  |  | 0.10458 | 0.10458 | 0.047288 | -0.0099347 | -0.068634 | -0.13951 | -0.21249 | -0.2876 | -0.36508 | -0.44474 | -0.587 | -0.81824 | -1.0195 | -1.2138 | 0.10246 | 0.10245 | 0.047935 | -0.0065276 | -0.062362 | -0.12977 | -0.19919 | -0.27063 | -0.34431 | -0.42008 | -0.5554 | -0.77536 | -0.96685 | -1.1517 | 0.10236 | 0.10236 | 0.044608 | -0.013126 | -0.072313 | -0.14377 | -0.21737 | -0.29309 | -0.37121 | -0.45154 | -0.59498 | -0.82814 | -1.0311 | -1.227
| LETTEREWE | LW |  |  | 0.10458 | 0.10458 | 0.079032 | 0.053708 | 0.028468 | 0.0030622 | -0.022343 | -0.047858 | -0.073264 | -0.098779 | -0.15008 | -0.23673 | -0.3252 | -0.41584 | 0.10246 | 0.10245 | 0.07822 | 0.054039 | 0.029953 | 0.00577 | -0.018412 | -0.042698 | -0.066879 | -0.091166 | -0.14003 | -0.22254 | -0.30678 | -0.39309 | 0.10236 | 0.10236 | 0.07672 | 0.051097 | 0.025575 | -4.8545e-05 | -0.025672 | -0.051406 | -0.077029 | -0.10276 | -0.15452 | -0.24193 | -0.33117 | -0.4226
| LETTEREWE | ST |  |  | 0.10458 | 0.10458 | 0.087475 | 0.070593 | 0.053779 | 0.036897 | 0.019965 | 0.0029554 | -0.013982 | -0.030992 | -0.082297 | -0.16895 | -0.25742 | -0.34806 | 0.10246 | 0.10246 | 0.086283 | 0.070171 | 0.05412 | 0.038004 | 0.021887 | 0.0057016 | -0.010414 | -0.0266 | -0.07542 | -0.15787 | -0.24204 | -0.32828 | 0.10236 | 0.10236 | 0.085262 | 0.068183 | 0.051172 | 0.034092 | 0.017011 | -0.00014241 | -0.017222 | -0.034376 | -0.086116 | -0.1735 | -0.26271 | -0.35412
| LETTEREWE | SP |  |  | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10247 | 0.10247 | 0.10247 | 0.10247 | 0.10246 | 0.10246 | 0.10245 | 0.10244 | 0.10244 | 0.10243 | 0.10241 | 0.10237 | 0.10234 | 0.10231 | 0.10237 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | 0.10235 | 0.10235 | 0.10234 | 0.10233 | 0.10231 | 0.1023
ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | YES | 5.7484 | 5.7472 | 5.7459 | 5.744 | 5.7374 | 5.7295 | 4.8844 | 4.7584 | 4.5975 | 4.4402 | 3.8487 | 3.2815 | 1.9556 | 1.139 | 5.5985 | 5.593 | 5.5852 | 4.999 | 4.9625 | 4.8535 | 4.6994 | 4.5461 | 4.3506 | 4.1587 | 3.4371 | 2.6694 | 1.0698 | 0.16556 | 5.657 | 5.6548 | 5.6518 | 5.6459 | 5.6243 | 4.9105 | 4.7509 | 4.591 | 4.386 | 4.1843 | 3.4265 | 2.6564 | 1.0615 | 0.15893
| LHANBRYDE | CT |  |  | 5.7484 | 5.7472 | 5.7459 | 5.744 | 5.7374 | 5.7295 | 4.9964 | 4.9033 | 4.7798 | 4.6324 | 4.1307 | 3.3984 | 1.9915 | 1.139 | 5.5985 | 5.593 | 5.5852 | 4.999 | 4.9625 | 4.9282 | 4.8421 | 4.7307 | 4.5828 | 4.4043 | 3.7966 | 2.9014 | 1.1987 | 0.16556 | 5.657 | 5.6548 | 5.6518 | 5.6459 | 5.6243 | 4.9912 | 4.8998 | 4.7847 | 4.6319 | 4.4448 | 3.8075 | 2.8866 | 1.1888 | 0.15893
| LHANBRYDE | LW |  |  | 5.7501 | 5.7501 | 5.7501 | 5.7501 | 5.7495 | 5.7483 | 4.8844 | 4.7584 | 4.5975 | 4.4402 | 3.8487 | 3.2815 | 1.9556 | 1.4493 | 5.6045 | 5.6039 | 5.6028 | 5.6002 | 4.9673 | 4.8535 | 4.6994 | 4.5461 | 4.3506 | 4.1587 | 3.4371 | 2.6694 | 1.0698 | 0.46735 | 5.6598 | 5.6597 | 5.6594 | 5.6587 | 5.6328 | 4.9105 | 4.7509 | 4.591 | 4.386 | 4.1843 | 3.4265 | 2.6564 | 1.0615 | 0.4609
| LHANBRYDE | ST |  |  | 5.7497 | 5.7495 | 5.7493 | 5.749 | 5.7465 | 5.7435 | 5.7399 | 4.9879 | 4.8837 | 4.7516 | 4.2984 | 3.6677 | 2.8176 | 2.0168 | 5.6018 | 5.599 | 5.5954 | 5.5886 | 4.9863 | 4.9599 | 4.9213 | 4.8282 | 4.7022 | 4.5411 | 3.9888 | 3.2171 | 2.1664 | 1.1601 | 5.6589 | 5.658 | 5.6569 | 5.6549 | 5.6407 | 5.6261 | 4.9812 | 4.8848 | 4.7544 | 4.5866 | 4.0067 | 3.2017 | 2.154 | 1.1513
| LHANBRYDE | SP |  |  | 5.7494 | 5.749 | 5.7487 | 5.7483 | 5.7482 | 5.7481 | 5.748 | 5.7479 | 5.7478 | 5.7471 | 4.9184 | 4.6719 | 4.4361 | 4.4219 | 5.6039 | 5.6032 | 5.6024 | 5.6015 | 5.5989 | 5.5846 | 4.9992 | 4.9885 | 4.9743 | 4.9549 | 4.7414 | 4.4408 | 4.158 | 4.0997 | 5.6592 | 5.6587 | 5.6582 | 5.6577 | 5.657 | 5.6533 | 5.6479 | 5.6425 | 5.6354 | 5.6255 | 4.7945 | 4.4805 | 4.1846 | 4.114
FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | 0.75213 | 0.75212 | 0.73844 | 0.72474 | 0.71066 | 0.69367 | 0.67614 | 0.6581 | 0.63949 | 0.6204 | 0.58621 | 0.53048 | 0.48156 | 0.43351 | 0.51997 | 0.51988 | 0.50904 | 0.49803 | 0.48669 | 0.47306 | 0.45902 | 0.44483 | 0.43018 | 0.41518 | 0.38823 | 0.35474 | 0.33444 | 0.080432 | 0.58012 | 0.57997 | 0.56585 | 0.55143 | 0.53657 | 0.51876 | 0.50042 | 0.48201 | 0.46302 | 0.44354 | 0.40856 | 0.35756 | 0.068571 | 0.033172
| LIDDESDALE | CT |  |  | 0.75213 | 0.75212 | 0.73844 | 0.72474 | 0.71066 | 0.69367 | 0.67614 | 0.6581 | 0.63949 | 0.6204 | 0.58621 | 0.53048 | 0.48156 | 0.43351 | 0.51997 | 0.51988 | 0.50904 | 0.49803 | 0.48669 | 0.47306 | 0.45902 | 0.44483 | 0.43018 | 0.41518 | 0.38823 | 0.35474 | 0.33444 | 0.080432 | 0.58012 | 0.57997 | 0.56585 | 0.55143 | 0.53657 | 0.51876 | 0.50042 | 0.48201 | 0.46302 | 0.44354 | 0.40856 | 0.35756 | 0.068571 | 0.033172
| LIDDESDALE | LW |  |  | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.52008 | 0.52007 | 0.52007 | 0.52006 | 0.52004 | 0.52003 | 0.52001 | 0.52 | 0.51999 | 0.51997 | 0.51993 | 0.51987 | 0.5198 | 0.51974 | 0.58029 | 0.58029 | 0.58028 | 0.58026 | 0.58023 | 0.58021 | 0.58019 | 0.58016 | 0.58014 | 0.58011 | 0.58004 | 0.57992 | 0.57981 | 0.57969
| LIDDESDALE | ST |  |  | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.52008 | 0.52008 | 0.52007 | 0.52007 | 0.52006 | 0.52006 | 0.52001 | 0.51996 | 0.51991 | 0.51988 | 0.5198 | 0.51967 | 0.51955 | 0.51942 | 0.5803 | 0.58029 | 0.58029 | 0.58028 | 0.58027 | 0.58026 | 0.58017 | 0.58008 | 0.57999 | 0.57994 | 0.5798 | 0.57958 | 0.57935 | 0.57913
| LIDDESDALE | SP |  |  | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.75215 | 0.52008 | 0.52008 | 0.52008 | 0.52008 | 0.52008 | 0.52007 | 0.52006 | 0.52004 | 0.52002 | 0.52001 | 0.51998 | 0.51993 | 0.51988 | 0.51984 | 0.5803 | 0.5803 | 0.5803 | 0.5803 | 0.5803 | 0.58029 | 0.58026 | 0.58023 | 0.58019 | 0.58017 | 0.58012 | 0.58003 | 0.57995 | 0.57987
KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | 3.6092 | 3.5366 | 3.4666 | 3.3783 | 2.3867 | 1.6953 | 0.9707 | 0.23927 | -0.71195 | -1.6232 | -4.2216 | -8.0099 | -11.5677 | -14.5213 | 2.279 | 2.2367 | 2.1945 | 2.1361 | 1.7059 | 0.87918 | 0.056054 | -0.78658 | -1.892 | -2.9575 | -5.9927 | -10.282 | -14.0991 | -17.2754 | 2.2645 | 2.2 | 2.1379 | 2.0595 | 1.8479 | 1.0393 | 0.23384 | -0.56969 | -1.6026 | -2.6306 | -5.6155 | -9.9843 | -14.0046 | -17.3154
| LIMEHILLOCKS | CT |  |  | 3.6092 | 3.5366 | 3.4666 | 3.3783 | 2.3867 | 2.0106 | 1.6389 | 1.22 | 0.63151 | -0.055148 | -2.4187 | -6.047 | -10.2602 | -14.5213 | 2.279 | 2.2367 | 2.1945 | 2.1361 | 1.8432 | 1.455 | 1.0705 | 0.63067 | -0.0030851 | -0.79945 | -3.5699 | -7.6495 | -12.2243 | -17.1789 | 2.2645 | 2.2 | 2.1379 | 2.0595 | 1.852 | 1.4436 | 1.04 | 0.58356 | -0.06152 | -0.82312 | -3.449 | -7.5578 | -12.3419 | -17.3154
| LIMEHILLOCKS | LW |  |  | 3.6753 | 3.6692 | 3.6634 | 3.6567 | 2.4223 | 1.6953 | 0.9707 | 0.23927 | -0.71195 | -1.6232 | -4.2216 | -8.0099 | -11.5677 | -14.3045 | 2.3174 | 2.3135 | 2.3093 | 2.303 | 1.7059 | 0.87918 | 0.056054 | -0.78658 | -1.892 | -2.9575 | -5.9927 | -10.282 | -14.0991 | -17.2754 | 2.3232 | 2.3178 | 2.3126 | 2.3067 | 1.8479 | 1.0393 | 0.23384 | -0.56969 | -1.6026 | -2.6306 | -5.6155 | -9.9843 | -14.0046 | -17.1957
| LIMEHILLOCKS | ST |  |  | 3.6775 | 3.6735 | 3.6695 | 3.6641 | 3.6512 | 3.6373 | 2.3256 | 1.9769 | 1.4713 | 0.82656 | -1.4906 | -4.8146 | -9.3596 | -12.5099 | 2.3183 | 2.3153 | 2.312 | 2.307 | 2.1559 | 1.9079 | 1.5967 | 1.2012 | 0.62678 | -0.10956 | -2.8211 | -6.6441 | -11.793 | -15.4743 | 2.3252 | 2.3216 | 2.318 | 2.3133 | 2.3009 | 2.0463 | 1.7409 | 1.3533 | 0.7914 | 0.07227 | -2.4933 | -6.2963 | -11.5394 | -15.2226
| LIMEHILLOCKS | SP |  |  | 3.6749 | 3.6695 | 3.6641 | 3.6588 | 3.6498 | 3.6409 | 3.6321 | 3.6231 | 3.6134 | 2.3083 | 1.3169 | 0.050097 | -1.2002 | -2.2835 | 2.3177 | 2.3147 | 2.3116 | 2.3085 | 2.2662 | 2.2187 | 2.1485 | 2.0551 | 1.857 | 1.5921 | 0.46693 | -0.98674 | -2.4116 | -3.6584 | 2.3228 | 2.318 | 2.3133 | 2.3085 | 2.3004 | 2.2924 | 2.2844 | 2.1804 | 1.9848 | 1.724 | 0.62034 | -0.77603 | -2.1309 | -3.3564
ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | YES | 13.2228 | 13.2228 | 13.2227 | 13.2227 | 13.2224 | 13.2222 | 13.2218 | 13.2215 | 13.2211 | 13.2208 | 13.22 | 13.2182 | 13.2152 | 13.2094 | 13.1526 | 13.1525 | 13.1522 | 13.1515 | 13.1506 | 13.1498 | 13.149 | 13.1461 | 13.1432 | 13.1407 | 13.1351 | 13.1325 | 13.1296 | 13.1237 | 13.1209 | 13.1208 | 13.1207 | 13.1204 | 13.1199 | 13.1194 | 13.1189 | 13.1175 | 13.1161 | 13.115 | 13.1125 | 13.1107 | 13.1077 | 13.1019
| LOCH CARNAN | CT |  |  | 13.2228 | 13.2228 | 13.2227 | 13.2227 | 13.2224 | 13.2222 | 13.2218 | 13.2215 | 13.2211 | 13.2208 | 13.22 | 13.2182 | 13.2152 | 13.2094 | 13.1526 | 13.1525 | 13.1522 | 13.1516 | 13.1507 | 13.1499 | 13.149 | 13.1461 | 13.1432 | 13.1407 | 13.1351 | 13.1325 | 13.1296 | 13.1237 | 13.1209 | 13.1208 | 13.1207 | 13.1204 | 13.1199 | 13.1194 | 13.1189 | 13.1175 | 13.1161 | 13.115 | 13.1125 | 13.1107 | 13.1077 | 13.1019
| LOCH CARNAN | LW |  |  | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.1527 | 13.1525 | 13.1522 | 13.1515 | 13.1506 | 13.1498 | 13.149 | 13.1482 | 13.1474 | 13.1466 | 13.1444 | 13.1412 | 13.1389 | 13.1375 | 13.1209 | 13.1209 | 13.1208 | 13.1205 | 13.1201 | 13.1198 | 13.1195 | 13.1192 | 13.1189 | 13.1186 | 13.1176 | 13.1166 | 13.1156 | 13.1153
| LOCH CARNAN | ST |  |  | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.1528 | 13.1527 | 13.1526 | 13.1523 | 13.152 | 13.1516 | 13.1504 | 13.1492 | 13.1481 | 13.1463 | 13.1418 | 13.1375 | 13.1372 | 13.1372 | 13.121 | 13.1209 | 13.1209 | 13.1208 | 13.1207 | 13.1205 | 13.12 | 13.1196 | 13.1191 | 13.1184 | 13.1168 | 13.1153 | 13.1153 | 13.1153
| LOCH CARNAN | SP |  |  | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.2229 | 13.1529 | 13.1529 | 13.1528 | 13.1528 | 13.1527 | 13.1526 | 13.1522 | 13.1517 | 13.1512 | 13.1505 | 13.1484 | 13.1453 | 13.1428 | 13.1405 | 13.121 | 13.121 | 13.121 | 13.121 | 13.121 | 13.1209 | 13.1207 | 13.1206 | 13.1204 | 13.1201 | 13.1193 | 13.118 | 13.1171 | 13.1164
GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.49983 | 0.49956 | 0.50061 | 0.5006 | 0.50058 | 0.50056 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.49982 | 0.4995 | 0.49917 | 0.49885 | 0.50059 | 0.50058 | 0.50058 | 0.50057 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.49983 | 0.49951 | 0.49918 | 0.49886
| LOCH GLASCARNOCH | CT |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.49998 | 0.50061 | 0.5006 | 0.50059 | 0.50057 | 0.50056 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.4998 | 0.49957 | 0.49934 | 0.50059 | 0.50058 | 0.50058 | 0.50057 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.49981 | 0.49958 | 0.49936
| LOCH GLASCARNOCH | LW |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.49983 | 0.49956 | 0.50061 | 0.5006 | 0.50058 | 0.50056 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.49982 | 0.4995 | 0.49917 | 0.49885 | 0.50059 | 0.50058 | 0.50058 | 0.50057 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.49983 | 0.49951 | 0.49918 | 0.49886
| LOCH GLASCARNOCH | ST |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50061 | 0.50061 | 0.5006 | 0.50059 | 0.50058 | 0.50056 | 0.50056 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.49993 | 0.49979 | 0.50059 | 0.50059 | 0.50058 | 0.50058 | 0.50057 | 0.50057 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.49994 | 0.4998
| LOCH GLASCARNOCH | SP |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.5006 | 0.5006 | 0.50059 | 0.50058 | 0.50058 | 0.50056 | 0.50055 | 0.50055 | 0.50055 | 0.50059 | 0.50059 | 0.50059 | 0.50059 | 0.50059 | 0.50059 | 0.50058 | 0.50058 | 0.50058 | 0.50058 | 0.50057 | 0.50056 | 0.50056 | 0.50056
FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | 5.3288 | 5.3286 | 5.3285 | 5.3282 | 5.3276 | 5.3268 | 5.326 | 5.3247 | 5.3234 | 5.3225 | 5.3194 | 5.3133 | 5.3045 | 4.9929 | 5.445 | 5.4446 | 5.4441 | 5.4429 | 5.4414 | 5.4398 | 5.4381 | 5.4342 | 5.4303 | 5.4265 | 5.4155 | 5.4014 | 5.3947 | 5.3817 | 5.3025 | 5.3024 | 5.3023 | 5.3021 | 5.3016 | 5.301 | 5.3003 | 5.2995 | 5.2986 | 5.2981 | 5.2963 | 5.2923 | 4.9701 | 4.9313
| LOCHALINE | CT |  |  | 5.3288 | 5.3286 | 5.3285 | 5.3282 | 5.3276 | 5.3268 | 5.326 | 5.3247 | 5.3234 | 5.3225 | 5.3194 | 5.3133 | 5.3045 | 4.9929 | 5.445 | 5.4446 | 5.4441 | 5.443 | 5.4414 | 5.4398 | 5.4381 | 5.4342 | 5.4303 | 5.4265 | 5.4155 | 5.4014 | 5.3947 | 5.3817 | 5.3025 | 5.3024 | 5.3023 | 5.3021 | 5.3016 | 5.301 | 5.3003 | 5.2995 | 5.2986 | 5.2981 | 5.2963 | 5.2923 | 4.9701 | 4.9313
| LOCHALINE | LW |  |  | 5.3289 | 5.3289 | 5.3288 | 5.3286 | 5.3284 | 5.3282 | 5.328 | 5.3279 | 5.3277 | 5.3275 | 5.3269 | 5.326 | 5.3251 | 5.3242 | 5.4451 | 5.4447 | 5.4442 | 5.4429 | 5.4414 | 5.44 | 5.4386 | 5.4372 | 5.4359 | 5.4344 | 5.4301 | 5.4234 | 5.4178 | 5.4122 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026 | 5.3026
| LOCHALINE | ST |  |  | 5.3289 | 5.3288 | 5.3288 | 5.3287 | 5.3284 | 5.328 | 5.3275 | 5.3271 | 5.3265 | 5.3261 | 5.3248 | 5.3227 | 5.3175 | 5.314 | 5.4452 | 5.445 | 5.4447 | 5.4443 | 5.4435 | 5.4425 | 5.4415 | 5.4404 | 5.4394 | 5.437 | 5.4303 | 5.4198 | 5.4078 | 5.4025 | 5.3026 | 5.3026 | 5.3025 | 5.3025 | 5.3023 | 5.302 | 5.3016 | 5.3012 | 5.3007 | 5.3006 | 5.3001 | 5.2994 | 5.2955 | 4.9995
| LOCHALINE | SP |  |  | 5.3288 | 5.3288 | 5.3287 | 5.3287 | 5.3286 | 5.3286 | 5.3285 | 5.3285 | 5.3285 | 5.3283 | 5.3276 | 5.3269 | 5.325 | 5.3214 | 5.4453 | 5.4452 | 5.4451 | 5.445 | 5.4448 | 5.4446 | 5.4444 | 5.4442 | 5.4439 | 5.4429 | 5.4402 | 5.4361 | 5.4311 | 5.4245 | 5.3025 | 5.3025 | 5.3024 | 5.3024 | 5.3023 | 5.3023 | 5.3023 | 5.3023 | 5.3023 | 5.3022 | 5.3019 | 5.3017 | 5.3002 | 5.2971
TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | 1.8385 | 1.8372 | 1.8321 | 1.8245 | 1.8159 | 1.8078 | 1.8009 | 1.7936 | 1.7859 | 1.7788 | 1.7646 | 1.7395 | 1.7171 | 1.6867 | 1.5811 | 1.5804 | 1.5749 | 1.5681 | 1.5605 | 1.5517 | 1.5428 | 1.5311 | 1.5193 | 1.5076 | 1.48 | 1.4572 | 1.4345 | 1.4013 | 1.6552 | 1.6535 | 1.6474 | 1.6382 | 1.6279 | 1.6168 | 1.6054 | 1.588 | 1.5704 | 1.5525 | 1.5306 | 1.5044 | 1.4763 | 1.4379
| LOCHDONHEAD | CT |  |  | 1.8385 | 1.8372 | 1.8321 | 1.8245 | 1.8159 | 1.8078 | 1.8009 | 1.7936 | 1.7859 | 1.7788 | 1.7646 | 1.7395 | 1.7171 | 1.6867 | 1.5811 | 1.5804 | 1.5749 | 1.5681 | 1.5605 | 1.5517 | 1.5428 | 1.5311 | 1.5193 | 1.5076 | 1.48 | 1.4572 | 1.4345 | 1.4013 | 1.6552 | 1.6535 | 1.6474 | 1.6382 | 1.6279 | 1.6168 | 1.6054 | 1.588 | 1.5704 | 1.5525 | 1.5306 | 1.5044 | 1.4763 | 1.4379
| LOCHDONHEAD | LW |  |  | 1.8386 | 1.8372 | 1.8349 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.8298 | 1.5813 | 1.5806 | 1.5795 | 1.5768 | 1.5738 | 1.5708 | 1.5679 | 1.5651 | 1.5623 | 1.5593 | 1.5504 | 1.5362 | 1.527 | 1.527 | 1.6553 | 1.6535 | 1.6506 | 1.6435 | 1.6356 | 1.6279 | 1.6203 | 1.6129 | 1.6057 | 1.5989 | 1.5989 | 1.5989 | 1.5989 | 1.5989
| LOCHDONHEAD | ST |  |  | 1.8392 | 1.8385 | 1.8375 | 1.8357 | 1.8332 | 1.8301 | 1.8292 | 1.829 | 1.8287 | 1.8287 | 1.8284 | 1.828 | 1.8259 | 1.8247 | 1.5815 | 1.5812 | 1.5807 | 1.5799 | 1.5786 | 1.577 | 1.5752 | 1.5733 | 1.5715 | 1.5685 | 1.5596 | 1.5454 | 1.5297 | 1.5219 | 1.656 | 1.6551 | 1.6539 | 1.6516 | 1.6485 | 1.6447 | 1.6402 | 1.6358 | 1.6314 | 1.6236 | 1.6008 | 1.5972 | 1.5951 | 1.5939
| LOCHDONHEAD | SP |  |  | 1.8398 | 1.8397 | 1.8396 | 1.8394 | 1.8387 | 1.8379 | 1.8368 | 1.8356 | 1.8341 | 1.8317 | 1.8294 | 1.8293 | 1.8285 | 1.8267 | 1.5818 | 1.5818 | 1.5817 | 1.5816 | 1.5813 | 1.5809 | 1.5803 | 1.5798 | 1.579 | 1.5778 | 1.5743 | 1.5688 | 1.563 | 1.5566 | 1.6568 | 1.6566 | 1.6565 | 1.6563 | 1.6554 | 1.6544 | 1.6529 | 1.6515 | 1.6497 | 1.6466 | 1.6376 | 1.6235 | 1.6096 | 1.5959
KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | 3.3572 | 3.3564 | 3.3039 | 3.251 | 3.1941 | 3.1255 | 3.0543 | 2.9802 | 2.859 | 2.7321 | 2.4991 | 2.1114 | 1.7504 | 1.3531 | 2.9813 | 2.98 | 2.9475 | 2.9135 | 2.8402 | 2.7263 | 2.6093 | 2.4895 | 2.3662 | 2.2417 | 1.9916 | 1.5764 | 1.1792 | 0.74533 | 3.1485 | 3.1444 | 3.0512 | 2.9508 | 2.8445 | 2.7192 | 2.5901 | 2.4575 | 2.3207 | 2.1826 | 1.9152 | 1.4716 | 1.0536 | 0.60014
| LOCHEARNHEAD | CT |  |  | 3.3572 | 3.3564 | 3.3039 | 3.251 | 3.1941 | 3.1255 | 3.0543 | 2.9802 | 2.859 | 2.7321 | 2.4991 | 2.1114 | 1.7504 | 1.3531 | 2.9813 | 2.98 | 2.9475 | 2.9135 | 2.8402 | 2.7263 | 2.6093 | 2.4895 | 2.3662 | 2.2417 | 1.9916 | 1.5764 | 1.1792 | 0.74533 | 3.1485 | 3.1444 | 3.0512 | 2.9508 | 2.8445 | 2.7192 | 2.5901 | 2.4575 | 2.3207 | 2.1826 | 1.9152 | 1.4716 | 1.0536 | 0.60014
| LOCHEARNHEAD | LW |  |  | 3.3582 | 3.3582 | 3.3381 | 3.318 | 3.298 | 3.2779 | 3.2578 | 3.2376 | 3.2175 | 3.1973 | 3.1567 | 3.0882 | 3.0182 | 2.9113 | 2.9828 | 2.9826 | 2.9704 | 2.9576 | 2.9448 | 2.932 | 2.9193 | 2.9064 | 2.8782 | 2.8425 | 2.7642 | 2.6337 | 2.5008 | 2.3658 | 3.1521 | 3.1511 | 3.1154 | 3.0771 | 3.0384 | 2.9998 | 2.9612 | 2.9226 | 2.8842 | 2.8454 | 2.7627 | 2.6242 | 2.4831 | 2.3393
| LOCHEARNHEAD | ST |  |  | 3.3579 | 3.3578 | 3.3442 | 3.3306 | 3.3157 | 3.3003 | 3.2847 | 3.2687 | 3.2524 | 3.238 | 3.1946 | 3.1213 | 3.0266 | 2.8842 | 2.9823 | 2.9818 | 2.9732 | 2.9641 | 2.9532 | 2.9418 | 2.9301 | 2.9181 | 2.9022 | 2.8701 | 2.7747 | 2.6162 | 2.4363 | 2.265 | 3.1505 | 3.1483 | 3.1228 | 3.0946 | 3.0633 | 3.0301 | 2.9972 | 2.9639 | 2.9306 | 2.8984 | 2.7861 | 2.6007 | 2.3944 | 2.1968
| LOCHEARNHEAD | SP |  |  | 3.3576 | 3.3573 | 3.357 | 3.3567 | 3.3533 | 3.35 | 3.3465 | 3.3427 | 3.3365 | 3.3294 | 3.3043 | 3.2824 | 3.04 | 2.9501 | 2.9824 | 2.9821 | 2.9817 | 2.9813 | 2.9775 | 2.9738 | 2.9699 | 2.9656 | 2.9587 | 2.9511 | 2.9243 | 2.8998 | 2.6549 | 2.5627 | 3.1522 | 3.1517 | 3.151 | 3.1504 | 3.1449 | 3.1392 | 3.1332 | 3.1268 | 3.1172 | 3.1069 | 3.0725 | 3.0258 | 2.7529 | 2.634
LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | 27.8141 | 27.8133 | 27.8123 | 27.8102 | 27.807 | 27.0946 | 26.9462 | 26.5611 | 25.8886 | 25.7366 | 22.2305 | 21.4179 | 20.8844 | 20.6381 | 24.9189 | 24.913 | 24.9041 | 24.8801 | 24.8535 | 24.1962 | 23.9951 | 23.5928 | 20.6895 | 20.5381 | 20.0841 | 19.2675 | 18.73 | 18.4798 | 26.1389 | 26.1366 | 26.1334 | 26.1256 | 26.1164 | 25.4185 | 25.2549 | 24.8648 | 24.1875 | 21.1097 | 20.6583 | 19.8458 | 19.3122 | 19.066
| LOCHEE | CT |  |  | 27.8141 | 27.8133 | 27.8123 | 27.8102 | 27.807 | 27.7359 | 27.678 | 27.6194 | 27.5199 | 27.462 | 27.2878 | 26.7561 | 26.1347 | 25.7683 | 24.9189 | 24.913 | 24.9042 | 24.8836 | 24.8605 | 24.7699 | 24.693 | 24.6108 | 24.4881 | 24.4051 | 24.1566 | 23.505 | 20.9501 | 20.5881 | 26.1389 | 26.1366 | 26.1334 | 26.126 | 26.117 | 26.0403 | 25.9769 | 25.9115 | 25.8052 | 25.7401 | 25.5445 | 24.9781 | 24.3218 | 23.9208
| LOCHEE | LW |  |  | 27.8144 | 27.8139 | 27.8132 | 27.8112 | 27.809 | 27.7242 | 27.6395 | 27.5548 | 27.4701 | 27.4019 | 27.1971 | 26.5654 | 25.8332 | 25.4322 | 24.9197 | 24.9136 | 24.9041 | 24.8801 | 24.8535 | 24.7448 | 24.6367 | 24.5291 | 24.4221 | 24.3297 | 24.0533 | 23.3063 | 20.6487 | 20.252 | 26.1394 | 26.1373 | 26.134 | 26.1256 | 26.1164 | 26.0247 | 25.9332 | 25.8419 | 25.7508 | 25.6755 | 25.4501 | 24.7851 | 24.0194 | 20.8495
| LOCHEE | ST |  |  | 27.8146 | 27.8142 | 27.8138 | 27.813 | 27.8117 | 27.3313 | 26.9462 | 26.5611 | 25.8886 | 25.7366 | 22.2305 | 21.4179 | 20.8844 | 20.6381 | 24.9214 | 24.9179 | 24.9131 | 24.9041 | 24.8916 | 24.3977 | 23.9951 | 23.5928 | 20.6895 | 20.5381 | 20.0841 | 19.2675 | 18.73 | 18.4798 | 26.14 | 26.1387 | 26.137 | 26.1339 | 26.1293 | 25.645 | 25.2549 | 24.8648 | 24.1875 | 21.1097 | 20.6583 | 19.8458 | 19.3122 | 19.066
| LOCHEE | SP |  |  | 27.8148 | 27.8147 | 27.8146 | 27.8145 | 27.8142 | 27.0946 | 27.0941 | 27.0936 | 26.3737 | 26.2466 | 25.8655 | 22.1228 | 21.6767 | 21.5333 | 24.9248 | 24.9243 | 24.9237 | 24.923 | 24.9195 | 24.1962 | 24.19 | 24.1838 | 23.4566 | 21.0452 | 20.6648 | 19.9805 | 19.5329 | 19.3882 | 26.1411 | 26.1409 | 26.1406 | 26.1404 | 26.1392 | 25.4185 | 25.4163 | 25.4142 | 24.6922 | 24.5632 | 24.1765 | 20.5507 | 20.1045 | 19.9611
PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | YES | 16.8549 | 16.8526 | 16.8453 | 16.8368 | 16.775 | 16.1734 | 15.9189 | 15.5096 | 14.8044 | 14.6463 | 14.178 | 13.1101 | 12.2964 | 11.9416 | 13.3577 | 13.3553 | 13.3499 | 13.3432 | 13.2832 | 12.6711 | 12.4216 | 12.0123 | 11.3072 | 11.1491 | 10.6808 | 9.6821 | 8.8099 | 8.1616 | 13.7343 | 13.7319 | 13.7226 | 13.712 | 13.648 | 13.0587 | 12.7982 | 12.3889 | 11.6838 | 11.5257 | 11.0574 | 9.996 | 9.1823 | 8.8276
| LOCHGILPHEAD | CT |  |  | 16.8549 | 16.8526 | 16.8453 | 16.8368 | 16.775 | 16.642 | 16.5165 | 16.3859 | 16.1916 | 16.1083 | 15.8724 | 14.722 | 13.7948 | 13.101 | 13.3577 | 13.3553 | 13.3499 | 13.3432 | 13.2832 | 13.1524 | 13.0293 | 12.901 | 12.7091 | 12.6284 | 12.3969 | 10.9478 | 9.556 | 8.4041 | 13.7343 | 13.7319 | 13.7226 | 13.712 | 13.648 | 13.5124 | 13.3843 | 13.2508 | 13.0537 | 12.9676 | 12.7264 | 11.5239 | 10.1376 | 8.9913
| LOCHGILPHEAD | LW |  |  | 16.8712 | 16.8712 | 16.8583 | 16.8583 | 16.7901 | 16.6422 | 16.492 | 16.3365 | 16.1472 | 16.0654 | 15.8227 | 14.7869 | 13.9628 | 13.543 | 13.3688 | 13.3688 | 13.3611 | 13.3611 | 13.2929 | 13.145 | 12.9947 | 12.8392 | 12.65 | 12.5682 | 12.3254 | 11.4281 | 10.604 | 10.1842 | 13.7564 | 13.7564 | 13.7377 | 13.7377 | 13.6695 | 13.5216 | 13.3713 | 13.2158 | 13.0266 | 12.9448 | 12.702 | 11.6795 | 10.8554 | 10.4356
| LOCHGILPHEAD | ST |  |  | 16.8573 | 16.8567 | 16.8561 | 16.8552 | 16.8178 | 16.3227 | 15.9189 | 15.5096 | 14.8044 | 14.6463 | 14.178 | 13.1101 | 12.2964 | 11.9416 | 13.3601 | 13.3595 | 13.3588 | 13.358 | 13.3206 | 12.8254 | 12.4216 | 12.0123 | 11.3072 | 11.1491 | 10.6808 | 9.6821 | 8.8099 | 8.1616 | 13.7367 | 13.7361 | 13.7354 | 13.7346 | 13.6972 | 13.202 | 12.7982 | 12.3889 | 11.6838 | 11.5257 | 11.0574 | 9.996 | 9.1823 | 8.8276
| LOCHGILPHEAD | SP |  |  | 16.8689 | 16.8677 | 16.8664 | 16.8652 | 16.8603 | 16.1734 | 16.1685 | 16.1631 | 15.4721 | 15.3413 | 14.9429 | 14.2621 | 13.4552 | 13.1329 | 13.3666 | 13.3654 | 13.3641 | 13.3629 | 13.358 | 12.6711 | 12.6662 | 12.6608 | 11.9698 | 11.839 | 11.4406 | 10.7598 | 9.9529 | 9.6306 | 13.7542 | 13.7529 | 13.7517 | 13.7504 | 13.7456 | 13.0587 | 13.0538 | 13.0483 | 12.3574 | 12.2265 | 11.8281 | 11.1473 | 10.3404 | 10.0182
CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | 4.9481 | 4.948 | 4.9398 | 4.9315 | 4.9225 | 4.9116 | 4.9003 | 4.8885 | 4.8762 | 4.8642 | 4.8415 | 4.8028 | 4.7642 | 4.7167 | 1.8184 | 1.8183 | 1.8145 | 1.8107 | 1.8063 | 1.8009 | 1.7952 | 1.7893 | 1.783 | 1.7773 | 1.7657 | 1.7449 | 1.7007 | 1.6269 | 1.3189 | 1.3188 | 1.3075 | 1.2962 | 1.284 | 1.2693 | 1.2541 | 1.2383 | 1.2203 | 1.1967 | 1.1462 | 1.0624 | 0.98046 | 0.88788
| LOCHGOILHEAD | CT |  |  | 4.9481 | 4.948 | 4.9398 | 4.9315 | 4.9225 | 4.9116 | 4.9003 | 4.8885 | 4.8762 | 4.8642 | 4.8415 | 4.8028 | 4.7642 | 4.7167 | 1.8184 | 1.8183 | 1.8145 | 1.8107 | 1.8063 | 1.8009 | 1.7952 | 1.7893 | 1.783 | 1.7773 | 1.7657 | 1.7449 | 1.7007 | 1.6269 | 1.3189 | 1.3188 | 1.3075 | 1.2962 | 1.284 | 1.2693 | 1.2541 | 1.2383 | 1.2203 | 1.1967 | 1.1462 | 1.0624 | 0.98046 | 0.88788
| LOCHGOILHEAD | LW |  |  | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 4.9483 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.8186 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3191 | 1.3156 | 1.307 | 1.2985
| LOCHGOILHEAD | ST |  |  | 4.9483 | 4.9483 | 4.9482 | 4.9482 | 4.9479 | 4.9476 | 4.9473 | 4.9469 | 4.9464 | 4.9462 | 4.9458 | 4.945 | 4.941 | 4.9387 | 1.8186 | 1.8185 | 1.8185 | 1.8185 | 1.8182 | 1.8179 | 1.8175 | 1.8171 | 1.8167 | 1.8165 | 1.816 | 1.8153 | 1.8113 | 1.809 | 1.3191 | 1.3191 | 1.319 | 1.319 | 1.3187 | 1.3184 | 1.3181 | 1.3177 | 1.3172 | 1.317 | 1.3166 | 1.2977 | 1.2754 | 1.2542
| LOCHGOILHEAD | SP |  |  | 4.9482 | 4.9482 | 4.9482 | 4.9481 | 4.9481 | 4.9481 | 4.9481 | 4.9481 | 4.9481 | 4.948 | 4.9478 | 4.9476 | 4.9466 | 4.9442 | 1.8185 | 1.8185 | 1.8184 | 1.8184 | 1.8184 | 1.8184 | 1.8184 | 1.8184 | 1.8184 | 1.8183 | 1.8181 | 1.8179 | 1.8168 | 1.8145 | 1.319 | 1.319 | 1.319 | 1.3189 | 1.3189 | 1.3189 | 1.3189 | 1.3189 | 1.3189 | 1.3188 | 1.3186 | 1.3184 | 1.3174 | 1.3106
GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | 3.3359 | 3.3302 | 3.1413 | 2.9709 | 2.3939 | 2.0904 | 1.7777 | 1.4503 | 1.1091 | 0.75991 | 0.12888 | -0.91395 | -1.8372 | -2.7555 | 3.3516 | 3.3512 | 3.1992 | 3.047 | 2.4042 | 2.1162 | 1.8009 | 1.4773 | 1.1437 | 0.80196 | 0.17442 | -0.85048 | -1.7636 | -2.6731 | 3.2531 | 3.2521 | 3.0243 | 2.2936 | 2.0257 | 1.7048 | 1.3744 | 1.0354 | 0.6838 | 0.32063 | -0.33566 | -1.4074 | -2.3559 | -3.2988
| LOCHINVER | CT |  |  | 3.3359 | 3.3302 | 3.1413 | 2.9709 | 2.3939 | 2.0904 | 1.7777 | 1.4503 | 1.1091 | 0.75991 | 0.12888 | -0.91395 | -1.8372 | -2.7555 | 3.3516 | 3.3512 | 3.1992 | 3.047 | 2.4042 | 2.1162 | 1.8009 | 1.4773 | 1.1437 | 0.80196 | 0.17442 | -0.85048 | -1.7636 | -2.6731 | 3.2531 | 3.2521 | 3.0243 | 2.2936 | 2.0257 | 1.7048 | 1.3744 | 1.0354 | 0.6838 | 0.32063 | -0.33566 | -1.4074 | -2.3559 | -3.2988
| LOCHINVER | LW |  |  | 3.3405 | 3.3386 | 3.2556 | 3.1681 | 3.0801 | 3.0085 | 2.9396 | 2.4859 | 2.3801 | 2.2714 | 2.0506 | 1.6783 | 1.2923 | 0.89429 | 3.3521 | 3.3521 | 3.2849 | 3.2177 | 3.1507 | 3.0835 | 3.0162 | 2.476 | 2.4003 | 2.3005 | 2.0743 | 1.6935 | 1.305 | 0.90782 | 3.254 | 3.2538 | 3.153 | 3.0517 | 2.4708 | 2.3561 | 2.2416 | 2.1266 | 2.0122 | 1.897 | 1.661 | 1.2635 | 0.85795 | 0.4432
| LOCHINVER | ST |  |  | 3.3412 | 3.3403 | 3.2857 | 3.2301 | 3.1736 | 3.1161 | 3.0532 | 3.0062 | 2.9594 | 2.9125 | 2.3292 | 1.9503 | 1.5597 | 1.1625 | 3.3521 | 3.352 | 3.3072 | 3.2623 | 3.2173 | 3.1721 | 3.1268 | 3.0812 | 3.0358 | 2.9906 | 2.3383 | 1.9552 | 1.5501 | 1.1386 | 3.254 | 3.2539 | 3.1867 | 3.1194 | 3.052 | 2.9842 | 2.433 | 2.3538 | 2.2749 | 2.194 | 1.9507 | 1.5416 | 1.1206 | 0.69276
| LOCHINVER | SP |  |  | 3.342 | 3.3418 | 3.3133 | 3.2848 | 3.2564 | 3.2292 | 3.2002 | 3.1716 | 3.143 | 3.1145 | 3.0457 | 2.9593 | 2.4953 | 2.3866 | 3.352 | 3.3519 | 3.328 | 3.304 | 3.2809 | 3.2588 | 3.2374 | 3.2164 | 3.196 | 3.1764 | 3.1204 | 3.0371 | 2.4587 | 2.3676 | 3.254 | 3.2539 | 3.2182 | 3.1824 | 3.1477 | 3.1145 | 3.0822 | 3.0505 | 3.0197 | 2.9898 | 2.416 | 2.2675 | 2.1326 | 2.0088
LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | 38.5099 | 38.5026 | 38.4923 | 38.4708 | 38.3061 | 37.77 | 37.5543 | 37.1307 | 36.4055 | 36.2095 | 35.6094 | 34.6137 | 33.8304 | 33.372 | 34.5272 | 34.5004 | 34.4609 | 34.3697 | 34.147 | 33.7088 | 33.2664 | 32.8127 | 31.9969 | 31.646 | 30.6027 | 29.2236 | 28.4879 | 21.7852 | 31.6478 | 31.6336 | 31.6132 | 31.5674 | 31.3825 | 30.9006 | 30.6158 | 30.1606 | 29.3949 | 29.145 | 28.3625 | 27.0504 | 19.2317 | 17.7417
| LOCHSIDE | CT |  |  | 38.5099 | 38.5026 | 38.4923 | 38.4708 | 38.4247 | 38.3093 | 38.2051 | 38.0976 | 37.9377 | 37.8235 | 37.5074 | 36.6681 | 35.6612 | 34.8322 | 34.5272 | 34.5004 | 34.4609 | 34.3697 | 34.1951 | 33.9617 | 33.7412 | 33.5165 | 33.2119 | 32.9279 | 32.2056 | 31.3199 | 30.3896 | 29.615 | 31.6478 | 31.6336 | 31.6132 | 31.5674 | 31.4765 | 31.32 | 31.1753 | 31.0269 | 30.8166 | 30.6405 | 30.0738 | 29.179 | 20.8882 | 18.4325
| LOCHSIDE | LW |  |  | 38.5174 | 38.5159 | 38.5134 | 38.5072 | 38.3061 | 38.0171 | 37.7222 | 37.4141 | 37.0144 | 36.8551 | 36.4113 | 35.2684 | 34.1004 | 33.5329 | 34.5505 | 34.5426 | 34.5302 | 34.4991 | 34.147 | 33.7088 | 33.2664 | 32.8127 | 32.2353 | 31.9255 | 31.0206 | 29.9279 | 28.832 | 21.7852 | 31.6608 | 31.657 | 31.6511 | 31.6362 | 31.3825 | 31.0415 | 30.6951 | 30.3364 | 29.8747 | 29.6528 | 28.9215 | 27.7999 | 19.2317 | 17.7417
| LOCHSIDE | ST |  |  | 38.5166 | 38.5147 | 38.5124 | 38.5083 | 38.486 | 37.9735 | 37.5543 | 37.1307 | 36.4055 | 36.2095 | 35.6094 | 34.6137 | 33.8304 | 33.372 | 34.5497 | 34.5426 | 34.5334 | 34.5161 | 34.4284 | 33.85 | 33.3524 | 32.8382 | 31.9969 | 31.646 | 30.6027 | 29.2236 | 28.4879 | 28.0851 | 31.6599 | 31.6562 | 31.6515 | 31.6429 | 31.5977 | 31.0623 | 30.6158 | 30.1606 | 29.3949 | 29.145 | 28.3625 | 27.0504 | 20.7725 | 18.6518
| LOCHSIDE | SP |  |  | 38.5172 | 38.5162 | 38.5152 | 38.5141 | 38.5095 | 37.77 | 37.7615 | 37.7531 | 37.0079 | 36.8636 | 36.4175 | 35.6448 | 35.0879 | 34.8453 | 34.5552 | 34.5535 | 34.5515 | 34.5494 | 34.5266 | 33.7663 | 33.7242 | 33.6828 | 32.8942 | 32.6935 | 32.0295 | 30.969 | 30.1767 | 29.778 | 31.6623 | 31.6611 | 31.6597 | 31.6583 | 31.6473 | 30.9006 | 30.8804 | 30.8604 | 30.1001 | 29.9361 | 29.4141 | 28.5411 | 27.896 | 27.56
BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | 5.6192 | 5.6186 | 5.6179 | 5.6173 | 4.9812 | 2.3143 | 2.148 | 1.9267 | 1.6241 | 1.3277 | 0.21266 | -1.2319 | -3.5822 | -4.4644 | 5.5871 | 5.5856 | 5.5832 | 5.5769 | 4.7432 | 1.9624 | 1.6833 | 1.4057 | 1.0516 | 0.70367 | -0.60524 | -2.2979 | -5.0544 | -6.0887 | 4.9845 | 4.9837 | 4.9827 | 4.9802 | 4.7503 | 1.9888 | 1.7288 | 1.4701 | 1.1154 | 0.76599 | -0.54849 | -2.2483 | -5.0165 | -6.0552
| LOGIE PERT | CT |  |  | 5.6192 | 5.6186 | 5.6179 | 5.6173 | 5.6159 | 3.114 | 2.4482 | 2.3675 | 2.2476 | 2.0868 | 1.3165 | 0.24517 | -1.9255 | -3.3215 | 5.5871 | 5.5856 | 5.5834 | 5.5786 | 4.9019 | 2.2963 | 2.1914 | 2.0569 | 1.8574 | 1.5981 | 0.69069 | -0.56193 | -3.1059 | -4.7396 | 4.9845 | 4.9837 | 4.9827 | 4.9803 | 4.8979 | 2.2995 | 2.2016 | 2.0763 | 1.8902 | 1.6488 | 0.75296 | -0.50487 | -3.0595 | -4.7001
| LOGIE PERT | LW |  |  | 5.6194 | 5.619 | 5.6184 | 5.6184 | 4.9812 | 2.3143 | 2.148 | 1.9267 | 1.6241 | 1.3277 | 0.21266 | -1.2319 | -3.5822 | -4.4644 | 5.5872 | 5.5857 | 5.5832 | 5.5769 | 4.7432 | 1.9624 | 1.6833 | 1.4057 | 1.0516 | 0.70367 | -0.60524 | -2.2979 | -5.0544 | -6.0887 | 4.9847 | 4.984 | 4.9829 | 4.9802 | 4.7503 | 1.9888 | 1.7288 | 1.4701 | 1.1154 | 0.76599 | -0.54849 | -2.2483 | -5.0165 | -6.0552
| LOGIE PERT | ST |  |  | 5.6195 | 5.6193 | 5.619 | 5.6185 | 5.6177 | 3.1168 | 2.4641 | 2.3842 | 2.2685 | 2.1161 | 1.3597 | 0.32346 | -1.0358 | -2.6578 | 5.5878 | 5.587 | 5.586 | 5.5839 | 4.9239 | 2.321 | 2.2155 | 2.0812 | 1.8873 | 1.6326 | 0.73939 | -0.47533 | -2.0656 | -3.9685 | 4.985 | 4.9846 | 4.9841 | 4.9832 | 4.9185 | 2.3226 | 2.2243 | 2.0993 | 1.9186 | 1.6815 | 0.80182 | -0.41803 | -2.015 | -3.9259
| LOGIE PERT | SP |  |  | 5.6197 | 5.6196 | 5.6195 | 5.6194 | 5.6181 | 3.118 | 3.118 | 3.1179 | 3.1178 | 2.467 | 2.2399 | 1.8842 | 1.5071 | 1.1662 | 5.5885 | 5.5883 | 5.5881 | 5.5879 | 5.5593 | 2.4757 | 2.4251 | 2.3754 | 2.3091 | 2.219 | 1.8358 | 1.3546 | 0.91615 | 0.51777 | 4.9852 | 4.9851 | 4.985 | 4.9849 | 4.9722 | 2.4578 | 2.4196 | 2.3733 | 2.3116 | 2.2278 | 1.871 | 1.4197 | 0.97942 | 0.57939
MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | 30.8413 | 31.8053 | 31.7981 | 31.7854 | 31.7442 | 31.714 | 31.6797 | 31.64 | 31.5938 | 31.5685 | 31.4839 | 30.8409 | 21.3535 | 18.6011 | 27.6639 | 28.5662 | 28.5424 | 28.495 | 28.3441 | 28.1637 | 27.9591 | 27.8458 | 27.6708 | 27.6455 | 27.5609 | 20.8955 | 16.9719 | 13.8279 | 28.8014 | 29.7106 | 29.6963 | 29.6664 | 29.571 | 29.4957 | 29.4181 | 29.3101 | 29.1787 | 29.0484 | 28.6145 | 20.8994 | 16.9867 | 13.8504
| LONGHAUGH | CT |  |  | 30.8413 | 31.8053 | 31.7981 | 31.7854 | 31.7442 | 31.714 | 31.6797 | 31.64 | 31.5938 | 31.5685 | 31.4839 | 30.8409 | 21.3535 | 18.6011 | 27.6639 | 28.5662 | 28.5424 | 28.495 | 28.3441 | 28.2034 | 28.059 | 27.8458 | 27.6708 | 27.6455 | 27.5609 | 20.8955 | 16.9719 | 13.8279 | 28.8014 | 29.7106 | 29.6963 | 29.6664 | 29.571 | 29.4957 | 29.4181 | 29.3101 | 29.1787 | 29.0484 | 28.6145 | 20.8994 | 16.9867 | 13.8504
| LONGHAUGH | LW |  |  | 30.8488 | 31.8184 | 31.8178 | 31.8162 | 31.7893 | 31.787 | 31.7834 | 31.7783 | 31.7686 | 31.7665 | 31.7577 | 31.3055 | 22.126 | 21.0611 | 27.6815 | 28.5979 | 28.5922 | 28.578 | 28.3693 | 28.1637 | 27.9591 | 27.8553 | 27.8456 | 27.8435 | 27.8347 | 20.9856 | 17.7446 | 16.4869 | 28.8131 | 29.7314 | 29.7287 | 29.7219 | 29.6066 | 29.5244 | 29.4417 | 29.3583 | 29.2505 | 29.15 | 28.7735 | 20.9906 | 17.7594 | 16.5054
| LONGHAUGH | ST |  |  | 30.8464 | 31.8143 | 31.8118 | 31.8076 | 31.7843 | 31.7655 | 31.7523 | 31.7368 | 31.7184 | 31.7124 | 31.6937 | 31.4384 | 31.2593 | 21.6138 | 27.6713 | 28.5799 | 28.5649 | 28.54 | 28.4257 | 28.308 | 28.1917 | 28.0539 | 27.8729 | 27.7894 | 27.7707 | 27.6041 | 19.8064 | 17.1037 | 28.8075 | 29.7216 | 29.7139 | 29.6999 | 29.6316 | 29.5681 | 29.5143 | 29.4507 | 29.3683 | 29.2699 | 28.9409 | 28.3754 | 19.8722 | 17.1774
| LONGHAUGH | SP |  |  | 30.8464 | 31.8149 | 31.8133 | 31.8116 | 31.8077 | 31.8033 | 31.7969 | 31.7906 | 31.7822 | 31.7796 | 31.7714 | 31.7641 | 31.6994 | 31.6113 | 27.6804 | 28.5978 | 28.5948 | 28.5917 | 28.5597 | 28.5275 | 28.4818 | 28.4368 | 28.3774 | 28.2901 | 27.9506 | 27.8411 | 27.7764 | 27.6883 | 28.8112 | 29.7293 | 29.7271 | 29.7248 | 29.7094 | 29.6915 | 29.6657 | 29.6403 | 29.6067 | 29.5696 | 29.431 | 29.2522 | 29.037 | 28.8074
ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | YES | 20.2063 | 20.2037 | 20.2009 | 20.1966 | 20.1829 | 20.1665 | 20.1474 | 20.1253 | 20.1004 | 20.0862 | 20.0389 | 19.9291 | 19.7484 | 19.3979 | 18.3353 | 18.3285 | 18.3194 | 18.3 | 18.2702 | 18.238 | 18.2034 | 18.1235 | 18.0419 | 17.9662 | 17.7368 | 17.3607 | 17.1013 | 16.6732 | 18.3655 | 18.3613 | 18.356 | 18.3458 | 18.3257 | 18.3032 | 18.2779 | 18.2331 | 18.2067 | 18.1925 | 18.1452 | 18.0353 | 17.8547 | 17.5041
| LOSSIEMOUTH | CT |  |  | 20.2063 | 20.2037 | 20.2009 | 20.1966 | 20.1829 | 20.1665 | 20.1474 | 20.1253 | 20.1004 | 20.0862 | 20.0389 | 19.9291 | 19.7484 | 19.3979 | 18.3353 | 18.3285 | 18.3194 | 18.3 | 18.2702 | 18.238 | 18.2034 | 18.1235 | 18.0419 | 17.9662 | 17.7368 | 17.3607 | 17.1013 | 16.6732 | 18.3655 | 18.3613 | 18.356 | 18.3458 | 18.3257 | 18.3032 | 18.2779 | 18.2331 | 18.2067 | 18.1925 | 18.1452 | 18.0353 | 17.8547 | 17.5041
| LOSSIEMOUTH | LW |  |  | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 20.2099 | 18.341 | 18.3384 | 18.3342 | 18.3238 | 18.3122 | 18.3008 | 18.2897 | 18.2789 | 18.2683 | 18.2568 | 18.2228 | 18.1681 | 18.113 | 18.0585 | 18.37 | 18.369 | 18.3673 | 18.3632 | 18.3586 | 18.3542 | 18.3498 | 18.3455 | 18.3414 | 18.3369 | 18.3235 | 18.3162 | 18.3162 | 18.3162
| LOSSIEMOUTH | ST |  |  | 20.2092 | 20.2087 | 20.2082 | 20.2077 | 20.203 | 20.1974 | 20.1908 | 20.1833 | 20.1749 | 20.1722 | 20.1638 | 20.15 | 20.0777 | 20.0368 | 18.3385 | 18.3341 | 18.3286 | 18.3183 | 18.3004 | 18.279 | 18.2414 | 18.2035 | 18.1653 | 18.122 | 17.9958 | 17.7926 | 17.5324 | 17.433 | 18.3686 | 18.3666 | 18.3641 | 18.3597 | 18.3498 | 18.338 | 18.3192 | 18.2998 | 18.2812 | 18.2785 | 18.2701 | 18.2562 | 18.184 | 18.143
| LOSSIEMOUTH | SP |  |  | 20.2088 | 20.2082 | 20.2076 | 20.207 | 20.2069 | 20.2068 | 20.2067 | 20.2065 | 20.2064 | 20.2055 | 20.2025 | 20.2001 | 20.185 | 20.1522 | 18.3417 | 18.3406 | 18.3393 | 18.338 | 18.334 | 18.3293 | 18.319 | 18.3088 | 18.2958 | 18.2791 | 18.2304 | 18.1565 | 18.0741 | 17.9778 | 18.3696 | 18.3688 | 18.3679 | 18.367 | 18.3654 | 18.3635 | 18.3594 | 18.3553 | 18.3501 | 18.343 | 18.322 | 18.3064 | 18.2913 | 18.2585
BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | 1.3991 | 0.90794 | 0.71097 | 0.44347 | 0.14632 | -0.16453 | -0.4954 | -0.86079 | -1.3086 | -1.4832 | -1.7935 | -2.9602 | -3.8484 | -5.0522 | 1.302 | 0.95462 | 0.78831 | 0.56731 | 0.32689 | 0.070317 | -0.20825 | -0.52496 | -0.92419 | -1.0744 | -1.3548 | -2.4709 | -3.3066 | -4.1367 | 0.94015 | 0.72299 | 0.51122 | 0.22995 | -0.067813 | -0.37935 | -0.71092 | -1.0792 | -1.5299 | -1.7078 | -2.0274 | -3.2091 | -4.1124 | -5.3
| LOWER OLLACH | CT |  |  | 1.3991 | 0.90794 | 0.71097 | 0.44347 | 0.14632 | -0.16453 | -0.4954 | -0.86079 | -1.3086 | -1.4832 | -1.7935 | -2.9602 | -3.8484 | -4.4125 | 1.302 | 0.95462 | 0.78831 | 0.56731 | 0.32689 | 0.070317 | -0.20825 | -0.52496 | -0.92419 | -1.0744 | -1.3548 | -2.4709 | -3.3066 | -3.8149 | 0.94015 | 0.72299 | 0.51122 | 0.22995 | -0.067813 | -0.37935 | -0.71092 | -1.0792 | -1.5299 | -1.7078 | -2.0274 | -3.2091 | -4.1124 | -4.6912
| LOWER OLLACH | LW |  |  | 1.5752 | 1.5591 | 1.5435 | 1.5256 | 1.3397 | 0.86032 | 0.66013 | 0.4184 | 0.047017 | -0.048508 | -0.36583 | -1.1496 | -1.8711 | -2.331 | 1.4111 | 1.4011 | 1.3914 | 1.3801 | 0.98968 | 0.81031 | 0.62432 | 0.39772 | 0.042856 | -0.047797 | -0.35766 | -1.1165 | -1.7971 | -2.2082 | 1.2871 | 1.2711 | 1.2557 | 1.2386 | 0.88398 | 0.68672 | 0.48171 | 0.23511 | -0.14128 | -0.24213 | -0.57563 | -1.3751 | -2.1006 | -2.5643
| LOWER OLLACH | ST |  |  | 1.5813 | 1.5706 | 1.5598 | 1.5455 | 1.5312 | 1.5172 | 1.5003 | 1.4704 | 1.3906 | 1.3577 | 0.94464 | -0.34463 | -2.492 | -5.0522 | 1.4149 | 1.4082 | 1.4015 | 1.3925 | 1.3835 | 1.3746 | 1.3635 | 1.3393 | 1.2653 | 1.2378 | 0.9184 | -0.19425 | -2.0352 | -4.1367 | 1.2932 | 1.2825 | 1.2719 | 1.2577 | 1.2438 | 1.2308 | 1.2151 | 1.1864 | 0.91254 | 0.86974 | 0.72585 | -0.57951 | -2.7338 | -5.3
| LOWER OLLACH | SP |  |  | 1.6093 | 1.5598 | 1.5455 | 1.5311 | 1.5099 | 1.489 | 1.4684 | 1.4458 | 1.4155 | 1.3816 | 0.94731 | 0.72605 | -1.8137 | -4.6984 | 1.4411 | 1.4015 | 1.3926 | 1.3837 | 1.3706 | 1.3576 | 1.3447 | 1.3297 | 1.3069 | 1.2803 | 0.95611 | 0.74324 | -1.5346 | -3.9236 | 1.3215 | 1.2718 | 1.2577 | 1.2437 | 1.224 | 1.2047 | 1.1856 | 0.9871 | 0.95125 | 0.91196 | 0.75666 | 0.51466 | -2.0362 | -4.9208
KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.064361 | 0.06195 | 0.20688 | 0.20681 | 0.20671 | 0.20644 | 0.2062 | 0.20612 | 0.20606 | 0.20606 | 0.20606 | 0.20606 | 0.20606 | 0.19799 | 0.085435 | 0.082729 | 0.20863 | 0.20862 | 0.20859 | 0.20852 | 0.20845 | 0.20837 | 0.2083 | 0.20823 | 0.20822 | 0.20822 | 0.20822 | 0.1992 | 0.059002 | 0.056363
| LUBNAIG | CT |  |  | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.064361 | 0.06195 | 0.20688 | 0.20683 | 0.20675 | 0.20656 | 0.20635 | 0.2062 | 0.20615 | 0.20606 | 0.20606 | 0.20606 | 0.20606 | 0.19799 | 0.085435 | 0.082729 | 0.20863 | 0.20862 | 0.2086 | 0.20855 | 0.2085 | 0.20845 | 0.2084 | 0.20831 | 0.20822 | 0.20822 | 0.20822 | 0.1992 | 0.059002 | 0.056363
| LUBNAIG | LW |  |  | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.065571 | 0.063692 | 0.20688 | 0.20681 | 0.20671 | 0.20644 | 0.2062 | 0.20612 | 0.20606 | 0.20606 | 0.20606 | 0.20606 | 0.20606 | 0.1988 | 0.086794 | 0.084685 | 0.20863 | 0.20862 | 0.20859 | 0.20852 | 0.20845 | 0.20837 | 0.2083 | 0.20823 | 0.20822 | 0.20822 | 0.20822 | 0.20822 | 0.060252 | 0.05831
| LUBNAIG | ST |  |  | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.1368 | 0.13526 | 0.20691 | 0.20687 | 0.20683 | 0.20675 | 0.20663 | 0.2065 | 0.20637 | 0.20625 | 0.20619 | 0.20613 | 0.20606 | 0.20606 | 0.14476 | 0.14303 | 0.20864 | 0.20863 | 0.20862 | 0.2086 | 0.20857 | 0.20854 | 0.2085 | 0.20847 | 0.20844 | 0.20838 | 0.20822 | 0.20822 | 0.13205 | 0.13036
| LUBNAIG | SP |  |  | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.21268 | 0.20694 | 0.20693 | 0.20693 | 0.20692 | 0.20689 | 0.20685 | 0.20681 | 0.20677 | 0.20671 | 0.20661 | 0.20633 | 0.20613 | 0.20606 | 0.20606 | 0.20865 | 0.20865 | 0.20864 | 0.20864 | 0.20864 | 0.20863 | 0.20861 | 0.2086 | 0.20859 | 0.20856 | 0.20849 | 0.20838 | 0.20827 | 0.20822
LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | 19.9702 | 19.9659 | 19.9604 | 19.9347 | 19.8932 | 19.3423 | 19.1761 | 18.8288 | 14.4521 | 14.3089 | 13.8881 | 12.6108 | 11.3071 | 10.7658 | 18.2995 | 18.2852 | 18.2647 | 18.2032 | 18.059 | 17.4621 | 13.6882 | 13.3449 | 12.7546 | 12.6114 | 12.1906 | 11.1252 | 10.0546 | 8.2137 | 18.1713 | 18.1521 | 18.1245 | 18.0463 | 17.9094 | 17.3129 | 16.9101 | 16.7972 | 12.9539 | 12.825 | 12.4396 | 11.3673 | 9.4948 | 8.0784
| LUNANHEAD | CT |  |  | 19.9702 | 19.9659 | 19.9604 | 19.9347 | 19.8932 | 19.7878 | 19.6864 | 19.5738 | 19.4133 | 19.3175 | 19.0291 | 13.5182 | 11.6878 | 10.9083 | 18.2995 | 18.2852 | 18.2647 | 18.2032 | 18.1233 | 17.9803 | 17.8418 | 17.6775 | 17.4662 | 17.3154 | 13.5981 | 12.2445 | 10.671 | 9.4398 | 18.1713 | 18.1521 | 18.1245 | 18.0463 | 17.9684 | 17.8273 | 17.6907 | 17.529 | 17.3204 | 17.1724 | 16.7294 | 11.8182 | 9.4948 | 8.3593
| LUNANHEAD | LW |  |  | 19.9753 | 19.9746 | 19.9735 | 19.9531 | 19.9194 | 19.8057 | 19.6793 | 19.5368 | 19.3507 | 19.2511 | 18.9392 | 13.3903 | 11.56 | 11.0465 | 18.3111 | 18.3057 | 18.2971 | 18.2579 | 18.2033 | 18.0692 | 17.9228 | 17.7607 | 17.5555 | 13.7697 | 13.4667 | 12.1167 | 10.7526 | 10.2391 | 18.1861 | 18.1784 | 18.1662 | 18.1179 | 18.0532 | 17.9125 | 17.7671 | 17.6061 | 17.4019 | 17.2826 | 16.9127 | 12.7527 | 10.6562 | 9.3991
| LUNANHEAD | ST |  |  | 19.9872 | 19.9723 | 19.9705 | 19.9576 | 19.9355 | 19.5187 | 19.1761 | 18.8288 | 14.4521 | 14.3089 | 13.8881 | 12.6108 | 11.3071 | 10.9185 | 18.4132 | 18.2999 | 18.2901 | 18.2619 | 18.2191 | 17.7774 | 13.6882 | 13.3449 | 12.7546 | 12.6114 | 12.1906 | 11.1252 | 10.0546 | 9.666 | 18.3319 | 18.1708 | 18.1572 | 18.1217 | 18.0688 | 17.621 | 17.2512 | 16.8773 | 16.257 | 13.7287 | 13.2973 | 11.3673 | 9.771 | 9.1564
| LUNANHEAD | SP |  |  | 19.9867 | 19.9719 | 19.9704 | 19.9659 | 19.9324 | 19.3423 | 19.2861 | 19.2516 | 18.6623 | 18.5527 | 14.5319 | 13.9403 | 13.0986 | 10.7658 | 18.4185 | 18.3104 | 18.3079 | 18.3024 | 18.059 | 17.4621 | 17.0406 | 16.7531 | 13.2736 | 13.164 | 12.8344 | 12.2428 | 10.8711 | 8.2137 | 18.3399 | 18.1866 | 18.1837 | 18.1777 | 17.9094 | 17.3129 | 16.9101 | 16.7972 | 12.9539 | 12.825 | 12.4396 | 11.7609 | 10.3555 | 8.0784
PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | 0.11749 | 0.11748 | 0.11747 | 0.11746 | 0.11741 | 0.11735 | 0.11729 | 0.11722 | 0.11714 | 0.11709 | 0.11694 | 0.11657 | 0.095498 | 0.089812 | 0.11294 | 0.1128 | 0.11257 | 0.1121 | 0.11201 | 0.11195 | 0.11188 | 0.11182 | 0.11174 | 0.11168 | 0.11154 | 0.094979 | 0.089014 | 0.082534 | 0.11142 | 0.11137 | 0.11131 | 0.1113 | 0.11126 | 0.11119 | 0.11113 | 0.11107 | 0.11098 | 0.11093 | 0.099237 | 0.093655 | 0.087668 | 0.081164
| LUSSAGIVEN | CT |  |  | 0.11749 | 0.11748 | 0.11747 | 0.11746 | 0.11741 | 0.11735 | 0.11729 | 0.11722 | 0.11714 | 0.11709 | 0.11694 | 0.11657 | 0.095498 | 0.089812 | 0.11294 | 0.11282 | 0.11263 | 0.11225 | 0.11201 | 0.11195 | 0.11188 | 0.11182 | 0.11174 | 0.11168 | 0.11154 | 0.094979 | 0.089014 | 0.082534 | 0.11142 | 0.11137 | 0.11131 | 0.1113 | 0.11126 | 0.11119 | 0.11113 | 0.11107 | 0.11098 | 0.11093 | 0.099381 | 0.093655 | 0.087668 | 0.081164
| LUSSAGIVEN | LW |  |  | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.097254 | 0.093141 | 0.11294 | 0.1128 | 0.11257 | 0.1121 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.095693 | 0.090813 | 0.08598 | 0.11143 | 0.11137 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.099237 | 0.094368 | 0.089467 | 0.084614
| LUSSAGIVEN | ST |  |  | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.113 | 0.11293 | 0.11284 | 0.11266 | 0.11243 | 0.11219 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.098171 | 0.094829 | 0.11146 | 0.11143 | 0.11139 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.096857 | 0.0935
| LUSSAGIVEN | SP |  |  | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.1175 | 0.11307 | 0.11306 | 0.11305 | 0.11303 | 0.11297 | 0.11289 | 0.11275 | 0.11262 | 0.11246 | 0.11231 | 0.11209 | 0.11209 | 0.11209 | 0.11209 | 0.11156 | 0.11155 | 0.11153 | 0.11151 | 0.11144 | 0.11141 | 0.11136 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134 | 0.11134
LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | 14.5355 | 14.5296 | 14.5211 | 14.5017 | 14.4777 | 14.4532 | 14.4279 | 14.3873 | 14.3464 | 14.3064 | 14.1863 | 14.0069 | 13.838 | 13.6705 | 13.3964 | 13.3896 | 13.3798 | 13.3573 | 13.3299 | 13.3021 | 13.2736 | 13.2272 | 13.1806 | 13.1346 | 12.9962 | 12.7915 | 12.5791 | 12.3731 | 13.1206 | 13.1138 | 13.104 | 13.0814 | 13.0539 | 13.0259 | 12.9974 | 12.9508 | 12.9041 | 12.8578 | 12.7338 | 12.6297 | 12.5357 | 12.3947
| LYNDHURST | CT |  |  | 14.5355 | 14.5296 | 14.5211 | 14.5017 | 14.4777 | 14.4532 | 14.4279 | 14.3873 | 14.3464 | 14.3064 | 14.1863 | 14.0069 | 13.838 | 13.6705 | 13.3964 | 13.3896 | 13.3798 | 13.3573 | 13.3299 | 13.3021 | 13.2736 | 13.2272 | 13.1806 | 13.1346 | 12.9962 | 12.7915 | 12.5791 | 12.3731 | 13.1206 | 13.1138 | 13.104 | 13.0814 | 13.0539 | 13.0259 | 12.9974 | 12.9508 | 12.9041 | 12.8578 | 12.7338 | 12.6297 | 12.5357 | 12.3947
| LYNDHURST | LW |  |  | 14.5397 | 14.5369 | 14.5325 | 14.5215 | 14.5092 | 14.4973 | 14.4855 | 14.4741 | 14.4629 | 14.4508 | 14.4149 | 14.3571 | 14.299 | 14.2414 | 13.4011 | 13.3978 | 13.3926 | 13.3797 | 13.3653 | 13.3512 | 13.3375 | 13.324 | 13.3108 | 13.2966 | 13.2544 | 13.1866 | 13.1182 | 13.0506 | 13.1253 | 13.122 | 13.1168 | 13.1038 | 13.0894 | 13.0753 | 13.0614 | 13.0479 | 13.0347 | 13.0204 | 12.9781 | 12.9099 | 12.8413 | 12.7915
| LYNDHURST | ST |  |  | 14.5389 | 14.5359 | 14.5321 | 14.5249 | 14.5136 | 14.5001 | 14.4817 | 14.4633 | 14.4449 | 14.4208 | 14.3505 | 14.2376 | 14.1098 | 14.0173 | 13.4002 | 13.3968 | 13.3924 | 13.3839 | 13.3709 | 13.3554 | 13.3342 | 13.3131 | 13.292 | 13.2638 | 13.1819 | 13.0501 | 12.9062 | 12.7972 | 13.1245 | 13.121 | 13.1166 | 13.1081 | 13.095 | 13.0795 | 13.0582 | 13.037 | 13.0158 | 12.9875 | 12.9052 | 12.7766 | 12.7063 | 12.6567
| LYNDHURST | SP |  |  | 14.5414 | 14.5408 | 14.5402 | 14.5395 | 14.5368 | 14.5335 | 14.528 | 14.5225 | 14.5155 | 14.5061 | 14.4789 | 14.437 | 14.3933 | 14.3456 | 13.4032 | 13.4026 | 13.4018 | 13.401 | 13.3978 | 13.3941 | 13.3876 | 13.3812 | 13.3729 | 13.3619 | 13.3301 | 13.2811 | 13.2306 | 13.1766 | 13.1275 | 13.1268 | 13.1261 | 13.1253 | 13.1221 | 13.1183 | 13.1118 | 13.1053 | 13.097 | 13.086 | 13.0541 | 13.0048 | 12.9542 | 12.9
THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | 1.4586 | 1.4585 | 1.4583 | 1.9581 | 1.8593 | 1.7578 | 1.4601 | 1.3475 | 1.1856 | 1.1577 | 1.0778 | 0.8963 | 0.76376 | 0.71689 | 1.2984 | 1.2979 | 1.2971 | 1.7955 | 1.6939 | 1.4876 | 1.3826 | 1.2701 | 1.1082 | 1.0803 | 1.0004 | 0.81887 | 0.68633 | 0.6209 | 1.252 | 1.2517 | 1.2513 | 1.7505 | 1.6506 | 1.47 | 1.365 | 1.2525 | 1.0906 | 1.0627 | 0.98282 | 0.80128 | 0.65676 | 0.58909
| LYNESS | CT |  |  | 1.4586 | 1.4585 | 1.4583 | 1.9581 | 1.8925 | 1.8219 | 1.7473 | 1.4763 | 1.3658 | 1.3469 | 1.306 | 1.0124 | 0.83825 | 0.77489 | 1.2984 | 1.2979 | 1.2971 | 1.7955 | 1.7286 | 1.6566 | 1.4771 | 1.3989 | 1.2884 | 1.2695 | 1.2286 | 0.92334 | 0.71644 | 0.6209 | 1.252 | 1.2517 | 1.2513 | 1.7505 | 1.6844 | 1.6132 | 1.4595 | 1.3813 | 1.2708 | 1.2519 | 1.211 | 0.88984 | 0.6838 | 0.58909
| LYNESS | LW |  |  | 1.4588 | 1.4588 | 1.4588 | 1.9588 | 1.8593 | 1.7578 | 1.4601 | 1.3475 | 1.1856 | 1.1577 | 1.0778 | 0.8963 | 0.76376 | 0.71689 | 1.2986 | 1.2981 | 1.2974 | 1.7955 | 1.6939 | 1.4876 | 1.3826 | 1.2701 | 1.1082 | 1.0803 | 1.0004 | 0.81887 | 0.68633 | 0.62795 | 1.2521 | 1.252 | 1.2517 | 1.7509 | 1.6506 | 1.47 | 1.365 | 1.2525 | 1.0906 | 1.0627 | 0.98282 | 0.80128 | 0.65676 | 0.59445
| LYNESS | ST |  |  | 1.4588 | 1.4588 | 1.4587 | 1.9587 | 1.9583 | 1.9579 | 1.9575 | 1.957 | 1.9563 | 1.9561 | 1.9556 | 1.9546 | 1.9494 | 1.9465 | 1.2987 | 1.2984 | 1.2981 | 1.7975 | 1.7964 | 1.795 | 1.7921 | 1.7892 | 1.7862 | 1.7833 | 1.776 | 1.767 | 1.759 | 1.756 | 1.2522 | 1.252 | 1.2519 | 1.7516 | 1.751 | 1.7502 | 1.7488 | 1.7473 | 1.7458 | 1.7445 | 1.7412 | 1.737 | 1.7311 | 1.7282
| LYNESS | SP |  |  | 1.4587 | 1.4587 | 1.4586 | 1.9585 | 1.9585 | 1.9585 | 1.9585 | 1.9585 | 1.9585 | 1.9584 | 1.9581 | 1.9579 | 1.9564 | 1.9531 | 1.2989 | 1.2988 | 1.2987 | 1.7986 | 1.7983 | 1.7981 | 1.7972 | 1.7963 | 1.7952 | 1.794 | 1.7906 | 1.7856 | 1.78 | 1.7733 | 1.2522 | 1.2521 | 1.2521 | 1.752 | 1.7519 | 1.7518 | 1.7514 | 1.751 | 1.7506 | 1.7501 | 1.7486 | 1.7465 | 1.7432 | 1.7386
STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | 0.22671 | 0.2267 | 0.22408 | 0.22146 | 0.21873 | 0.21545 | 0.21248 | 0.2099 | 0.2076 | 0.19787 | 0.1912 | 0.18026 | 0.17033 | 0.16013 | 0.22724 | 0.22718 | 0.22487 | 0.22293 | 0.22161 | 0.22009 | 0.21853 | 0.21666 | 0.21476 | 0.21281 | 0.19399 | 0.18247 | 0.17198 | 0.16122 | 0.22154 | 0.22151 | 0.21887 | 0.21619 | 0.21339 | 0.21024 | 0.20726 | 0.2042 | 0.19713 | 0.19331 | 0.18601 | 0.17405 | 0.1631 | 0.15189
| MAARUIG | CT |  |  | 0.22671 | 0.2267 | 0.22408 | 0.22146 | 0.21873 | 0.21545 | 0.21248 | 0.2099 | 0.2076 | 0.19787 | 0.1912 | 0.18026 | 0.17033 | 0.16013 | 0.22724 | 0.22718 | 0.22487 | 0.22293 | 0.22161 | 0.22009 | 0.21853 | 0.21666 | 0.21476 | 0.21281 | 0.19399 | 0.18247 | 0.17198 | 0.16122 | 0.22154 | 0.22151 | 0.21887 | 0.21619 | 0.21339 | 0.21024 | 0.20726 | 0.2042 | 0.19713 | 0.19331 | 0.18601 | 0.17405 | 0.1631 | 0.15189
| MAARUIG | LW |  |  | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22725 | 0.22718 | 0.22708 | 0.22682 | 0.22652 | 0.22624 | 0.22596 | 0.22573 | 0.22552 | 0.22528 | 0.22478 | 0.22451 | 0.22451 | 0.22451 | 0.22155 | 0.22153 | 0.22149 | 0.22138 | 0.22127 | 0.22115 | 0.22104 | 0.22094 | 0.22088 | 0.2208 | 0.22058 | 0.22057 | 0.22057 | 0.22057
| MAARUIG | ST |  |  | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22728 | 0.22724 | 0.2272 | 0.22712 | 0.22701 | 0.22687 | 0.22651 | 0.22616 | 0.22585 | 0.22565 | 0.22505 | 0.22457 | 0.22451 | 0.22451 | 0.22156 | 0.22155 | 0.22153 | 0.2215 | 0.22146 | 0.2214 | 0.22126 | 0.22113 | 0.22099 | 0.22092 | 0.22073 | 0.22057 | 0.22057 | 0.22057
| MAARUIG | SP |  |  | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22672 | 0.22731 | 0.2273 | 0.2273 | 0.22729 | 0.22726 | 0.22722 | 0.2271 | 0.22698 | 0.22683 | 0.22673 | 0.22644 | 0.22598 | 0.22564 | 0.22531 | 0.22158 | 0.22157 | 0.22157 | 0.22157 | 0.22156 | 0.22154 | 0.22149 | 0.22145 | 0.22139 | 0.22135 | 0.22123 | 0.22105 | 0.22091 | 0.22081
LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | 21.9436 | 21.8339 | 21.7259 | 21.5894 | 21.4404 | 21.229 | 21.0298 | 20.7745 | 20.1319 | 19.9739 | 19.4974 | 14.4247 | 13.7743 | 13.3527 | 19.7038 | 19.586 | 19.4533 | 19.2306 | 18.9857 | 18.6796 | 18.3866 | 18.1587 | 14.938 | 14.7878 | 14.3363 | 13.5288 | 12.8787 | 11.7434 | 20.9339 | 20.8111 | 20.6857 | 20.5262 | 20.3529 | 20.1178 | 19.8952 | 19.6713 | 19.0428 | 18.8699 | 14.8168 | 14.0075 | 13.3583 | 12.0776
| MACALPINE ROAD | CT |  |  | 21.9436 | 21.8339 | 21.7259 | 21.5894 | 21.4404 | 21.229 | 21.0298 | 20.8297 | 20.5934 | 20.4576 | 20.1204 | 19.3005 | 14.2678 | 13.3527 | 19.7038 | 19.586 | 19.4533 | 19.2306 | 18.9857 | 18.6796 | 18.3866 | 18.1587 | 17.9044 | 17.7259 | 17.3935 | 14.8253 | 13.3192 | 11.7434 | 20.9339 | 20.8111 | 20.6857 | 20.5262 | 20.3529 | 20.1178 | 19.8952 | 19.6713 | 19.4118 | 19.2524 | 18.8469 | 14.8353 | 13.6851 | 12.0776
| MACALPINE ROAD | LW |  |  | 22.0457 | 22.0367 | 22.0278 | 22.0165 | 22.0039 | 21.9144 | 21.8239 | 21.7327 | 21.6409 | 21.5636 | 21.3296 | 20.7395 | 19.9787 | 19.5244 | 19.8152 | 19.8033 | 19.7886 | 19.7602 | 19.7285 | 19.6207 | 19.5127 | 19.4044 | 19.2963 | 19.2011 | 18.9148 | 18.2426 | 14.9358 | 14.5387 | 21.0485 | 21.0378 | 21.0263 | 21.0092 | 20.99 | 20.8941 | 20.7973 | 20.6997 | 20.6018 | 20.5204 | 20.2742 | 19.6644 | 18.8836 | 14.8543
| MACALPINE ROAD | ST |  |  | 22.046 | 22.0377 | 22.0288 | 22.0155 | 21.9935 | 21.5294 | 21.1526 | 20.7745 | 20.1319 | 19.9739 | 19.4974 | 14.4247 | 13.7743 | 13.5132 | 19.796 | 19.7689 | 19.7346 | 19.6716 | 19.5814 | 19.0351 | 18.6065 | 18.1776 | 14.938 | 14.7878 | 14.3363 | 13.5288 | 12.8787 | 12.6186 | 21.0436 | 21.0293 | 21.0126 | 20.9844 | 20.9471 | 20.4683 | 20.082 | 19.6946 | 19.0428 | 18.8699 | 14.8168 | 14.0075 | 13.3583 | 13.0986
| MACALPINE ROAD | SP |  |  | 22.0429 | 22.0338 | 22.0247 | 22.0154 | 22.0022 | 21.3288 | 21.316 | 21.3033 | 20.6304 | 20.4991 | 20.1057 | 19.4009 | 14.6151 | 14.4348 | 19.813 | 19.8028 | 19.792 | 19.7808 | 19.7499 | 19.0549 | 19.0266 | 18.9985 | 18.305 | 18.1428 | 14.9331 | 14.2751 | 13.8046 | 13.6474 | 21.0458 | 21.0356 | 21.0252 | 21.0146 | 20.9951 | 20.3144 | 20.2961 | 20.2779 | 19.598 | 19.4581 | 19.0472 | 14.6963 | 14.2015 | 14.0231
MACDUFF | MACDUFF NEW | MINIMUM HEADROOM | NJ 70363 63908 | YES | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | CT |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | LW |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | ST |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | SP |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | 3.6841 | 3.6835 | 3.6829 | 3.6819 | 3.6788 | 3.6752 | 3.6709 | 3.6659 | 3.6603 | 3.6571 | 3.6464 | 3.6217 | 3.5811 | 3.5022 | 3.1611 | 3.158 | 3.1535 | 3.1435 | 3.1305 | 3.1173 | 3.1035 | 3.0914 | 3.0858 | 3.0826 | 3.072 | 2.4752 | 2.3249 | 2.138 | 3.2486 | 3.2475 | 3.246 | 3.2431 | 3.2379 | 3.2322 | 3.2259 | 3.2192 | 3.2119 | 3.2069 | 3.1909 | 2.4105 | 2.2597 | 2.0723
| MACHRIE | CT |  |  | 3.6841 | 3.6835 | 3.6829 | 3.6819 | 3.6788 | 3.6752 | 3.6709 | 3.6659 | 3.6603 | 3.6571 | 3.6464 | 3.6217 | 3.5811 | 3.5022 | 3.1611 | 3.158 | 3.1535 | 3.1435 | 3.1305 | 3.1173 | 3.1035 | 3.0914 | 3.0858 | 3.0826 | 3.072 | 2.4752 | 2.3249 | 2.138 | 3.2486 | 3.2475 | 3.246 | 3.2431 | 3.2379 | 3.2322 | 3.2259 | 3.2192 | 3.2119 | 3.2069 | 3.1909 | 2.4105 | 2.2597 | 2.0723
| MACHRIE | LW |  |  | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.6849 | 3.1645 | 3.1642 | 3.1638 | 3.1626 | 3.1613 | 3.1601 | 3.1589 | 3.1577 | 3.1565 | 3.1552 | 3.1515 | 3.1454 | 3.1393 | 3.1333 | 3.25 | 3.2499 | 3.2498 | 3.2496 | 3.2493 | 3.249 | 3.2488 | 3.2485 | 3.2482 | 3.248 | 3.2472 | 3.2459 | 3.2446 | 3.2433
| MACHRIE | ST |  |  | 3.6848 | 3.6847 | 3.6846 | 3.6845 | 3.6836 | 3.6825 | 3.6813 | 3.6799 | 3.6783 | 3.6778 | 3.6762 | 3.6736 | 3.66 | 3.6522 | 3.1645 | 3.1643 | 3.164 | 3.1635 | 3.1622 | 3.1605 | 3.1545 | 3.1484 | 3.1422 | 3.1362 | 3.1184 | 3.0991 | 3.0855 | 3.0778 | 3.2498 | 3.2497 | 3.2496 | 3.2494 | 3.2484 | 3.2472 | 3.245 | 3.2426 | 3.24 | 3.2383 | 3.2333 | 3.2251 | 3.2059 | 2.4992
| MACHRIE | SP |  |  | 3.6847 | 3.6845 | 3.6844 | 3.6843 | 3.6843 | 3.6842 | 3.6842 | 3.6842 | 3.6841 | 3.6839 | 3.6833 | 3.6828 | 3.6794 | 3.6722 | 3.1645 | 3.1644 | 3.1642 | 3.1641 | 3.1639 | 3.1637 | 3.1621 | 3.1605 | 3.1585 | 3.1561 | 3.1492 | 3.1389 | 3.1263 | 3.1103 | 3.2498 | 3.2496 | 3.2495 | 3.2494 | 3.2493 | 3.2493 | 3.2489 | 3.2485 | 3.2481 | 3.2474 | 3.2454 | 3.2428 | 3.2375 | 3.2283
FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | 8.3016 | 8.3012 | 8.2957 | 8.29 | 8.2826 | 8.2738 | 8.2643 | 8.2543 | 8.2435 | 8.2343 | 8.2143 | 8.1767 | 8.1308 | 7.3898 | 8.2105 | 8.2094 | 8.2044 | 8.1976 | 8.1891 | 8.1796 | 8.1696 | 8.1472 | 8.1246 | 8.1024 | 8.0498 | 7.4272 | 7.2973 | 7.1429 | 8.2504 | 8.249 | 8.243 | 8.2348 | 8.2247 | 8.2135 | 8.2018 | 8.1759 | 8.1497 | 8.1237 | 8.0524 | 7.9755 | 7.4149 | 7.2882
| MALLAIG | CT |  |  | 8.3016 | 8.3012 | 8.2957 | 8.29 | 8.2826 | 8.2738 | 8.2643 | 8.2543 | 8.2435 | 8.2343 | 8.2143 | 8.1767 | 8.1308 | 7.3898 | 8.2105 | 8.2094 | 8.2044 | 8.1976 | 8.1891 | 8.1796 | 8.1696 | 8.1472 | 8.1246 | 8.1024 | 8.0498 | 7.4272 | 7.2973 | 7.1429 | 8.2504 | 8.249 | 8.243 | 8.2348 | 8.2247 | 8.2135 | 8.2018 | 8.1759 | 8.1497 | 8.1237 | 8.0524 | 7.9755 | 7.4149 | 7.2882
| MALLAIG | LW |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.211 | 8.2101 | 8.2086 | 8.205 | 8.2009 | 8.1969 | 8.193 | 8.1892 | 8.1855 | 8.1814 | 8.1695 | 8.1502 | 8.1309 | 8.1117 | 8.2509 | 8.2497 | 8.2478 | 8.243 | 8.2377 | 8.2325 | 8.2275 | 8.2225 | 8.2177 | 8.2124 | 8.1969 | 8.172 | 8.1468 | 8.1219
| MALLAIG | ST |  |  | 8.3021 | 8.302 | 8.302 | 8.3019 | 8.3013 | 8.3006 | 8.2997 | 8.2988 | 8.2977 | 8.2973 | 8.2963 | 8.2945 | 8.2852 | 8.2799 | 8.2113 | 8.2108 | 8.2101 | 8.2089 | 8.2067 | 8.2041 | 8.197 | 8.1898 | 8.1827 | 8.1731 | 8.1452 | 8.1004 | 8.0746 | 7.4452 | 8.2513 | 8.2506 | 8.2498 | 8.2482 | 8.2455 | 8.2424 | 8.2334 | 8.2244 | 8.2154 | 8.203 | 8.1672 | 8.1096 | 8.0829 | 8.0693
| MALLAIG | SP |  |  | 8.302 | 8.3019 | 8.3018 | 8.3017 | 8.3017 | 8.3017 | 8.3016 | 8.3016 | 8.3016 | 8.3014 | 8.3009 | 8.3005 | 8.2979 | 8.2922 | 8.2117 | 8.2115 | 8.2113 | 8.2111 | 8.2107 | 8.2101 | 8.208 | 8.2059 | 8.2032 | 8.1995 | 8.1886 | 8.1718 | 8.1538 | 8.1338 | 8.2517 | 8.2516 | 8.2514 | 8.2511 | 8.2506 | 8.2499 | 8.2471 | 8.2444 | 8.2409 | 8.2361 | 8.2221 | 8.2005 | 8.1779 | 8.1536
KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | YES | 3.3075 | 3.3064 | 3.305 | 3.3031 | 3.1549 | 2.9942 | 2.8233 | 2.6429 | 2.0774 | 1.5746 | -0.3531 | -2.8421 | -6.0001 | -8.8294 | 4.966 | 4.9649 | 4.9635 | 4.9616 | 4.6401 | 4.114 | 3.5888 | 3.0618 | 2.3797 | 1.7824 | -0.44904 | -2.9949 | -6.0431 | -9.1109 | 4.3319 | 4.3307 | 4.3294 | 4.3275 | 4.1793 | 4.0186 | 3.5387 | 2.9913 | 2.2666 | 1.6266 | -0.76521 | -3.5627 | -6.8204 | -10.0936
| MARNOCH | CT |  |  | 3.3075 | 3.3064 | 3.305 | 3.3031 | 3.1549 | 2.9942 | 2.8233 | 2.6429 | 2.3887 | 2.0087 | 0.57831 | -2.6177 | -6.0001 | -8.8294 | 4.966 | 4.9649 | 4.9635 | 4.9616 | 4.7003 | 4.3275 | 3.9469 | 3.523 | 2.9195 | 2.4172 | 0.72887 | -2.6346 | -6.0431 | -9.1109 | 4.3319 | 4.3307 | 4.3294 | 4.3275 | 4.1793 | 4.0186 | 3.8386 | 3.436 | 2.8633 | 2.3521 | 0.54725 | -3.0853 | -6.8204 | -10.0936
| MARNOCH | LW |  |  | 3.3092 | 3.3092 | 3.3092 | 3.3092 | 3.2525 | 3.1928 | 3.1176 | 2.6652 | 2.0774 | 1.5746 | -0.3531 | -2.8421 | -4.3577 | -5.9846 | 4.9677 | 4.9677 | 4.9677 | 4.9677 | 4.6401 | 4.114 | 3.5888 | 3.0618 | 2.3797 | 1.7824 | -0.44904 | -2.9949 | -4.3953 | -6.1688 | 4.3336 | 4.3336 | 4.3336 | 4.3336 | 4.2768 | 4.0234 | 3.5387 | 2.9913 | 2.2666 | 1.6266 | -0.76521 | -3.5627 | -5.1679 | -7.0676
| MARNOCH | ST |  |  | 3.3089 | 3.3087 | 3.3084 | 3.3082 | 3.2805 | 3.2505 | 3.2211 | 3.1872 | 3.1333 | 2.9815 | 1.667 | -0.54228 | -4.2497 | -7.7651 | 4.9674 | 4.9672 | 4.9669 | 4.9667 | 4.939 | 4.7414 | 4.5276 | 4.2624 | 3.8798 | 3.4277 | 1.8628 | -0.58249 | -4.3302 | -8.0348 | 4.3332 | 4.333 | 4.3328 | 4.3325 | 4.3049 | 4.2748 | 4.2454 | 4.1583 | 3.8046 | 3.3797 | 1.7016 | -0.95201 | -5.0891 | -9.1204
| MARNOCH | SP |  |  | 3.3086 | 3.3083 | 3.3079 | 3.3076 | 3.3037 | 3.3 | 3.2962 | 3.2918 | 3.2847 | 3.2766 | 3.247 | 2.6885 | 1.7765 | 1.0994 | 4.9671 | 4.9667 | 4.9664 | 4.9661 | 4.9622 | 4.9585 | 4.9547 | 4.8834 | 4.764 | 4.5995 | 3.9142 | 3.0583 | 2.0296 | 1.2432 | 4.3329 | 4.3326 | 4.3323 | 4.3319 | 4.3281 | 4.3244 | 4.3205 | 4.3162 | 4.3091 | 4.301 | 3.8459 | 2.9758 | 1.8944 | 1.0585
BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | 4.7381 | 4.5599 | 3.8994 | 3.6013 | 3.1962 | 2.7398 | 2.2563 | 1.7706 | 1.1646 | 0.94037 | 0.5136 | -1.2966 | -2.6 | -3.7858 | 4.4526 | 3.9905 | 3.8043 | 3.5348 | 3.1538 | 2.7492 | 2.3178 | 1.8954 | 1.3515 | 1.1589 | 0.77143 | -0.97682 | -2.2177 | -2.9926 | 4.3508 | 3.8555 | 3.6096 | 3.2694 | 2.8203 | 2.3467 | 1.8481 | 1.3538 | 0.73922 | 0.50634 | 0.060706 | -1.7802 | -3.1125 | -4.2073
| MARYBANK | CT |  |  | 4.7381 | 4.5599 | 3.8994 | 3.6013 | 3.1962 | 2.7398 | 2.2563 | 1.7706 | 1.1646 | 0.94037 | 0.5136 | -1.2966 | -2.6 | -3.396 | 4.4526 | 3.9905 | 3.8043 | 3.5348 | 3.1538 | 2.7492 | 2.3178 | 1.8954 | 1.3515 | 1.1589 | 0.77143 | -0.97682 | -2.2177 | -2.948 | 4.3508 | 3.8555 | 3.6096 | 3.2694 | 2.8203 | 2.3467 | 1.8481 | 1.3538 | 0.73922 | 0.50634 | 0.060706 | -1.7802 | -3.1125 | -3.9368
| MARYBANK | LW |  |  | 4.9004 | 4.8857 | 4.8714 | 4.8547 | 4.703 | 4.547 | 3.979 | 3.775 | 3.4602 | 3.3745 | 3.071 | 2.277 | 1.5711 | 1.1412 | 4.5689 | 4.5575 | 4.5463 | 4.5326 | 4.3846 | 3.9625 | 3.7982 | 3.5965 | 3.2847 | 3.2019 | 2.9081 | 2.1333 | 1.4509 | 1.0515 | 4.5147 | 4.4998 | 4.4854 | 4.4688 | 4.3173 | 3.8987 | 3.7288 | 3.5209 | 3.2023 | 3.1125 | 2.7967 | 1.9819 | 1.2542 | 0.80097
| MARYBANK | ST |  |  | 4.9045 | 4.8935 | 4.882 | 4.8659 | 4.7864 | 4.702 | 4.6206 | 4.5183 | 3.8665 | 3.7998 | 3.5929 | 2.094 | -0.38213 | -3.7858 | 4.5698 | 4.5594 | 4.548 | 4.5305 | 4.4591 | 3.996 | 3.9008 | 3.7847 | 3.5781 | 3.5117 | 3.3074 | 1.9666 | -0.18167 | -2.9926 | 4.5201 | 4.5099 | 4.4998 | 4.4863 | 4.4105 | 3.9603 | 3.8632 | 3.7454 | 3.5369 | 3.4683 | 3.2553 | 1.7074 | -0.78339 | -4.2073
| MARYBANK | SP |  |  | 4.8989 | 4.8854 | 4.8719 | 4.8584 | 4.8289 | 4.7998 | 4.7714 | 4.7402 | 4.6947 | 4.6445 | 4.4472 | 3.7404 | -0.34797 | -3.3588 | 4.5674 | 4.5568 | 4.5461 | 4.5353 | 4.5087 | 4.4821 | 4.4613 | 4.4384 | 4.4014 | 4.3593 | 3.8314 | 3.5623 | -0.089852 | -2.6345 | 4.5132 | 4.4996 | 4.4861 | 4.4725 | 4.4437 | 4.4155 | 4.3874 | 4.3563 | 4.3112 | 3.9574 | 3.7398 | 3.4439 | -0.70894 | -3.7356
LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | 20.7872 | 20.668 | 20.4888 | 20.2776 | 20.0417 | 19.7793 | 19.4973 | 19.1908 | 18.8196 | 18.6228 | 18.2446 | 12.1377 | 8.3748 | 3.3232 | 18.3188 | 18.2008 | 18.0279 | 17.7898 | 17.5217 | 17.2305 | 16.2715 | 15.9955 | 13.5997 | 13.3458 | 12.7147 | 9.6948 | 6.3792 | 2.1915 | 18.9862 | 18.8525 | 18.6549 | 18.4055 | 18.1293 | 17.8275 | 17.2476 | 13.7636 | 13.2837 | 12.9735 | 12.245 | 8.7704 | 4.8558 | -0.27878
| MARYTON | CT |  |  | 20.7872 | 20.668 | 20.4888 | 20.2776 | 20.0417 | 19.7793 | 19.4973 | 19.1908 | 18.8196 | 18.6228 | 18.2446 | 12.1377 | 8.3748 | 3.3232 | 18.3188 | 18.2008 | 18.0279 | 17.7898 | 17.5217 | 17.2305 | 16.2715 | 15.9955 | 13.5997 | 13.3458 | 12.7147 | 9.6948 | 6.4319 | 2.1915 | 18.9862 | 18.8525 | 18.6549 | 18.4055 | 18.1293 | 17.8275 | 17.2476 | 13.7636 | 13.2837 | 12.9735 | 12.245 | 8.7704 | 4.8558 | -0.27878
| MARYTON | LW |  |  | 20.8972 | 20.8875 | 20.8499 | 20.8109 | 20.7613 | 20.7008 | 20.6289 | 20.528 | 20.3674 | 20.2955 | 20.0712 | 18.963 | 18.3807 | 17.9943 | 18.4244 | 18.4092 | 18.3683 | 18.309 | 18.2362 | 18.1534 | 18.0601 | 17.9386 | 17.7584 | 17.6647 | 17.3701 | 16.2434 | 13.6489 | 12.8191 | 19.1077 | 19.0941 | 19.0507 | 18.9975 | 18.9322 | 18.8562 | 18.7691 | 18.6533 | 18.478 | 18.3903 | 18.1187 | 13.7705 | 13.2212 | 12.4913
| MARYTON | ST |  |  | 20.8999 | 20.8928 | 20.8668 | 20.8386 | 20.8031 | 20.7648 | 20.7221 | 20.6677 | 20.5769 | 20.5313 | 20.3824 | 14.1217 | 11.0497 | 7.8091 | 18.4222 | 18.4064 | 18.373 | 18.3256 | 18.2621 | 18.189 | 17.4507 | 17.3511 | 17.216 | 17.1167 | 16.8128 | 11.6427 | 8.914 | 6.1867 | 19.1085 | 19.0964 | 19.064 | 19.0235 | 18.9715 | 18.9134 | 18.553 | 18.4811 | 18.3732 | 18.3074 | 18.0995 | 11.0924 | 7.8401 | 4.5145
| MARYTON | SP |  |  | 20.8945 | 20.8847 | 20.875 | 20.8652 | 20.8522 | 20.8393 | 20.8264 | 20.8123 | 20.793 | 20.7697 | 20.672 | 13.7024 | 9.3138 | 5.6764 | 18.4268 | 18.4172 | 18.4073 | 18.3972 | 18.1654 | 17.9018 | 17.5053 | 17.1427 | 17.0922 | 17.072 | 16.9831 | 10.8573 | 6.3792 | 2.7932 | 19.1074 | 19.0966 | 19.0857 | 19.0746 | 18.9553 | 18.8207 | 18.6458 | 18.504 | 18.3149 | 18.2833 | 18.1617 | 10.3784 | 5.5556 | 1.5979
STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | 7.6722 | 7.5827 | 7.4962 | 7.3845 | 7.197 | 6.7712 | 6.3511 | 5.8738 | 5.1961 | 4.3708 | 4.1629 | 2.6831 | 2.254 | 1.7785 | 6.6861 | 6.5939 | 6.4973 | 6.3548 | 5.809 | 5.3273 | 4.8513 | 4.3002 | 3.5205 | 2.5769 | 2.3725 | 1.0632 | 0.63532 | -0.44835 | 7.1427 | 7.0605 | 6.9808 | 6.8767 | 6.7483 | 6.4064 | 5.9033 | 5.3261 | 4.5194 | 3.5615 | 3.3363 | 1.7911 | 1.3339 | 0.71448
| MAUD | CT |  |  | 7.6722 | 7.5827 | 7.4962 | 7.3845 | 7.197 | 6.7712 | 6.3511 | 5.8738 | 5.1961 | 4.3708 | 4.1629 | 2.6831 | 2.254 | 1.7785 | 6.6861 | 6.5939 | 6.4973 | 6.3548 | 5.809 | 5.3273 | 4.8513 | 4.3002 | 3.5205 | 2.5769 | 2.3725 | 1.0632 | 0.63532 | 0.17046 | 7.1427 | 7.0605 | 6.9808 | 6.8767 | 6.7483 | 6.4064 | 5.9033 | 5.3261 | 4.5194 | 3.5615 | 3.3363 | 1.7911 | 1.3339 | 0.83057
| MAUD | LW |  |  | 7.7539 | 7.7465 | 7.7394 | 7.7312 | 7.7185 | 7.7013 | 7.6794 | 7.6522 | 7.6096 | 7.5894 | 7.5187 | 5.606 | 5.374 | 2.2931 | 6.7476 | 6.7422 | 6.7364 | 6.7275 | 6.7094 | 6.6827 | 6.6516 | 6.6156 | 6.5645 | 6.5351 | 6.4374 | 4.1142 | 3.8915 | 0.28741 | 7.2177 | 7.2109 | 7.2042 | 7.1961 | 7.1836 | 7.1667 | 7.1453 | 7.1185 | 7.0766 | 7.057 | 6.9885 | 5.0889 | 4.8459 | 1.2125
| MAUD | ST |  |  | 7.7566 | 7.7516 | 7.7465 | 7.7398 | 7.7316 | 7.5305 | 7.2321 | 6.8564 | 6.3013 | 5.543 | 5.4433 | 4.6184 | 3.0589 | 2.124 | 6.7476 | 6.7424 | 6.7365 | 6.7269 | 6.3363 | 5.9646 | 5.5873 | 5.1112 | 4.4289 | 3.5423 | 3.4382 | 2.6726 | 1.1069 | 0.039819 | 7.2199 | 7.2151 | 7.2101 | 7.2032 | 7.1739 | 7.145 | 6.8135 | 6.3352 | 5.6507 | 4.762 | 4.6513 | 3.7734 | 2.0669 | 0.98773
| MAUD | SP |  |  | 7.7532 | 7.7465 | 7.7398 | 7.7331 | 7.7234 | 7.7137 | 7.7041 | 7.6577 | 7.4661 | 7.2129 | 6.1208 | 4.6439 | 3.2795 | 2.0452 | 6.7477 | 6.7435 | 6.7391 | 6.7346 | 6.6389 | 6.5145 | 6.3288 | 6.146 | 5.906 | 5.5868 | 4.2397 | 2.5311 | 0.97015 | -0.44835 | 7.2171 | 7.211 | 7.2048 | 7.1986 | 7.184 | 7.1687 | 7.15 | 7.1315 | 7.1097 | 6.8014 | 5.4466 | 3.7233 | 2.1473 | 0.71448
MYBSTER | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | 5.5818 | 5.5816 | 5.5813 | 5.5809 | 5.3644 | 5.1313 | 4.885 | 4.6272 | 4.2621 | 4.2008 | 4.0698 | 1.6733 | 1.1131 | 0.93976 | 3.9891 | 3.988 | 3.9863 | 3.9817 | 3.7624 | 3.5257 | 2.3882 | 2.1303 | 1.7653 | 1.7039 | 1.5729 | 0.60807 | 0.047881 | -0.16383 | 4.5038 | 4.5035 | 4.5031 | 4.5025 | 4.2857 | 4.0523 | 2.4976 | 2.2398 | 1.8748 | 1.8134 | 1.6824 | 0.71754 | 0.15735 | -0.016027
| MELVICH | CT |  |  | 5.5818 | 5.5816 | 5.5813 | 5.5809 | 5.3644 | 5.1313 | 4.885 | 4.6272 | 4.2621 | 4.2008 | 4.0698 | 1.6733 | 1.1131 | 0.93976 | 3.9891 | 3.988 | 3.9863 | 3.9825 | 3.7624 | 3.5257 | 2.3882 | 2.1303 | 1.7653 | 1.7039 | 1.5729 | 0.60807 | 0.047881 | -0.16383 | 4.5038 | 4.5035 | 4.5031 | 4.5025 | 4.2857 | 4.0523 | 2.4976 | 2.2398 | 1.8748 | 1.8134 | 1.6824 | 0.71754 | 0.15735 | -0.016027
| MELVICH | LW |  |  | 5.5821 | 5.5821 | 5.5821 | 5.5821 | 5.4165 | 5.2476 | 5.0731 | 4.8858 | 4.6165 | 4.5701 | 4.4373 | 4.1353 | 2.4833 | 2.4053 | 3.9894 | 3.9882 | 3.9863 | 3.9817 | 3.8109 | 3.637 | 3.4575 | 2.389 | 2.1197 | 2.0733 | 1.9405 | 1.6385 | 1.418 | 1.3401 | 4.5041 | 4.504 | 4.5039 | 4.5035 | 4.3375 | 4.1682 | 3.9933 | 2.4985 | 2.2291 | 2.1828 | 2.0499 | 1.748 | 1.5275 | 1.4495
| MELVICH | ST |  |  | 5.5821 | 5.5821 | 5.5821 | 5.5821 | 5.582 | 5.5818 | 5.5817 | 5.5815 | 5.5814 | 5.5813 | 5.5811 | 5.5809 | 5.5793 | 5.5785 | 3.9898 | 3.9893 | 3.9885 | 3.987 | 3.9849 | 3.9824 | 3.9747 | 3.9671 | 3.9597 | 3.9503 | 3.9229 | 3.9177 | 3.9162 | 3.9153 | 4.5041 | 4.5041 | 4.504 | 4.5039 | 4.5036 | 4.5033 | 4.5026 | 4.5018 | 4.5011 | 4.5003 | 4.4979 | 4.4942 | 4.4892 | 4.4849
| MELVICH | SP |  |  | 5.5821 | 5.582 | 5.582 | 5.582 | 5.582 | 5.582 | 5.582 | 5.582 | 5.582 | 5.5819 | 5.5818 | 5.5817 | 5.5812 | 5.58 | 3.9904 | 3.9903 | 3.9901 | 3.99 | 3.9895 | 3.9888 | 3.9863 | 3.9838 | 3.9807 | 3.9769 | 3.9662 | 3.9496 | 3.9334 | 3.9174 | 4.5042 | 4.5041 | 4.5041 | 4.5041 | 4.504 | 4.504 | 4.5038 | 4.5036 | 4.5033 | 4.503 | 4.502 | 4.5006 | 4.4988 | 4.4964
CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | 26.3574 | 26.2528 | 26.1514 | 26.0282 | 25.8987 | 25.7704 | 25.6431 | 25.5167 | 25.3926 | 25.3265 | 25.1296 | 24.8954 | 24.5843 | 24.8814 | 23.7086 | 23.6095 | 23.5066 | 23.359 | 23.201 | 23.0662 | 22.9696 | 22.8721 | 22.7751 | 22.7184 | 22.5574 | 22.3766 | 19.318 | 19.1401 | 24.6595 | 24.5443 | 24.4294 | 24.2789 | 24.1207 | 23.9642 | 23.8093 | 23.6737 | 23.5464 | 23.4785 | 23.2767 | 23.0386 | 22.7237 | 23.0168
| MENZIESHILL | CT |  |  | 26.3574 | 26.2528 | 26.1514 | 26.0282 | 25.8987 | 25.7704 | 25.6431 | 25.5167 | 25.3926 | 25.3265 | 25.1296 | 24.8954 | 24.5843 | 24.8814 | 23.7086 | 23.6095 | 23.5066 | 23.359 | 23.201 | 23.0662 | 22.9696 | 22.8721 | 22.7751 | 22.7184 | 22.5574 | 22.3766 | 19.318 | 19.1401 | 24.6595 | 24.5443 | 24.4294 | 24.2789 | 24.1207 | 23.9642 | 23.8093 | 23.6737 | 23.5464 | 23.4785 | 23.2767 | 23.0386 | 22.7237 | 23.0168
| MENZIESHILL | LW |  |  | 26.4538 | 26.4453 | 26.4371 | 26.4277 | 26.4171 | 26.4053 | 26.3926 | 26.3791 | 26.365 | 26.3503 | 26.2338 | 26.951 | 26.8618 | 26.7749 | 23.7991 | 23.7885 | 23.7759 | 23.7534 | 23.7283 | 23.7027 | 23.6766 | 23.6502 | 23.6237 | 23.5954 | 23.4519 | 24.1134 | 24.043 | 23.9742 | 24.7651 | 24.7544 | 24.743 | 24.726 | 24.707 | 24.687 | 24.6662 | 24.6446 | 24.6226 | 24.5994 | 24.4547 | 25.1308 | 25.0342 | 24.9444
| MENZIESHILL | ST |  |  | 26.4563 | 26.4502 | 26.4441 | 26.4359 | 26.4238 | 26.4109 | 26.3956 | 26.3797 | 26.3633 | 26.353 | 26.2839 | 26.226 | 26.1147 | 26.834 | 23.7907 | 23.7737 | 23.7527 | 23.7153 | 23.6629 | 23.6015 | 23.5371 | 23.473 | 23.4223 | 23.4087 | 23.3441 | 23.2739 | 23.1481 | 23.8536 | 24.7627 | 24.7505 | 24.7365 | 24.7131 | 24.6805 | 24.6431 | 24.6028 | 24.5638 | 24.5472 | 24.5366 | 24.4654 | 24.4061 | 24.2935 | 25.0115
| MENZIESHILL | SP |  |  | 26.4519 | 26.4436 | 26.4353 | 26.427 | 26.4157 | 26.4046 | 26.3936 | 26.3827 | 26.372 | 26.3605 | 26.3262 | 26.2635 | 26.184 | 26.8846 | 23.7989 | 23.7905 | 23.7819 | 23.7731 | 23.7539 | 23.7329 | 23.7081 | 23.6835 | 23.6546 | 23.6318 | 23.5649 | 23.453 | 23.3283 | 24.0345 | 24.7639 | 24.7546 | 24.7452 | 24.7356 | 24.7191 | 24.7017 | 24.6826 | 24.6637 | 24.6427 | 24.6244 | 24.5703 | 24.4759 | 24.3667 | 25.0604
KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | YES | 3.4736 | 3.3829 | 3.2955 | 3.1823 | 2.8929 | 2.5638 | 2.2228 | 1.851 | 1.3464 | 0.99994 | -0.90555 | -4.2248 | -10.619 | -15.7613 | 2.8322 | 2.7531 | 2.6619 | 2.5307 | 2.1972 | 1.8742 | 1.5385 | 1.1683 | 0.64821 | 0.21883 | -2.0135 | -4.8145 | -10.849 | -15.4934 | 2.8077 | 2.7078 | 2.6088 | 2.4724 | 2.1839 | 1.8979 | 1.5992 | 1.2729 | 0.82912 | 0.52404 | -1.3192 | -4.581 | -11.2938 | -16.6009
| METHLICK | CT |  |  | 3.4736 | 3.3829 | 3.2955 | 3.1823 | 2.8929 | 2.5638 | 2.2228 | 1.851 | 1.3464 | 0.99994 | -0.86581 | -4.2248 | -10.619 | -15.7613 | 2.8322 | 2.7531 | 2.6619 | 2.5307 | 2.1972 | 1.8742 | 1.5385 | 1.1683 | 0.65517 | 0.27614 | -1.5413 | -4.8145 | -10.849 | -15.4934 | 2.8077 | 2.7078 | 2.6088 | 2.4724 | 2.1839 | 1.8979 | 1.5992 | 1.2729 | 0.82912 | 0.52404 | -1.1563 | -4.581 | -11.2938 | -16.6009
| METHLICK | LW |  |  | 3.5562 | 3.5487 | 3.5415 | 3.5331 | 3.3164 | 2.9528 | 2.5864 | 2.2005 | 1.674 | 1.2981 | -0.90555 | -3.5002 | -6.9702 | -8.1931 | 2.8708 | 2.8672 | 2.8638 | 2.8596 | 2.4833 | 2.0737 | 1.662 | 1.2316 | 0.64821 | 0.21883 | -2.0135 | -4.7473 | -8.5294 | -9.8867 | 2.8935 | 2.8865 | 2.8798 | 2.8669 | 2.572 | 2.2752 | 1.975 | 1.6252 | 1.1341 | 0.79709 | -1.3192 | -4.1711 | -8.0586 | -9.438
| METHLICK | ST |  |  | 3.5589 | 3.5538 | 3.5487 | 3.5419 | 3.4917 | 3.3321 | 3.1721 | 2.9742 | 2.6695 | 2.3968 | 1.0487 | -2.6321 | -6.7793 | -11.0335 | 2.8716 | 2.8689 | 2.8662 | 2.8622 | 2.6866 | 2.4986 | 2.3204 | 2.0994 | 1.7613 | 1.445 | 0.039426 | -3.3579 | -7.3017 | -11.3629 | 2.8956 | 2.8883 | 2.8775 | 2.8598 | 2.7233 | 2.5853 | 2.4534 | 2.2902 | 2.0337 | 1.8092 | 0.59538 | -2.9923 | -7.3397 | -11.8446
| METHLICK | SP |  |  | 3.5554 | 3.5486 | 3.5417 | 3.5349 | 3.5187 | 3.5028 | 3.4868 | 3.4517 | 3.3596 | 3.245 | 2.7734 | 1.0631 | -1.6241 | -3.6485 | 2.8702 | 2.867 | 2.8637 | 2.8604 | 2.8479 | 2.7941 | 2.72 | 2.6451 | 2.5432 | 2.4149 | 1.8825 | 0.35628 | -2.1325 | -3.9269 | 2.8928 | 2.8865 | 2.8802 | 2.8738 | 2.8351 | 2.7924 | 2.7392 | 2.6848 | 2.6105 | 2.5187 | 2.1418 | 0.62329 | -1.9009 | -3.7796
SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | 6.9734 | 6.9729 | 6.9722 | 6.9709 | 6.937 | 6.9018 | 6.8654 | 6.8266 | 6.7713 | 6.7606 | 6.7298 | 6.6626 | 6.6116 | 6.5893 | 6.6841 | 6.6836 | 6.683 | 6.6819 | 6.6486 | 6.6138 | 6.5778 | 6.5393 | 6.4843 | 6.474 | 6.4443 | 6.3789 | 5.9678 | 5.9522 | 6.757 | 6.7566 | 6.7563 | 6.7557 | 6.7236 | 6.6895 | 6.6543 | 6.6166 | 6.5624 | 6.5529 | 6.5256 | 6.4641 | 6.4188 | 6.4021
| MID YELL | CT |  |  | 6.9734 | 6.9729 | 6.9722 | 6.9709 | 6.9684 | 6.9658 | 6.9628 | 6.9504 | 6.9378 | 6.9256 | 6.8887 | 6.8602 | 6.8317 | 6.7859 | 6.6841 | 6.6836 | 6.683 | 6.6819 | 6.6798 | 6.6774 | 6.6747 | 6.6649 | 6.6551 | 6.6457 | 6.6173 | 6.5679 | 6.5107 | 6.4367 | 6.757 | 6.7566 | 6.7563 | 6.7557 | 6.7542 | 6.7523 | 6.7502 | 6.7463 | 6.7422 | 6.739 | 6.7291 | 6.7096 | 6.6828 | 6.6385
| MID YELL | LW |  |  | 6.9738 | 6.9734 | 6.9729 | 6.9716 | 6.937 | 6.9018 | 6.8654 | 6.8266 | 6.7713 | 6.7606 | 6.7298 | 6.6626 | 6.6116 | 6.5893 | 6.6844 | 6.6842 | 6.6838 | 6.6829 | 6.6486 | 6.6138 | 6.5778 | 6.5393 | 6.4843 | 6.474 | 6.4443 | 6.3789 | 5.9678 | 5.9522 | 6.7573 | 6.7573 | 6.7572 | 6.757 | 6.7236 | 6.6895 | 6.6543 | 6.6166 | 6.5624 | 6.5529 | 6.5256 | 6.4641 | 6.4188 | 6.4021
| MID YELL | ST |  |  | 6.9739 | 6.9737 | 6.9735 | 6.973 | 6.9723 | 6.9715 | 6.9662 | 6.961 | 6.9559 | 6.9487 | 6.9276 | 6.8948 | 6.8859 | 6.8782 | 6.6845 | 6.6844 | 6.6842 | 6.6839 | 6.6833 | 6.6826 | 6.6787 | 6.6748 | 6.6709 | 6.6656 | 6.6501 | 6.6252 | 6.5983 | 6.5727 | 6.7573 | 6.7573 | 6.7572 | 6.7572 | 6.7569 | 6.7566 | 6.7556 | 6.7545 | 6.7534 | 6.7522 | 6.7487 | 6.7429 | 6.7351 | 6.7284
| MID YELL | SP |  |  | 6.974 | 6.974 | 6.9739 | 6.9739 | 6.9737 | 6.9735 | 6.9716 | 6.9698 | 6.9673 | 6.9645 | 6.9564 | 6.9437 | 6.9315 | 6.9191 | 6.6846 | 6.6845 | 6.6845 | 6.6845 | 6.6843 | 6.6842 | 6.6828 | 6.6815 | 6.6796 | 6.6776 | 6.6716 | 6.6623 | 6.6531 | 6.6437 | 6.7573 | 6.7573 | 6.7573 | 6.7573 | 6.7572 | 6.7572 | 6.7569 | 6.7566 | 6.7562 | 6.7557 | 6.7544 | 6.7523 | 6.7499 | 6.747
KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | 8.227 | 8.2262 | 8.2253 | 8.224 | 8.2187 | 7.2116 | 7.2026 | 7.1913 | 3.5187 | 2.7665 | 2.6717 | 1.8302 | 0.55596 | -0.49587 | 8.5777 | 8.5685 | 8.5551 | 8.5239 | 8.0893 | 6.7216 | 3.7691 | 3.3452 | 2.7126 | 1.8905 | 1.7888 | 0.99286 | -0.23201 | -1.5956 | 6.6813 | 6.6805 | 6.6795 | 6.6782 | 6.6729 | 3.9158 | 3.5387 | 3.0844 | 2.4063 | 1.524 | 1.4165 | 0.51928 | -0.78079 | -2.1081
| MIDMAR | CT |  |  | 8.227 | 8.2262 | 8.2253 | 8.224 | 8.2187 | 7.2116 | 7.2026 | 7.1913 | 3.5187 | 2.7665 | 2.6717 | 1.8302 | 0.55596 | 0.29354 | 8.5777 | 8.5685 | 8.5551 | 8.5239 | 8.0893 | 6.7216 | 3.7691 | 3.3452 | 2.7126 | 1.8905 | 1.7888 | 0.99286 | -0.1068 | -0.38028 | 6.6813 | 6.6805 | 6.6795 | 6.6782 | 6.6729 | 3.9158 | 3.5387 | 3.0844 | 2.4063 | 1.524 | 1.4165 | 0.51928 | -0.78079 | -1.0638
| MIDMAR | LW |  |  | 8.2282 | 8.2282 | 8.2282 | 8.2282 | 8.2248 | 7.2178 | 7.207 | 7.1917 | 7.1628 | 7.1567 | 7.1302 | 3.5978 | 2.4269 | -0.49587 | 8.5862 | 8.5841 | 8.5809 | 8.5728 | 8.5604 | 7.5446 | 7.5252 | 7.5015 | 7.4643 | 7.4493 | 7.3964 | 2.9607 | 1.9867 | -1.2579 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.679 | 5.672 | 5.6613 | 5.646 | 5.6171 | 5.6109 | 5.5844 | 2.631 | 1.4633 | -2.0174
| MIDMAR | ST |  |  | 8.2279 | 8.2277 | 8.2275 | 8.2272 | 8.2246 | 7.221 | 7.2165 | 7.2105 | 3.6083 | 2.868 | 2.8096 | 2.2819 | 0.83036 | -0.031771 | 8.5801 | 8.5733 | 8.5643 | 8.5472 | 8.1699 | 6.8098 | 3.8651 | 3.4323 | 2.8082 | 1.9988 | 1.9359 | 1.4206 | -0.012726 | -0.94953 | 6.6821 | 6.6819 | 6.6817 | 6.6815 | 6.6789 | 5.6753 | 3.6408 | 3.1765 | 2.5071 | 1.6382 | 1.5715 | 0.99659 | -0.59646 | -1.5976
| MIDMAR | SP |  |  | 8.2276 | 8.2273 | 8.2269 | 8.2266 | 8.2265 | 7.2264 | 7.2263 | 7.226 | 7.2256 | 7.2246 | 3.5153 | 2.1169 | 0.82798 | -0.34059 | 8.5862 | 8.585 | 8.5836 | 8.5821 | 8.4832 | 7.3701 | 7.2011 | 7.0349 | 6.8137 | 3.9241 | 2.7046 | 1.1758 | -0.23201 | -1.5956 | 6.6818 | 6.6815 | 6.6812 | 6.6809 | 6.6808 | 5.6807 | 5.6805 | 5.6803 | 5.6799 | 3.7035 | 2.3944 | 0.75324 | -0.74405 | -2.1081
BRIDGE OF DUN | MILL RD MONTROSE | MINIMUM HEADROOM | NO 71317 57683 | YES | 14.9844 | 14.933 | 14.8811 | 14.6442 | 14.4197 | 13.737 | 9.8837 | 9.1551 | 8.4012 | 8.1153 | 7.2574 | 5.3748 | 3.2495 | 2.0508 | 12.3719 | 12.3169 | 12.2593 | 12.0338 | 11.7676 | 9.9364 | 9.2262 | 8.4909 | 7.7307 | 7.4377 | 6.5217 | 4.3937 | 1.9517 | 0.47514 | 12.7691 | 12.7145 | 12.6575 | 12.4308 | 12.169 | 11.4724 | 9.3281 | 8.5963 | 7.8395 | 7.5503 | 6.6828 | 4.7846 | 2.4452 | 1.0015
| MILL RD MONTROSE | CT |  |  | 15.1342 | 15.0948 | 15.0548 | 15.0501 | 14.8537 | 14.4923 | 14.1635 | 13.8369 | 13.4108 | 13.1996 | 9.4156 | 5.6263 | 3.2495 | 2.0546 | 12.5214 | 12.4786 | 12.4336 | 12.4168 | 12.2074 | 11.8333 | 11.4916 | 11.152 | 9.5944 | 9.3754 | 8.6792 | 4.612 | 1.9517 | 0.47514 | 12.9187 | 12.8762 | 12.8317 | 12.8163 | 12.6082 | 12.2355 | 11.8951 | 11.5488 | 9.7014 | 9.4865 | 8.8409 | 5.034 | 2.4452 | 1.0015
| MILL RD MONTROSE | LW |  |  | 14.9844 | 14.933 | 14.8811 | 14.8771 | 14.4197 | 13.737 | 9.8837 | 9.1551 | 8.4012 | 8.1153 | 7.2574 | 5.3748 | 3.3116 | 2.0508 | 12.3719 | 12.3169 | 12.2593 | 12.241 | 11.7676 | 9.9364 | 9.2262 | 8.4909 | 7.7307 | 7.4377 | 6.5217 | 4.3937 | 2.0814 | 0.57156 | 12.7691 | 12.7145 | 12.6575 | 12.6407 | 12.169 | 11.4724 | 9.3281 | 8.5963 | 7.8395 | 7.5503 | 6.6828 | 4.7846 | 2.5671 | 1.0862
| MILL RD MONTROSE | ST |  |  | 15.2865 | 15.2606 | 15.2345 | 15.2329 | 15.1036 | 14.9736 | 13.9141 | 9.7027 | 9.5741 | 9.1588 | 7.9126 | 5.7907 | 4.3597 | 3.6303 | 12.6752 | 12.6472 | 12.6185 | 12.6116 | 12.4753 | 12.337 | 11.2653 | 9.0549 | 8.9212 | 8.5007 | 7.2394 | 5.0618 | 3.4562 | 2.5524 | 13.0722 | 13.0445 | 13.0161 | 13.0098 | 12.8742 | 12.7367 | 11.6663 | 9.1516 | 9.0206 | 8.6028 | 7.3496 | 5.2165 | 3.7744 | 3.0209
| MILL RD MONTROSE | SP |  |  | 15.4379 | 15.425 | 15.4121 | 14.6442 | 14.5807 | 14.5171 | 14.453 | 14.3889 | 14.3245 | 13.9915 | 9.8367 | 8.1069 | 6.9607 | 6.545 | 12.8285 | 12.8153 | 12.8021 | 12.0338 | 11.9684 | 11.9024 | 11.8343 | 11.7663 | 11.6969 | 11.3592 | 9.1956 | 7.4564 | 6.3014 | 5.8775 | 13.2254 | 13.2122 | 13.1991 | 12.4308 | 12.3655 | 12.2998 | 12.2322 | 12.1646 | 12.0957 | 11.7585 | 9.2887 | 7.5545 | 6.4042 | 5.9847
ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | YES | 24.396 | 24.2357 | 24.08 | 23.8728 | 23.6311 | 23.3716 | 23.0891 | 22.7772 | 22.3695 | 22.2084 | 21.8769 | 14.1518 | 10.5613 | 6.0291 | 19.3261 | 19.1991 | 19.0694 | 18.8785 | 18.6481 | 18.3986 | 18.1249 | 17.8187 | 17.4872 | 17.3713 | 13.3666 | 10.5219 | 6.7719 | 2.3912 | 18.2939 | 18.1403 | 17.9912 | 17.7925 | 17.5592 | 17.3077 | 17.0329 | 13.7596 | 13.1926 | 12.8691 | 12.0703 | 9.1466 | 4.7857 | -0.092141
| MILNATHORT | CT |  |  | 24.396 | 24.2357 | 24.08 | 23.8728 | 23.6311 | 23.3716 | 23.0891 | 22.7772 | 22.3695 | 22.2084 | 21.8769 | 14.1518 | 11.952 | 9.9905 | 19.3261 | 19.1991 | 19.0694 | 18.8785 | 18.6481 | 18.3986 | 18.1249 | 17.8187 | 17.4872 | 17.3713 | 13.3666 | 10.5219 | 7.9254 | 5.9381 | 18.2939 | 18.1403 | 17.9912 | 17.7925 | 17.5592 | 17.3077 | 17.0329 | 13.7596 | 13.1926 | 12.8691 | 12.0703 | 9.1466 | 6.3472 | 4.2633
| MILNATHORT | LW |  |  | 24.5446 | 24.5317 | 24.5193 | 24.5049 | 24.4774 | 24.4367 | 24.382 | 24.2921 | 24.1244 | 24.0666 | 23.8445 | 22.9025 | 21.5747 | 21.1582 | 19.4502 | 19.4344 | 19.4187 | 19.3972 | 19.3619 | 19.3141 | 19.253 | 19.1573 | 18.9854 | 18.9226 | 18.6874 | 17.821 | 16.6977 | 12.6472 | 18.4363 | 18.424 | 18.4121 | 18.3984 | 18.3716 | 18.3317 | 18.2778 | 18.1888 | 18.0222 | 17.9655 | 17.747 | 16.8253 | 12.5605 | 11.3555
| MILNATHORT | ST |  |  | 24.5477 | 24.5379 | 24.5281 | 24.515 | 24.4898 | 24.4602 | 24.4242 | 24.3733 | 24.2749 | 24.2379 | 24.111 | 22.8406 | 13.6858 | 10.3667 | 19.4348 | 19.4159 | 19.393 | 19.3534 | 19.2908 | 19.2157 | 19.1491 | 19.0681 | 18.9403 | 18.8764 | 18.6728 | 13.5937 | 10.26 | 6.9681 | 18.4392 | 18.4298 | 18.4203 | 18.4078 | 18.383 | 18.3539 | 18.3185 | 18.2682 | 18.1703 | 18.1339 | 18.0088 | 12.5138 | 8.6974 | 4.8037
| MILNATHORT | SP |  |  | 24.5405 | 24.5272 | 24.5139 | 24.5006 | 24.4832 | 24.466 | 24.4488 | 24.43 | 24.405 | 24.3747 | 24.2497 | 21.0399 | 10.5613 | 6.0291 | 19.4474 | 19.4334 | 19.4189 | 19.4055 | 19.29 | 19.1592 | 18.9742 | 18.8775 | 18.86 | 18.837 | 18.7333 | 11.2279 | 6.7719 | 2.3912 | 18.4322 | 18.4195 | 18.4067 | 18.3938 | 18.3772 | 18.3607 | 18.3442 | 18.3262 | 13.6658 | 13.5912 | 13.3387 | 9.6505 | 4.7857 | -0.092141
MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | 24.9761 | 24.9738 | 24.9712 | 24.9673 | 24.9548 | 24.9399 | 24.9224 | 24.9024 | 24.8798 | 24.8668 | 24.8238 | 24.724 | 24.5596 | 24.2407 | 15.7472 | 15.7387 | 15.7268 | 15.7009 | 15.6648 | 15.6266 | 15.5862 | 15.515 | 15.4498 | 15.4224 | 15.3535 | 15.2536 | 13.5185 | 12.7711 | 8.7647 | 8.7617 | 8.7582 | 8.7521 | 8.7373 | 8.7201 | 8.7003 | 8.6752 | 8.6476 | 8.6293 | 8.5702 | 8.4444 | 8.2248 | 7.5388
| MILTON OF CRAIGIE | CT |  |  | 24.9761 | 24.9738 | 24.9712 | 24.9673 | 24.9548 | 24.9399 | 24.9224 | 24.9024 | 24.8798 | 24.8668 | 24.8238 | 24.724 | 24.5596 | 24.2407 | 15.7472 | 15.7387 | 15.7268 | 15.7009 | 15.6648 | 15.6266 | 15.5862 | 15.515 | 15.4498 | 15.4224 | 15.3535 | 15.2536 | 13.5185 | 12.7711 | 8.7647 | 8.7617 | 8.7582 | 8.7521 | 8.7373 | 8.7201 | 8.7003 | 8.6752 | 8.6476 | 8.6293 | 8.5702 | 8.4444 | 8.2248 | 7.5388
| MILTON OF CRAIGIE | LW |  |  | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 15.755 | 15.7526 | 15.7489 | 15.7395 | 15.7291 | 15.7189 | 15.7089 | 15.6992 | 15.6896 | 15.6793 | 15.6488 | 15.5996 | 15.5541 | 15.5387 | 8.7684 | 8.7681 | 8.7678 | 8.7668 | 8.7658 | 8.7648 | 8.7638 | 8.7628 | 8.7619 | 8.7609 | 8.7579 | 8.753 | 8.7481 | 8.7432
| MILTON OF CRAIGIE | ST |  |  | 24.9787 | 24.9782 | 24.9777 | 24.9772 | 24.9726 | 24.967 | 24.9606 | 24.9533 | 24.945 | 24.9423 | 24.9341 | 24.9205 | 24.8495 | 24.8093 | 15.7516 | 15.7468 | 15.7406 | 15.729 | 15.7094 | 15.6859 | 15.6585 | 15.6307 | 15.6024 | 15.5637 | 15.4922 | 15.4502 | 15.3792 | 15.339 | 8.7674 | 8.7665 | 8.7655 | 8.7638 | 8.7577 | 8.7504 | 8.7419 | 8.7325 | 8.7223 | 8.716 | 8.6975 | 8.6672 | 8.5798 | 8.5231
| MILTON OF CRAIGIE | SP |  |  | 24.9781 | 24.9774 | 24.9766 | 24.9759 | 24.9758 | 24.9756 | 24.9755 | 24.9753 | 24.9752 | 24.9741 | 24.9704 | 24.9676 | 24.9494 | 24.9097 | 15.7551 | 15.7538 | 15.7524 | 15.7509 | 15.7465 | 15.7414 | 15.7344 | 15.7275 | 15.7187 | 15.7036 | 15.6594 | 15.5929 | 15.5203 | 15.4658 | 8.7672 | 8.7664 | 8.7656 | 8.7648 | 8.7643 | 8.7636 | 8.7628 | 8.762 | 8.761 | 8.7585 | 8.7508 | 8.7417 | 8.7176 | 8.6724
STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | 18.5126 | 18.5095 | 18.5062 | 18.5011 | 18.4787 | 18.4524 | 18.4217 | 18.3865 | 18.3427 | 13.9461 | 12.4333 | 9.1942 | 6.4834 | 2.912 | 17.0975 | 17.0944 | 17.0911 | 17.086 | 17.0636 | 17.0373 | 13.546 | 12.9681 | 12.229 | 11.5133 | 9.7356 | 6.3758 | 3.6448 | -0.5064 | 16.9158 | 16.907 | 16.8951 | 16.8696 | 16.765 | 16.6128 | 13.6083 | 13.0198 | 12.2684 | 11.5403 | 9.7457 | 6.1667 | 3.2595 | -0.84473
| MINTLAW | CT |  |  | 18.5126 | 18.5095 | 18.5062 | 18.5011 | 18.4787 | 18.4524 | 18.4217 | 18.3865 | 18.3427 | 18.323 | 13.1027 | 9.3099 | 6.4834 | 2.912 | 17.0975 | 17.0944 | 17.0911 | 17.086 | 17.0636 | 17.0373 | 17.0066 | 13.7768 | 13.2841 | 12.6683 | 10.5555 | 6.5696 | 3.6448 | -0.5064 | 16.9158 | 16.907 | 16.8951 | 16.8696 | 16.765 | 16.6672 | 16.5659 | 16.4482 | 13.3434 | 12.7172 | 10.5687 | 6.3595 | 3.2595 | -0.84473
| MINTLAW | LW |  |  | 18.517 | 18.517 | 18.517 | 18.517 | 18.5069 | 18.4945 | 18.4795 | 18.4611 | 18.4304 | 13.9461 | 12.4333 | 9.1942 | 7.6303 | 5.7993 | 17.1018 | 17.1018 | 17.1018 | 17.1018 | 17.0918 | 17.0794 | 13.546 | 12.9681 | 12.229 | 11.5133 | 9.7356 | 6.3758 | 4.9154 | 2.7354 | 16.9256 | 16.9246 | 16.9231 | 16.9194 | 16.7665 | 16.6128 | 13.6083 | 13.0198 | 12.2684 | 11.5403 | 9.7457 | 6.1667 | 4.5285 | 2.3582
| MINTLAW | ST |  |  | 18.5158 | 18.5151 | 18.5143 | 18.5134 | 18.502 | 18.4885 | 18.4735 | 18.4558 | 18.4318 | 18.425 | 13.6662 | 10.7413 | 7.1728 | 5.2729 | 17.1007 | 17.1 | 17.0992 | 17.0983 | 17.0869 | 17.0734 | 17.0584 | 17.0407 | 13.7247 | 13.1632 | 11.1896 | 7.9753 | 3.9312 | 1.7114 | 16.9229 | 16.9201 | 16.9166 | 16.9104 | 16.8384 | 16.7663 | 16.6901 | 16.5972 | 16.4685 | 13.219 | 11.2113 | 7.8758 | 3.7803 | 1.5959
| MINTLAW | SP |  |  | 18.5146 | 18.5133 | 18.512 | 18.5107 | 18.5099 | 18.5091 | 18.5083 | 18.5073 | 18.5058 | 18.5025 | 18.4902 | 18.4787 | 14.0385 | 13.2013 | 17.0995 | 17.0982 | 17.0969 | 17.0956 | 17.0948 | 17.094 | 17.0932 | 17.0922 | 17.0907 | 17.0874 | 13.7365 | 12.6729 | 11.6328 | 10.6715 | 16.9237 | 16.9221 | 16.9205 | 16.9187 | 16.9018 | 16.8824 | 16.8531 | 16.8242 | 16.7856 | 16.7326 | 16.5149 | 12.7192 | 11.6631 | 10.6867
BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | YES | 21.451 | 21.3463 | 21.2439 | 21.1007 | 20.9393 | 20.7695 | 20.5882 | 20.3897 | 20.1353 | 20.0261 | 19.803 | 14.3574 | 11.3869 | 6.1628 | 19.2792 | 19.1782 | 19.0718 | 18.9017 | 18.7087 | 18.5074 | 18.3492 | 18.168 | 17.9375 | 17.8211 | 17.5308 | 16.1216 | 11.0867 | 6.7284 | 19.6002 | 19.4893 | 19.3791 | 19.2198 | 19.0415 | 18.8551 | 18.6576 | 18.4397 | 18.1658 | 18.0373 | 17.8248 | 13.3274 | 10.1782 | 4.8651
| MONTROSE NORTH | CT |  |  | 21.451 | 21.3463 | 21.2439 | 21.1007 | 20.9393 | 20.7695 | 20.5882 | 20.3897 | 20.1353 | 20.0261 | 19.803 | 18.3657 | 11.3869 | 6.1628 | 19.2792 | 19.1782 | 19.0718 | 18.9017 | 18.7087 | 18.5074 | 18.3492 | 18.168 | 17.9375 | 17.8211 | 17.5308 | 16.5198 | 11.0867 | 6.7284 | 19.6002 | 19.4893 | 19.3791 | 19.2198 | 19.0415 | 18.8551 | 18.6576 | 18.4397 | 18.1658 | 18.0373 | 17.8248 | 16.4416 | 10.1782 | 4.8651
| MONTROSE NORTH | LW |  |  | 21.5476 | 21.5389 | 21.5301 | 21.5191 | 21.5068 | 21.4934 | 21.479 | 21.4524 | 21.4008 | 21.3731 | 21.2709 | 21.0184 | 20.6694 | 20.4478 | 19.3722 | 19.3615 | 19.3487 | 19.3258 | 19.3001 | 19.274 | 19.2474 | 19.209 | 19.1465 | 19.1069 | 18.9701 | 18.6635 | 18.2808 | 18.0708 | 19.7023 | 19.6925 | 19.6822 | 19.6675 | 19.6511 | 19.6337 | 19.6154 | 19.5849 | 19.5294 | 19.4975 | 19.3829 | 19.11 | 18.7374 | 18.4942
| MONTROSE NORTH | ST |  |  | 21.5495 | 21.5426 | 21.5354 | 21.5254 | 21.4348 | 21.3376 | 21.2402 | 21.126 | 20.9361 | 20.8821 | 20.7281 | 14.3574 | 11.7415 | 8.4928 | 19.3703 | 19.3589 | 19.3453 | 19.3225 | 19.214 | 19.095 | 18.9651 | 18.8192 | 18.5981 | 18.4994 | 18.2161 | 16.1216 | 11.6485 | 8.9423 | 19.7034 | 19.695 | 19.6859 | 19.6722 | 19.5766 | 19.4734 | 19.3673 | 19.2446 | 19.0463 | 18.9805 | 18.7922 | 13.3274 | 10.794 | 7.4883
| MONTROSE NORTH | SP |  |  | 21.5457 | 21.5373 | 21.5289 | 21.5204 | 21.5086 | 21.4969 | 21.4846 | 21.4715 | 21.4548 | 21.4349 | 21.3591 | 19.4042 | 14.5127 | 13.221 | 19.3726 | 19.3647 | 19.3567 | 19.3486 | 19.3335 | 19.3174 | 19.2958 | 19.2735 | 19.2444 | 19.2084 | 19.0857 | 17.7688 | 16.619 | 13.4994 | 19.7009 | 19.6921 | 19.6833 | 19.6744 | 19.661 | 19.6474 | 19.632 | 19.6159 | 19.5954 | 19.5707 | 19.4811 | 17.4907 | 13.5119 | 12.3145
TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | 4.4921 | 4.4915 | 4.4896 | 4.4875 | 4.4232 | 2.3681 | 1.6295 | 0.88873 | 0.7469 | 0.71345 | -0.90729 | -1.5562 | -2.9819 | -6.9945 | 3.6568 | 3.6537 | 3.6483 | 3.6374 | 2.3454 | 1.4774 | 0.6036 | -0.27104 | -0.41468 | -0.45009 | -2.418 | -3.1215 | -4.599 | -9.3811 | 4.0263 | 4.0219 | 2.4979 | 2.4836 | 1.7383 | 0.98251 | 0.22807 | -0.52844 | -0.67047 | -0.70416 | -2.3682 | -3.0244 | -4.4096 | -9.1951
| MOSSAT | CT |  |  | 4.4921 | 4.4915 | 4.4896 | 4.4875 | 4.439 | 4.3857 | 4.3282 | 4.2666 | 1.9454 | 1.3074 | -0.90729 | -1.5562 | -2.9082 | -6.9945 | 3.6568 | 3.6537 | 3.6483 | 3.6374 | 3.4144 | 2.4446 | 2.0916 | 1.6552 | 1.0056 | 0.24096 | -2.418 | -3.1215 | -4.599 | -9.3811 | 4.0263 | 4.0219 | 2.4979 | 2.4836 | 2.1269 | 1.8163 | 1.5042 | 1.1198 | 0.55228 | -0.10087 | -2.3682 | -3.0244 | -4.4096 | -9.1951
| MOSSAT | LW |  |  | 4.4929 | 4.4929 | 4.4929 | 4.4929 | 4.4232 | 2.3681 | 1.6295 | 0.88873 | 0.7469 | 0.71345 | 0.60926 | -1.3373 | -2.488 | -5.0459 | 3.6588 | 3.6572 | 3.6547 | 3.6483 | 2.3454 | 1.4774 | 0.6036 | -0.27104 | -0.41468 | -0.45009 | -0.56008 | -2.8586 | -4.1081 | -7.1215 | 4.029 | 4.0266 | 4.0227 | 2.4968 | 1.7383 | 0.98251 | 0.22807 | -0.52844 | -0.67047 | -0.70416 | -0.80903 | -2.7969 | -3.9469 | -6.9222
| MOSSAT | ST |  |  | 4.4928 | 4.4928 | 4.4927 | 4.4927 | 4.4613 | 4.4271 | 4.3941 | 4.356 | 2.0994 | 1.4743 | -0.70705 | -1.1189 | -2.9819 | -5.2783 | 3.6586 | 3.6571 | 3.6551 | 3.6512 | 3.4416 | 3.3807 | 2.2106 | 1.7863 | 1.1651 | 0.41452 | -2.2069 | -2.6663 | -4.4517 | -7.1653 | 4.0287 | 4.0264 | 4.0234 | 4.0176 | 2.2009 | 1.9137 | 1.6184 | 1.2483 | 0.70869 | 0.068861 | -2.1641 | -2.5816 | -4.408 | -7.1224
| MOSSAT | SP |  |  | 4.4928 | 4.4927 | 4.4927 | 4.4926 | 4.488 | 4.4836 | 4.4789 | 4.4737 | 4.4651 | 4.4557 | 2.1026 | 0.91535 | -0.53922 | -1.6193 | 3.66 | 3.6598 | 3.6595 | 3.6592 | 3.604 | 3.5416 | 3.4595 | 3.4411 | 3.4151 | 2.2793 | 1.1427 | -0.28138 | -1.9393 | -3.2101 | 4.0308 | 4.0305 | 4.0301 | 4.0296 | 2.4368 | 2.3515 | 2.2205 | 2.0909 | 1.917 | 1.6861 | 0.70888 | -0.50615 | -1.9846 | -3.0871
THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | 12.415 | 12.2968 | 12.1825 | 12.0353 | 11.8879 | 11.7442 | 11.6038 | 11.4645 | 11.3419 | 11.275 | 11.1559 | 10.9453 | 10.7129 | 10.3851 | 10.5538 | 10.4532 | 10.3543 | 10.2217 | 10.0873 | 9.9558 | 9.827 | 9.6791 | 9.5453 | 9.4767 | 9.3949 | 9.2447 | 9.0665 | 7.213 | 10.5188 | 10.4023 | 10.2898 | 10.1456 | 10.0012 | 9.8604 | 9.7228 | 9.5888 | 9.4712 | 9.409 | 9.3033 | 9.1142 | 7.2669 | 6.7102
| MOUNT PLEASANT | CT |  |  | 12.415 | 12.2968 | 12.1825 | 12.0353 | 11.8879 | 11.7442 | 11.6038 | 11.4645 | 11.3419 | 11.275 | 11.1559 | 10.9453 | 10.7129 | 10.3851 | 10.5538 | 10.4532 | 10.3543 | 10.2217 | 10.0873 | 9.9558 | 9.827 | 9.6791 | 9.5453 | 9.4767 | 9.3949 | 9.2447 | 9.0665 | 7.213 | 10.5188 | 10.4023 | 10.2898 | 10.1456 | 10.0012 | 9.8604 | 9.7228 | 9.5888 | 9.4712 | 9.409 | 9.3033 | 9.1142 | 7.2669 | 6.7102
| MOUNT PLEASANT | LW |  |  | 12.5227 | 12.5128 | 12.5032 | 12.4916 | 12.4786 | 12.4644 | 12.449 | 12.4327 | 12.4174 | 12.4014 | 12.3514 | 12.262 | 12.1766 | 12.083 | 10.6447 | 10.635 | 10.6246 | 10.609 | 10.5915 | 10.5731 | 10.554 | 10.5342 | 10.5154 | 10.4955 | 10.4343 | 10.3287 | 10.2261 | 10.1171 | 10.6252 | 10.6156 | 10.6064 | 10.5957 | 10.5837 | 10.5704 | 10.5561 | 10.5407 | 10.5263 | 10.5114 | 10.4643 | 10.38 | 10.2995 | 10.2109
| MOUNT PLEASANT | ST |  |  | 12.5262 | 12.5193 | 12.5125 | 12.5033 | 12.492 | 12.4803 | 12.4644 | 12.4484 | 12.4321 | 12.4188 | 12.3751 | 12.3095 | 12.2151 | 12.1419 | 10.6481 | 10.6416 | 10.6349 | 10.6253 | 10.6128 | 10.5995 | 10.5677 | 10.5361 | 10.5047 | 10.4715 | 10.371 | 10.2133 | 10.0369 | 9.9835 | 10.6285 | 10.6219 | 10.6152 | 10.6063 | 10.5954 | 10.5842 | 10.5708 | 10.5571 | 10.5431 | 10.5326 | 10.4973 | 10.4451 | 10.3639 | 10.3037
| MOUNT PLEASANT | SP |  |  | 12.5217 | 12.5128 | 12.5039 | 12.4949 | 12.482 | 12.4693 | 12.4561 | 12.443 | 12.43 | 12.4166 | 12.3771 | 12.3027 | 12.2314 | 12.1536 | 10.6451 | 10.6376 | 10.6301 | 10.6225 | 10.6112 | 10.5998 | 10.583 | 10.5663 | 10.5481 | 10.5284 | 10.4709 | 10.3709 | 10.2744 | 10.1729 | 10.6241 | 10.6152 | 10.6064 | 10.5975 | 10.5849 | 10.5724 | 10.5601 | 10.5479 | 10.5359 | 10.5237 | 10.4878 | 10.419 | 10.3529 | 10.28
BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | YES | 33.0749 | 33.0711 | 33.0594 | 33.0456 | 33.0176 | 32.9841 | 32.9463 | 32.9037 | 32.8568 | 32.8254 | 32.7368 | 32.5443 | 32.2509 | 31.7076 | 28.8144 | 28.8006 | 28.7743 | 28.7254 | 28.6594 | 28.5888 | 28.5143 | 28.4293 | 28.3409 | 28.2643 | 28.0414 | 27.6995 | 27.4146 | 26.8796 | 29.983 | 29.9792 | 29.9681 | 29.955 | 29.9276 | 29.8949 | 29.8578 | 29.8161 | 29.7701 | 29.7394 | 29.6524 | 29.4624 | 29.1712 | 28.6301
| MUIR OF ORD | CT |  |  | 33.0749 | 33.0711 | 33.0594 | 33.0456 | 33.0176 | 32.9841 | 32.9463 | 32.9037 | 32.8568 | 32.8254 | 32.7368 | 32.5443 | 32.2509 | 31.7076 | 28.8144 | 28.8006 | 28.7743 | 28.7254 | 28.6594 | 28.5888 | 28.5143 | 28.4293 | 28.3409 | 28.2643 | 28.0414 | 27.6995 | 27.4146 | 26.8796 | 29.983 | 29.9792 | 29.9681 | 29.955 | 29.9276 | 29.8949 | 29.8578 | 29.8161 | 29.7701 | 29.7394 | 29.6524 | 29.4624 | 29.1712 | 28.6301
| MUIR OF ORD | LW |  |  | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 33.0802 | 28.8292 | 28.8275 | 28.8249 | 28.8182 | 28.8108 | 28.8035 | 28.7964 | 28.7895 | 28.7827 | 28.7754 | 28.7537 | 28.7187 | 28.6835 | 28.6486 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883 | 29.9883
| MUIR OF ORD | ST |  |  | 33.079 | 33.0782 | 33.0774 | 33.0764 | 33.0684 | 33.0589 | 33.0478 | 33.0352 | 33.021 | 33.0163 | 33.0022 | 32.9787 | 32.8562 | 32.7868 | 28.8226 | 28.8158 | 28.807 | 28.7906 | 28.7619 | 28.7273 | 28.6931 | 28.6577 | 28.6212 | 28.5864 | 28.4848 | 28.3207 | 28.0587 | 27.9029 | 29.9871 | 29.9863 | 29.9855 | 29.9845 | 29.9765 | 29.967 | 29.956 | 29.9433 | 29.9291 | 29.9244 | 29.9103 | 29.8868 | 29.7643 | 29.6949
| MUIR OF ORD | SP |  |  | 33.0778 | 33.0765 | 33.0752 | 33.0739 | 33.0737 | 33.0734 | 33.0731 | 33.0729 | 33.0726 | 33.0706 | 33.064 | 33.0589 | 33.0259 | 32.9541 | 28.8272 | 28.8251 | 28.8228 | 28.8203 | 28.8141 | 28.8067 | 28.7987 | 28.7909 | 28.7809 | 28.7672 | 28.7267 | 28.6687 | 28.5858 | 28.4668 | 29.9859 | 29.9846 | 29.9833 | 29.982 | 29.9818 | 29.9815 | 29.9813 | 29.981 | 29.9807 | 29.9787 | 29.9721 | 29.967 | 29.934 | 29.8622
BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | 7.7848 | 7.784 | 7.7831 | 7.7818 | 7.7079 | 7.6251 | 7.546 | 7.4564 | 7.3129 | 7.2831 | 7.2088 | 6.9216 | 5.6335 | 5.4662 | 7.053 | 7.0514 | 7.0494 | 7.0453 | 6.9725 | 6.8878 | 6.8007 | 6.7031 | 5.9337 | 5.8848 | 5.7549 | 5.3781 | 4.8663 | 4.6368 | 7.0053 | 7.0042 | 7.003 | 7.0008 | 6.9273 | 6.8438 | 6.7622 | 6.6715 | 6.5279 | 5.9894 | 5.8674 | 5.5035 | 4.9931 | 4.7636
| MUIREND | CT |  |  | 7.7848 | 7.784 | 7.7831 | 7.7818 | 7.7774 | 7.7722 | 7.7661 | 7.759 | 7.751 | 7.7465 | 7.7313 | 7.6964 | 7.6386 | 7.5267 | 7.053 | 7.0514 | 7.0494 | 7.0453 | 7.0379 | 7.0298 | 7.0208 | 7.0003 | 6.9791 | 6.9603 | 6.9198 | 6.8848 | 5.8416 | 5.5907 | 7.0053 | 7.0042 | 7.003 | 7.0008 | 6.9954 | 6.9893 | 6.9823 | 6.974 | 6.9661 | 6.9615 | 6.9464 | 6.9114 | 5.9683 | 5.7174
| MUIREND | LW |  |  | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.786 | 7.0546 | 7.0541 | 7.0534 | 7.0516 | 7.0495 | 7.0475 | 7.0456 | 7.0437 | 7.0418 | 7.0398 | 7.0338 | 7.0242 | 7.0146 | 7.005 | 7.0066 | 7.0065 | 7.0062 | 7.0057 | 7.005 | 7.0044 | 7.0038 | 7.0032 | 7.0026 | 7.0019 | 7.0011 | 7.0011 | 7.0011 | 7.0011
| MUIREND | ST |  |  | 7.7858 | 7.7856 | 7.7855 | 7.7853 | 7.7079 | 7.6251 | 7.546 | 7.4564 | 7.3129 | 7.2831 | 7.2088 | 6.9216 | 5.6335 | 5.4662 | 7.0543 | 7.0537 | 7.0529 | 7.0515 | 6.9725 | 6.8878 | 6.8007 | 6.7031 | 5.9337 | 5.8848 | 5.7549 | 5.3781 | 4.8663 | 4.6368 | 7.0063 | 7.0061 | 7.0057 | 7.0052 | 6.9273 | 6.8438 | 6.7622 | 6.6715 | 6.5279 | 5.9894 | 5.8674 | 5.5035 | 4.9931 | 4.7636
| MUIREND | SP |  |  | 7.7855 | 7.7853 | 7.785 | 7.7848 | 7.7847 | 7.7847 | 7.7846 | 7.7846 | 7.7845 | 7.7841 | 7.7829 | 7.7819 | 7.7755 | 7.7615 | 7.0545 | 7.0542 | 7.0538 | 7.0535 | 7.053 | 7.0524 | 7.0497 | 7.047 | 7.0435 | 7.0394 | 7.0276 | 7.0101 | 6.988 | 6.9592 | 7.0063 | 7.006 | 7.0057 | 7.0054 | 7.0052 | 7.005 | 7.0041 | 7.0032 | 7.0021 | 7.0006 | 6.9979 | 6.9969 | 6.9905 | 6.9766
NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | YES | 24.4814 | 24.4727 | 24.4613 | 24.4384 | 24.3976 | 24.3529 | 24.3036 | 24.2445 | 24.1811 | 24.1344 | 23.9866 | 23.6902 | 23.2701 | 22.5583 | 20.7225 | 20.6935 | 20.6518 | 20.5565 | 20.4378 | 20.3165 | 20.192 | 20.036 | 19.8772 | 19.7275 | 19.379 | 18.9242 | 18.4161 | 17.8107 | 20.478 | 20.4503 | 20.4104 | 20.3194 | 20.2054 | 20.0887 | 19.9687 | 19.8185 | 19.6655 | 19.596 | 19.4035 | 19.0344 | 18.5408 | 17.8107
| NAIRN CENTRAL | CT |  |  | 24.4814 | 24.4727 | 24.4613 | 24.4384 | 24.3976 | 24.3529 | 24.3036 | 24.2445 | 24.1811 | 24.1344 | 23.9866 | 23.6902 | 23.2701 | 22.5583 | 20.7225 | 20.6935 | 20.6518 | 20.5565 | 20.4378 | 20.3165 | 20.192 | 20.036 | 19.8772 | 19.7275 | 19.379 | 18.9242 | 18.4161 | 17.8107 | 20.478 | 20.4503 | 20.4104 | 20.3194 | 20.2054 | 20.0887 | 19.9687 | 19.8185 | 19.6655 | 19.596 | 19.4035 | 19.0344 | 18.5408 | 17.8107
| NAIRN CENTRAL | LW |  |  | 24.4916 | 24.4905 | 24.4888 | 24.4845 | 24.4797 | 24.4751 | 24.4705 | 24.466 | 24.4617 | 24.4569 | 24.443 | 24.4205 | 24.3978 | 24.3754 | 20.7504 | 20.7443 | 20.7346 | 20.7105 | 20.6836 | 20.6573 | 20.6316 | 20.6064 | 20.5818 | 20.5552 | 20.4765 | 20.3497 | 20.2221 | 20.0957 | 20.5049 | 20.4991 | 20.4899 | 20.4669 | 20.4414 | 20.4164 | 20.3919 | 20.368 | 20.3446 | 20.3194 | 20.2445 | 20.124 | 20.0026 | 19.8825
| NAIRN CENTRAL | ST |  |  | 24.5134 | 24.4856 | 24.4819 | 24.4751 | 24.4592 | 24.4401 | 24.4172 | 24.3931 | 24.3674 | 24.348 | 24.2911 | 24.1987 | 24.0068 | 23.8689 | 20.8793 | 20.7266 | 20.709 | 20.6753 | 20.623 | 20.5603 | 20.4835 | 20.4065 | 20.329 | 20.2416 | 19.9868 | 19.6299 | 19.3109 | 19.0919 | 20.6274 | 20.4822 | 20.4654 | 20.4333 | 20.3832 | 20.3231 | 20.2495 | 20.1757 | 20.1014 | 20.018 | 19.7751 | 19.6289 | 19.3908 | 19.2069
| NAIRN CENTRAL | SP |  |  | 24.5148 | 24.5134 | 24.4872 | 24.4856 | 24.4832 | 24.4804 | 24.4763 | 24.4723 | 24.4672 | 24.4598 | 24.4377 | 24.4073 | 24.3549 | 24.2708 | 20.8907 | 20.8879 | 20.7456 | 20.7421 | 20.7294 | 20.7142 | 20.6924 | 20.6709 | 20.6434 | 20.6095 | 20.5106 | 20.3599 | 20.1947 | 20.0041 | 20.6382 | 20.6355 | 20.5001 | 20.4967 | 20.4846 | 20.4702 | 20.4495 | 20.429 | 20.4029 | 20.3706 | 20.2762 | 20.1328 | 19.9743 | 19.7901
STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | 1.4703 | 5.2075 | 5.1468 | 5.0706 | 4.9616 | 4.8519 | 4.7419 | 4.6317 | 4.507 | 4.4608 | 4.3784 | 3.9581 | 3.2103 | 2.8377 | 1.5383 | 5.3039 | 5.2706 | 5.2288 | 5.153 | 5.0313 | 4.901 | 4.7728 | 4.6302 | 4.5607 | 4.4043 | 3.8794 | 3.2083 | 2.8302 | 1.3899 | 5.1328 | 5.0777 | 5.0087 | 4.9066 | 4.8036 | 4.7001 | 4.5962 | 4.4774 | 4.4225 | 4.2581 | 3.6825 | 2.9028 | 2.5013
| NEW PITSLIGO | CT |  |  | 1.4703 | 5.2075 | 5.1468 | 5.0706 | 4.9616 | 4.8519 | 4.7419 | 4.6317 | 4.507 | 4.4608 | 4.3784 | 3.9581 | 3.2103 | 2.8377 | 1.5383 | 5.3039 | 5.2706 | 5.2288 | 5.153 | 5.0313 | 4.901 | 4.7728 | 4.6302 | 4.5607 | 4.4043 | 3.8794 | 3.2083 | 2.8302 | 1.3899 | 5.1328 | 5.0777 | 5.0087 | 4.9066 | 4.8036 | 4.7001 | 4.5962 | 4.4774 | 4.4225 | 4.2581 | 3.6825 | 2.9028 | 2.5013
| NEW PITSLIGO | LW |  |  | 1.5278 | 5.3226 | 5.3176 | 5.3119 | 5.2888 | 5.2648 | 5.2396 | 5.2125 | 5.1768 | 5.163 | 5.1211 | 4.8855 | 4.438 | 4.3236 | 1.5701 | 5.3673 | 5.3646 | 5.3614 | 5.3413 | 5.3205 | 5.2989 | 5.2756 | 5.2439 | 5.2343 | 5.2055 | 5.0372 | 4.5954 | 4.4526 | 1.4421 | 5.2374 | 5.2329 | 5.2277 | 5.2052 | 5.1818 | 5.1573 | 5.1311 | 5.0961 | 5.0832 | 5.0439 | 4.8268 | 4.4191 | 4.266
| NEW PITSLIGO | ST |  |  | 1.5294 | 5.3258 | 5.3222 | 5.3173 | 5.3032 | 5.2882 | 5.2723 | 5.2552 | 5.2325 | 5.2237 | 5.1967 | 5.0583 | 4.7727 | 4.69 | 1.5708 | 5.3688 | 5.3667 | 5.3639 | 5.3518 | 5.3389 | 5.3254 | 5.3106 | 5.2901 | 5.2834 | 5.2638 | 5.1106 | 4.7657 | 4.6067 | 1.4436 | 5.2403 | 5.2369 | 5.2325 | 5.2188 | 5.2042 | 5.1888 | 5.1721 | 5.1499 | 5.1415 | 5.1161 | 4.9867 | 4.7037 | 4.5376
| NEW PITSLIGO | SP |  |  | 1.5268 | 5.3218 | 5.3168 | 5.3118 | 5.3038 | 5.296 | 5.2882 | 5.2803 | 5.2717 | 5.2626 | 5.2342 | 5.1893 | 5.0642 | 4.9833 | 1.5692 | 5.3663 | 5.3634 | 5.3605 | 5.3556 | 5.3508 | 5.346 | 5.3412 | 5.3355 | 5.3293 | 5.3093 | 5.2811 | 5.1725 | 5.1074 | 1.4411 | 5.2366 | 5.232 | 5.2274 | 5.2201 | 5.2128 | 5.2056 | 5.1984 | 5.1904 | 5.1818 | 5.1552 | 5.1136 | 4.9919 | 4.9143
DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | 0.36989 | 0.3698 | 0.36795 | 0.36605 | 0.36374 | 0.36098 | 0.35806 | 0.35495 | 0.35167 | 0.34872 | 0.3428 | 0.29013 | 0.26339 | 0.23068 | 0.34868 | 0.34845 | 0.34658 | 0.34439 | 0.34176 | 0.33897 | 0.33686 | 0.3346 | 0.33219 | 0.33014 | 0.29959 | 0.27547 | 0.24807 | 0.21469 | 0.35133 | 0.35103 | 0.34914 | 0.34677 | 0.34411 | 0.34113 | 0.33807 | 0.33483 | 0.33141 | 0.32832 | 0.29478 | 0.26675 | 0.23665 | 0.20065
| NEWTON | CT |  |  | 0.36989 | 0.3698 | 0.36795 | 0.36605 | 0.36374 | 0.36098 | 0.35806 | 0.35495 | 0.35167 | 0.34872 | 0.3428 | 0.29013 | 0.26339 | 0.23068 | 0.34868 | 0.34845 | 0.34658 | 0.34439 | 0.34176 | 0.33897 | 0.33686 | 0.3346 | 0.33219 | 0.33014 | 0.29959 | 0.27547 | 0.24807 | 0.21469 | 0.35133 | 0.35103 | 0.34914 | 0.34677 | 0.34411 | 0.34113 | 0.33807 | 0.33483 | 0.33141 | 0.32832 | 0.29478 | 0.26675 | 0.23665 | 0.20065
| NEWTON | LW |  |  | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.37002 | 0.3488 | 0.34863 | 0.34838 | 0.34774 | 0.34703 | 0.34639 | 0.34584 | 0.3453 | 0.34526 | 0.34526 | 0.34526 | 0.34526 | 0.34526 | 0.34526 | 0.35144 | 0.35118 | 0.35101 | 0.35076 | 0.35059 | 0.35059 | 0.35059 | 0.35059 | 0.35059 | 0.35059 | 0.35059 | 0.35059 | 0.35059 | 0.35059
| NEWTON | ST |  |  | 0.37 | 0.36999 | 0.36997 | 0.36996 | 0.36981 | 0.36964 | 0.36945 | 0.36922 | 0.36897 | 0.36889 | 0.36864 | 0.36822 | 0.36606 | 0.36483 | 0.34884 | 0.34875 | 0.34862 | 0.34841 | 0.34799 | 0.3475 | 0.34698 | 0.34643 | 0.34586 | 0.34452 | 0.34388 | 0.34346 | 0.3413 | 0.28973 | 0.35152 | 0.35138 | 0.35119 | 0.35098 | 0.35073 | 0.35043 | 0.35011 | 0.34979 | 0.34954 | 0.34946 | 0.34921 | 0.34879 | 0.34663 | 0.29199
| NEWTON | SP |  |  | 0.36996 | 0.36993 | 0.3699 | 0.36986 | 0.36986 | 0.36985 | 0.36985 | 0.36984 | 0.36983 | 0.36978 | 0.36962 | 0.36949 | 0.36869 | 0.36692 | 0.34888 | 0.34884 | 0.34879 | 0.34874 | 0.34866 | 0.34856 | 0.34845 | 0.34833 | 0.34818 | 0.34754 | 0.34577 | 0.34473 | 0.34392 | 0.34216 | 0.35161 | 0.35156 | 0.3515 | 0.35145 | 0.35132 | 0.35117 | 0.35098 | 0.35088 | 0.35082 | 0.35054 | 0.35019 | 0.35007 | 0.34926 | 0.3475
REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | 24.2416 | 24.2354 | 24.2282 | 24.1992 | 24.1174 | 24.0238 | 23.92 | 23.8056 | 23.6694 | 23.5999 | 23.393 | 14.1394 | 10.8554 | 6.6158 | 21.2379 | 21.1734 | 21.0788 | 20.8409 | 20.3858 | 19.9478 | 19.5046 | 19.155 | 18.7054 | 18.2591 | 12.0038 | 8.4783 | 5.0611 | 0.24878 | 21.5699 | 21.5489 | 21.5194 | 21.437 | 21.2599 | 21.0783 | 20.8879 | 20.7135 | 20.4972 | 20.3264 | 12.5475 | 8.8913 | 5.3306 | 0.56997
| NEWTONHILL | CT |  |  | 24.2416 | 24.2354 | 24.2282 | 24.1992 | 24.1174 | 24.0238 | 23.92 | 23.8056 | 23.6694 | 23.5999 | 23.393 | 14.1394 | 10.8554 | 6.6158 | 21.2379 | 21.1734 | 21.0788 | 20.8409 | 20.3858 | 19.9478 | 19.5046 | 19.155 | 18.7054 | 18.2591 | 12.0038 | 8.4783 | 5.0611 | 0.24878 | 21.5699 | 21.5489 | 21.5194 | 21.437 | 21.2599 | 21.0783 | 20.8879 | 20.7135 | 20.4972 | 20.3264 | 12.5475 | 8.8913 | 5.3306 | 0.56997
| NEWTONHILL | LW |  |  | 24.2507 | 24.2507 | 24.2507 | 24.2297 | 24.1641 | 24.0946 | 24.0216 | 23.942 | 23.8307 | 23.7876 | 23.6637 | 23.3695 | 14.3236 | 12.401 | 21.3096 | 21.3067 | 21.3022 | 21.2698 | 20.8494 | 20.4288 | 20.0083 | 19.5848 | 19.0394 | 18.5612 | 12.9091 | 10.4052 | 8.9085 | 6.7202 | 21.5951 | 21.5943 | 21.5932 | 21.5693 | 21.4131 | 21.2539 | 21.0922 | 20.9248 | 20.7026 | 20.5484 | 13.4903 | 10.8558 | 9.1879 | 6.9795
| NEWTONHILL | ST |  |  | 24.2477 | 24.2458 | 24.2439 | 24.2298 | 24.1793 | 24.1227 | 24.0629 | 23.9962 | 23.9096 | 23.8768 | 23.7974 | 23.598 | 12.1999 | 10.0663 | 21.2685 | 21.2317 | 21.1834 | 21.0799 | 20.7762 | 20.4507 | 20.1975 | 19.9034 | 19.5176 | 19.1184 | 13.4741 | 10.6315 | 6.3127 | 3.8504 | 21.5823 | 21.5715 | 21.5578 | 21.5208 | 21.4057 | 21.2804 | 21.1713 | 21.0465 | 20.8835 | 20.7571 | 20.4117 | 11.0819 | 6.6684 | 4.2357
| NEWTONHILL | SP |  |  | 24.2437 | 24.24 | 24.2361 | 24.2287 | 24.2218 | 24.2149 | 24.2078 | 24.2003 | 24.1917 | 24.177 | 24.1343 | 24.0901 | 23.7234 | 23.4189 | 21.2979 | 21.2892 | 21.2796 | 21.2657 | 21.189 | 21.1009 | 21.0107 | 20.9212 | 20.8045 | 20.6585 | 20.0837 | 19.3539 | 18.3914 | 13.2826 | 21.5869 | 21.5819 | 21.5765 | 21.5674 | 21.5427 | 21.5151 | 21.4868 | 21.4583 | 21.4221 | 21.3739 | 21.1953 | 20.976 | 20.4572 | 20.0332
ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9583 | 7.9583 | 7.9582 | 7.9582 | 7.9582 | 7.9581 | 7.9581 | 7.9581 | 7.958 | 7.958 | 7.9579 | 7.9577 | 7.9576 | 7.9574
| NIGG | CT |  |  | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9583 | 7.9583 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9581 | 7.9581 | 7.9581 | 7.9581 | 7.958 | 7.9579 | 7.9578 | 7.9576
| NIGG | LW |  |  | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9583 | 7.9583 | 7.9582 | 7.9582 | 7.9582 | 7.9581 | 7.9581 | 7.9581 | 7.958 | 7.958 | 7.9579 | 7.9577 | 7.9576 | 7.9574
| NIGG | ST |  |  | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9583 | 7.9583 | 7.9583 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9581 | 7.958 | 7.958 | 7.9579
| NIGG | SP |  |  | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 8.2344 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9377 | 7.9583 | 7.9583 | 7.9583 | 7.9583 | 7.9583 | 7.9583 | 7.9583 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9582 | 7.9581
CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | 18.97 | 18.9688 | 18.9674 | 18.9653 | 18.9586 | 18.9506 | 18.9412 | 18.9304 | 18.9182 | 18.9113 | 18.8881 | 18.8345 | 18.746 | 18.5746 | 18.2014 | 18.1959 | 18.1881 | 18.1709 | 18.1478 | 18.1238 | 18.0987 | 18.066 | 18.0323 | 18.0022 | 17.9101 | 17.7537 | 17.5799 | 17.3244 | 18.0637 | 18.0611 | 18.0577 | 18.0509 | 18.039 | 18.0259 | 18.0116 | 17.9938 | 17.9749 | 17.9607 | 17.9158 | 17.8269 | 17.7237 | 17.5522
| NINEWELLS | CT |  |  | 18.97 | 18.9688 | 18.9674 | 18.9653 | 18.9586 | 18.9506 | 18.9412 | 18.9304 | 18.9182 | 18.9113 | 18.8881 | 18.8345 | 18.746 | 18.5746 | 18.2014 | 18.1959 | 18.1881 | 18.1709 | 18.1478 | 18.1238 | 18.0987 | 18.066 | 18.0323 | 18.0022 | 17.9101 | 17.7537 | 17.5799 | 17.3244 | 18.0637 | 18.0611 | 18.0577 | 18.0509 | 18.039 | 18.0259 | 18.0116 | 17.9938 | 17.9749 | 17.9607 | 17.9158 | 17.8269 | 17.7237 | 17.5522
| NINEWELLS | LW |  |  | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.9718 | 18.2063 | 18.2046 | 18.2019 | 18.1952 | 18.1877 | 18.1804 | 18.1732 | 18.1662 | 18.1593 | 18.1519 | 18.1299 | 18.0946 | 18.059 | 18.0237 | 18.0664 | 18.0659 | 18.0651 | 18.0629 | 18.0606 | 18.0583 | 18.056 | 18.0538 | 18.0516 | 18.0493 | 18.0424 | 18.0312 | 18.02 | 18.0089
| NINEWELLS | ST |  |  | 18.9714 | 18.9711 | 18.9709 | 18.9705 | 18.9679 | 18.9648 | 18.9611 | 18.957 | 18.9523 | 18.9508 | 18.9462 | 18.9384 | 18.8982 | 18.8754 | 18.2033 | 18.1993 | 18.1942 | 18.1845 | 18.1691 | 18.1506 | 18.1296 | 18.1084 | 18.087 | 18.0702 | 18.0209 | 17.9417 | 17.8341 | 17.758 | 18.0652 | 18.0638 | 18.062 | 18.0587 | 18.0521 | 18.0441 | 18.035 | 18.0254 | 18.0155 | 18.0092 | 17.9905 | 17.9602 | 17.8976 | 17.8531
| NINEWELLS | SP |  |  | 18.971 | 18.9706 | 18.9702 | 18.9698 | 18.9697 | 18.9696 | 18.9695 | 18.9694 | 18.9693 | 18.9687 | 18.9666 | 18.965 | 18.9544 | 18.9314 | 18.2065 | 18.2056 | 18.2047 | 18.2037 | 18.2003 | 18.1964 | 18.1908 | 18.1852 | 18.1781 | 18.1714 | 18.1519 | 18.1231 | 18.087 | 18.0401 | 18.066 | 18.0654 | 18.0648 | 18.0642 | 18.0631 | 18.0618 | 18.06 | 18.0582 | 18.0559 | 18.0534 | 18.0458 | 18.0355 | 18.0169 | 17.9864
THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.24066 | 0.24055 | 0.24037 | 0.23992 | 0.23942 | 0.23892 | 0.2385 | 0.23812 | 0.23775 | 0.2372 | 0.23659 | 0.23659 | 0.23659 | 0.23659 | 0.23436 | 0.23432 | 0.23425 | 0.23407 | 0.23387 | 0.23368 | 0.23349 | 0.23335 | 0.23323 | 0.23302 | 0.2328 | 0.2328 | 0.2328 | 0.2328
| NORTH HOY | CT |  |  | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.24067 | 0.24058 | 0.24044 | 0.24011 | 0.23976 | 0.23942 | 0.23908 | 0.23838 | 0.23776 | 0.2372 | 0.23659 | 0.23659 | 0.23659 | 0.23659 | 0.23437 | 0.23433 | 0.23428 | 0.23415 | 0.23401 | 0.23387 | 0.23374 | 0.23343 | 0.23323 | 0.23302 | 0.2328 | 0.2328 | 0.2328 | 0.2328
| NORTH HOY | LW |  |  | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.24066 | 0.24055 | 0.24037 | 0.23992 | 0.23942 | 0.23892 | 0.2385 | 0.23812 | 0.23775 | 0.23735 | 0.23671 | 0.23659 | 0.23659 | 0.23659 | 0.23436 | 0.23432 | 0.23425 | 0.23407 | 0.23387 | 0.23368 | 0.23349 | 0.23335 | 0.23323 | 0.2331 | 0.2328 | 0.2328 | 0.2328 | 0.2328
| NORTH HOY | ST |  |  | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.24071 | 0.24065 | 0.24058 | 0.24044 | 0.24024 | 0.24001 | 0.23979 | 0.23957 | 0.23936 | 0.23881 | 0.23751 | 0.23662 | 0.23659 | 0.23659 | 0.23438 | 0.23436 | 0.23433 | 0.23428 | 0.2342 | 0.23411 | 0.23402 | 0.23393 | 0.23385 | 0.23363 | 0.23315 | 0.2328 | 0.2328 | 0.2328
| NORTH HOY | SP |  |  | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.26257 | 0.24076 | 0.24076 | 0.24075 | 0.24074 | 0.24068 | 0.24062 | 0.24054 | 0.24047 | 0.24037 | 0.24015 | 0.23952 | 0.2386 | 0.23786 | 0.23723 | 0.2344 | 0.2344 | 0.2344 | 0.23439 | 0.23437 | 0.23435 | 0.23432 | 0.23429 | 0.23425 | 0.23416 | 0.23391 | 0.23354 | 0.23326 | 0.23304
PERSLEY | NORTHFIELD | MINIMUM HEADROOM | NJ 90728 08364 | NO | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4424 | 17.4353 | 17.4261 | 17.4078 | 17.3747 | 17.338 | 17.2973 | 17.1952 | 17.09 | 16.995 | 16.7253 | 16.4904 | 16.2245 | 13.4079 | 16.7066 | 16.7016 | 16.6954 | 16.6844 | 16.6591 | 16.6301 | 16.597 | 16.5371 | 16.4734 | 16.4234 | 16.2939 | 16.0657 | 15.7998 | 12.7076
| NORTHFIELD | CT |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4424 | 17.4353 | 17.4261 | 17.4078 | 17.3747 | 17.338 | 17.2973 | 17.1952 | 17.09 | 16.995 | 16.7253 | 16.4904 | 16.2245 | 13.4079 | 16.7066 | 16.7016 | 16.6954 | 16.6844 | 16.6591 | 16.6301 | 16.597 | 16.5371 | 16.4734 | 16.4234 | 16.2939 | 16.0657 | 15.7998 | 12.7076
| NORTHFIELD | LW |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4503 | 17.4491 | 17.4471 | 17.4421 | 17.4365 | 17.4311 | 17.4257 | 17.4205 | 17.4154 | 17.4099 | 17.3936 | 17.3673 | 17.3409 | 17.3147 | 16.713 | 16.7125 | 16.7118 | 16.7098 | 16.7076 | 16.7054 | 16.7033 | 16.7013 | 16.6993 | 16.6971 | 16.6907 | 16.6804 | 16.67 | 16.6597
| NORTHFIELD | ST |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4495 | 17.4481 | 17.4464 | 17.4437 | 17.433 | 17.4202 | 17.393 | 17.3642 | 17.3342 | 17.2803 | 17.1228 | 16.8844 | 16.6624 | 16.5877 | 16.7119 | 16.7108 | 16.7096 | 16.7079 | 16.6985 | 16.6873 | 16.6693 | 16.6497 | 16.6286 | 16.6043 | 16.5332 | 16.4414 | 16.2515 | 16.1629
| NORTHFIELD | SP |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4487 | 17.4471 | 17.4454 | 17.4437 | 17.4421 | 17.4402 | 17.4343 | 17.4284 | 17.4209 | 17.3998 | 17.3375 | 17.246 | 17.1291 | 16.9744 | 16.7108 | 16.7093 | 16.7078 | 16.7062 | 16.7054 | 16.7045 | 16.702 | 16.6996 | 16.6964 | 16.6868 | 16.6579 | 16.6185 | 16.5507 | 16.4477
BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | 5.5346 | 5.534 | 4.9777 | 3.8512 | 3.254 | 3.2468 | 3.2355 | 3.2148 | 3.1939 | 2.9151 | 1.5682 | -1.1199 | -3.4811 | -5.8006 | 5.6647 | 5.6641 | 5.4481 | 3.5069 | 2.9257 | 2.899 | 2.8721 | 2.8502 | 2.828 | 2.6502 | 1.3989 | -0.89704 | -3.1167 | -5.3804 | 5.2434 | 5.2421 | 4.7453 | 3.4888 | 2.817 | 2.8133 | 2.809 | 2.804 | 2.7705 | 2.4799 | 1.1382 | -1.5671 | -3.9436 | -6.2777
| NOSTIE BRIDGE | CT |  |  | 5.5346 | 5.534 | 4.9777 | 3.8512 | 3.254 | 3.2468 | 3.2355 | 3.2148 | 3.1939 | 3.174 | 1.5682 | -1.1199 | -3.4811 | -5.8006 | 5.6647 | 5.6641 | 5.4481 | 3.5069 | 2.9257 | 2.899 | 2.8721 | 2.8502 | 2.828 | 2.8069 | 1.3989 | -0.89704 | -3.1167 | -5.3804 | 5.2434 | 5.2421 | 4.7453 | 3.4888 | 2.817 | 2.8133 | 2.809 | 2.804 | 2.7984 | 2.7951 | 1.1382 | -1.5671 | -3.9436 | -6.2777
| NOSTIE BRIDGE | LW |  |  | 5.5355 | 5.5355 | 5.2592 | 5.0172 | 4.8705 | 3.9853 | 3.7437 | 3.5012 | 3.2088 | 2.9151 | 2.3233 | 1.3242 | 0.30409 | -0.74081 | 5.6655 | 5.6655 | 5.57 | 5.4744 | 3.8933 | 3.6449 | 3.3967 | 3.1476 | 2.8997 | 2.6502 | 2.1404 | 1.2814 | 0.40485 | -0.49178 | 5.2448 | 5.2446 | 5.0081 | 4.8001 | 3.9291 | 3.6398 | 3.3504 | 3.0598 | 2.7705 | 2.4799 | 1.8956 | 0.89393 | -0.13289 | -1.1847
| NOSTIE BRIDGE | ST |  |  | 5.5354 | 5.5353 | 5.351 | 5.1668 | 5.0165 | 4.9174 | 4.8183 | 3.9717 | 3.8046 | 3.6365 | 3.0918 | 2.0883 | 1.0549 | 0.0015167 | 5.6654 | 5.6653 | 5.6016 | 5.5378 | 5.4736 | 3.9752 | 3.8032 | 3.6306 | 3.4588 | 3.2858 | 2.7653 | 1.8895 | 0.98798 | 0.071011 | 5.2447 | 5.2445 | 5.0826 | 4.9384 | 4.7996 | 4.66 | 3.8293 | 3.6344 | 3.4402 | 3.2461 | 2.6604 | 1.6623 | 0.62194 | -0.43854
| NOSTIE BRIDGE | SP |  |  | 5.5353 | 5.5352 | 5.4371 | 5.3389 | 5.2326 | 5.1312 | 5.0323 | 4.9695 | 4.9047 | 4.84 | 3.9489 | 3.5719 | 2.5207 | 2.0185 | 5.6654 | 5.6653 | 5.6313 | 5.5973 | 5.5532 | 5.5111 | 5.4696 | 5.4274 | 3.9981 | 3.9016 | 3.6117 | 3.2258 | 2.1664 | 1.6647 | 5.2448 | 5.2447 | 5.1586 | 5.0725 | 4.9853 | 4.9062 | 4.829 | 4.7516 | 4.6685 | 3.9462 | 3.6368 | 3.2111 | 2.1172 | 1.5855
TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | YES | 37.4798 | 37.4309 | 37.3819 | 37.1408 | 36.9412 | 36.2921 | 35.6185 | 34.9205 | 34.1979 | 33.9283 | 33.1196 | 31.1898 | 22.2585 | 20.0194 | 31.0444 | 30.8858 | 30.8138 | 30.7024 | 30.2516 | 29.5398 | 28.8049 | 28.0469 | 27.2658 | 26.9328 | 21.8143 | 19.903 | 16.7817 | 14.4635 | 33.0633 | 32.8879 | 32.8123 | 32.6612 | 32.2315 | 31.5101 | 30.7659 | 29.9987 | 29.259 | 28.9894 | 28.1806 | 20.4652 | 17.2344 | 14.9054
| OBAN | CT |  |  | 37.6207 | 37.5801 | 37.5372 | 37.5288 | 37.3216 | 36.9586 | 36.6215 | 36.2796 | 35.8424 | 35.6233 | 34.9607 | 31.1898 | 22.2585 | 20.0194 | 31.1512 | 30.9722 | 30.8651 | 30.7029 | 30.3303 | 29.8049 | 29.3083 | 28.8453 | 28.2923 | 27.9753 | 27.2667 | 19.903 | 16.7817 | 14.4635 | 33.1649 | 32.9646 | 32.8473 | 32.6612 | 32.3838 | 32.0213 | 31.6847 | 31.3433 | 30.9066 | 30.688 | 30.0264 | 20.4652 | 17.2344 | 14.9054
| OBAN | LW |  |  | 37.4798 | 37.4309 | 37.3819 | 37.3819 | 36.9412 | 36.2921 | 35.6185 | 34.9205 | 34.1979 | 33.9283 | 33.1196 | 31.3689 | 29.4557 | 22.7894 | 31.0444 | 30.8858 | 30.8138 | 30.7562 | 30.2516 | 29.5398 | 28.8049 | 28.0469 | 27.2658 | 26.9328 | 21.8143 | 20.0636 | 18.1504 | 16.9747 | 33.0633 | 32.8879 | 32.8123 | 32.746 | 32.2315 | 31.5101 | 30.7659 | 29.9987 | 29.259 | 28.9894 | 28.1806 | 21.4447 | 19.5315 | 18.2417
| OBAN | ST |  |  | 37.7721 | 37.7467 | 37.7213 | 37.7201 | 37.5882 | 37.4545 | 36.4658 | 35.4752 | 35.3358 | 34.9466 | 33.7787 | 31.7964 | 30.35 | 29.6022 | 31.3198 | 31.2678 | 31.1118 | 31.0424 | 30.8179 | 30.5734 | 29.4925 | 28.4116 | 28.184 | 27.7092 | 26.2927 | 20.4911 | 19.0447 | 18.297 | 33.3361 | 33.28 | 33.104 | 33.0242 | 32.7855 | 32.5239 | 31.5268 | 30.5362 | 30.3968 | 30.0077 | 28.8397 | 21.8722 | 20.1137 | 18.9017
| OBAN | SP |  |  | 37.9173 | 37.9033 | 37.8893 | 37.1408 | 37.0794 | 37.0178 | 36.9563 | 36.8947 | 36.8331 | 36.5246 | 35.598 | 33.998 | 32.9021 | 32.4319 | 31.4909 | 31.4736 | 31.4554 | 30.7024 | 30.6162 | 30.5253 | 30.4334 | 30.3417 | 30.2416 | 29.8994 | 28.8754 | 27.1227 | 21.5969 | 21.1266 | 33.5112 | 33.4933 | 33.4745 | 32.7208 | 32.6309 | 32.5354 | 32.4388 | 32.3425 | 32.2366 | 31.8892 | 30.8503 | 29.0742 | 27.9632 | 27.4929
MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | 16.1235 | 16.1187 | 16.1147 | 16.1106 | 16.0967 | 16.0804 | 16.0614 | 16.0394 | 16.0145 | 16.0003 | 15.9532 | 15.8437 | 15.6635 | 15.3141 | 14.8565 | 14.854 | 14.8512 | 14.8471 | 14.8332 | 14.8169 | 14.7978 | 14.7759 | 14.7509 | 14.7367 | 14.6896 | 14.5802 | 14.4 | 14.0506 | 15.4901 | 15.4865 | 15.4822 | 15.4746 | 15.4569 | 15.4369 | 15.4141 | 15.3784 | 15.3399 | 15.3111 | 15.2205 | 15.0406 | 14.7892 | 14.3698
| OLD CRAIGIE ROAD | CT |  |  | 16.1235 | 16.1187 | 16.1147 | 16.1106 | 16.0967 | 16.0804 | 16.0614 | 16.0394 | 16.0145 | 16.0003 | 15.9532 | 15.8437 | 15.6635 | 15.3141 | 14.8565 | 14.854 | 14.8512 | 14.8471 | 14.8332 | 14.8169 | 14.7978 | 14.7759 | 14.7509 | 14.7367 | 14.6896 | 14.5802 | 14.4 | 14.0506 | 15.4901 | 15.4865 | 15.4822 | 15.4746 | 15.4569 | 15.4369 | 15.4141 | 15.3784 | 15.3399 | 15.3111 | 15.2205 | 15.0406 | 14.7892 | 14.3698
| OLD CRAIGIE ROAD | LW |  |  | 16.1286 | 16.1277 | 16.1263 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 16.1237 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 14.8601 | 15.4944 | 15.494 | 15.4934 | 15.4917 | 15.4899 | 15.4881 | 15.4863 | 15.4846 | 15.4829 | 15.4811 | 15.4757 | 15.467 | 15.4583 | 15.4496
| OLD CRAIGIE ROAD | ST |  |  | 16.1261 | 16.1233 | 16.1224 | 16.122 | 16.1186 | 16.1146 | 16.1098 | 16.1044 | 16.0983 | 16.0963 | 16.0903 | 16.0803 | 16.0279 | 15.9982 | 14.8596 | 14.8592 | 14.8589 | 14.8585 | 14.8551 | 14.851 | 14.8463 | 14.8409 | 14.8348 | 14.8328 | 14.8268 | 14.8167 | 14.7644 | 14.7347 | 15.493 | 15.4915 | 15.4897 | 15.4864 | 15.4791 | 15.4703 | 15.4581 | 15.4453 | 15.432 | 15.4203 | 15.3862 | 15.3311 | 15.2339 | 15.1596
| OLD CRAIGIE ROAD | SP |  |  | 16.1281 | 16.1273 | 16.1264 | 16.1255 | 16.1232 | 16.121 | 16.1209 | 16.1208 | 16.1207 | 16.1199 | 16.1173 | 16.1153 | 16.1025 | 16.0744 | 14.8592 | 14.8587 | 14.8582 | 14.8577 | 14.8576 | 14.8575 | 14.8574 | 14.8573 | 14.8572 | 14.8564 | 14.8538 | 14.8518 | 14.8389 | 14.8109 | 15.4937 | 15.4931 | 15.4924 | 15.4917 | 15.4906 | 15.4893 | 15.4867 | 15.4842 | 15.4809 | 15.4764 | 15.4629 | 15.4439 | 15.415 | 15.3719
KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | YES | 9.626 | 9.5419 | 9.539 | 9.5347 | 9.5205 | 9.5035 | 9.4835 | 9.4602 | 9.4335 | 9.4187 | 7.3457 | 4.9592 | 2.6611 | 1.3306 | 6.9747 | 6.9722 | 6.9693 | 6.9649 | 6.9508 | 6.9338 | 6.9137 | 6.8905 | 6.8637 | 6.6771 | 5.9052 | 3.6625 | 1.1574 | -0.45111 | 12.1009 | 12.0687 | 12.0575 | 12.0334 | 11.9912 | 11.9612 | 11.9284 | 11.8923 | 11.8497 | 11.8154 | 11.7009 | 6.0834 | 3.4391 | 1.867
| OLDMELDRUM | CT |  |  | 9.626 | 9.5419 | 9.539 | 9.5347 | 9.5205 | 9.5035 | 9.4835 | 9.4602 | 9.4335 | 9.4187 | 7.3457 | 4.9592 | 2.6611 | 1.3306 | 6.9747 | 6.9722 | 6.9693 | 6.9649 | 6.9508 | 6.9338 | 6.9137 | 6.8905 | 6.8637 | 6.6771 | 5.9052 | 3.6625 | 1.1574 | -0.45111 | 12.1009 | 12.0687 | 12.0575 | 12.0334 | 11.9912 | 11.9612 | 11.9284 | 11.8923 | 11.8497 | 11.8154 | 11.7009 | 6.0834 | 3.4391 | 1.867
| OLDMELDRUM | LW |  |  | 9.6484 | 9.5606 | 9.5556 | 9.5482 | 9.5476 | 9.5465 | 9.5447 | 9.5422 | 9.5374 | 9.5364 | 7.4798 | 5.2255 | 3.231 | 2.7246 | 6.9785 | 6.9785 | 6.9785 | 6.9785 | 6.9779 | 6.9768 | 6.975 | 6.9725 | 6.9677 | 6.8119 | 6.031 | 3.9263 | 1.7602 | 1.1105 | 12.1099 | 12.0849 | 12.0834 | 12.0796 | 12.0378 | 12.0126 | 11.9956 | 11.978 | 11.9545 | 11.9346 | 11.8604 | 6.3475 | 4.0375 | 3.4066
| OLDMELDRUM | ST |  |  | 9.6307 | 9.6129 | 9.5458 | 9.545 | 9.5383 | 9.5301 | 9.5206 | 9.5095 | 9.4966 | 9.4923 | 7.6475 | 6.1924 | 4.8552 | 3.7913 | 6.9774 | 6.9768 | 6.9761 | 6.9753 | 6.9685 | 6.9604 | 6.9509 | 6.9398 | 6.9268 | 6.9162 | 6.262 | 4.7935 | 3.3052 | 1.9547 | 12.1041 | 12.0986 | 12.0675 | 12.0542 | 12.0163 | 11.9944 | 11.9749 | 11.9525 | 11.9253 | 11.9039 | 11.8331 | 11.038 | 5.8426 | 4.5296
| OLDMELDRUM | SP |  |  | 9.6465 | 9.6434 | 9.6398 | 9.636 | 9.6086 | 9.5766 | 9.5416 | 9.5413 | 9.541 | 9.5391 | 9.5324 | 9.5268 | 9.482 | 7.7298 | 6.9762 | 6.975 | 6.9738 | 6.9726 | 6.9724 | 6.9721 | 6.9719 | 6.9716 | 6.9712 | 6.9694 | 6.9627 | 6.9571 | 6.7518 | 6.3877 | 12.1077 | 12.106 | 12.1041 | 12.1021 | 12.0942 | 12.085 | 12.0739 | 12.063 | 12.0486 | 12.0302 | 11.9901 | 11.9526 | 11.8797 | 11.7818
THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | 11.9428 | 11.9318 | 11.9163 | 11.8826 | 11.8355 | 11.7859 | 11.7335 | 11.6207 | 11.5399 | 11.5136 | 11.4294 | 11.0627 | 10.7178 | 10.2962 | 9.9623 | 9.9531 | 9.9405 | 9.9205 | 9.9022 | 9.8809 | 9.8563 | 9.8247 | 9.7898 | 9.7671 | 9.6935 | 7.402 | 6.5526 | 5.5803 | 10.7537 | 10.7409 | 10.7229 | 10.683 | 10.6522 | 10.6328 | 10.6101 | 10.584 | 10.5546 | 10.5378 | 10.4818 | 10.1628 | 7.3564 | 6.3986
| ORMLIE | CT |  |  | 11.9428 | 11.9318 | 11.9163 | 11.8826 | 11.8355 | 11.7859 | 11.7335 | 11.6207 | 11.5399 | 11.5136 | 11.4294 | 11.0627 | 10.7178 | 10.2962 | 9.9623 | 9.9531 | 9.9405 | 9.9205 | 9.9022 | 9.8809 | 9.8563 | 9.8247 | 9.7898 | 9.7671 | 9.6935 | 7.402 | 6.5526 | 5.5803 | 10.7537 | 10.7409 | 10.7229 | 10.683 | 10.6522 | 10.6328 | 10.6101 | 10.584 | 10.5546 | 10.5378 | 10.4818 | 10.1628 | 7.3564 | 6.3986
| ORMLIE | LW |  |  | 11.9518 | 11.9474 | 11.9404 | 11.9229 | 11.9035 | 11.8844 | 11.8658 | 11.8476 | 11.8298 | 11.8105 | 11.7535 | 11.481 | 11.3866 | 11.3772 | 9.9702 | 9.9669 | 9.9615 | 9.9481 | 9.9365 | 9.9353 | 9.9341 | 9.9329 | 9.9318 | 9.9306 | 9.9269 | 9.8063 | 9.7494 | 9.7436 | 10.7638 | 10.7584 | 10.7499 | 10.7286 | 10.7049 | 10.6842 | 10.6842 | 10.6842 | 10.6842 | 10.6842 | 10.6842 | 10.4951 | 10.4111 | 10.4111
| ORMLIE | ST |  |  | 12.029 | 11.9441 | 11.937 | 11.9239 | 11.9009 | 11.8735 | 11.8243 | 11.7748 | 11.7248 | 11.6604 | 11.5994 | 11.4567 | 11.292 | 11.2104 | 10.0293 | 9.9639 | 9.9584 | 9.9481 | 9.9291 | 9.9194 | 9.9084 | 9.8962 | 9.8828 | 9.8754 | 9.8533 | 9.7599 | 9.6421 | 7.377 | 10.8578 | 10.7547 | 10.7462 | 10.7304 | 10.7038 | 10.672 | 10.6595 | 10.6499 | 10.639 | 10.6355 | 10.6248 | 10.5123 | 10.3771 | 10.3243
| ORMLIE | SP |  |  | 12.0331 | 11.9524 | 11.9508 | 11.9491 | 11.9442 | 11.9384 | 11.9251 | 11.9119 | 11.895 | 11.8701 | 11.7972 | 11.6868 | 11.6335 | 11.5813 | 10.0324 | 9.9702 | 9.9688 | 9.9673 | 9.9635 | 9.959 | 9.9487 | 9.9386 | 9.9317 | 9.9291 | 9.9208 | 9.9108 | 9.8849 | 9.8364 | 10.863 | 10.7649 | 10.7631 | 10.7612 | 10.7553 | 10.7483 | 10.7321 | 10.7161 | 10.6956 | 10.6785 | 10.6746 | 10.6716 | 10.6521 | 10.6097
DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | 3.048 | 3.0467 | 3.0362 | 3.0234 | 3.0094 | 2.9935 | 2.9772 | 2.9562 | 2.9368 | 2.9259 | 2.9051 | 2.8693 | 2.8329 | 2.447 | 3.0541 | 3.0531 | 3.0406 | 3.0263 | 3.0108 | 2.9929 | 2.9746 | 2.9523 | 2.9295 | 2.9065 | 2.8729 | 2.8308 | 2.465 | 2.3783 | 3.0066 | 3.0065 | 2.995 | 2.9839 | 2.9732 | 2.9603 | 2.9468 | 2.9329 | 2.9183 | 2.9041 | 2.8773 | 2.4981 | 2.3983 | 2.2898
| OTTER FERRY | CT |  |  | 3.048 | 3.0467 | 3.0362 | 3.0234 | 3.0094 | 2.9935 | 2.9772 | 2.9562 | 2.9368 | 2.9259 | 2.9051 | 2.8693 | 2.8329 | 2.447 | 3.0541 | 3.0531 | 3.0406 | 3.0263 | 3.0108 | 2.9929 | 2.9746 | 2.9523 | 2.9295 | 2.9065 | 2.8729 | 2.8308 | 2.465 | 2.3783 | 3.0066 | 3.0065 | 2.995 | 2.9839 | 2.9732 | 2.9603 | 2.9468 | 2.9329 | 2.9183 | 2.9041 | 2.8773 | 2.4981 | 2.3983 | 2.2898
| OTTER FERRY | LW |  |  | 3.0481 | 3.0468 | 3.0446 | 3.0391 | 3.0331 | 3.0271 | 3.0216 | 3.0216 | 3.0216 | 3.0216 | 3.0216 | 3.0216 | 3.0216 | 3.0216 | 3.0543 | 3.0532 | 3.0515 | 3.0473 | 3.0425 | 3.0379 | 3.0334 | 3.029 | 3.0246 | 3.0199 | 3.0061 | 2.9895 | 2.9892 | 2.9892 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069 | 3.0069
| OTTER FERRY | ST |  |  | 3.0486 | 3.0479 | 3.047 | 3.0452 | 3.0426 | 3.0394 | 3.034 | 3.0286 | 3.0233 | 3.0189 | 3.0183 | 3.0173 | 3.0121 | 3.0092 | 3.0547 | 3.0541 | 3.0534 | 3.052 | 3.0499 | 3.0473 | 3.043 | 3.0386 | 3.0343 | 3.0296 | 3.0158 | 2.9938 | 2.9798 | 2.9769 | 3.0068 | 3.0068 | 3.0068 | 3.0067 | 3.0064 | 3.006 | 3.0055 | 3.005 | 3.0044 | 3.0042 | 3.0036 | 3.0026 | 2.9974 | 2.9945
| OTTER FERRY | SP |  |  | 3.0493 | 3.0492 | 3.0491 | 3.0489 | 3.0483 | 3.0475 | 3.0458 | 3.0442 | 3.042 | 3.0397 | 3.0329 | 3.0224 | 3.0207 | 3.0195 | 3.0552 | 3.0551 | 3.055 | 3.0549 | 3.0544 | 3.0538 | 3.0524 | 3.0512 | 3.0495 | 3.0477 | 3.0424 | 3.0341 | 3.0259 | 3.0177 | 3.0068 | 3.0068 | 3.0068 | 3.0068 | 3.0068 | 3.0068 | 3.0068 | 3.0068 | 3.0068 | 3.0067 | 3.0066 | 3.0065 | 3.006 | 3.0048
GLENAGNES | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | 48.1193 | 48.1193 | 48.1193 | 48.1192 | 48.108 | 47.3333 | 47.204 | 46.7972 | 46.0853 | 45.9257 | 45.4469 | 44.585 | 43.833 | 43.4368 | 43.1639 | 43.1541 | 43.1514 | 43.1448 | 43.1374 | 42.3772 | 42.2273 | 41.817 | 41.1017 | 40.9387 | 40.45 | 38.2612 | 37.5301 | 37.1018 | 43.0135 | 43.0135 | 43.0135 | 43.0135 | 43.0022 | 42.2275 | 42.0983 | 41.6914 | 40.9795 | 40.8199 | 40.3411 | 38.2167 | 37.4873 | 37.0606
| OVERGATE | CT |  |  | 48.1193 | 48.1193 | 48.1193 | 48.1192 | 48.1191 | 48.047 | 47.9893 | 47.9316 | 47.8306 | 47.7729 | 47.5999 | 47.0577 | 46.4276 | 46.085 | 43.164 | 43.1544 | 43.1524 | 43.1476 | 43.1423 | 43.0652 | 43.0025 | 42.9399 | 42.8342 | 42.7714 | 42.5832 | 42.0166 | 41.3619 | 41.013 | 43.0135 | 43.0135 | 43.0135 | 43.0135 | 43.0134 | 42.9413 | 42.8836 | 42.8258 | 42.7249 | 42.6672 | 42.4941 | 41.952 | 41.3219 | 40.9792
| OVERGATE | LW |  |  | 48.1193 | 48.1193 | 48.1193 | 48.1193 | 48.1193 | 48.0316 | 47.9439 | 47.8561 | 47.7684 | 47.6982 | 47.4877 | 46.828 | 46.0616 | 45.6469 | 43.1639 | 43.1541 | 43.1514 | 43.1448 | 43.1374 | 43.0425 | 42.9477 | 42.8531 | 42.7586 | 42.6811 | 42.449 | 41.756 | 40.9896 | 37.8719 | 43.0136 | 43.0136 | 43.0136 | 43.0136 | 43.0136 | 42.9258 | 42.8381 | 42.7504 | 42.6626 | 42.5925 | 42.3819 | 41.7222 | 38.6373 | 37.8412
| OVERGATE | ST |  |  | 48.1193 | 48.1193 | 48.1193 | 48.1193 | 48.1193 | 47.6108 | 47.204 | 46.7972 | 46.0853 | 45.9257 | 45.4469 | 44.585 | 44.0232 | 43.7644 | 43.1646 | 43.1637 | 43.1545 | 43.1524 | 43.1496 | 42.6377 | 42.2273 | 41.817 | 41.1017 | 40.9387 | 40.45 | 38.2612 | 37.5301 | 37.1018 | 43.0136 | 43.0136 | 43.0136 | 43.0136 | 43.0136 | 42.5051 | 42.0983 | 41.6914 | 40.9795 | 40.8199 | 40.3411 | 38.2167 | 37.4873 | 37.0606
| OVERGATE | SP |  |  | 48.1193 | 48.1193 | 48.1193 | 48.1193 | 48.108 | 47.3333 | 47.322 | 47.3094 | 46.525 | 46.3687 | 45.8869 | 45.0927 | 43.833 | 43.4368 | 43.1654 | 43.1652 | 43.1651 | 43.165 | 43.1528 | 42.3772 | 42.3648 | 42.351 | 41.5651 | 41.4074 | 40.9217 | 40.1211 | 37.9003 | 37.4452 | 43.0136 | 43.0136 | 43.0136 | 43.0136 | 43.0022 | 42.2275 | 42.2163 | 42.2037 | 41.4193 | 41.2629 | 40.7812 | 39.9869 | 37.8477 | 37.3975
CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | 0.16346 | 0.16346 | 0.13106 | 0.099327 | 0.066795 | 0.02752 | -0.012925 | -0.054563 | -0.09756 | -0.14184 | -0.2209 | -0.34941 | -0.46128 | -0.56926 | 0.15785 | 0.1578 | 0.12732 | 0.096981 | 0.065871 | 0.028329 | -0.010327 | -0.050191 | -0.091303 | -0.13359 | -0.20931 | -0.33241 | -0.43969 | -0.54327 | 0.15782 | 0.1578 | 0.1256 | 0.093523 | 0.060596 | 0.020849 | -0.020082 | -0.062237 | -0.10572 | -0.15043 | -0.23037 | -0.3603 | -0.47346 | -0.58271
| OVERSCAIG | CT |  |  | 0.16346 | 0.16346 | 0.13106 | 0.099327 | 0.066795 | 0.02752 | -0.012925 | -0.054563 | -0.09756 | -0.14184 | -0.2209 | -0.34941 | -0.46128 | -0.56926 | 0.15785 | 0.15781 | 0.12732 | 0.096981 | 0.065871 | 0.028329 | -0.010327 | -0.050191 | -0.091303 | -0.13359 | -0.20931 | -0.33241 | -0.43969 | -0.54327 | 0.15782 | 0.1578 | 0.1256 | 0.093523 | 0.060596 | 0.020849 | -0.020082 | -0.062237 | -0.10572 | -0.15043 | -0.23037 | -0.3603 | -0.47346 | -0.58271
| OVERSCAIG | LW |  |  | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.15785 | 0.1578 | 0.15772 | 0.15754 | 0.15736 | 0.15721 | 0.15712 | 0.15709 | 0.15708 | 0.15708 | 0.15708 | 0.15708 | 0.15708 | 0.14841 | 0.15782 | 0.1578 | 0.15777 | 0.1577 | 0.15761 | 0.15756 | 0.15751 | 0.15747 | 0.15747 | 0.15747 | 0.15747 | 0.15747 | 0.15747 | 0.14873
| OVERSCAIG | ST |  |  | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.15787 | 0.15784 | 0.15781 | 0.15775 | 0.15767 | 0.15758 | 0.15734 | 0.15717 | 0.15709 | 0.15708 | 0.15708 | 0.15708 | 0.15708 | 0.14915 | 0.15783 | 0.15782 | 0.1578 | 0.15778 | 0.15775 | 0.15771 | 0.15761 | 0.15754 | 0.15747 | 0.15747 | 0.15747 | 0.15747 | 0.15747 | 0.14945
| OVERSCAIG | SP |  |  | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.16346 | 0.15789 | 0.15789 | 0.15788 | 0.15788 | 0.15786 | 0.15783 | 0.15773 | 0.15763 | 0.15752 | 0.15745 | 0.15726 | 0.1571 | 0.15708 | 0.15708 | 0.15783 | 0.15783 | 0.15783 | 0.15783 | 0.15782 | 0.15781 | 0.15777 | 0.15773 | 0.15769 | 0.15766 | 0.15758 | 0.15749 | 0.15747 | 0.15747
KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | NO | 9.0113 | 9.0037 | 8.9938 | 8.9746 | 8.6497 | 8.4982 | 8.3458 | 8.1921 | 5.97 | 5.5376 | 4.1518 | 2.1067 | 0.26687 | -1.4349 | 7.5589 | 7.5545 | 7.5486 | 7.5374 | 7.2974 | 7.2619 | 5.417 | 4.8325 | 4.0848 | 3.3506 | 1.5472 | -0.91363 | -3.0332 | -5.0251 | 7.9466 | 7.9443 | 7.9414 | 7.9358 | 7.8027 | 7.7263 | 5.6149 | 5.0322 | 4.2867 | 3.5548 | 1.7568 | -0.69675 | -2.8108 | -4.7969
| PARK | CT |  |  | 9.0153 | 9.0112 | 9.0053 | 8.992 | 8.7593 | 8.6568 | 8.5929 | 8.5125 | 8.3945 | 8.2505 | 5.441 | 3.2744 | 1.8198 | -1.2065 | 7.5609 | 7.5582 | 7.5544 | 7.5461 | 7.4086 | 7.2914 | 7.2762 | 7.2666 | 5.7098 | 5.1528 | 3.2048 | 0.50772 | -1.2286 | -4.7723 | 7.9471 | 7.9454 | 7.9431 | 7.9383 | 7.869 | 7.8088 | 7.7476 | 7.7034 | 5.9068 | 5.3514 | 3.4093 | 0.72014 | -1.0112 | -4.5446
| PARK | LW |  |  | 9.0189 | 9.0175 | 9.0152 | 9.0097 | 8.6497 | 8.4982 | 8.3458 | 8.1921 | 5.97 | 5.5376 | 4.1518 | 2.1067 | 1.5073 | -0.33839 | 7.5635 | 7.5627 | 7.5614 | 7.5581 | 7.2974 | 7.2931 | 5.417 | 4.8325 | 4.0848 | 3.3506 | 1.5472 | -0.91363 | -1.6146 | -3.7837 | 7.9489 | 7.9485 | 7.9479 | 7.9463 | 7.8027 | 7.7263 | 5.6149 | 5.0322 | 4.2867 | 3.5548 | 1.7568 | -0.69675 | -1.3958 | -3.5584
| PARK | ST |  |  | 9.0113 | 9.0037 | 8.9938 | 8.9746 | 8.7411 | 8.6266 | 8.5492 | 8.4537 | 8.3135 | 8.1693 | 5.3584 | 3.2216 | 0.26687 | -1.4349 | 7.5589 | 7.5545 | 7.5486 | 7.5374 | 7.3942 | 7.2619 | 7.2428 | 7.2205 | 5.5918 | 5.0411 | 3.1164 | 0.4601 | -3.0332 | -5.0251 | 7.9466 | 7.9443 | 7.9414 | 7.9358 | 7.8573 | 7.779 | 7.7044 | 7.6537 | 5.7889 | 5.2398 | 3.321 | 0.67243 | -2.8108 | -4.7969
| PARK | SP |  |  | 9.0184 | 9.0172 | 9.0158 | 9.0143 | 9.0079 | 8.9432 | 8.8498 | 8.7577 | 8.6878 | 8.6389 | 8.4308 | 8.1851 | 5.7704 | 5.2507 | 7.563 | 7.5622 | 7.5612 | 7.5602 | 7.5564 | 7.5188 | 7.4644 | 7.4107 | 7.3394 | 7.2966 | 5.7364 | 4.7076 | 3.7668 | 2.9062 | 7.9484 | 7.9478 | 7.9472 | 7.9466 | 7.9447 | 7.9264 | 7.8999 | 7.8738 | 7.839 | 7.7924 | 5.9333 | 4.9077 | 3.9696 | 3.1115
ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | YES | 3.8326 | 3.832 | 3.8314 | 3.8305 | 3.8274 | 3.8237 | 3.8194 | 3.8145 | 3.8089 | 3.8057 | 3.7952 | 3.7706 | 3.7302 | 3.6519 | 3.3304 | 3.3282 | 3.3253 | 3.3189 | 3.31 | 3.3005 | 3.2906 | 3.2791 | 3.2719 | 3.2669 | 3.251 | 3.2177 | 3.1685 | 2.3617 | 3.2503 | 3.2467 | 3.2416 | 3.239 | 3.2359 | 3.2323 | 3.228 | 3.223 | 3.2175 | 3.2143 | 3.2038 | 3.1792 | 2.4518 | 2.2642
| PEDDIESTON | CT |  |  | 3.8326 | 3.832 | 3.8314 | 3.8305 | 3.8274 | 3.8237 | 3.8194 | 3.8145 | 3.8089 | 3.8057 | 3.7952 | 3.7706 | 3.7302 | 3.6519 | 3.3304 | 3.3282 | 3.3253 | 3.3189 | 3.31 | 3.3005 | 3.2906 | 3.2791 | 3.2719 | 3.2669 | 3.251 | 3.2177 | 3.1685 | 2.3617 | 3.2503 | 3.2467 | 3.2416 | 3.239 | 3.2359 | 3.2323 | 3.228 | 3.223 | 3.2175 | 3.2143 | 3.2038 | 3.1792 | 2.4518 | 2.2642
| PEDDIESTON | LW |  |  | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.8334 | 3.3324 | 3.332 | 3.3313 | 3.3295 | 3.3276 | 3.3256 | 3.3238 | 3.3219 | 3.3201 | 3.3182 | 3.3124 | 3.3032 | 3.2971 | 3.2947 | 3.2536 | 3.2527 | 3.2513 | 3.2479 | 3.244 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242
| PEDDIESTON | ST |  |  | 3.8333 | 3.8332 | 3.8331 | 3.833 | 3.8321 | 3.8311 | 3.83 | 3.8286 | 3.8271 | 3.8266 | 3.8251 | 3.8227 | 3.8097 | 3.8023 | 3.331 | 3.3293 | 3.3272 | 3.3231 | 3.3169 | 3.3095 | 3.3038 | 3.298 | 3.2922 | 3.2903 | 3.2853 | 3.2772 | 3.2587 | 3.2458 | 3.2508 | 3.2477 | 3.2436 | 3.2416 | 3.2407 | 3.2397 | 3.2385 | 3.2372 | 3.2357 | 3.2352 | 3.2337 | 3.2312 | 3.2182 | 3.2109
| PEDDIESTON | SP |  |  | 3.8332 | 3.8331 | 3.833 | 3.8329 | 3.8329 | 3.8329 | 3.8328 | 3.8328 | 3.8328 | 3.8326 | 3.8321 | 3.8317 | 3.8291 | 3.8235 | 3.3325 | 3.3323 | 3.3321 | 3.3318 | 3.331 | 3.33 | 3.3285 | 3.327 | 3.3251 | 3.3231 | 3.3172 | 3.3085 | 3.2981 | 3.2875 | 3.2539 | 3.2536 | 3.2532 | 3.2528 | 3.2512 | 3.2493 | 3.2464 | 3.2435 | 3.2414 | 3.2412 | 3.2407 | 3.2403 | 3.2377 | 3.2321
PETERHEAD GRANGE | PETERHEAD GRANGE 11kV | MINIMUM HEADROOM | NK 11738 46516 | NO | 36.177 | 36.1655 | 36.0932 | 36.0637 | 35.993 | 35.9179 | 35.8356 | 35.7464 | 35.6399 | 35.5548 | 35.2703 | 33.9969 | 21.836 | 18.0401 | 31.944 | 31.8898 | 31.2866 | 31.1045 | 30.8104 | 30.6785 | 30.6282 | 30.5701 | 30.5026 | 30.4657 | 30.342 | 20.5653 | 17.2328 | 12.9179 | 32.6063 | 32.5382 | 31.8517 | 31.7625 | 31.5784 | 31.3995 | 31.2147 | 31.0466 | 30.9791 | 30.9423 | 30.8185 | 20.6296 | 17.3541 | 13.1275
| PETERHEAD GRANGE 11kV | CT |  |  | 36.177 | 36.1655 | 36.0932 | 36.0637 | 35.993 | 35.9179 | 35.8356 | 35.7464 | 35.6399 | 35.5548 | 35.2703 | 33.9969 | 21.836 | 18.0401 | 31.944 | 31.8898 | 31.2866 | 31.1045 | 30.8104 | 30.6785 | 30.6282 | 30.5701 | 30.5026 | 30.4657 | 30.342 | 20.5653 | 17.2328 | 12.9179 | 32.6063 | 32.5382 | 31.8517 | 31.7625 | 31.5784 | 31.3995 | 31.2147 | 31.0466 | 30.9791 | 30.9423 | 30.8185 | 20.6296 | 17.3541 | 13.1275
| PETERHEAD GRANGE 11kV | LW |  |  | 36.1917 | 36.1911 | 36.1331 | 36.1309 | 36.0915 | 36.0508 | 36.0088 | 35.9651 | 35.9058 | 35.8568 | 35.6724 | 34.6857 | 34.5213 | 22.7729 | 32.002 | 31.9968 | 31.4645 | 31.444 | 31.095 | 30.8314 | 30.7805 | 30.7734 | 30.7601 | 30.7573 | 30.7451 | 21.3233 | 19.8636 | 18.1383 | 32.6784 | 32.6717 | 31.9854 | 31.9589 | 31.7757 | 31.6153 | 31.4548 | 31.2939 | 31.2367 | 31.2338 | 31.2216 | 21.3865 | 19.9476 | 18.2649
| PETERHEAD GRANGE 11kV | ST |  |  | 36.1878 | 36.1845 | 36.1807 | 36.1743 | 36.1387 | 36.0992 | 36.0555 | 36.0045 | 35.9413 | 35.8884 | 35.7132 | 35.0796 | 34.5351 | 21.6134 | 31.9864 | 31.9694 | 31.9471 | 31.9053 | 31.7102 | 31.509 | 31.2952 | 31.0456 | 30.7801 | 30.6553 | 30.6236 | 30.359 | 20.419 | 16.7187 | 32.659 | 32.6375 | 32.6093 | 32.556 | 32.3091 | 32.0553 | 31.8321 | 31.7035 | 31.539 | 31.3497 | 31.1002 | 30.6712 | 20.5822 | 16.9698
| PETERHEAD GRANGE 11kV | SP |  |  | 36.1869 | 36.184 | 36.181 | 36.1778 | 36.1719 | 36.165 | 36.1554 | 36.1459 | 36.1334 | 36.1138 | 36.0384 | 35.9463 | 35.7694 | 35.5428 | 31.9984 | 31.9933 | 31.9876 | 31.9815 | 31.9304 | 31.8712 | 31.7882 | 31.7065 | 31.5987 | 31.4529 | 30.9208 | 30.742 | 30.6346 | 30.4731 | 32.6751 | 32.6693 | 32.6627 | 32.6557 | 32.59 | 32.5137 | 32.407 | 32.3018 | 32.1631 | 31.9763 | 31.661 | 31.3155 | 31.1111 | 30.9497
PETERHEAD GRANGE | PHEAD NORTH ST | MINIMUM HEADROOM | NK 13470 46450 | NO | 38.1149 | 38.1145 | 38.114 | 38.1134 | 38.1111 | 38.1085 | 38.1054 | 38.1018 | 38.0978 | 38.0955 | 38.0879 | 38.0702 | 38.0411 | 37.9846 | 31.0268 | 31.0195 | 31.0078 | 30.9785 | 30.946 | 30.9141 | 30.883 | 30.8525 | 30.8227 | 30.7905 | 30.6778 | 30.5292 | 30.4012 | 30.247 | 28.4177 | 28.4098 | 28.3973 | 28.3661 | 28.3314 | 28.2974 | 28.2641 | 28.2316 | 28.1998 | 28.1655 | 28.0471 | 27.8378 | 27.6153 | 27.5543
| PHEAD NORTH ST | CT |  |  | 38.1149 | 38.1145 | 38.114 | 38.1134 | 38.1111 | 38.1085 | 38.1054 | 38.1018 | 38.0978 | 38.0955 | 38.0879 | 38.0702 | 38.0411 | 37.9846 | 31.0268 | 31.0204 | 31.011 | 30.9891 | 30.9641 | 30.9391 | 30.9142 | 30.8752 | 30.8366 | 30.7966 | 30.6778 | 30.5292 | 30.4012 | 30.247 | 28.4177 | 28.4109 | 28.4009 | 28.3775 | 28.351 | 28.3245 | 28.2982 | 28.2568 | 28.2158 | 28.1734 | 28.0471 | 27.8378 | 27.6153 | 27.5543
| PHEAD NORTH ST | LW |  |  | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 38.1155 | 31.0269 | 31.0195 | 31.0078 | 30.9785 | 30.946 | 30.9141 | 30.883 | 30.8525 | 30.8227 | 30.7905 | 30.6951 | 30.5831 | 30.4987 | 30.4151 | 28.4177 | 28.4098 | 28.3973 | 28.3661 | 28.3314 | 28.2974 | 28.2641 | 28.2316 | 28.1998 | 28.1655 | 28.0637 | 27.8998 | 27.7348 | 27.6852
| PHEAD NORTH ST | ST |  |  | 38.1154 | 38.1154 | 38.1154 | 38.1154 | 38.1151 | 38.1148 | 38.1145 | 38.114 | 38.1136 | 38.1134 | 38.113 | 38.1122 | 38.1084 | 38.1061 | 31.0298 | 31.0262 | 31.0214 | 31.0121 | 30.9993 | 30.9841 | 30.9677 | 30.9515 | 30.9358 | 30.9108 | 30.8383 | 30.7226 | 30.615 | 30.5512 | 28.4209 | 28.417 | 28.4118 | 28.4019 | 28.3883 | 28.3721 | 28.3546 | 28.3374 | 28.3206 | 28.294 | 28.2167 | 28.0933 | 27.9689 | 27.8465
| PHEAD NORTH ST | SP |  |  | 38.1154 | 38.1154 | 38.1154 | 38.1153 | 38.1153 | 38.1153 | 38.1153 | 38.1153 | 38.1153 | 38.1153 | 38.1152 | 38.115 | 38.1144 | 38.1129 | 31.0334 | 31.0328 | 31.0322 | 31.0316 | 31.028 | 31.0238 | 31.0184 | 31.013 | 31.006 | 30.9961 | 30.9674 | 30.9225 | 30.8802 | 30.84 | 28.4246 | 28.4241 | 28.4234 | 28.4227 | 28.4189 | 28.4145 | 28.4087 | 28.4029 | 28.3955 | 28.3849 | 28.3542 | 28.3063 | 28.2613 | 28.2184
FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | YES | 15.9509 | 15.9464 | 15.7562 | 15.5585 | 15.3508 | 15.103 | 14.8473 | 14.5524 | 14.2495 | 13.9545 | 11.2741 | 10.2567 | 9.3204 | 8.3309 | 13.5843 | 13.5797 | 13.4079 | 13.2284 | 13.0423 | 12.899 | 12.7513 | 10.9993 | 10.6746 | 10.3447 | 9.7158 | 8.6781 | 7.6566 | 6.544 | 13.3407 | 13.3388 | 13.075 | 12.8758 | 12.667 | 12.4151 | 12.1546 | 10.7457 | 10.3991 | 10.03 | 9.3286 | 8.1728 | 7.1121 | 5.9542
| PINEGROVE | CT |  |  | 15.9509 | 15.9464 | 15.7562 | 15.5585 | 15.3508 | 15.103 | 14.8473 | 14.5524 | 14.2495 | 13.9545 | 11.2741 | 10.2567 | 9.3204 | 8.3309 | 13.5843 | 13.5797 | 13.4079 | 13.2284 | 13.0423 | 12.899 | 12.7513 | 10.9993 | 10.6746 | 10.3447 | 9.7158 | 8.6781 | 7.6566 | 6.544 | 13.3407 | 13.3388 | 13.075 | 12.8758 | 12.667 | 12.4151 | 12.1546 | 10.7457 | 10.3991 | 10.03 | 9.3286 | 8.1728 | 7.1121 | 5.9542
| PINEGROVE | LW |  |  | 15.9528 | 15.9492 | 15.8619 | 15.7659 | 15.6687 | 15.5715 | 15.4746 | 15.3777 | 15.2815 | 15.1837 | 14.9721 | 14.6184 | 14.3027 | 14.0836 | 13.5862 | 13.5825 | 13.5032 | 13.415 | 13.3255 | 13.236 | 13.1469 | 13.0578 | 12.9694 | 12.8973 | 12.7764 | 12.6742 | 10.7825 | 10.4023 | 13.3424 | 13.3417 | 13.2177 | 13.1015 | 13.0144 | 12.9269 | 12.8394 | 12.7515 | 12.664 | 12.5762 | 12.3995 | 10.9691 | 10.5508 | 10.1234
| PINEGROVE | ST |  |  | 15.9538 | 15.9515 | 15.8943 | 15.8344 | 15.7715 | 15.7066 | 15.6325 | 15.5581 | 15.484 | 15.3981 | 15.1423 | 14.718 | 14.4162 | 14.1816 | 13.5872 | 13.5849 | 13.533 | 13.4785 | 13.4208 | 13.3611 | 13.292 | 13.2226 | 13.1535 | 13.0722 | 12.8388 | 12.7313 | 10.899 | 10.4684 | 13.3424 | 13.3418 | 13.2592 | 13.176 | 13.0991 | 13.0387 | 12.9778 | 12.9164 | 12.8549 | 12.7952 | 12.6154 | 12.3117 | 10.7225 | 10.2473
| PINEGROVE | SP |  |  | 15.9556 | 15.9551 | 15.9256 | 15.8961 | 15.866 | 15.8368 | 15.8054 | 15.7744 | 15.7427 | 15.7068 | 15.6041 | 15.4491 | 15.3038 | 15.1653 | 13.5891 | 13.5886 | 13.562 | 13.5354 | 13.5081 | 13.4815 | 13.4525 | 13.424 | 13.3945 | 13.3607 | 13.2637 | 13.1171 | 12.9793 | 12.8552 | 13.3427 | 13.3424 | 13.2986 | 13.2547 | 13.212 | 13.1712 | 13.131 | 13.0993 | 13.0729 | 13.0471 | 12.9738 | 12.865 | 12.7636 | 12.6665
TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | YES | 9.0266 | 9.0254 | 9.0205 | 9.0148 | 9.0043 | 9.2292 | 9.2151 | 9.1994 | 9.1821 | 9.1702 | 9.1376 | 9.0683 | 8.9653 | 8.7775 | 7.6392 | 7.6361 | 7.6254 | 7.6101 | 7.5893 | 8.1161 | 8.0914 | 8.0502 | 8.0078 | 7.9688 | 7.8608 | 7.6847 | 6.0579 | 5.5827 | 7.8001 | 7.7941 | 7.784 | 7.7756 | 7.7624 | 8.2965 | 8.279 | 8.2598 | 8.2389 | 8.2233 | 8.184 | 8.104 | 7.9917 | 6.2038
| PITLOCHRY | CT |  |  | 9.0266 | 9.0254 | 9.0205 | 9.0148 | 9.0043 | 9.2292 | 9.2151 | 9.1994 | 9.1821 | 9.1702 | 9.1376 | 9.0683 | 8.9653 | 8.7775 | 7.6392 | 7.6361 | 7.6254 | 7.6101 | 7.5893 | 8.1161 | 8.0914 | 8.0502 | 8.0078 | 7.9688 | 7.8608 | 7.6847 | 6.0579 | 5.5827 | 7.8001 | 7.7941 | 7.784 | 7.7756 | 7.7624 | 8.2965 | 8.279 | 8.2598 | 8.2389 | 8.2233 | 8.184 | 8.104 | 7.9917 | 6.2038
| PITLOCHRY | LW |  |  | 9.0285 | 9.0285 | 9.0285 | 9.0285 | 9.0285 | 9.266 | 9.266 | 9.266 | 9.266 | 9.266 | 9.266 | 9.266 | 9.266 | 9.266 | 7.6409 | 7.6385 | 7.6348 | 7.6255 | 7.6152 | 8.1551 | 8.1452 | 8.1355 | 8.126 | 8.1158 | 8.0855 | 8.0367 | 7.9876 | 7.939 | 7.8015 | 7.7957 | 7.7946 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
| PITLOCHRY | ST |  |  | 9.0281 | 9.0279 | 9.0277 | 9.0274 | 9.0251 | 9.2598 | 9.2565 | 9.2528 | 9.2486 | 9.2473 | 9.2431 | 9.2362 | 9.2004 | 9.1801 | 7.6415 | 7.6401 | 7.6384 | 7.6351 | 7.6288 | 8.1713 | 8.1562 | 8.141 | 8.1256 | 8.109 | 8.0607 | 7.983 | 7.8772 | 7.8055 | 7.8035 | 7.8004 | 7.7964 | 7.7935 | 7.7912 | 8.3384 | 8.3351 | 8.3315 | 8.3273 | 8.3259 | 8.3218 | 8.3149 | 8.279 | 8.2587
| PITLOCHRY | SP |  |  | 9.0281 | 9.0278 | 9.0276 | 9.0273 | 9.0273 | 9.2647 | 9.2647 | 9.2646 | 9.2646 | 9.2642 | 9.263 | 9.2621 | 9.256 | 9.2428 | 7.6425 | 7.6421 | 7.6417 | 7.6412 | 7.6401 | 8.1887 | 8.1847 | 8.1808 | 8.1758 | 8.1695 | 8.151 | 8.1231 | 8.0917 | 8.0547 | 7.8062 | 7.8056 | 7.8049 | 7.8041 | 7.8013 | 8.348 | 8.3433 | 8.3433 | 8.3432 | 8.3429 | 8.3417 | 8.3407 | 8.3346 | 8.3214
ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | YES | 5.9596 | 5.9585 | 5.9573 | 5.9555 | 5.9495 | 5.9426 | 5.9344 | 5.925 | 5.9144 | 5.9084 | 5.8881 | 3.1939 | 2.8877 | 2.5126 | 3.7721 | 3.7703 | 3.7681 | 3.7639 | 3.7553 | 3.7459 | 3.7352 | 3.7216 | 3.707 | 3.6965 | 3.5608 | 2.6018 | 2.2729 | 1.8755 | 3.8867 | 3.8856 | 3.8844 | 3.8825 | 3.8766 | 3.8696 | 3.8615 | 3.852 | 3.8415 | 3.8354 | 3.8152 | 3.0882 | 3.0112 | 2.7188
| POLLACHAR | CT |  |  | 5.9596 | 5.9585 | 5.9573 | 5.9555 | 5.9495 | 5.9426 | 5.9344 | 5.925 | 5.9144 | 5.9084 | 5.8881 | 3.1939 | 2.8877 | 2.5126 | 3.7721 | 3.7703 | 3.7681 | 3.7639 | 3.7553 | 3.7459 | 3.7352 | 3.7216 | 3.707 | 3.6965 | 3.5608 | 2.6018 | 2.2729 | 1.8755 | 3.8867 | 3.8856 | 3.8844 | 3.8825 | 3.8766 | 3.8696 | 3.8615 | 3.852 | 3.8415 | 3.8354 | 3.8152 | 3.0882 | 3.0112 | 2.7188
| POLLACHAR | LW |  |  | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 5.9611 | 3.5477 | 3.5477 | 3.5477 | 3.7741 | 3.7739 | 3.7736 | 3.7727 | 3.7718 | 3.7709 | 3.77 | 3.7692 | 3.7684 | 3.7674 | 3.7648 | 3.2558 | 3.205 | 3.1547 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.8882 | 3.2081 | 3.2081 | 3.2081
| POLLACHAR | ST |  |  | 5.9609 | 5.9607 | 5.9606 | 5.9605 | 5.9591 | 5.9575 | 5.9557 | 5.9536 | 5.9512 | 5.9504 | 5.948 | 3.894 | 3.8214 | 3.6664 | 3.774 | 3.7737 | 3.7735 | 3.773 | 3.7714 | 3.7693 | 3.7655 | 3.7615 | 3.7572 | 3.7535 | 3.7427 | 3.3554 | 3.1769 | 3.0077 | 3.888 | 3.8878 | 3.8877 | 3.8875 | 3.8862 | 3.8846 | 3.8827 | 3.8806 | 3.8782 | 3.8775 | 3.8751 | 3.5312 | 3.5107 | 3.4991
| POLLACHAR | SP |  |  | 5.9609 | 5.9608 | 5.9608 | 5.9607 | 5.9606 | 5.9606 | 5.9606 | 5.9606 | 5.9606 | 5.9604 | 5.96 | 5.9596 | 5.9573 | 5.9524 | 3.7741 | 3.774 | 3.7739 | 3.7738 | 3.7737 | 3.7735 | 3.7728 | 3.7721 | 3.7711 | 3.7699 | 3.7661 | 3.7607 | 3.7535 | 3.744 | 3.888 | 3.8879 | 3.8878 | 3.8877 | 3.8877 | 3.8877 | 3.8877 | 3.8877 | 3.8876 | 3.8875 | 3.8871 | 3.8867 | 3.8844 | 3.8795
FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.099531 | 0.10629 | 0.10624 | 0.10616 | 0.10599 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.098633 | 0.097022 | 0.1065 | 0.10648 | 0.10645 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.098823 | 0.097205
| POOR HOUSE | CT |  |  | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.10629 | 0.10625 | 0.10619 | 0.10606 | 0.10593 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.099506 | 0.1065 | 0.10648 | 0.10646 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.0997
| POOR HOUSE | LW |  |  | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.099531 | 0.10629 | 0.10624 | 0.10616 | 0.10599 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.098633 | 0.097022 | 0.1065 | 0.10648 | 0.10645 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.098823 | 0.097205
| POOR HOUSE | ST |  |  | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.10631 | 0.10628 | 0.10625 | 0.10619 | 0.10611 | 0.10602 | 0.10594 | 0.10587 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10653 | 0.10649 | 0.10648 | 0.10646 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643
| POOR HOUSE | SP |  |  | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.10633 | 0.10632 | 0.10632 | 0.10632 | 0.10629 | 0.10627 | 0.10624 | 0.10621 | 0.10617 | 0.10613 | 0.10602 | 0.10587 | 0.10585 | 0.10585 | 0.10656 | 0.10656 | 0.10655 | 0.10655 | 0.10651 | 0.10649 | 0.10647 | 0.10646 | 0.10645 | 0.10643 | 0.10643 | 0.10643 | 0.10643 | 0.10643
PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | 3.713 | 3.7117 | 3.7079 | 3.7019 | 3.6945 | 3.6865 | 3.678 | 3.6649 | 3.6515 | 3.6386 | 3.6157 | 3.5763 | 3.4863 | 3.4187 | 3.2861 | 3.2858 | 3.284 | 3.2821 | 3.279 | 3.2753 | 3.2711 | 3.2666 | 3.2617 | 3.258 | 3.2487 | 3.2296 | 3.1789 | 2.4283 | 3.1131 | 3.1099 | 3.1054 | 3.1 | 3.0934 | 3.0884 | 3.083 | 3.0772 | 3.0711 | 3.066 | 3.0544 | 3.0315 | 2.4598 | 2.293
| PORT ASKAIG | CT |  |  | 3.713 | 3.7117 | 3.7079 | 3.7019 | 3.6945 | 3.6865 | 3.678 | 3.6649 | 3.6515 | 3.6386 | 3.6157 | 3.5763 | 3.4863 | 3.4187 | 3.2861 | 3.2858 | 3.284 | 3.2821 | 3.279 | 3.2753 | 3.2711 | 3.2666 | 3.2617 | 3.258 | 3.2487 | 3.2296 | 3.1789 | 2.4283 | 3.1131 | 3.11 | 3.1054 | 3.1 | 3.0934 | 3.0884 | 3.083 | 3.0772 | 3.0711 | 3.066 | 3.0544 | 3.0315 | 2.4598 | 2.293
| PORT ASKAIG | LW |  |  | 3.7133 | 3.7121 | 3.7102 | 3.7053 | 3.6999 | 3.6946 | 3.6894 | 3.6844 | 3.6794 | 3.6752 | 3.6686 | 3.658 | 3.6046 | 3.594 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.2865 | 3.263 | 3.263 | 3.1133 | 3.1099 | 3.1083 | 3.1049 | 3.1036 | 3.1036 | 3.1036 | 3.1036 | 3.1036 | 3.1036 | 3.1036 | 3.1036 | 3.0601 | 3.0601
| PORT ASKAIG | ST |  |  | 3.7138 | 3.7132 | 3.7124 | 3.7108 | 3.7085 | 3.7058 | 3.7014 | 3.6969 | 3.6926 | 3.6869 | 3.6725 | 3.6612 | 3.6262 | 3.6139 | 3.2865 | 3.2865 | 3.2865 | 3.2864 | 3.2862 | 3.286 | 3.2857 | 3.2854 | 3.285 | 3.2849 | 3.2846 | 3.284 | 3.2691 | 3.2674 | 3.1147 | 3.113 | 3.1107 | 3.1087 | 3.107 | 3.1051 | 3.1028 | 3.1025 | 3.1021 | 3.102 | 3.1017 | 3.1011 | 3.0763 | 3.0745
| PORT ASKAIG | SP |  |  | 3.7143 | 3.7142 | 3.7141 | 3.7139 | 3.7133 | 3.7126 | 3.7112 | 3.7099 | 3.7081 | 3.7058 | 3.6992 | 3.6891 | 3.6786 | 3.6698 | 3.2864 | 3.2864 | 3.2863 | 3.2863 | 3.2863 | 3.2863 | 3.2863 | 3.2863 | 3.2863 | 3.2862 | 3.286 | 3.2858 | 3.2846 | 3.2821 | 3.1163 | 3.116 | 3.1157 | 3.1154 | 3.1137 | 3.1117 | 3.1089 | 3.108 | 3.1067 | 3.1051 | 3.1031 | 3.1029 | 3.1017 | 3.0992
PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | 7.2823 | 7.2816 | 7.2808 | 7.2793 | 7.2761 | 7.2725 | 7.2684 | 7.2625 | 7.2562 | 7.2516 | 7.243 | 6.9468 | 6.9167 | 6.8584 | 6.2318 | 6.2289 | 6.2244 | 6.2125 | 6.1993 | 6.1863 | 6.1737 | 6.1542 | 6.1283 | 6.1108 | 6.1029 | 5.935 | 5.9049 | 5.8465 | 5.8655 | 5.8643 | 5.8628 | 5.8596 | 5.8547 | 5.8493 | 5.8436 | 5.8335 | 5.8231 | 5.8139 | 5.7859 | 5.5048 | 5.4747 | 5.4163
| PORT ELLEN | CT |  |  | 7.2823 | 7.2816 | 7.2808 | 7.2793 | 7.2761 | 7.2725 | 7.2684 | 7.2625 | 7.2562 | 7.2516 | 7.243 | 6.9468 | 6.9167 | 6.8584 | 6.2318 | 6.2289 | 6.2248 | 6.2155 | 6.2039 | 6.1921 | 6.1801 | 6.1542 | 6.1283 | 6.1108 | 6.1029 | 5.935 | 5.9049 | 5.8465 | 5.8655 | 5.8643 | 5.8628 | 5.8596 | 5.8547 | 5.8493 | 5.8436 | 5.8335 | 5.8231 | 5.8139 | 5.7859 | 5.5048 | 5.4747 | 5.4163
| PORT ELLEN | LW |  |  | 7.2829 | 7.2826 | 7.2821 | 7.281 | 7.2797 | 7.2784 | 7.2772 | 7.2759 | 7.2748 | 7.2735 | 7.2714 | 6.9935 | 6.9935 | 6.9935 | 6.2322 | 6.2292 | 6.2244 | 6.2125 | 6.1993 | 6.1863 | 6.1737 | 6.1613 | 6.1491 | 6.136 | 6.1313 | 5.9817 | 5.9817 | 5.9817 | 5.866 | 5.8652 | 5.8638 | 5.8603 | 5.8565 | 5.8528 | 5.8491 | 5.8455 | 5.842 | 5.8383 | 5.8271 | 5.5514 | 5.5514 | 5.5514
| PORT ELLEN | ST |  |  | 7.2829 | 7.2826 | 7.2823 | 7.2818 | 7.2803 | 7.2786 | 7.276 | 7.2732 | 7.2703 | 7.2682 | 7.262 | 7.1198 | 7.1046 | 7.0959 | 6.2333 | 6.2317 | 6.2296 | 6.2257 | 6.2197 | 6.2124 | 6.1989 | 6.1854 | 6.1719 | 6.1558 | 6.1216 | 6.0438 | 6.0286 | 6.0199 | 5.8662 | 5.8657 | 5.865 | 5.8638 | 5.8614 | 5.8584 | 5.8536 | 5.8485 | 5.8434 | 5.8383 | 5.8235 | 5.6632 | 5.648 | 5.6393
| PORT ELLEN | SP |  |  | 7.283 | 7.2828 | 7.2827 | 7.2825 | 7.2824 | 7.2822 | 7.2818 | 7.2813 | 7.2808 | 7.28 | 7.2777 | 7.2745 | 7.2691 | 7.2604 | 6.2346 | 6.2343 | 6.234 | 6.2336 | 6.2321 | 6.2304 | 6.2263 | 6.2221 | 6.2169 | 6.2106 | 6.1923 | 6.1642 | 6.1352 | 6.1203 | 5.8666 | 5.8664 | 5.8662 | 5.866 | 5.8656 | 5.8651 | 5.8639 | 5.8627 | 5.8611 | 5.8592 | 5.8535 | 5.8451 | 5.8346 | 5.8214
DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | YES | 10.537 | 10.4323 | 10.3308 | 10.2007 | 10.0704 | 9.9434 | 9.8194 | 9.697 | 9.5946 | 9.5378 | 9.4347 | 9.2545 | 9.0628 | 7.1672 | 9.0663 | 8.9757 | 8.8848 | 8.7583 | 8.6293 | 8.5032 | 8.4329 | 8.3672 | 8.3113 | 8.2814 | 8.2255 | 6.7041 | 6.256 | 5.7328 | 8.9157 | 8.8065 | 8.7016 | 8.567 | 8.432 | 8.3006 | 8.1722 | 8.0442 | 7.9365 | 7.8746 | 6.8239 | 6.5289 | 6.1164 | 5.5684
| PORTREE | CT |  |  | 10.537 | 10.4323 | 10.3308 | 10.2007 | 10.0704 | 9.9434 | 9.8194 | 9.697 | 9.5946 | 9.5378 | 9.4347 | 9.2545 | 9.0628 | 7.1672 | 9.0663 | 8.9757 | 8.8848 | 8.7583 | 8.6293 | 8.5032 | 8.4329 | 8.3672 | 8.3113 | 8.2814 | 8.2255 | 6.7041 | 6.256 | 5.7328 | 8.9157 | 8.8065 | 8.7016 | 8.567 | 8.432 | 8.3006 | 8.1722 | 8.0442 | 7.9365 | 7.8746 | 6.8239 | 6.5289 | 6.1164 | 5.5684
| PORTREE | LW |  |  | 10.6322 | 10.6232 | 10.6142 | 10.6027 | 10.5898 | 10.5759 | 10.561 | 10.5454 | 10.5313 | 10.5165 | 10.4705 | 10.3893 | 10.3162 | 10.2394 | 9.1469 | 9.1364 | 9.1239 | 9.1017 | 9.0769 | 9.0515 | 9.0258 | 8.9996 | 8.975 | 8.9489 | 8.8695 | 8.7498 | 8.7173 | 8.6828 | 9.0144 | 9.0042 | 8.9934 | 8.9779 | 8.9614 | 8.9454 | 8.9285 | 8.9108 | 8.8947 | 8.8779 | 8.8257 | 8.7342 | 8.669 | 8.6008
| PORTREE | ST |  |  | 10.6355 | 10.6295 | 10.6234 | 10.615 | 10.6057 | 10.5963 | 10.5836 | 10.571 | 10.5587 | 10.5468 | 10.5083 | 10.4522 | 10.3864 | 10.3333 | 9.1509 | 9.1444 | 9.1373 | 9.1264 | 9.1131 | 9.0985 | 9.0721 | 9.0461 | 9.0205 | 8.9887 | 8.8932 | 8.7787 | 8.7445 | 8.7203 | 9.0182 | 9.0115 | 9.0046 | 8.9949 | 8.9837 | 8.9721 | 8.9553 | 8.9405 | 8.926 | 8.911 | 8.8634 | 8.8042 | 8.7529 | 8.7142
| PORTREE | SP |  |  | 10.632 | 10.6243 | 10.6166 | 10.6089 | 10.5974 | 10.5861 | 10.5743 | 10.5627 | 10.5511 | 10.5392 | 10.5045 | 10.4381 | 10.381 | 10.3244 | 9.1496 | 9.1432 | 9.1367 | 9.1301 | 9.1193 | 9.1083 | 9.0935 | 9.0789 | 9.0629 | 9.0446 | 8.9914 | 8.8985 | 8.8152 | 8.7341 | 9.015 | 9.007 | 8.9991 | 8.9911 | 8.9788 | 8.9666 | 8.9531 | 8.9397 | 8.9258 | 8.9113 | 8.8728 | 8.8003 | 8.7376 | 8.6757
MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | 7.3677 | 7.3654 | 7.3624 | 7.3562 | 7.1573 | 7.1018 | 7.0556 | 4.5188 | 3.886 | 3.3163 | 1.1773 | -0.81254 | -2.7498 | -5.2299 | 7.0975 | 7.0957 | 7.0933 | 7.0886 | 4.9849 | 4.6819 | 4.239 | 3.6764 | 2.9513 | 2.2892 | -0.19715 | -2.5042 | -4.2537 | -7.1624 | 6.9607 | 6.9598 | 6.9589 | 6.9575 | 6.9219 | 4.9208 | 4.3713 | 3.8215 | 3.1127 | 2.4669 | 0.041716 | -2.1995 | -4.1898 | -7.0994
| PORTSOY | CT |  |  | 7.3677 | 7.3654 | 7.3624 | 7.3562 | 7.1876 | 7.1384 | 7.0863 | 7.0413 | 6.9863 | 4.7645 | 3.2377 | 0.95792 | -2.6002 | -5.2299 | 7.0975 | 7.0957 | 7.0933 | 7.0886 | 6.9587 | 6.842 | 4.8782 | 4.7085 | 4.4451 | 3.9679 | 2.1933 | -0.42285 | -4.0621 | -7.1624 | 6.9607 | 6.9598 | 6.9589 | 6.9575 | 6.9274 | 6.8942 | 6.8579 | 6.8186 | 4.6044 | 4.105 | 2.3741 | -0.18287 | -3.9957 | -7.0994
| PORTSOY | LW |  |  | 7.3688 | 7.3671 | 7.3644 | 7.3578 | 7.1573 | 7.1018 | 7.0556 | 4.5188 | 3.886 | 3.3163 | 1.1773 | -0.81254 | -2.7498 | -4.2767 | 7.0987 | 7.0975 | 7.0957 | 7.0911 | 4.9849 | 4.6819 | 4.239 | 3.6764 | 2.9513 | 2.2892 | -0.19715 | -2.5042 | -4.2537 | -6.0747 | 6.9619 | 6.9619 | 6.9619 | 6.9619 | 6.9219 | 4.9208 | 4.3713 | 3.8215 | 3.1127 | 2.4669 | 0.041716 | -2.1995 | -4.1898 | -6.0115
| PORTSOY | ST |  |  | 7.3692 | 7.3682 | 7.3669 | 7.3646 | 7.2223 | 7.1749 | 7.1414 | 7.1123 | 7.0798 | 4.9371 | 3.4577 | 1.3856 | -1.9933 | -3.5539 | 7.0989 | 7.0981 | 7.0972 | 7.0956 | 6.9922 | 6.8924 | 4.9485 | 4.8047 | 4.5918 | 4.1529 | 2.431 | 0.031457 | -3.6498 | -5.4772 | 6.9617 | 6.9615 | 6.9613 | 6.9611 | 6.9451 | 6.9275 | 6.91 | 6.8896 | 4.7697 | 4.2878 | 2.6086 | 0.26674 | -3.4423 | -5.2596
| PORTSOY | SP |  |  | 7.37 | 7.3697 | 7.3695 | 7.3692 | 7.3338 | 7.2938 | 7.2324 | 7.208 | 7.1937 | 7.1749 | 7.1494 | 4.519 | 3.6459 | 2.9421 | 7.0994 | 7.0992 | 7.099 | 7.0987 | 7.0737 | 7.0453 | 7.0022 | 6.9595 | 6.9018 | 4.98 | 4.5692 | 3.6551 | 2.6695 | 1.8601 | 6.9617 | 6.9615 | 6.9614 | 6.9613 | 6.9591 | 6.9571 | 6.9549 | 6.9525 | 6.9484 | 6.9438 | 4.7149 | 3.8041 | 2.8382 | 2.0474
WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | 21.7771 | 21.7749 | 21.7725 | 21.7688 | 21.757 | 21.7427 | 21.7261 | 21.707 | 21.6854 | 21.6732 | 21.6321 | 21.5371 | 21.3805 | 21.0769 | 17.81 | 17.7939 | 17.7725 | 17.7306 | 17.6722 | 17.6008 | 17.5368 | 17.473 | 17.4093 | 17.386 | 17.2778 | 17.0353 | 16.7298 | 16.2794 | 18.1059 | 18.1038 | 18.1014 | 18.0976 | 18.0858 | 18.0716 | 18.055 | 18.0358 | 18.0142 | 18.002 | 17.961 | 17.866 | 17.7094 | 17.4058
| QUEENS LANE NORTH | CT |  |  | 21.7771 | 21.7749 | 21.7725 | 21.7688 | 21.757 | 21.7427 | 21.7261 | 21.707 | 21.6854 | 21.6732 | 21.6321 | 21.5371 | 21.3805 | 21.0769 | 17.8123 | 17.7981 | 17.7776 | 17.7306 | 17.6723 | 17.6124 | 17.551 | 17.5029 | 17.4529 | 17.41 | 17.2778 | 17.0353 | 16.7298 | 16.2794 | 18.1059 | 18.1038 | 18.1014 | 18.0976 | 18.0858 | 18.0716 | 18.055 | 18.0358 | 18.0142 | 18.002 | 17.961 | 17.866 | 17.7094 | 17.4058
| QUEENS LANE NORTH | LW |  |  | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 21.7803 | 17.8254 | 17.8215 | 17.8154 | 17.8002 | 17.7833 | 17.7668 | 17.7506 | 17.7348 | 17.7193 | 17.7026 | 17.653 | 17.5733 | 17.493 | 17.4135 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092 | 18.1092
| QUEENS LANE NORTH | ST |  |  | 21.7795 | 21.779 | 21.7785 | 21.7778 | 21.7727 | 21.7665 | 21.7594 | 21.7512 | 21.742 | 21.739 | 21.7298 | 21.7147 | 21.6355 | 21.5907 | 17.81 | 17.7939 | 17.7725 | 17.7318 | 17.6722 | 17.6008 | 17.5368 | 17.473 | 17.4093 | 17.386 | 17.3178 | 17.2083 | 17.036 | 16.8983 | 18.1083 | 18.1079 | 18.1073 | 18.1067 | 18.1016 | 18.0954 | 18.0882 | 18.0801 | 18.0709 | 18.0678 | 18.0587 | 18.0436 | 17.9644 | 17.9195
| QUEENS LANE NORTH | SP |  |  | 21.7783 | 21.7773 | 21.7762 | 21.7751 | 21.775 | 21.7748 | 21.7745 | 21.7743 | 21.7741 | 21.7725 | 21.7671 | 21.7629 | 21.7361 | 21.6777 | 17.8247 | 17.822 | 17.8189 | 17.8157 | 17.8037 | 17.7896 | 17.772 | 17.7545 | 17.7323 | 17.7227 | 17.6941 | 17.6536 | 17.5928 | 17.5027 | 18.1072 | 18.1061 | 18.1051 | 18.104 | 18.1038 | 18.1036 | 18.1034 | 18.1032 | 18.1029 | 18.1013 | 18.096 | 18.0918 | 18.0649 | 18.0065
QUOICH | QUOICH PRIMARY | MINIMUM HEADROOM | NH 11700 01900 | YES | 1.289 | 3.589 | 3.541 | 3.4821 | 3.4217 | 3.3488 | 3.2736 | 3.1963 | 3.1165 | 3.0345 | 2.8881 | 2.6499 | 2.4422 | 2.2412 | 1.7641 | 4.064 | 4.0167 | 3.9678 | 3.9176 | 3.8571 | 3.7948 | 3.7304 | 3.664 | 3.5931 | 3.4519 | 3.2224 | 3.022 | 2.8279 | 1.4781 | 3.7781 | 3.7339 | 3.6898 | 3.6445 | 3.5898 | 3.5335 | 3.4755 | 3.4157 | 3.3543 | 3.2445 | 3.0659 | 2.9101 | 2.7558
| QUOICH PRIMARY | CT |  |  | 1.289 | 3.589 | 3.541 | 3.4821 | 3.4217 | 3.3488 | 3.2736 | 3.1963 | 3.1165 | 3.0345 | 2.8881 | 2.6499 | 2.4422 | 2.2412 | 1.7641 | 4.064 | 4.0167 | 3.9678 | 3.9176 | 3.8571 | 3.7948 | 3.7304 | 3.664 | 3.5931 | 3.4519 | 3.2224 | 3.022 | 2.8279 | 1.4781 | 3.7781 | 3.7339 | 3.6898 | 3.6445 | 3.5898 | 3.5335 | 3.4755 | 3.4157 | 3.3543 | 3.2445 | 3.0659 | 2.9101 | 2.7558
| QUOICH PRIMARY | LW |  |  | 1.289 | 3.589 | 3.5738 | 3.5477 | 3.5217 | 3.4955 | 3.4694 | 3.4432 | 3.417 | 3.3908 | 3.338 | 3.2489 | 3.1579 | 3.0647 | 1.7641 | 4.064 | 4.0434 | 4.0216 | 3.9996 | 3.9776 | 3.9556 | 3.9334 | 3.9114 | 3.8893 | 3.8442 | 3.7683 | 3.6908 | 3.6115 | 1.4781 | 3.7781 | 3.7585 | 3.7389 | 3.7194 | 3.6999 | 3.6803 | 3.6606 | 3.641 | 3.6214 | 3.5818 | 3.515 | 3.4468 | 3.377
| QUOICH PRIMARY | ST |  |  | 1.289 | 3.589 | 3.5796 | 3.5651 | 3.5478 | 3.5304 | 3.5129 | 3.4954 | 3.478 | 3.4605 | 3.4078 | 3.3186 | 3.2276 | 3.1344 | 1.7641 | 4.0641 | 4.0504 | 4.0365 | 4.022 | 4.0074 | 3.9928 | 3.978 | 3.9634 | 3.9485 | 3.9037 | 3.8282 | 3.7511 | 3.6722 | 1.4781 | 3.7781 | 3.765 | 3.752 | 3.739 | 3.7259 | 3.7129 | 3.6998 | 3.6867 | 3.6736 | 3.6341 | 3.5673 | 3.4991 | 3.4292
| QUOICH PRIMARY | SP |  |  | 1.289 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 3.589 | 1.7642 | 4.0642 | 4.0641 | 4.0641 | 4.0641 | 4.064 | 4.064 | 4.0639 | 4.0638 | 4.0636 | 4.0632 | 4.0626 | 4.062 | 4.0615 | 1.4781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781 | 3.7781
FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | 1.0172 | 1.0172 | 0.9686 | 0.92122 | 0.87264 | 0.81384 | 0.75324 | 0.69087 | 0.62654 | 0.56039 | 0.44226 | 0.25026 | 0.083111 | -0.078229 | 1.0136 | 1.0136 | 0.96782 | 0.92259 | 0.87622 | 0.82025 | 0.7626 | 0.70328 | 0.6421 | 0.57917 | 0.4668 | 0.28414 | 0.12512 | -0.028378 | 1.0141 | 1.0141 | 0.96551 | 0.91795 | 0.8688 | 0.80946 | 0.74835 | 0.68547 | 0.6206 | 0.5539 | 0.43479 | 0.24118 | 0.072629 | -0.090066
| RAHOY | CT |  |  | 1.0172 | 1.0172 | 0.9686 | 0.92122 | 0.87264 | 0.81384 | 0.75324 | 0.69087 | 0.62654 | 0.56039 | 0.44226 | 0.25026 | 0.083111 | -0.078229 | 1.0136 | 1.0136 | 0.96782 | 0.92259 | 0.87622 | 0.82025 | 0.7626 | 0.70328 | 0.6421 | 0.57917 | 0.4668 | 0.28414 | 0.12512 | -0.028378 | 1.0141 | 1.0141 | 0.96551 | 0.91795 | 0.8688 | 0.80946 | 0.74835 | 0.68547 | 0.6206 | 0.5539 | 0.43479 | 0.24118 | 0.072629 | -0.090066
| RAHOY | LW |  |  | 1.0172 | 1.0172 | 0.99496 | 0.97394 | 0.953 | 0.93197 | 0.91095 | 0.88984 | 0.86881 | 0.84766 | 0.80506 | 0.73311 | 0.65965 | 0.58439 | 1.0136 | 1.0136 | 0.99296 | 0.97288 | 0.95288 | 0.93279 | 0.91271 | 0.89254 | 0.87245 | 0.85228 | 0.8117 | 0.74316 | 0.67319 | 0.6015 | 1.0141 | 1.0141 | 0.99171 | 0.97082 | 0.95001 | 0.9288 | 0.90752 | 0.88615 | 0.86487 | 0.8435 | 0.80052 | 0.72793 | 0.65382 | 0.57789
| RAHOY | ST |  |  | 1.0172 | 1.0172 | 1.0077 | 0.98795 | 0.97399 | 0.95998 | 0.94596 | 0.93189 | 0.91787 | 0.90379 | 0.86134 | 0.7894 | 0.71594 | 0.64067 | 1.0136 | 1.0136 | 0.99966 | 0.98628 | 0.97295 | 0.95957 | 0.94618 | 0.93274 | 0.91936 | 0.90591 | 0.86537 | 0.7969 | 0.727 | 0.65538 | 1.0141 | 1.0141 | 0.99816 | 0.98474 | 0.97087 | 0.95694 | 0.94297 | 0.92872 | 0.91454 | 0.9003 | 0.85733 | 0.78477 | 0.71069 | 0.63478
| RAHOY | SP |  |  | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0136 | 1.0136 | 1.0136 | 1.0136 | 1.0136 | 1.0136 | 1.0136 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0134 | 1.0134 | 1.0141 | 1.0141 | 1.0141 | 1.0141 | 1.0141 | 1.0141 | 1.014 | 1.014 | 1.014 | 1.014 | 1.014 | 1.0139 | 1.0139 | 1.0139
INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | 38.5668 | 38.4429 | 38.3188 | 38.1468 | 37.9675 | 37.791 | 37.6169 | 37.4296 | 37.2679 | 37.1622 | 36.921 | 36.4957 | 36.0108 | 35.4016 | 32.9982 | 32.9164 | 32.8316 | 32.7061 | 32.5707 | 32.4461 | 32.3228 | 32.1781 | 32.0418 | 31.9406 | 31.6806 | 31.2246 | 30.7015 | 30.0022 | 33.4873 | 33.3623 | 33.2351 | 33.053 | 32.8624 | 32.6747 | 32.4895 | 32.2768 | 32.0802 | 31.9366 | 31.5826 | 30.9743 | 30.3045 | 29.458
| RAIGMORE | CT |  |  | 38.5668 | 38.4429 | 38.3188 | 38.1468 | 37.9675 | 37.791 | 37.6169 | 37.4296 | 37.2679 | 37.1622 | 36.921 | 36.4957 | 36.0108 | 35.4016 | 32.9982 | 32.9164 | 32.8316 | 32.7061 | 32.5707 | 32.4461 | 32.3228 | 32.1781 | 32.0418 | 31.9406 | 31.6806 | 31.2246 | 30.7015 | 30.0022 | 33.4873 | 33.3623 | 33.2351 | 33.053 | 32.8624 | 32.6747 | 32.4895 | 32.2768 | 32.0802 | 31.9366 | 31.5826 | 30.9743 | 30.3045 | 29.458
| RAIGMORE | LW |  |  | 38.6794 | 38.6668 | 38.6527 | 38.6297 | 38.6039 | 38.5773 | 38.5499 | 38.5217 | 38.4949 | 38.4666 | 38.3798 | 38.2317 | 38.0999 | 37.9671 | 33.0722 | 33.0624 | 33.0503 | 33.0277 | 33.0025 | 32.9769 | 32.9511 | 32.925 | 32.9 | 32.8732 | 32.7924 | 32.671 | 32.5549 | 32.4351 | 33.6001 | 33.5862 | 33.5699 | 33.541 | 33.5088 | 33.4759 | 33.4423 | 33.4082 | 33.3755 | 33.3408 | 33.2353 | 33.0572 | 32.8829 | 32.7022
| RAIGMORE | ST |  |  | 38.7452 | 38.665 | 38.65 | 38.6253 | 38.5897 | 38.549 | 38.4983 | 38.4473 | 38.3959 | 38.3493 | 38.2256 | 38.0455 | 37.7918 | 37.5844 | 33.1553 | 33.0559 | 33.0409 | 33.0148 | 32.9762 | 32.931 | 32.8745 | 32.8178 | 32.7618 | 32.7163 | 32.5808 | 32.3655 | 32.0758 | 31.831 | 33.6966 | 33.5809 | 33.562 | 33.5299 | 33.4843 | 33.4314 | 33.3652 | 33.299 | 33.2327 | 33.1698 | 32.9818 | 32.6843 | 32.3145 | 31.9914
| RAIGMORE | SP |  |  | 38.7463 | 38.7363 | 38.659 | 38.6487 | 38.631 | 38.6124 | 38.5898 | 38.5675 | 38.5423 | 38.5161 | 38.4391 | 38.3086 | 38.1721 | 38.0251 | 33.1598 | 33.1529 | 33.0587 | 33.0514 | 33.037 | 33.0214 | 33.0004 | 32.9797 | 32.9553 | 32.9296 | 32.8544 | 32.7338 | 32.6168 | 32.4777 | 33.7007 | 33.6905 | 33.5803 | 33.5698 | 33.5498 | 33.5286 | 33.5012 | 33.4742 | 33.4429 | 33.4104 | 33.3155 | 33.1572 | 32.9944 | 32.812
ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | 5.8381 | 5.7405 | 5.6464 | 5.5073 | 3.8925 | 3.4338 | 2.7643 | 2.0826 | 1.9122 | 1.2372 | -0.95683 | -3.3266 | -8.2957 | -15.9076 | 3.5967 | 3.5093 | 3.4213 | 3.28 | 2.7826 | 1.9423 | 1.105 | 0.2574 | 0.11493 | -0.23353 | -2.9668 | -5.0488 | -10.0206 | -16.8506 | 3.936 | 3.8231 | 3.7111 | 3.5385 | 3.0639 | 2.4735 | 1.6663 | 0.81513 | 0.66865 | 0.075402 | -2.6826 | -5.118 | -10.6825 | -18.6492
| REDFORD | CT |  |  | 5.8381 | 5.7405 | 5.6464 | 5.5073 | 3.8925 | 3.4872 | 3.0729 | 2.591 | 1.9122 | 1.2372 | -0.95683 | -3.3266 | -7.7117 | -15.9076 | 3.5967 | 3.5093 | 3.4213 | 3.28 | 2.7868 | 2.3427 | 1.8909 | 1.3553 | 0.58598 | -0.23353 | -2.9668 | -5.0488 | -8.8976 | -16.8506 | 3.936 | 3.8231 | 3.7111 | 3.5385 | 3.0639 | 2.6313 | 2.1888 | 1.6509 | 0.8891 | 0.075402 | -2.6826 | -5.118 | -9.7137 | -18.6492
| REDFORD | LW |  |  | 5.927 | 5.9189 | 5.9111 | 5.8906 | 5.8363 | 3.4338 | 2.7643 | 2.0826 | 1.9384 | 1.8745 | 1.6636 | -1.0076 | -2.5705 | -5.28 | 3.6752 | 3.666 | 3.6554 | 3.626 | 2.7826 | 1.9423 | 1.105 | 0.2574 | 0.11493 | 0.052772 | -0.15221 | -3.1025 | -4.7158 | -7.8558 | 5.5342 | 5.5261 | 5.5184 | 3.9843 | 3.2514 | 2.4735 | 1.6663 | 0.81513 | 0.66865 | 0.6023 | 0.38417 | -2.7294 | -4.4786 | -7.6554
| REDFORD | ST |  |  | 5.9299 | 5.9244 | 5.9189 | 5.9052 | 5.8896 | 5.8732 | 5.8545 | 3.6988 | 3.2245 | 2.6377 | 0.59281 | -2.8781 | -8.2957 | -13.2244 | 3.6745 | 3.665 | 3.654 | 3.629 | 3.2978 | 2.9816 | 2.6677 | 2.2671 | 1.6752 | 0.9317 | -1.6638 | -4.4764 | -10.0206 | -14.7229 | 5.537 | 5.5316 | 5.5261 | 3.9914 | 3.7036 | 3.4287 | 3.154 | 2.7788 | 2.2242 | 1.4921 | -1.1102 | -4.628 | -10.6825 | -16.0018
| REDFORD | SP |  |  | 5.9261 | 5.9187 | 5.9113 | 5.9019 | 5.8883 | 5.8737 | 5.8591 | 5.8433 | 5.8233 | 3.9892 | 3.0596 | -0.0584 | -2.7967 | -5.0856 | 3.6761 | 3.6694 | 3.6626 | 3.6537 | 3.559 | 3.4513 | 3.2951 | 3.1401 | 2.934 | 2.6586 | 1.4976 | -1.4465 | -4.186 | -6.4349 | 5.5333 | 5.5259 | 5.5185 | 5.5092 | 3.9246 | 3.8277 | 3.6892 | 3.5516 | 3.3697 | 3.128 | 2.04 | -1.3634 | -4.3543 | -6.8793
BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | YES | 17.1534 | 17.1501 | 17.1463 | 17.1407 | 17.1221 | 17.0992 | 17.0721 | 14.4761 | 13.7661 | 13.0624 | 12.1992 | 10.0183 | 7.2193 | 4.5942 | 15.5864 | 15.5658 | 15.5361 | 15.4883 | 15.3219 | 13.5562 | 12.8837 | 12.2149 | 11.3633 | 10.5259 | 9.5461 | 7.022 | 3.7209 | 0.78924 | 16.0205 | 16.014 | 16.0053 | 15.9882 | 15.9127 | 15.835 | 13.5388 | 12.8799 | 12.0395 | 11.2047 | 10.2246 | 7.6997 | 4.3976 | 1.4652
| REDGORTON | CT |  |  | 17.1534 | 17.1501 | 17.1463 | 17.1407 | 17.1221 | 17.0992 | 17.0721 | 17.0401 | 17.0015 | 14.2779 | 12.1992 | 10.0183 | 8.6546 | 4.5942 | 15.5864 | 15.5658 | 15.5361 | 15.4883 | 15.3332 | 15.2654 | 13.7241 | 13.3025 | 12.7232 | 12.007 | 9.5461 | 7.022 | 5.4723 | 0.78924 | 16.0205 | 16.014 | 16.0053 | 15.9882 | 15.9127 | 15.8409 | 15.7759 | 15.7225 | 13.3788 | 12.6728 | 10.2246 | 7.6997 | 6.1496 | 1.4652
| REDGORTON | LW |  |  | 17.1582 | 17.1582 | 17.1582 | 17.1582 | 17.1558 | 17.1509 | 17.1434 | 14.4761 | 13.7661 | 13.0624 | 12.9886 | 11.4255 | 10.6881 | 8.5548 | 15.6064 | 15.6022 | 15.5956 | 15.579 | 15.3219 | 13.5562 | 12.8837 | 12.2149 | 11.3633 | 10.5259 | 10.4424 | 8.6185 | 7.7655 | 5.2665 | 16.0282 | 16.0274 | 16.0261 | 16.023 | 15.9151 | 15.835 | 13.5388 | 12.8799 | 12.0395 | 11.2047 | 11.1211 | 9.2967 | 8.4434 | 5.9435
| REDGORTON | ST |  |  | 17.1569 | 17.156 | 17.1552 | 17.1542 | 17.1456 | 17.1348 | 17.1221 | 17.1069 | 17.0876 | 17.0815 | 12.672 | 10.7945 | 7.2193 | 5.0777 | 15.5961 | 15.584 | 15.5682 | 15.5384 | 15.4065 | 15.3009 | 15.2882 | 13.5665 | 13.0447 | 12.3785 | 10.0757 | 7.8822 | 3.7209 | 1.225 | 16.0252 | 16.0222 | 16.0186 | 16.0122 | 15.9569 | 15.9006 | 15.8418 | 15.7954 | 13.6943 | 13.0407 | 10.7543 | 8.5601 | 4.3976 | 1.9009
| REDGORTON | SP |  |  | 17.1555 | 17.1541 | 17.1527 | 17.1512 | 17.151 | 17.1507 | 17.1503 | 17.1499 | 17.1493 | 17.1469 | 17.1374 | 14.1697 | 13.1811 | 12.2253 | 15.6055 | 15.6025 | 15.5992 | 15.5956 | 15.529 | 15.4864 | 15.4353 | 15.385 | 15.3184 | 15.313 | 13.0954 | 11.8465 | 10.6785 | 9.5736 | 16.0258 | 16.0241 | 16.0224 | 16.0205 | 16.0078 | 15.9932 | 15.9717 | 15.9505 | 15.9224 | 15.8834 | 13.7449 | 12.5164 | 11.3573 | 10.2521
REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | 56.0193 | 55.975 | 55.9295 | 55.7182 | 55.4978 | 54.8083 | 53.846 | 52.8779 | 52.7019 | 52.2871 | 51.0279 | 48.9209 | 46.7263 | 37.8544 | 49.0148 | 48.9642 | 48.8541 | 48.6326 | 48.1627 | 47.2966 | 46.2255 | 45.1401 | 44.8735 | 44.4013 | 42.973 | 36.2598 | 34.4791 | 31.6013 | 50.097 | 50.0485 | 49.9962 | 49.7852 | 49.4809 | 48.6815 | 47.6839 | 46.6778 | 46.497 | 46.0873 | 44.8451 | 42.7624 | 35.2245 | 32.6101
| REDMOSS | CT |  |  | 56.1242 | 56.073 | 56.0134 | 55.9512 | 55.6955 | 55.2965 | 54.9221 | 54.5681 | 54.116 | 53.8536 | 53.043 | 49.3722 | 46.7263 | 37.8544 | 49.0761 | 48.9803 | 48.8541 | 48.6326 | 48.1627 | 47.5597 | 47.0692 | 46.6658 | 46.156 | 45.8259 | 44.8791 | 41.0152 | 34.4791 | 31.6013 | 50.1727 | 50.0917 | 50.0007 | 49.8869 | 49.5618 | 49.0968 | 48.7194 | 48.3699 | 47.923 | 47.6668 | 46.8763 | 43.2351 | 35.2245 | 32.6101
| REDMOSS | LW |  |  | 56.0193 | 55.975 | 55.9295 | 55.9208 | 55.4978 | 54.8809 | 54.2429 | 53.5837 | 52.8928 | 52.5969 | 51.676 | 49.7996 | 47.6327 | 46.4373 | 49.0148 | 48.9642 | 48.9086 | 48.8748 | 48.3252 | 47.5833 | 46.8219 | 46.0408 | 45.2025 | 44.7823 | 43.6497 | 41.6025 | 35.3186 | 34.2199 | 50.097 | 50.0485 | 49.9962 | 49.9707 | 49.4809 | 48.8234 | 48.1454 | 47.4468 | 46.7081 | 46.3908 | 45.4889 | 43.6379 | 35.9328 | 34.8456
| REDMOSS | ST |  |  | 56.2592 | 56.2259 | 56.1888 | 56.159 | 55.9894 | 54.8083 | 53.846 | 52.8779 | 52.7019 | 52.2871 | 51.0279 | 48.9209 | 47.2168 | 46.2549 | 49.2233 | 49.158 | 49.0783 | 48.9662 | 48.647 | 47.2966 | 46.2255 | 45.1401 | 44.8735 | 44.4013 | 42.973 | 36.2598 | 34.8351 | 34.0754 | 50.3159 | 50.2612 | 50.1956 | 50.1355 | 49.9174 | 48.6815 | 47.6839 | 46.6778 | 46.497 | 46.0873 | 44.8451 | 42.7624 | 35.4493 | 34.7162
| REDMOSS | SP |  |  | 56.3938 | 56.3794 | 56.3647 | 55.7182 | 55.6508 | 55.5809 | 55.5135 | 55.4462 | 55.3746 | 55.067 | 54.1293 | 52.5349 | 51.3973 | 50.8399 | 49.3888 | 49.3699 | 49.35 | 48.6976 | 48.5886 | 48.4696 | 48.3607 | 48.2525 | 48.1274 | 47.7658 | 46.6285 | 44.7637 | 43.5156 | 42.8702 | 50.4711 | 50.4537 | 50.4356 | 49.7852 | 49.6899 | 49.5871 | 49.5029 | 49.4224 | 49.3335 | 49.0084 | 48.006 | 46.3263 | 45.1972 | 44.6477
CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | 4.8899 | 4.8894 | 4.8066 | 4.7235 | 4.6367 | 3.8145 | 3.6096 | 3.396 | 3.1755 | 2.9504 | 2.5398 | 1.8581 | 1.2488 | 0.63085 | 4.4892 | 4.4864 | 4.4212 | 4.3765 | 3.7796 | 3.5932 | 3.401 | 3.2001 | 2.9927 | 2.7811 | 2.3946 | 1.712 | 1.0906 | 0.45999 | 4.4864 | 4.4859 | 4.3691 | 3.893 | 3.7412 | 3.5521 | 3.3494 | 3.1314 | 2.9068 | 2.6769 | 2.2455 | 1.5388 | 0.89932 | 0.25088
| RHICONICH | CT |  |  | 4.8899 | 4.8894 | 4.8066 | 4.7235 | 4.6367 | 3.8145 | 3.6096 | 3.396 | 3.1755 | 2.9504 | 2.5398 | 1.8581 | 1.2488 | 0.63085 | 4.4892 | 4.4864 | 4.4212 | 4.3765 | 3.7796 | 3.5932 | 3.401 | 3.2001 | 2.9927 | 2.7811 | 2.3946 | 1.712 | 1.0906 | 0.45999 | 4.4864 | 4.4859 | 4.3691 | 3.893 | 3.7412 | 3.5521 | 3.3494 | 3.1314 | 2.9068 | 2.6769 | 2.2455 | 1.5388 | 0.89932 | 0.25088
| RHICONICH | LW |  |  | 4.984 | 4.9838 | 4.9345 | 4.898 | 4.8616 | 4.825 | 4.7885 | 4.7517 | 4.7152 | 4.6785 | 4.6047 | 3.6859 | 3.4343 | 3.1768 | 4.5569 | 4.554 | 4.519 | 4.4771 | 4.4513 | 4.4317 | 4.4122 | 4.3926 | 3.8925 | 3.8264 | 3.6868 | 3.4528 | 3.2142 | 2.969 | 4.6008 | 4.6008 | 4.5492 | 4.4975 | 4.4461 | 4.3944 | 4.3428 | 4.2909 | 3.8335 | 3.7628 | 3.6126 | 3.361 | 3.0929 | 2.8181
| RHICONICH | ST |  |  | 4.8904 | 4.8904 | 4.866 | 4.8416 | 4.817 | 4.7922 | 4.7674 | 4.7423 | 4.7173 | 4.6927 | 4.6182 | 3.7115 | 3.4515 | 3.1879 | 4.4907 | 4.4893 | 4.467 | 4.4431 | 4.4272 | 4.4138 | 4.4003 | 4.3867 | 4.3731 | 3.8621 | 3.7142 | 3.4669 | 3.2115 | 2.9481 | 4.4869 | 4.4869 | 4.4524 | 4.418 | 4.3833 | 4.3485 | 4.3136 | 4.2785 | 3.8561 | 3.8025 | 3.6421 | 3.3744 | 3.0938 | 2.8039
| RHICONICH | SP |  |  | 4.9842 | 4.8904 | 4.8904 | 4.8904 | 4.8904 | 4.8904 | 4.8904 | 4.8904 | 4.8903 | 4.8903 | 4.8902 | 4.8901 | 4.8894 | 4.888 | 4.5593 | 4.4919 | 4.4916 | 4.4913 | 4.49 | 4.4884 | 4.4841 | 4.4798 | 4.4745 | 4.4675 | 4.4664 | 4.4663 | 4.4657 | 4.4643 | 4.6008 | 4.4869 | 4.4869 | 4.4869 | 4.4869 | 4.4869 | 4.4869 | 4.4868 | 4.4868 | 4.4868 | 4.4867 | 4.4866 | 4.4859 | 4.4845
DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | 31.2998 | 31.1645 | 31.0317 | 30.5255 | 30.4331 | 29.6526 | 29.0041 | 28.3556 | 27.2961 | 22.2706 | 21.4944 | 20.1734 | 19.2555 | 18.8077 | 26.6929 | 26.5719 | 26.4462 | 25.8656 | 25.7468 | 24.9343 | 24.2432 | 20.6887 | 19.6349 | 19.3785 | 18.6082 | 17.2983 | 16.3887 | 15.95 | 27.2974 | 27.1581 | 27.0204 | 26.5167 | 26.4183 | 25.6307 | 24.9728 | 21.0623 | 20.0096 | 19.7522 | 18.9775 | 17.6591 | 16.7436 | 16.2981
| ROSEBANK STREET | CT |  |  | 31.2998 | 31.1645 | 31.0317 | 30.8919 | 30.6404 | 30.295 | 29.9725 | 29.653 | 29.2788 | 29.0838 | 28.5815 | 21.4902 | 19.889 | 18.9846 | 26.6948 | 26.5719 | 26.4462 | 26.299 | 26.0367 | 25.6804 | 25.3467 | 25.0149 | 24.6282 | 24.4079 | 23.9361 | 19.1477 | 17.5885 | 16.7292 | 27.2974 | 27.1581 | 27.0204 | 26.8713 | 26.6101 | 26.2552 | 25.9235 | 25.5948 | 25.2116 | 25.008 | 24.4817 | 19.0359 | 17.4416 | 16.5443
| ROSEBANK STREET | LW |  |  | 31.3129 | 31.2724 | 31.2312 | 31.2142 | 30.9281 | 30.5078 | 30.0718 | 29.6201 | 29.153 | 28.9606 | 28.3814 | 27.1931 | 21.1249 | 20.2688 | 26.6929 | 26.6485 | 26.6001 | 26.5625 | 26.2536 | 25.8113 | 25.354 | 24.8817 | 24.3947 | 24.1807 | 20.7767 | 19.6408 | 18.3437 | 17.5217 | 27.3134 | 27.2716 | 27.2283 | 27.2064 | 26.9149 | 26.4892 | 26.0479 | 25.5911 | 25.119 | 24.9211 | 21.1097 | 19.9479 | 18.6216 | 17.7707
| ROSEBANK STREET | ST |  |  | 31.493 | 31.4695 | 31.4451 | 30.5255 | 30.4331 | 29.6526 | 29.0041 | 28.3556 | 27.2961 | 22.2706 | 21.4944 | 20.1734 | 19.2555 | 18.8077 | 26.8684 | 26.8381 | 26.8042 | 25.8656 | 25.7468 | 24.9343 | 24.2432 | 20.6887 | 19.6349 | 19.3785 | 18.6082 | 17.2983 | 16.3887 | 15.95 | 27.4927 | 27.4674 | 27.4407 | 26.5167 | 26.4183 | 25.6307 | 24.9728 | 21.0623 | 20.0096 | 19.7522 | 18.9775 | 17.6591 | 16.7436 | 16.2981
| ROSEBANK STREET | SP |  |  | 31.5802 | 31.5641 | 31.548 | 31.0868 | 31.0356 | 29.9536 | 29.9006 | 29.8478 | 28.7633 | 28.5529 | 27.9228 | 22.0501 | 21.3012 | 21.034 | 26.9644 | 26.949 | 26.9333 | 26.4725 | 26.4167 | 25.3288 | 25.2642 | 25.2 | 21.1101 | 20.906 | 20.2944 | 19.2298 | 18.5077 | 18.2659 | 27.5815 | 27.5651 | 27.5486 | 27.087 | 27.0341 | 25.9501 | 25.894 | 25.8381 | 24.7498 | 24.5372 | 20.6255 | 19.5381 | 18.7927 | 18.5287
KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | YES | 10.148 | 10.136 | 10.1173 | 10.075 | 9.8535 | 9.8012 | 9.7476 | 9.6922 | 9.6175 | 9.5624 | 9.5038 | 2.8395 | 1.5567 | 0.048552 | 8.8648 | 8.8545 | 8.8381 | 8.8016 | 8.6589 | 8.6133 | 8.5658 | 8.5166 | 8.4899 | 8.4715 | 3.1677 | 0.32159 | -1.1788 | -2.9493 | 8.3384 | 8.3232 | 8.2997 | 8.2912 | 8.2843 | 8.2756 | 8.2654 | 8.2533 | 8.2381 | 4.7089 | 2.5411 | -0.32899 | -1.8266 | -3.5938
| ROTHES | CT |  |  | 10.148 | 10.136 | 10.1173 | 10.075 | 9.8812 | 9.8235 | 9.7907 | 9.7541 | 9.7033 | 9.6485 | 9.5038 | 4.9004 | 2.9219 | 0.38681 | 8.8648 | 8.8545 | 8.8381 | 8.8016 | 8.6589 | 8.6302 | 8.6002 | 8.5666 | 8.5203 | 8.4715 | 4.9234 | 2.7392 | 0.46255 | -2.4925 | 8.3384 | 8.3232 | 8.2997 | 8.2912 | 8.2843 | 8.2756 | 8.2654 | 8.2533 | 8.2381 | 8.23 | 4.297 | 2.1007 | -0.20093 | -3.1528
| ROTHES | LW |  |  | 10.1594 | 10.1569 | 10.153 | 10.1432 | 9.8535 | 9.8012 | 9.7476 | 9.6922 | 9.6175 | 9.5624 | 9.5493 | 2.8395 | 1.5567 | 0.048552 | 8.8747 | 8.8726 | 8.8693 | 8.8609 | 8.6593 | 8.6133 | 8.5658 | 8.5166 | 8.4899 | 8.4869 | 3.1677 | 0.32159 | -1.1788 | -2.9493 | 8.3525 | 8.3494 | 8.3444 | 8.3318 | 8.2972 | 8.2937 | 8.2884 | 8.2809 | 8.2666 | 4.7089 | 2.5411 | -0.32899 | -1.8266 | -3.5938
| ROTHES | ST |  |  | 10.1592 | 10.157 | 10.1541 | 10.1488 | 10.0116 | 9.8807 | 9.8385 | 9.8096 | 9.7683 | 9.7207 | 9.5679 | 9.5359 | 2.9698 | 0.15658 | 8.8745 | 8.8726 | 8.8701 | 8.8655 | 8.7485 | 8.6659 | 8.6453 | 8.6194 | 8.5826 | 8.5408 | 8.4924 | 3.2227 | 0.48447 | -2.8186 | 8.3523 | 8.3496 | 8.346 | 8.3392 | 8.2958 | 8.2929 | 8.2894 | 8.2849 | 8.2783 | 8.2763 | 4.6673 | 2.5965 | -0.16652 | -3.4634
| ROTHES | SP |  |  | 10.1609 | 10.1604 | 10.1597 | 10.1589 | 10.1229 | 10.0816 | 10.0164 | 9.9523 | 9.8672 | 9.8465 | 9.7756 | 9.6862 | 9.5636 | 9.5118 | 8.8759 | 8.8754 | 8.8748 | 8.8741 | 8.8435 | 8.8083 | 8.7529 | 8.6983 | 8.6679 | 8.6532 | 8.591 | 8.5135 | 8.4648 | 4.9204 | 8.3547 | 8.354 | 8.3532 | 8.3523 | 8.306 | 8.2975 | 8.2974 | 8.2973 | 8.2971 | 8.2965 | 8.2936 | 8.2902 | 4.988 | 4.3019
DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | YES | 27.3176 | 27.3166 | 27.3154 | 27.3135 | 27.3077 | 26.7251 | 26.6028 | 26.2847 | 23.1677 | 23.0429 | 22.6686 | 21.9952 | 21.5379 | 21.325 | 24.5191 | 24.5071 | 24.4896 | 24.4549 | 24.4152 | 23.9238 | 23.7231 | 23.3793 | 21.7108 | 21.5839 | 21.2036 | 20.4688 | 19.811 | 19.3985 | 24.2168 | 24.2129 | 24.2076 | 24.1958 | 24.1793 | 23.6236 | 23.4784 | 23.1522 | 21.679 | 21.5517 | 21.0788 | 20.2087 | 19.5568 | 19.1501
| ROTHESAY | CT |  |  | 27.3176 | 27.3166 | 27.3154 | 27.3135 | 27.3077 | 27.2448 | 27.192 | 27.1378 | 27.0489 | 26.9982 | 26.8438 | 26.3767 | 23.2498 | 22.8363 | 24.5191 | 24.5071 | 24.4896 | 24.4549 | 24.4152 | 24.319 | 24.2335 | 24.1487 | 24.0297 | 23.9464 | 23.7539 | 21.9019 | 21.016 | 20.2863 | 24.2168 | 24.2129 | 24.2076 | 24.1958 | 24.1793 | 24.1059 | 24.0428 | 23.979 | 23.8836 | 23.833 | 23.6786 | 21.6531 | 20.7766 | 20.0562
| ROTHESAY | LW |  |  | 27.3192 | 27.3192 | 27.3192 | 27.3192 | 27.3192 | 27.2511 | 27.1829 | 27.1148 | 27.0467 | 26.9922 | 26.8286 | 26.3162 | 23.1594 | 22.8373 | 24.5271 | 24.5213 | 24.5121 | 24.4889 | 24.4676 | 24.379 | 24.2909 | 24.2033 | 24.1161 | 24.0409 | 23.8163 | 23.2301 | 21.4387 | 20.9169 | 24.2201 | 24.2186 | 24.2162 | 24.2103 | 24.2037 | 24.1291 | 24.0547 | 23.9804 | 23.9063 | 23.8452 | 23.6634 | 21.9752 | 21.1842 | 20.6683
| ROTHESAY | ST |  |  | 27.319 | 27.3189 | 27.3187 | 27.3186 | 27.3172 | 26.9207 | 26.6028 | 26.2847 | 23.1677 | 23.0429 | 22.6686 | 21.9952 | 21.5379 | 21.325 | 24.5265 | 24.5211 | 24.5139 | 24.5003 | 24.4814 | 24.0671 | 23.7231 | 23.3793 | 21.7108 | 21.5839 | 21.2036 | 20.4688 | 19.811 | 19.3985 | 24.2197 | 24.2183 | 24.2163 | 24.2127 | 24.2067 | 23.8045 | 23.4784 | 23.1522 | 21.679 | 21.5517 | 21.0788 | 20.2087 | 19.5568 | 19.1501
| ROTHESAY | SP |  |  | 27.3189 | 27.3187 | 27.3185 | 27.3183 | 27.3183 | 26.7251 | 26.725 | 26.725 | 26.1318 | 26.0273 | 23.152 | 22.5884 | 22.2168 | 22.0905 | 24.5315 | 24.5305 | 24.5295 | 24.5284 | 24.5232 | 23.9238 | 23.9125 | 23.9013 | 23.2949 | 22.017 | 21.701 | 21.1336 | 20.7585 | 20.629 | 24.2209 | 24.2205 | 24.2201 | 24.2197 | 24.2183 | 23.6236 | 23.6206 | 23.6178 | 23.0209 | 21.9867 | 21.6702 | 21.1022 | 20.7265 | 20.5635
THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | 1.7719 | 1.7718 | 1.7716 | 1.7713 | 1.7704 | 1.7693 | 1.7681 | 1.7658 | 1.7605 | 1.7556 | 1.7409 | 1.7148 | 1.684 | 1.6423 | 1.8394 | 1.8392 | 1.839 | 1.8387 | 1.8379 | 1.8368 | 1.8355 | 1.8341 | 1.8325 | 1.8315 | 1.8285 | 1.8213 | 1.8095 | 1.7867 | 1.6448 | 1.6446 | 1.6445 | 1.6278 | 1.6027 | 1.5779 | 1.5533 | 1.5473 | 1.5411 | 1.5352 | 1.5176 | 1.4867 | 1.4512 | 1.4047
| ROUSAY | CT |  |  | 1.7719 | 1.7718 | 1.7716 | 1.7713 | 1.7704 | 1.7693 | 1.7681 | 1.7658 | 1.7605 | 1.7556 | 1.7409 | 1.7148 | 1.684 | 1.6423 | 1.8394 | 1.8392 | 1.839 | 1.8387 | 1.8379 | 1.8368 | 1.8355 | 1.8341 | 1.8325 | 1.8315 | 1.8285 | 1.8213 | 1.8095 | 1.7867 | 1.6448 | 1.6446 | 1.6445 | 1.6278 | 1.6027 | 1.5779 | 1.5533 | 1.5473 | 1.5411 | 1.5352 | 1.5176 | 1.4867 | 1.4512 | 1.4047
| ROUSAY | LW |  |  | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6353 | 1.6232 | 1.6113
| ROUSAY | ST |  |  | 1.7722 | 1.7722 | 1.7721 | 1.7721 | 1.7721 | 1.772 | 1.7719 | 1.7717 | 1.7716 | 1.7715 | 1.7714 | 1.7712 | 1.7699 | 1.764 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8395 | 1.8394 | 1.8393 | 1.8392 | 1.839 | 1.839 | 1.8388 | 1.8386 | 1.8374 | 1.8367 | 1.645 | 1.645 | 1.645 | 1.645 | 1.6375 | 1.6217 | 1.6158 | 1.6101 | 1.6045 | 1.6012 | 1.5916 | 1.5762 | 1.56 | 1.5444
| ROUSAY | SP |  |  | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.7722 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.8396 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 1.6406 | 1.6355
CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | 27.0528 | 27.0494 | 27.0454 | 27.0395 | 27.0203 | 26.9975 | 26.9707 | 26.94 | 26.9052 | 26.8855 | 26.8195 | 26.6665 | 26.4146 | 25.9258 | 24.2763 | 24.2544 | 24.2227 | 24.1508 | 24.0606 | 23.9678 | 23.8737 | 23.7963 | 23.7155 | 23.661 | 23.5922 | 23.4392 | 23.1873 | 20.3298 | 24.5749 | 24.5642 | 24.5493 | 24.5175 | 24.4703 | 24.42 | 24.3662 | 24.319 | 24.2697 | 24.2343 | 24.1218 | 23.9208 | 23.6688 | 20.5707
| RUTHRIESTON | CT |  |  | 27.0528 | 27.0494 | 27.0454 | 27.0395 | 27.0203 | 26.9975 | 26.9707 | 26.94 | 26.9052 | 26.8855 | 26.8195 | 26.6665 | 26.4146 | 25.9258 | 24.2763 | 24.2544 | 24.2227 | 24.1508 | 24.0606 | 23.9678 | 23.8737 | 23.7963 | 23.7155 | 23.661 | 23.5922 | 23.4392 | 23.1873 | 20.3298 | 24.5749 | 24.5642 | 24.5493 | 24.5175 | 24.4703 | 24.42 | 24.3662 | 24.319 | 24.2697 | 24.2343 | 24.1218 | 23.9208 | 23.6688 | 20.5707
| RUTHRIESTON | LW |  |  | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 27.058 | 24.3004 | 24.2986 | 24.2958 | 24.2887 | 24.2809 | 24.2733 | 24.2658 | 24.2584 | 24.2513 | 24.2435 | 24.2206 | 24.1836 | 24.1465 | 24.1096 | 24.5875 | 24.5868 | 24.5857 | 24.583 | 24.5799 | 24.5769 | 24.5739 | 24.571 | 24.5682 | 24.5652 | 24.5561 | 24.5416 | 24.527 | 24.5125
| RUTHRIESTON | ST |  |  | 27.0566 | 27.0558 | 27.055 | 27.0539 | 27.0454 | 27.0352 | 27.0233 | 27.0097 | 26.9945 | 26.9895 | 26.9745 | 26.9493 | 26.8183 | 26.7439 | 24.2809 | 24.2631 | 24.2397 | 24.1951 | 24.1275 | 24.0464 | 23.9767 | 23.9087 | 23.8485 | 23.8107 | 23.7472 | 23.722 | 23.591 | 23.5166 | 24.579 | 24.5716 | 24.5618 | 24.5436 | 24.5119 | 24.4738 | 24.4392 | 24.4033 | 24.3728 | 24.3574 | 24.3123 | 24.2388 | 24.0725 | 23.9982
| RUTHRIESTON | SP |  |  | 27.0552 | 27.0538 | 27.0523 | 27.0507 | 27.0505 | 27.0502 | 27.0499 | 27.0496 | 27.0492 | 27.047 | 27.0395 | 27.0336 | 26.9958 | 26.9137 | 24.2961 | 24.2926 | 24.2886 | 24.2843 | 24.2691 | 24.2511 | 24.2329 | 24.2149 | 24.1918 | 24.1739 | 24.1208 | 24.0434 | 23.9386 | 23.7988 | 24.5842 | 24.5819 | 24.5794 | 24.5768 | 24.5707 | 24.5634 | 24.5561 | 24.5488 | 24.5395 | 24.5311 | 24.5056 | 24.4716 | 24.4075 | 24.3018
FORT WILLIAM | SALEN | MINIMUM HEADROOM | NM 69002 65519 | YES | 3.2736 | 3.2731 | 3.257 | 3.2405 | 3.2217 | 3.1992 | 3.1755 | 3.1506 | 3.1246 | 3.1 | 3.0518 | 2.2939 | 2.0665 | 1.809 | 3.0171 | 3.0158 | 2.9991 | 2.9806 | 2.9596 | 2.935 | 2.9094 | 2.8798 | 2.8491 | 2.8196 | 2.3946 | 2.1846 | 1.9585 | 1.6933 | 3.1739 | 3.1734 | 3.1563 | 3.139 | 3.1193 | 3.0956 | 3.0707 | 3.0447 | 3.0174 | 2.9915 | 2.4243 | 2.1739 | 1.915 | 1.6263
| SALEN | CT |  |  | 3.2736 | 3.2731 | 3.257 | 3.2405 | 3.2217 | 3.1992 | 3.1755 | 3.1506 | 3.1246 | 3.1 | 3.0518 | 2.2939 | 2.0665 | 1.809 | 3.0171 | 3.0158 | 2.9991 | 2.9806 | 2.9596 | 2.935 | 2.9094 | 2.8798 | 2.8491 | 2.8196 | 2.3946 | 2.1846 | 1.9585 | 1.6933 | 3.1739 | 3.1734 | 3.1563 | 3.139 | 3.1193 | 3.0956 | 3.0707 | 3.0447 | 3.0174 | 2.9915 | 2.4243 | 2.1739 | 1.915 | 1.6263
| SALEN | LW |  |  | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 3.2743 | 2.4057 | 3.0177 | 3.0168 | 3.0153 | 3.0116 | 3.0075 | 3.0035 | 2.9996 | 2.9957 | 2.992 | 2.9879 | 2.9759 | 2.4269 | 2.3081 | 2.1878 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 3.1746 | 2.4076 | 2.2873
| SALEN | ST |  |  | 3.2742 | 3.2742 | 3.2741 | 3.274 | 3.2733 | 3.2725 | 3.2716 | 3.2705 | 3.2693 | 3.2689 | 3.2677 | 3.2657 | 3.2552 | 2.4676 | 3.018 | 3.0175 | 3.0168 | 3.0155 | 3.0133 | 3.0106 | 3.0064 | 3.002 | 2.9977 | 2.9934 | 2.9809 | 2.497 | 2.3794 | 2.2649 | 3.1745 | 3.1745 | 3.1744 | 3.1743 | 3.1736 | 3.1728 | 3.1719 | 3.1708 | 3.1696 | 3.1692 | 3.168 | 3.166 | 2.4808 | 2.3644
| SALEN | SP |  |  | 3.2742 | 3.2741 | 3.274 | 3.274 | 3.2739 | 3.2739 | 3.2739 | 3.2739 | 3.2739 | 3.2738 | 3.2734 | 3.2731 | 3.2711 | 3.2667 | 3.0184 | 3.0183 | 3.0181 | 3.0179 | 3.0175 | 3.0169 | 3.0158 | 3.0147 | 3.0133 | 3.0117 | 3.0068 | 2.9996 | 2.9911 | 2.9806 | 3.1745 | 3.1744 | 3.1743 | 3.1743 | 3.1742 | 3.1742 | 3.1742 | 3.1742 | 3.1742 | 3.1741 | 3.1737 | 3.1733 | 3.1714 | 3.167
TAYNUILT | SALEN 2 | MINIMUM HEADROOM | NM 57252 42849 | YES | 4.3052 | 4.3048 | 4.2952 | 4.2854 | 4.274 | 4.2603 | 4.2459 | 4.2308 | 4.2148 | 4.2 | 4.1704 | 3.8349 | 2.4837 | 2.4072 | 3.149 | 3.1475 | 3.1377 | 3.1252 | 3.1108 | 3.0946 | 3.0779 | 3.0502 | 3.022 | 2.9939 | 2.9225 | 2.3096 | 2.1557 | 2.0642 | 3.1474 | 3.147 | 3.14 | 3.1327 | 3.1238 | 3.1132 | 3.102 | 3.0901 | 3.0775 | 3.0662 | 3.0428 | 2.1257 | 1.9748 | 1.8865
| SALEN 2 | CT |  |  | 4.3052 | 4.3048 | 4.2952 | 4.2854 | 4.274 | 4.2603 | 4.2459 | 4.2308 | 4.2148 | 4.2 | 4.1704 | 3.8349 | 2.4837 | 2.4072 | 3.149 | 3.1475 | 3.1377 | 3.1252 | 3.1108 | 3.0946 | 3.0779 | 3.0502 | 3.022 | 2.9939 | 2.9225 | 2.3096 | 2.1557 | 2.0642 | 3.1474 | 3.147 | 3.14 | 3.1327 | 3.1238 | 3.1132 | 3.102 | 3.0901 | 3.0775 | 3.0662 | 3.0428 | 2.1257 | 1.9748 | 1.8865
| SALEN 2 | LW |  |  | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.1069 | 4.1069 | 4.1069 | 3.1494 | 3.148 | 3.1457 | 3.1401 | 3.1338 | 3.1276 | 3.1216 | 3.1156 | 3.1099 | 3.1036 | 3.0851 | 2.9701 | 2.9401 | 2.9198 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 2.4891 | 2.4494 | 2.41
| SALEN 2 | ST |  |  | 4.3056 | 4.3056 | 4.3056 | 4.3056 | 4.3055 | 4.3054 | 4.3053 | 4.3052 | 4.3051 | 4.305 | 4.3049 | 4.1632 | 4.162 | 4.2455 | 3.15 | 3.1493 | 3.1484 | 3.1466 | 3.1441 | 3.1411 | 3.1316 | 3.1224 | 3.1134 | 3.1031 | 3.0734 | 2.9409 | 2.8959 | 2.9687 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1478 | 3.1477 | 3.1476 | 3.1475 | 3.1473 | 3.1473 | 3.1471 | 3.0277 | 2.455 | 2.4765
| SALEN 2 | SP |  |  | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3057 | 4.3899 | 3.1507 | 3.1506 | 3.1505 | 3.1504 | 3.1497 | 3.1489 | 3.1458 | 3.1427 | 3.1389 | 3.1348 | 3.1233 | 3.1053 | 3.0883 | 3.1564 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.1479 | 3.2321
THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | 1.6833 | 1.6831 | 2.183 | 2.1828 | 2.1504 | 2.1168 | 2.0819 | 2.0446 | 1.9747 | 1.9627 | 1.9282 | 1.8423 | 1.3907 | 1.32 | 1.438 | 1.4314 | 1.9217 | 1.9048 | 1.8769 | 1.853 | 1.8276 | 1.7916 | 1.7193 | 1.7046 | 1.4643 | 1.2734 | 1.1372 | 1.0581 | 1.3728 | 1.3701 | 1.8662 | 1.8595 | 1.8354 | 1.8053 | 1.7694 | 1.7311 | 1.4774 | 1.4606 | 1.4176 | 1.2277 | 1.0925 | 1.0143
| SANDAY | CT |  |  | 1.6833 | 1.6831 | 2.183 | 2.1828 | 2.1606 | 2.1367 | 2.1114 | 2.0847 | 2.0337 | 2.0247 | 2.005 | 1.8528 | 1.3907 | 1.32 | 1.438 | 1.4314 | 1.9217 | 1.9048 | 1.8769 | 1.853 | 1.8276 | 1.801 | 1.75 | 1.741 | 1.4643 | 1.2734 | 1.1372 | 1.0581 | 1.3728 | 1.3701 | 1.8662 | 1.8595 | 1.8354 | 1.8115 | 1.7862 | 1.7595 | 1.4774 | 1.4606 | 1.4176 | 1.2277 | 1.0925 | 1.0143
| SANDAY | LW |  |  | 1.6834 | 1.6834 | 2.1834 | 2.1834 | 2.1504 | 2.1168 | 2.0819 | 2.0446 | 1.9747 | 1.9627 | 1.9282 | 1.8423 | 1.4872 | 1.4631 | 1.4448 | 1.4442 | 1.9432 | 1.9408 | 1.9051 | 1.8688 | 1.8315 | 1.7916 | 1.7193 | 1.7046 | 1.6634 | 1.4399 | 1.3719 | 1.3459 | 1.3756 | 1.3754 | 1.875 | 1.874 | 1.84 | 1.8053 | 1.7694 | 1.7311 | 1.6603 | 1.6472 | 1.4996 | 1.4137 | 1.3398 | 1.2956
| SANDAY | ST |  |  | 1.6834 | 1.6834 | 2.1834 | 2.1833 | 2.168 | 2.1516 | 2.1359 | 2.1182 | 2.0844 | 2.0775 | 2.0601 | 1.9886 | 1.8807 | 1.8454 | 1.445 | 1.4446 | 1.9441 | 1.9432 | 1.9267 | 1.9089 | 1.8885 | 1.8662 | 1.828 | 1.8177 | 1.7927 | 1.7108 | 1.4783 | 1.4244 | 1.3757 | 1.3755 | 1.8753 | 1.8749 | 1.8591 | 1.8422 | 1.8246 | 1.8051 | 1.7696 | 1.7613 | 1.7408 | 1.6654 | 1.4337 | 1.3745
| SANDAY | SP |  |  | 1.6834 | 1.6834 | 2.1833 | 2.1833 | 2.181 | 2.1788 | 2.1766 | 2.1741 | 2.1699 | 2.1655 | 2.1495 | 2.1329 | 1.9456 | 1.8855 | 1.4453 | 1.4452 | 1.9451 | 1.945 | 1.9424 | 1.9398 | 1.936 | 1.9319 | 1.9259 | 1.9201 | 1.9004 | 1.8781 | 1.6854 | 1.4831 | 1.3758 | 1.3757 | 1.8757 | 1.8756 | 1.8732 | 1.8709 | 1.868 | 1.8648 | 1.86 | 1.855 | 1.8376 | 1.8187 | 1.6293 | 1.4569
DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | YES | 9.9255 | 9.6505 | 9.6443 | 9.6374 | 9.6251 | 9.6104 | 9.5942 | 9.5759 | 9.556 | 9.5419 | 9.5045 | 9.4255 | 7.4812 | 7.037 | 8.1471 | 7.9464 | 7.942 | 7.9369 | 7.9265 | 7.9141 | 7.339 | 7.2712 | 7.2027 | 7.1358 | 6.938 | 6.5992 | 6.2198 | 5.751 | 8.5929 | 8.3235 | 8.3179 | 8.3116 | 8.2999 | 8.2859 | 8.2704 | 8.2529 | 7.2871 | 7.2154 | 7.0055 | 6.6471 | 6.2488 | 5.7613
| SANDBANK | CT |  |  | 9.9255 | 9.6505 | 9.6443 | 9.6374 | 9.6251 | 9.6104 | 9.5942 | 9.5759 | 9.556 | 9.5419 | 9.5045 | 9.4255 | 7.4812 | 7.037 | 8.1471 | 7.9464 | 7.942 | 7.9369 | 7.9265 | 7.9141 | 7.339 | 7.2712 | 7.2027 | 7.1358 | 6.938 | 6.5992 | 6.2198 | 5.751 | 8.5929 | 8.3235 | 8.3179 | 8.3116 | 8.2999 | 8.2859 | 8.2704 | 8.2529 | 7.2871 | 7.2154 | 7.0055 | 6.6471 | 6.2488 | 5.7613
| SANDBANK | LW |  |  | 9.9275 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 9.6538 | 8.1517 | 7.9498 | 7.9498 | 7.9498 | 7.9498 | 7.9498 | 7.9498 | 7.9498 | 7.9498 | 7.9498 | 7.307 | 7.2054 | 7.1031 | 7.0017 | 8.5949 | 8.3269 | 8.3269 | 8.3269 | 8.3269 | 8.3269 | 8.3269 | 8.3269 | 8.3269 | 8.3269 | 8.3269 | 7.2981 | 7.1906 | 7.0842
| SANDBANK | ST |  |  | 9.927 | 9.6531 | 9.6528 | 9.6525 | 9.6497 | 9.6463 | 9.6423 | 9.6378 | 9.6327 | 9.631 | 9.626 | 9.6176 | 9.5739 | 9.5492 | 8.1476 | 7.949 | 7.9488 | 7.9484 | 7.9456 | 7.9422 | 7.9382 | 7.324 | 7.2865 | 7.2478 | 7.1352 | 6.9542 | 6.74 | 6.5453 | 8.5945 | 8.3262 | 8.3259 | 8.3255 | 8.3227 | 8.3193 | 8.3154 | 8.3108 | 8.3058 | 7.3438 | 7.2258 | 7.0361 | 6.8133 | 6.61
| SANDBANK | SP |  |  | 9.9267 | 9.9264 | 9.6523 | 9.6519 | 9.6519 | 9.6518 | 9.6517 | 9.6516 | 9.6515 | 9.651 | 9.649 | 9.6475 | 9.6376 | 9.6163 | 8.1529 | 8.1517 | 7.9483 | 7.9479 | 7.9478 | 7.9477 | 7.9476 | 7.9476 | 7.9475 | 7.9469 | 7.9449 | 7.3379 | 7.2665 | 7.1874 | 8.5942 | 8.5938 | 8.3254 | 8.325 | 8.3249 | 8.3249 | 8.3248 | 8.3247 | 8.3246 | 8.324 | 8.3221 | 8.3205 | 8.3107 | 7.2811
SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | 4.0717 | 4.0298 | 3.9678 | 3.9033 | 3.8153 | 3.6993 | 3.5797 | 3.2438 | 2.8488 | 2.3463 | 4.0987 | 3.8153 | 2.3463 | 4.0298 | 4.0437 | 3.9966 | 3.9251 | 3.852 | 3.7514 | 3.6195 | 3.4858 | 3.183 | 2.8239 | 2.3767 | 4.0709 | 3.7514 | 2.3767 | 3.9966 | 4.0459 | 3.9984 | 3.928 | 3.8553 | 3.7558 | 3.6248 | 3.4908 | 3.1391 | 2.7164 | 2.1904 | 4.0765 | 3.7558 | 2.1904 | 3.9984
| SANDWICK | CT |  |  | 4.0717 | 4.0298 | 3.9678 | 3.9033 | 3.8153 | 3.6993 | 3.5797 | 3.2438 | 2.8488 | 2.3463 | 4.0987 | 3.8153 | 2.3463 | 4.0298 | 4.0437 | 3.9966 | 3.9251 | 3.852 | 3.7514 | 3.6195 | 3.4858 | 3.183 | 2.8239 | 2.3767 | 4.0709 | 3.7514 | 2.3767 | 3.9966 | 4.0459 | 3.9984 | 3.928 | 3.8553 | 3.7558 | 3.6248 | 3.4908 | 3.1391 | 2.7164 | 2.1904 | 4.0765 | 3.7558 | 2.1904 | 3.9984
| SANDWICK | LW |  |  | 4.0841 | 4.062 | 4.0329 | 3.9976 | 3.9567 | 3.875 | 3.7913 | 3.4932 | 3.1695 | 2.841 | 4.1013 | 3.9567 | 2.841 | 4.062 | 4.0569 | 4.0333 | 4.0004 | 3.9609 | 3.9143 | 3.8213 | 3.7272 | 3.4613 | 3.1643 | 2.865 | 4.0709 | 3.9143 | 2.865 | 4.0333 | 4.0599 | 4.0349 | 4.002 | 3.9623 | 3.9161 | 3.8239 | 3.7299 | 3.4242 | 3.082 | 2.7328 | 4.0795 | 3.9161 | 2.7328 | 4.0349
| SANDWICK | ST |  |  | 4.0844 | 4.0626 | 4.0339 | 4.0008 | 3.9575 | 3.8785 | 3.8013 | 3.6452 | 3.4622 | 3.3098 | 4.1015 | 3.9575 | 3.3098 | 4.0626 | 4.0572 | 4.034 | 4.0015 | 3.9637 | 3.9157 | 3.8254 | 3.7373 | 3.6086 | 3.4488 | 3.3138 | 4.0709 | 3.9157 | 3.3138 | 4.034 | 4.0603 | 4.0356 | 4.0031 | 3.9657 | 3.9173 | 3.8279 | 3.7407 | 3.5838 | 3.4007 | 3.2421 | 4.0797 | 3.9173 | 3.2421 | 4.0356
| SANDWICK | SP |  |  | 4.0908 | 4.0791 | 4.0682 | 4.0589 | 4.0503 | 4.0378 | 4.021 | 3.6842 | 3.6327 | 3.4792 | 4.1044 | 4.0503 | 3.4792 | 4.0791 | 4.0641 | 4.0518 | 4.0403 | 4.0302 | 4.0209 | 4.0069 | 3.9881 | 3.7165 | 3.6717 | 3.5423 | 4.0709 | 4.0209 | 3.5423 | 4.0518 | 4.0677 | 4.0544 | 4.042 | 4.0315 | 4.0219 | 4.0078 | 3.989 | 3.6602 | 3.6089 | 3.4493 | 4.083 | 4.0219 | 3.4493 | 4.0544
SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | 8.5461 | 8.5418 | 8.5361 | 8.525 | 8.5049 | 8.4828 | 8.4583 | 8.4348 | 8.4088 | 8.3918 | 8.3368 | 8.2189 | 8.0395 | 7.7137 | 6.616 | 6.595 | 6.5644 | 6.4937 | 6.4095 | 6.3243 | 6.2398 | 6.1933 | 6.1447 | 6.1031 | 6.0114 | 5.8423 | 5.6491 | 3.7007 | 7.4756 | 7.4719 | 7.467 | 7.4577 | 7.4396 | 7.4196 | 7.397 | 7.3746 | 7.3498 | 7.3339 | 7.2824 | 7.1703 | 6.9966 | 6.6764
| SCALLOWAY | CT |  |  | 8.5461 | 8.5418 | 8.5361 | 8.525 | 8.5049 | 8.4828 | 8.4583 | 8.4348 | 8.4088 | 8.3918 | 8.3368 | 8.2189 | 8.0395 | 7.7137 | 6.616 | 6.595 | 6.5644 | 6.4937 | 6.4095 | 6.3243 | 6.2398 | 6.1933 | 6.1447 | 6.1031 | 6.0114 | 5.8423 | 5.6491 | 3.7007 | 7.4756 | 7.4719 | 7.467 | 7.4577 | 7.4396 | 7.4196 | 7.397 | 7.3746 | 7.3498 | 7.3339 | 7.2824 | 7.1703 | 6.9966 | 6.6764
| SCALLOWAY | LW |  |  | 8.5515 | 8.5515 | 8.5514 | 8.5511 | 8.5508 | 8.5505 | 8.5502 | 8.5499 | 8.5496 | 8.5493 | 8.5483 | 8.5468 | 8.5454 | 8.5439 | 6.6395 | 6.6389 | 6.6379 | 6.6354 | 6.6326 | 6.6298 | 6.6272 | 6.6245 | 6.622 | 6.6192 | 6.611 | 6.5978 | 6.5845 | 6.5713 | 7.4805 | 7.4805 | 7.4804 | 7.4802 | 7.4799 | 7.4797 | 7.4795 | 7.4792 | 7.479 | 7.4788 | 7.4781 | 7.477 | 7.4759 | 7.4747
| SCALLOWAY | ST |  |  | 8.5491 | 8.5471 | 8.5447 | 8.5404 | 8.5301 | 8.5177 | 8.5078 | 8.4969 | 8.4851 | 8.4788 | 8.4603 | 8.43 | 8.3342 | 8.2736 | 6.6243 | 6.6111 | 6.5935 | 6.5601 | 6.5103 | 6.4506 | 6.4206 | 6.39 | 6.3588 | 6.3278 | 6.2402 | 6.1343 | 6.0046 | 5.9115 | 7.4785 | 7.4769 | 7.4749 | 7.4715 | 7.4625 | 7.4516 | 7.4423 | 7.432 | 7.4208 | 7.4154 | 7.3991 | 7.3725 | 7.2803 | 7.2233
| SCALLOWAY | SP |  |  | 8.5497 | 8.5486 | 8.5474 | 8.5462 | 8.5447 | 8.5428 | 8.5418 | 8.5408 | 8.5395 | 8.537 | 8.5289 | 8.5198 | 8.4919 | 8.4374 | 6.6359 | 6.6332 | 6.6302 | 6.627 | 6.6142 | 6.5991 | 6.5915 | 6.5841 | 6.5746 | 6.5624 | 6.5264 | 6.4739 | 6.4049 | 6.3116 | 7.4787 | 7.4776 | 7.4766 | 7.4754 | 7.4742 | 7.4728 | 7.472 | 7.4712 | 7.4702 | 7.4679 | 7.4607 | 7.453 | 7.4264 | 7.3732
TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | 0.13736 | 0.13733 | 0.1373 | 0.13725 | 0.13709 | 0.1369 | 0.13668 | 0.13641 | 0.13612 | 0.13596 | 0.13541 | 0.13413 | 0.13202 | 0.12794 | 0.12628 | 0.12621 | 0.12612 | 0.12593 | 0.12563 | 0.1253 | 0.12494 | 0.12437 | 0.12379 | 0.12338 | 0.12239 | 0.1211 | 0.119 | 0.11491 | 0.12914 | 0.12904 | 0.12892 | 0.12873 | 0.12851 | 0.12826 | 0.12799 | 0.12764 | 0.12734 | 0.12718 | 0.12664 | 0.12535 | 0.12325 | 0.11916
| SCAMMADALE | CT |  |  | 0.13736 | 0.13733 | 0.1373 | 0.13725 | 0.13709 | 0.1369 | 0.13668 | 0.13641 | 0.13612 | 0.13596 | 0.13541 | 0.13413 | 0.13202 | 0.12794 | 0.12628 | 0.12621 | 0.12612 | 0.12593 | 0.12563 | 0.1253 | 0.12494 | 0.12437 | 0.12379 | 0.12338 | 0.12239 | 0.1211 | 0.119 | 0.11491 | 0.12914 | 0.12904 | 0.12892 | 0.12873 | 0.12851 | 0.12826 | 0.12799 | 0.12764 | 0.12734 | 0.12718 | 0.12664 | 0.12535 | 0.12325 | 0.11916
| SCAMMADALE | LW |  |  | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.12632 | 0.12627 | 0.1262 | 0.12601 | 0.1258 | 0.1256 | 0.1254 | 0.1252 | 0.12503 | 0.12486 | 0.12438 | 0.12438 | 0.12438 | 0.12438 | 0.12917 | 0.1291 | 0.12898 | 0.12885 | 0.12877 | 0.12869 | 0.12863 | 0.12863 | 0.12863 | 0.12863 | 0.12863 | 0.12863 | 0.12863 | 0.12863
| SCAMMADALE | ST |  |  | 0.13739 | 0.13738 | 0.13737 | 0.13736 | 0.13729 | 0.13718 | 0.13708 | 0.13694 | 0.1368 | 0.13675 | 0.13661 | 0.13637 | 0.13512 | 0.13441 | 0.12633 | 0.1263 | 0.12625 | 0.12618 | 0.12603 | 0.12583 | 0.12528 | 0.12473 | 0.12424 | 0.12401 | 0.12359 | 0.12335 | 0.12209 | 0.12139 | 0.1292 | 0.12915 | 0.12909 | 0.12898 | 0.12879 | 0.12865 | 0.12837 | 0.12816 | 0.12803 | 0.12797 | 0.12784 | 0.12759 | 0.12634 | 0.12564
| SCAMMADALE | SP |  |  | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.1374 | 0.12636 | 0.12636 | 0.12636 | 0.12635 | 0.12633 | 0.1263 | 0.12617 | 0.12603 | 0.12583 | 0.12575 | 0.12551 | 0.12514 | 0.12484 | 0.12458 | 0.12924 | 0.12924 | 0.12923 | 0.12922 | 0.12919 | 0.12914 | 0.12893 | 0.12886 | 0.12878 | 0.12875 | 0.12865 | 0.12863 | 0.12863 | 0.12863
ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | YES | 17.6326 | 17.6294 | 17.6256 | 17.62 | 17.6019 | 17.5801 | 17.5547 | 17.5252 | 17.4913 | 17.4725 | 17.4095 | 13.5334 | 11.8479 | 10.3356 | 16.2315 | 16.2056 | 16.168 | 16.0815 | 15.9404 | 15.8033 | 15.7119 | 15.6824 | 15.6485 | 15.6297 | 13.2207 | 12.0191 | 10.0798 | 8.3822 | 15.7393 | 15.7303 | 15.7178 | 15.7009 | 15.6827 | 15.6609 | 15.6355 | 15.606 | 15.5722 | 13.5893 | 12.8062 | 11.6021 | 9.666 | 7.9708
| SCONE | CT |  |  | 17.6326 | 17.6294 | 17.6256 | 17.62 | 17.6019 | 17.5801 | 17.5547 | 17.5252 | 17.4913 | 17.4725 | 17.4095 | 13.5334 | 11.8479 | 10.3356 | 16.2315 | 16.2056 | 16.168 | 16.0815 | 15.9404 | 15.8033 | 15.7119 | 15.6824 | 15.6485 | 15.6297 | 13.2207 | 12.0191 | 10.0798 | 8.3822 | 15.7393 | 15.7303 | 15.7178 | 15.7009 | 15.6827 | 15.6609 | 15.6355 | 15.606 | 15.5722 | 13.5893 | 12.8062 | 11.6021 | 9.666 | 7.9708
| SCONE | LW |  |  | 17.6374 | 17.6374 | 17.6374 | 17.6374 | 17.6369 | 17.6359 | 17.6344 | 17.6322 | 17.628 | 17.6271 | 17.6233 | 14.3585 | 13.1287 | 12.6245 | 16.2589 | 16.2561 | 16.2516 | 16.2404 | 16.1449 | 16.05 | 15.9556 | 15.8616 | 15.7852 | 15.7844 | 15.7805 | 12.9268 | 11.4824 | 10.8903 | 15.7524 | 15.7513 | 15.7495 | 15.7451 | 15.7204 | 15.7168 | 15.7152 | 15.713 | 15.7089 | 15.708 | 13.4249 | 12.5088 | 11.067 | 10.4761
| SCONE | ST |  |  | 17.6362 | 17.6354 | 17.6346 | 17.6336 | 17.6255 | 17.6157 | 17.6043 | 17.5912 | 17.5758 | 17.5709 | 17.5555 | 14.3754 | 13.3423 | 12.2325 | 16.2439 | 16.229 | 16.2094 | 16.1721 | 16.083 | 15.9845 | 15.9035 | 15.8131 | 15.733 | 15.7281 | 15.7127 | 12.9619 | 11.7709 | 10.4788 | 15.7457 | 15.7407 | 15.7351 | 15.7248 | 15.7063 | 15.6965 | 15.6851 | 15.672 | 15.6566 | 15.6517 | 13.4525 | 12.5436 | 11.3547 | 10.0648
| SCONE | SP |  |  | 17.6349 | 17.6335 | 17.6321 | 17.6306 | 17.6304 | 17.6301 | 17.6298 | 17.6295 | 17.6291 | 17.627 | 17.6194 | 17.6132 | 17.5655 | 17.4843 | 16.256 | 16.2526 | 16.2487 | 16.2446 | 16.2213 | 16.194 | 16.166 | 16.1383 | 16.1021 | 16.0585 | 15.8943 | 15.7704 | 15.7227 | 15.6415 | 15.7497 | 15.7475 | 15.7451 | 15.7426 | 15.735 | 15.7278 | 15.7205 | 15.7132 | 15.7099 | 15.7078 | 15.7003 | 15.694 | 15.6463 | 13.491
THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | 1.414 | 1.4139 | 1.4137 | 1.4134 | 1.3821 | 1.3498 | 1.3163 | 1.2805 | 1.229 | 1.22 | 0.98842 | 0.92906 | 0.089569 | 0.060258 | 1.2427 | 1.2423 | 1.2419 | 1.2409 | 1.2082 | 1.1748 | 0.98387 | 0.94823 | 0.89695 | 0.88812 | 0.86283 | 0.80535 | 0.10943 | 0.072402 | 1.3108 | 1.3102 | 1.3095 | 1.3074 | 1.2735 | 1.2391 | 0.96932 | 0.93236 | 0.87981 | 0.8696 | 0.84023 | 0.77616 | -0.12288 | -0.15431
| SHAPINSAY | CT |  |  | 1.414 | 1.4139 | 1.4137 | 1.4134 | 1.3938 | 1.3727 | 1.3503 | 1.3266 | 1.2933 | 1.2871 | 1.2728 | 0.96876 | 0.11868 | 0.076607 | 1.2427 | 1.2423 | 1.2419 | 1.2409 | 1.2206 | 1.1987 | 1.1757 | 0.99425 | 0.96139 | 0.95555 | 0.9425 | 0.83879 | 0.12357 | 0.072402 | 1.3108 | 1.3102 | 1.3095 | 1.3078 | 1.2867 | 1.2641 | 1.2403 | 0.97881 | 0.94336 | 0.93469 | 0.9133 | 0.80525 | -0.10271 | -0.15064
| SHAPINSAY | LW |  |  | 1.4142 | 1.4141 | 1.414 | 1.4138 | 1.3821 | 1.3498 | 1.3163 | 1.2805 | 1.229 | 1.22 | 0.98842 | 0.92906 | 0.089569 | 0.060258 | 1.2428 | 1.2425 | 1.2421 | 1.2409 | 1.2082 | 1.1748 | 0.98387 | 0.94823 | 0.89695 | 0.88812 | 0.86283 | 0.80535 | 0.10943 | 0.075334 | 1.3109 | 1.3103 | 1.3095 | 1.3074 | 1.2735 | 1.2391 | 0.96932 | 0.93236 | 0.87981 | 0.8696 | 0.84023 | 0.77616 | -0.12288 | -0.15431
| SHAPINSAY | ST |  |  | 1.4141 | 1.4141 | 1.414 | 1.414 | 1.4137 | 1.4133 | 1.4128 | 1.4122 | 1.4116 | 1.4112 | 1.4101 | 1.4082 | 0.81671 | 0.80531 | 1.2429 | 1.2427 | 1.2425 | 1.2421 | 1.2415 | 1.2406 | 1.2388 | 1.237 | 1.2352 | 1.2334 | 1.2281 | 1.2198 | 0.74731 | 0.73008 | 1.311 | 1.3108 | 1.3104 | 1.3097 | 1.3086 | 1.3073 | 1.3041 | 1.301 | 1.2979 | 1.2947 | 1.2853 | 1.2702 | 0.61503 | 0.59986
| SHAPINSAY | SP |  |  | 1.4141 | 1.4141 | 1.414 | 1.414 | 1.4139 | 1.4139 | 1.4138 | 1.4137 | 1.4136 | 1.4134 | 1.4129 | 1.4122 | 1.4106 | 1.4076 | 1.243 | 1.2429 | 1.2428 | 1.2428 | 1.2426 | 1.2425 | 1.2419 | 1.2414 | 1.2407 | 1.24 | 1.2379 | 1.2347 | 1.2308 | 1.2256 | 1.3112 | 1.3112 | 1.3111 | 1.311 | 1.3107 | 1.3104 | 1.3094 | 1.3085 | 1.3072 | 1.3059 | 1.3021 | 1.2964 | 1.2901 | 1.2826
BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | 1.369 | 4.3687 | 4.3189 | 4.2689 | 3.9287 | 3.8119 | 3.6914 | 3.5646 | 3.4337 | 3.3003 | 3.0552 | 2.6528 | 2.2845 | 1.9027 | 1.5086 | 4.5083 | 4.4813 | 4.4554 | 3.9107 | 3.7941 | 3.6728 | 3.5421 | 3.4072 | 3.2697 | 3.0146 | 2.5958 | 2.2169 | 1.8287 | 1.2879 | 4.2874 | 4.1902 | 3.9422 | 3.8433 | 3.7247 | 3.6023 | 3.4701 | 3.3339 | 3.1949 | 2.9338 | 2.5055 | 2.1164 | 1.718
| SHIELDAIG | CT |  |  | 1.369 | 4.3687 | 4.3189 | 4.2689 | 3.9287 | 3.8119 | 3.6914 | 3.5646 | 3.4337 | 3.3003 | 3.0552 | 2.6528 | 2.2845 | 1.9027 | 1.5086 | 4.5083 | 4.4813 | 4.4554 | 3.9107 | 3.7941 | 3.6728 | 3.5421 | 3.4072 | 3.2697 | 3.0146 | 2.5958 | 2.2169 | 1.8287 | 1.2879 | 4.2874 | 4.1902 | 3.9422 | 3.8433 | 3.7247 | 3.6023 | 3.4701 | 3.3339 | 3.1949 | 2.9338 | 2.5055 | 2.1164 | 1.718
| SHIELDAIG | LW |  |  | 1.3695 | 4.3695 | 4.3475 | 4.3256 | 4.3037 | 4.2817 | 3.999 | 3.9608 | 3.9188 | 3.8765 | 3.7903 | 3.6449 | 3.4965 | 3.3448 | 1.5091 | 4.5091 | 4.4973 | 4.4854 | 4.474 | 4.4628 | 3.9825 | 3.9394 | 3.8965 | 3.8532 | 3.7636 | 3.613 | 3.4593 | 3.3024 | 1.2884 | 4.2881 | 4.2442 | 4.2 | 4.1607 | 3.9575 | 3.9134 | 3.8693 | 3.8254 | 3.7811 | 3.6891 | 3.5345 | 3.3768 | 3.2157
| SHIELDAIG | ST |  |  | 1.3695 | 4.3694 | 4.3547 | 4.3401 | 4.3251 | 4.3101 | 4.295 | 4.2798 | 4.2645 | 3.9717 | 3.8864 | 3.7413 | 3.5832 | 3.4239 | 1.509 | 4.509 | 4.5011 | 4.4932 | 4.485 | 4.4768 | 4.4689 | 4.4609 | 3.9897 | 3.9575 | 3.8607 | 3.6987 | 3.5299 | 3.36 | 1.2885 | 4.2883 | 4.2591 | 4.2297 | 4.2004 | 4.1733 | 3.9855 | 3.9529 | 3.9206 | 3.8872 | 3.7874 | 3.6202 | 3.4462 | 3.2711
| SHIELDAIG | SP |  |  | 1.3694 | 4.3693 | 4.3693 | 4.3692 | 4.3692 | 4.3692 | 4.3692 | 4.3692 | 4.3692 | 4.3691 | 4.3688 | 4.3686 | 4.3671 | 4.3639 | 1.509 | 4.5089 | 4.5089 | 4.5088 | 4.5088 | 4.5088 | 4.5088 | 4.5088 | 4.5087 | 4.5087 | 4.5084 | 4.5081 | 4.5067 | 4.5035 | 1.2886 | 4.2885 | 4.2884 | 4.2883 | 4.2882 | 4.288 | 4.2873 | 4.2866 | 4.2858 | 4.2847 | 4.2816 | 4.2789 | 4.2775 | 4.2743
SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | 2.9892 | 2.9889 | 2.9705 | 2.9517 | 2.9317 | 2.9075 | 2.8826 | 2.855 | 2.8263 | 2.8019 | 2.7699 | 2.4545 | 2.3545 | 2.2424 | 2.7055 | 2.7053 | 2.6865 | 2.6676 | 2.6487 | 2.6316 | 2.6216 | 2.6107 | 2.4681 | 2.4355 | 2.3683 | 2.2565 | 2.1478 | 2.0273 | 2.8065 | 2.8062 | 2.7835 | 2.7605 | 2.7361 | 2.7068 | 2.6764 | 2.6433 | 2.4962 | 2.4624 | 2.3921 | 2.272 | 2.1496 | 2.0155
| SHIN | CT |  |  | 2.9892 | 2.9889 | 2.9705 | 2.9517 | 2.9317 | 2.9075 | 2.8826 | 2.855 | 2.8263 | 2.8019 | 2.7699 | 2.4545 | 2.3545 | 2.2424 | 2.7055 | 2.7053 | 2.6865 | 2.6676 | 2.6487 | 2.6316 | 2.6216 | 2.6107 | 2.4681 | 2.4355 | 2.3683 | 2.2565 | 2.1478 | 2.0273 | 2.8065 | 2.8062 | 2.7835 | 2.7605 | 2.7361 | 2.7068 | 2.6764 | 2.6433 | 2.4962 | 2.4624 | 2.3921 | 2.272 | 2.1496 | 2.0155
| SHIN | LW |  |  | 2.9895 | 2.9894 | 2.9892 | 2.9886 | 2.9879 | 2.9873 | 2.9866 | 2.986 | 2.9854 | 2.9848 | 2.9828 | 2.9797 | 2.9766 | 2.9735 | 2.7058 | 2.7058 | 2.7057 | 2.7055 | 2.7053 | 2.705 | 2.7048 | 2.7046 | 2.7044 | 2.7041 | 2.7035 | 2.7024 | 2.7012 | 2.7001 | 2.8068 | 2.8066 | 2.8064 | 2.8059 | 2.8052 | 2.8046 | 2.804 | 2.8034 | 2.8029 | 2.8022 | 2.8004 | 2.7974 | 2.7945 | 2.7915
| SHIN | ST |  |  | 2.9895 | 2.9894 | 2.9893 | 2.9891 | 2.9885 | 2.9879 | 2.9856 | 2.9832 | 2.9809 | 2.9792 | 2.9742 | 2.9662 | 2.9547 | 2.9451 | 2.7058 | 2.7058 | 2.7057 | 2.7056 | 2.7052 | 2.7048 | 2.7037 | 2.7025 | 2.7014 | 2.7007 | 2.6985 | 2.6951 | 2.6881 | 2.6831 | 2.8068 | 2.8067 | 2.8066 | 2.8064 | 2.8058 | 2.8052 | 2.803 | 2.8007 | 2.7984 | 2.7968 | 2.7921 | 2.7844 | 2.7748 | 2.7722
| SHIN | SP |  |  | 2.9896 | 2.9895 | 2.9895 | 2.9894 | 2.9893 | 2.9892 | 2.9886 | 2.9879 | 2.9871 | 2.9864 | 2.9845 | 2.9815 | 2.9778 | 2.9726 | 2.7058 | 2.7058 | 2.7057 | 2.7056 | 2.7056 | 2.7056 | 2.7053 | 2.7051 | 2.7048 | 2.7045 | 2.7036 | 2.7025 | 2.7003 | 2.6968 | 2.8068 | 2.8068 | 2.8067 | 2.8066 | 2.8066 | 2.8065 | 2.8058 | 2.8052 | 2.8044 | 2.8038 | 2.8019 | 2.7991 | 2.7955 | 2.7905
FORT WILLIAM | SHONA BEAG | MINIMUM HEADROOM | NM 67173 74363 | YES | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939
| SHONA BEAG | CT |  |  | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939
| SHONA BEAG | LW |  |  | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939
| SHONA BEAG | ST |  |  | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939
| SHONA BEAG | SP |  |  | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.11144 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10905 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939 | 0.10939
KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | YES | 41.6623 | 41.6479 | 41.6283 | 41.5894 | 41.5085 | 41.4225 | 41.329 | 41.2401 | 41.1348 | 41.0544 | 40.841 | 40.1204 | 28.0296 | 24.6049 | 35.7955 | 35.7317 | 35.6385 | 35.4622 | 35.2351 | 35.0362 | 34.8314 | 34.669 | 34.5301 | 34.4901 | 34.3558 | 26.9425 | 22.2968 | 18.4382 | 36.533 | 36.4361 | 36.2932 | 35.9594 | 35.5413 | 35.4193 | 35.2903 | 35.1779 | 35.0431 | 34.926 | 34.5343 | 27.5017 | 22.8685 | 19.0187
| SKENE | CT |  |  | 41.6623 | 41.6479 | 41.6283 | 41.5894 | 41.5085 | 41.4225 | 41.329 | 41.2401 | 41.1348 | 41.0544 | 40.841 | 40.1204 | 28.0296 | 24.6049 | 35.7955 | 35.7317 | 35.6385 | 35.4622 | 35.2351 | 35.0362 | 34.8314 | 34.669 | 34.5301 | 34.4901 | 34.3558 | 26.9425 | 22.2968 | 18.4382 | 36.533 | 36.4361 | 36.2932 | 35.9594 | 35.5413 | 35.4193 | 35.2903 | 35.1779 | 35.0431 | 34.926 | 34.5343 | 27.5017 | 22.8685 | 19.0187
| SKENE | LW |  |  | 41.6804 | 41.6798 | 41.6789 | 41.6764 | 41.6422 | 41.607 | 41.5707 | 41.5329 | 41.4818 | 41.4395 | 41.2889 | 40.8734 | 40.8325 | 40.8143 | 35.8649 | 35.8604 | 35.8531 | 35.8349 | 35.5882 | 35.4156 | 35.2832 | 35.155 | 34.9909 | 34.835 | 34.8036 | 34.5478 | 25.3717 | 23.8615 | 36.637 | 36.6298 | 36.6183 | 36.5895 | 36.1996 | 35.8125 | 35.599 | 35.5324 | 35.4453 | 35.3667 | 35.0731 | 34.507 | 25.9378 | 24.4322
| SKENE | ST |  |  | 41.6702 | 41.6618 | 41.651 | 41.6319 | 41.5762 | 41.5124 | 41.4591 | 41.3982 | 41.3254 | 41.2762 | 41.1139 | 40.8323 | 40.4543 | 28.3806 | 35.81 | 35.7604 | 35.6945 | 35.5722 | 35.3733 | 35.2018 | 35.0845 | 34.9514 | 34.7886 | 34.6628 | 34.6214 | 34.4269 | 25.7484 | 22.5393 | 36.5521 | 36.4746 | 36.3716 | 36.175 | 35.7523 | 35.5333 | 35.4597 | 35.3757 | 35.2742 | 35.1924 | 34.9203 | 34.4654 | 26.3638 | 23.1639
| SKENE | SP |  |  | 41.6721 | 41.6672 | 41.662 | 41.6565 | 41.6469 | 41.6356 | 41.6256 | 41.6158 | 41.6029 | 41.5835 | 41.5103 | 41.4251 | 41.2275 | 40.9315 | 35.8523 | 35.8419 | 35.8303 | 35.8179 | 35.75 | 35.6705 | 35.602 | 35.5438 | 35.4813 | 35.4071 | 35.1795 | 34.9044 | 34.631 | 34.3898 | 36.6215 | 36.6074 | 36.5916 | 36.5743 | 36.4673 | 36.3419 | 36.2339 | 36.1272 | 35.9874 | 35.8275 | 35.5248 | 35.379 | 35.1284 | 34.7825
BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | 8.3594 | 8.3587 | 8.3529 | 8.3469 | 8.3376 | 8.3266 | 8.3145 | 8.3013 | 8.2869 | 8.2758 | 8.249 | 8.195 | 8.1207 | 7.9931 | 7.2281 | 7.227 | 7.2215 | 7.2151 | 7.2053 | 7.194 | 7.1817 | 7.1658 | 7.149 | 7.1352 | 7.0992 | 7.0304 | 6.0424 | 5.7334 | 7.2885 | 7.2872 | 7.2805 | 7.2724 | 7.261 | 7.2478 | 7.2335 | 7.2141 | 7.1936 | 7.177 | 7.1505 | 7.0971 | 6.0994 | 5.7974
| SKULAMUS | CT |  |  | 8.3594 | 8.3587 | 8.3529 | 8.3469 | 8.3376 | 8.3266 | 8.3145 | 8.3013 | 8.2869 | 8.2758 | 8.249 | 8.195 | 8.1207 | 7.9931 | 7.2281 | 7.227 | 7.2215 | 7.2151 | 7.2053 | 7.194 | 7.1817 | 7.1658 | 7.149 | 7.1352 | 7.0992 | 7.0304 | 6.0424 | 5.7334 | 7.2885 | 7.2872 | 7.2805 | 7.2724 | 7.261 | 7.2478 | 7.2335 | 7.2141 | 7.1936 | 7.177 | 7.1505 | 7.0971 | 6.0994 | 5.7974
| SKULAMUS | LW |  |  | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 8.3606 | 7.2293 | 7.229 | 7.2286 | 7.2275 | 7.2263 | 7.2251 | 7.224 | 7.2229 | 7.2218 | 7.2206 | 7.2171 | 7.2114 | 7.2058 | 7.2001 | 7.2897 | 7.2892 | 7.2885 | 7.2866 | 7.2845 | 7.2825 | 7.2805 | 7.2786 | 7.2767 | 7.2746 | 7.2685 | 7.2604 | 7.2604 | 7.2604
| SKULAMUS | ST |  |  | 8.3604 | 8.3603 | 8.3602 | 8.3601 | 8.359 | 8.3578 | 8.3563 | 8.3547 | 8.3528 | 8.3522 | 8.3503 | 8.3473 | 8.3312 | 8.3221 | 7.2292 | 7.229 | 7.2287 | 7.2282 | 7.2267 | 7.2248 | 7.2212 | 7.2175 | 7.2136 | 7.2106 | 7.2019 | 7.1878 | 7.1609 | 7.1409 | 7.2897 | 7.2894 | 7.2889 | 7.2882 | 7.2863 | 7.2841 | 7.2789 | 7.2736 | 7.2682 | 7.2635 | 7.2508 | 7.2471 | 7.231 | 7.2219
| SKULAMUS | SP |  |  | 8.3604 | 8.3603 | 8.3602 | 8.3601 | 8.3601 | 8.36 | 8.36 | 8.36 | 8.36 | 8.3598 | 8.3593 | 8.3589 | 8.3563 | 8.3507 | 7.2293 | 7.2292 | 7.2291 | 7.2289 | 7.2288 | 7.2286 | 7.2279 | 7.2272 | 7.2263 | 7.2252 | 7.222 | 7.2174 | 7.2109 | 7.2016 | 7.2899 | 7.2898 | 7.2896 | 7.2895 | 7.2892 | 7.2889 | 7.2877 | 7.2865 | 7.2849 | 7.2831 | 7.278 | 7.2704 | 7.261 | 7.2505
WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | 36.0497 | 36.0452 | 36.0401 | 36.0325 | 44.7375 | 44.7075 | 44.6724 | 44.6318 | 44.585 | 44.5591 | 44.4725 | 44.2547 | 44.1641 | 43.5256 | 31.7414 | 31.7233 | 31.6978 | 31.6415 | 39.7902 | 39.6643 | 39.5344 | 39.3618 | 39.1557 | 38.9364 | 38.3022 | 37.3386 | 37.0836 | 36.3856 | 32.0092 | 31.9993 | 31.9862 | 31.9594 | 40.1726 | 40.1049 | 40.0325 | 39.9399 | 39.8305 | 39.7284 | 39.46 | 39.0072 | 38.5324 | 37.8544
| SPRINGHILL | CT |  |  | 36.0497 | 36.0452 | 36.0401 | 36.0325 | 44.7375 | 44.7075 | 44.6724 | 44.6318 | 44.585 | 44.5591 | 44.4725 | 44.2547 | 44.1641 | 43.5256 | 31.7414 | 31.7233 | 31.6978 | 31.6415 | 39.7902 | 39.6643 | 39.5344 | 39.3618 | 39.1557 | 38.9364 | 38.3022 | 37.3386 | 37.0836 | 36.3856 | 32.0092 | 31.9993 | 31.9862 | 31.9594 | 40.1726 | 40.1049 | 40.0325 | 39.9399 | 39.8305 | 39.7284 | 39.46 | 39.0072 | 38.5324 | 37.8544
| SPRINGHILL | LW |  |  | 36.0563 | 36.0563 | 36.0563 | 36.0563 | 44.7856 | 44.7841 | 44.7818 | 44.7785 | 44.7723 | 44.7709 | 44.7652 | 44.9978 | 44.9754 | 44.9654 | 31.761 | 31.7587 | 31.755 | 31.7459 | 39.8913 | 39.7573 | 39.624 | 39.4912 | 39.3229 | 39.1588 | 38.6271 | 38.2254 | 37.93 | 37.8789 | 32.0209 | 32.02 | 32.0186 | 32.015 | 40.2415 | 40.1879 | 40.1341 | 40.0798 | 40.0098 | 39.9444 | 39.7629 | 39.7956 | 39.4512 | 39.3154
| SPRINGHILL | ST |  |  | 36.0545 | 36.0532 | 36.0521 | 36.0505 | 44.7683 | 44.7536 | 44.7364 | 44.7165 | 44.6935 | 44.686 | 44.6628 | 44.6156 | 44.6571 | 44.5412 | 31.7457 | 31.731 | 31.712 | 31.676 | 39.8493 | 39.7339 | 39.6335 | 39.5186 | 39.3746 | 39.2018 | 38.6746 | 37.9969 | 37.6546 | 37.4484 | 32.0138 | 32.0072 | 31.999 | 31.9839 | 40.2146 | 40.1602 | 40.1103 | 40.053 | 39.9824 | 39.9098 | 39.7078 | 39.4618 | 39.2645 | 38.8717
| SPRINGHILL | SP |  |  | 36.0527 | 36.0507 | 36.0487 | 36.0467 | 44.7764 | 44.776 | 44.7756 | 44.7751 | 44.7746 | 44.7715 | 44.7608 | 44.7519 | 44.6833 | 44.8205 | 31.7567 | 31.7528 | 31.7485 | 31.7439 | 39.9971 | 39.9659 | 39.9306 | 39.8958 | 39.8501 | 39.7868 | 39.5468 | 39.2321 | 38.8936 | 38.8244 | 32.017 | 32.0143 | 32.0114 | 32.0083 | 40.2776 | 40.2651 | 40.2509 | 40.237 | 40.2187 | 40.1919 | 40.091 | 39.9617 | 39.7905 | 39.8629
BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | YES | 6.4582 | 6.4571 | 6.455 | 6.4524 | 6.4454 | 6.4368 | 6.4267 | 6.3222 | 6.0705 | 5.8236 | 4.898 | 3.2172 | 1.2722 | 0.52989 | 6.4765 | 6.4681 | 6.4544 | 6.4249 | 6.3296 | 6.1877 | 6.0448 | 5.9023 | 5.6126 | 5.322 | 4.2328 | 2.4612 | 0.17439 | -0.69812 | 6.5016 | 6.5005 | 6.4981 | 6.4951 | 6.3402 | 6.1055 | 5.8723 | 5.6405 | 5.3461 | 5.0564 | 3.9704 | 2.0813 | -0.19858 | -1.0685
| ST CYRUS | CT |  |  | 6.4582 | 6.4571 | 6.455 | 6.4524 | 6.4454 | 6.4368 | 6.4267 | 6.4152 | 6.3873 | 6.1734 | 5.4421 | 3.9155 | 1.94 | 0.53959 | 6.4765 | 6.4681 | 6.4544 | 6.4249 | 6.3296 | 6.2433 | 6.1564 | 6.0611 | 5.9318 | 5.7489 | 4.8933 | 3.315 | 1.0079 | -0.61101 | 6.5016 | 6.5005 | 6.4981 | 6.4951 | 6.3477 | 6.212 | 6.0763 | 5.9276 | 5.7248 | 5.4748 | 4.6198 | 2.9203 | 0.61738 | -0.99954
| ST CYRUS | LW |  |  | 6.4598 | 6.4598 | 6.4598 | 6.4598 | 6.4589 | 6.4573 | 6.4547 | 6.3222 | 6.0705 | 5.8236 | 4.898 | 3.2172 | 1.2722 | 0.52989 | 6.4849 | 6.4834 | 6.4811 | 6.4753 | 6.3312 | 6.1877 | 6.0448 | 5.9023 | 5.6126 | 5.322 | 4.2328 | 2.4612 | 0.17439 | -0.69812 | 6.5032 | 6.5032 | 6.5032 | 6.5032 | 6.3402 | 6.1055 | 5.8723 | 5.6405 | 5.3461 | 5.0564 | 3.9704 | 2.0813 | -0.19858 | -1.0685
| ST CYRUS | ST |  |  | 6.4594 | 6.4591 | 6.4588 | 6.4585 | 6.4557 | 6.4523 | 6.4482 | 6.4434 | 6.4371 | 6.3668 | 5.6892 | 4.5136 | 2.5854 | 1.1565 | 6.4825 | 6.4793 | 6.4751 | 6.4673 | 6.4017 | 6.3368 | 6.2679 | 6.1843 | 6.0705 | 5.9296 | 5.1662 | 3.8872 | 1.9269 | 0.2497 | 6.5028 | 6.5025 | 6.5022 | 6.5019 | 6.4582 | 6.3538 | 6.2431 | 6.1089 | 5.9258 | 5.6956 | 4.9009 | 3.5644 | 1.4303 | -0.24194
| ST CYRUS | SP |  |  | 6.459 | 6.4586 | 6.4583 | 6.4578 | 6.4578 | 6.4577 | 6.4576 | 6.4575 | 6.4573 | 6.4566 | 6.4538 | 6.2191 | 5.8728 | 5.548 | 6.485 | 6.4842 | 6.4833 | 6.4824 | 6.4656 | 6.4463 | 6.4168 | 6.3878 | 6.3493 | 6.299 | 6.0921 | 5.7864 | 5.3839 | 5.0063 | 6.5024 | 6.5021 | 6.5017 | 6.5013 | 6.5012 | 6.5011 | 6.4818 | 6.4342 | 6.371 | 6.2889 | 5.9506 | 5.5193 | 5.118 | 4.7415
ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 09165377 | NO | 39.2337 | 39.233 | 39.2322 | 39.231 | 39.1744 | 39.1113 | 39.0444 | 38.9709 | 38.8619 | 38.8426 | 38.1093 | 37.5145 | 29.2178 | 27.7903 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 28.932 | 28.932 | 28.932 | 35.6669 | 35.664 | 35.6599 | 35.6509 | 35.5012 | 35.3328 | 35.1922 | 35.0518 | 34.8579 | 34.8216 | 29.1245 | 25.8659 | 24.381 | 22.7153
| ST FERGUS GAS TERM | CT |  |  | 39.2337 | 39.233 | 39.2322 | 39.231 | 39.1885 | 39.1419 | 39.0918 | 39.0381 | 38.9628 | 38.9472 | 38.2343 | 37.5145 | 37.2757 | 28.3296 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 35.6669 | 35.664 | 35.6599 | 35.6509 | 35.5544 | 35.4618 | 35.3662 | 35.2608 | 35.1296 | 35.0492 | 34.1914 | 28.3535 | 26.111 | 23.3781
| ST FERGUS GAS TERM | LW |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.1744 | 39.1113 | 39.0444 | 38.9709 | 38.8619 | 38.8426 | 38.1093 | 37.515 | 29.2178 | 27.7903 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 35.67 | 35.6697 | 35.6692 | 35.6679 | 35.5012 | 35.3328 | 35.1922 | 35.0518 | 34.8579 | 34.8216 | 29.1245 | 25.8659 | 24.381 | 22.7153
| ST FERGUS GAS TERM | ST |  |  | 39.2346 | 39.2344 | 39.2343 | 39.2341 | 39.2054 | 39.1743 | 39.1442 | 39.1096 | 39.0539 | 39.0419 | 38.6734 | 37.6456 | 37.3882 | 27.8858 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.7054 | 28.932 | 28.932 | 28.932 | 35.6694 | 35.6686 | 35.6676 | 35.6659 | 35.5947 | 35.5232 | 35.4523 | 35.3663 | 35.2443 | 35.1687 | 34.6412 | 28.7022 | 25.9499 | 22.8276
| ST FERGUS GAS TERM | SP |  |  | 39.2343 | 39.234 | 39.2337 | 39.2334 | 39.2293 | 39.2254 | 39.2213 | 39.2167 | 39.2091 | 39.2006 | 39.1696 | 39.1414 | 38.776 | 38.639 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35.6696 | 35.6693 | 35.6689 | 35.6685 | 35.6531 | 35.6362 | 35.6125 | 35.5887 | 35.5555 | 35.5123 | 35.3481 | 35.1999 | 34.755 | 34.618
ST FILLANS | ST FILLANS P S | MINIMUM HEADROOM | NN 69422464 | YES | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | CT |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | LW |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | ST |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | SP |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | 30.5057 | 30.5049 | 30.5041 | 30.5028 | 30.4987 | 30.4938 | 30.488 | 30.4814 | 30.474 | 30.4697 | 30.4555 | 30.4227 | 30.8738 | 30.7687 | 28.6638 | 28.6517 | 28.6356 | 28.6046 | 28.5617 | 28.5104 | 28.4346 | 28.3601 | 28.2868 | 28.2575 | 28.172 | 28.0156 | 28.2556 | 27.9424 | 28.4555 | 28.446 | 28.4334 | 28.4093 | 28.3758 | 28.3356 | 28.2764 | 28.2181 | 28.1608 | 28.1378 | 28.071 | 27.9328 | 28.2198 | 27.9529
| ST MACHAR | CT |  |  | 30.5057 | 30.5049 | 30.5041 | 30.5028 | 30.4987 | 30.4938 | 30.488 | 30.4814 | 30.474 | 30.4697 | 30.4555 | 30.4227 | 30.8738 | 30.7687 | 28.67 | 28.6629 | 28.6528 | 28.6292 | 28.6013 | 28.5729 | 28.5442 | 28.4965 | 28.4489 | 28.401 | 28.2576 | 28.0156 | 28.2556 | 27.9424 | 28.4601 | 28.4544 | 28.4463 | 28.4277 | 28.4051 | 28.3819 | 28.3583 | 28.3198 | 28.2811 | 28.2429 | 28.1283 | 27.9328 | 28.2198 | 27.9529
| ST MACHAR | LW |  |  | 30.5068 | 30.5068 | 30.5068 | 30.5068 | 30.5068 | 30.5068 | 30.5068 | 30.5068 | 30.5068 | 30.5068 | 31.012 | 31.012 | 31.012 | 31.012 | 28.673 | 28.6678 | 28.6596 | 28.6391 | 28.6162 | 28.5938 | 28.572 | 28.5506 | 28.5297 | 28.507 | 28.9453 | 28.8375 | 28.729 | 28.6215 | 28.4626 | 28.4586 | 28.4522 | 28.4362 | 28.4185 | 28.4011 | 28.3841 | 28.3674 | 28.3512 | 28.3336 | 28.7868 | 28.703 | 28.6186 | 28.535
| ST MACHAR | ST |  |  | 30.5066 | 30.5065 | 30.5064 | 30.5063 | 30.5053 | 30.5041 | 30.5027 | 30.5012 | 30.4994 | 30.4988 | 30.497 | 30.4941 | 30.984 | 30.9754 | 28.6638 | 28.6517 | 28.6356 | 28.6046 | 28.5617 | 28.5104 | 28.4346 | 28.3601 | 28.2868 | 28.2575 | 28.172 | 28.0355 | 28.3934 | 28.2531 | 28.4555 | 28.446 | 28.4334 | 28.4093 | 28.3758 | 28.3356 | 28.2764 | 28.2181 | 28.1608 | 28.1378 | 28.071 | 27.9641 | 28.3515 | 28.2405
| ST MACHAR | SP |  |  | 30.5065 | 30.5064 | 30.5062 | 30.5061 | 30.5061 | 30.506 | 30.506 | 30.506 | 30.506 | 30.5057 | 30.505 | 30.5045 | 31.0062 | 30.9984 | 28.6761 | 28.6748 | 28.6733 | 28.6717 | 28.6635 | 28.6538 | 28.6334 | 28.6132 | 28.5874 | 28.5758 | 28.5422 | 28.4904 | 28.944 | 28.8912 | 28.465 | 28.4639 | 28.4627 | 28.4614 | 28.4551 | 28.4475 | 28.4317 | 28.416 | 28.3959 | 28.3868 | 28.3606 | 28.3202 | 28.7845 | 28.7417
THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | 6.7181 | 6.7126 | 6.7047 | 6.6871 | 6.6583 | 6.6282 | 6.5968 | 6.5747 | 6.5486 | 6.535 | 6.4936 | 3.6881 | 3.579 | 3.4169 | 5.9489 | 5.9479 | 3.9934 | 3.9005 | 3.7904 | 3.6805 | 3.5705 | 3.5223 | 3.4708 | 3.4295 | 3.3063 | 2.4637 | 2.1925 | 1.8708 | 5.778 | 5.7751 | 5.7711 | 5.7628 | 5.744 | 5.7237 | 5.7019 | 5.683 | 5.6601 | 5.6498 | 3.9687 | 2.9257 | 2.6501 | 2.3242
| ST MARYS | CT |  |  | 6.7181 | 6.7126 | 6.7047 | 6.6871 | 6.6583 | 6.6282 | 6.5968 | 6.5747 | 6.5486 | 6.535 | 6.4936 | 3.6881 | 3.579 | 3.4169 | 5.9489 | 5.9479 | 3.9934 | 3.9005 | 3.7904 | 3.6805 | 3.5705 | 3.5223 | 3.4708 | 3.4295 | 3.3063 | 2.4637 | 2.1925 | 1.8708 | 5.778 | 5.7751 | 5.7711 | 5.7628 | 5.744 | 5.7237 | 5.7019 | 5.683 | 5.6601 | 5.6498 | 3.9687 | 2.9257 | 2.6501 | 2.3242
| ST MARYS | LW |  |  | 6.7243 | 6.724 | 6.7234 | 6.7221 | 6.7116 | 6.701 | 6.6901 | 6.6785 | 6.6626 | 6.6586 | 6.6469 | 3.8057 | 3.7819 | 3.7734 | 5.9506 | 5.9506 | 5.9506 | 5.9506 | 5.9416 | 5.9325 | 5.923 | 5.9129 | 3.9804 | 3.9693 | 3.9364 | 3.277 | 3.2116 | 3.1619 | 5.7815 | 5.7814 | 5.7812 | 5.7806 | 5.771 | 5.7613 | 5.7512 | 5.7405 | 5.7254 | 5.7223 | 5.7133 | 3.2071 | 3.1832 | 3.1735
| ST MARYS | ST |  |  | 6.7219 | 6.7196 | 6.7167 | 6.7112 | 6.6978 | 6.6822 | 6.6698 | 6.6565 | 6.6399 | 6.6332 | 6.6143 | 6.1863 | 6.1016 | 6.0541 | 5.9502 | 5.95 | 5.9498 | 5.9495 | 3.9697 | 3.9134 | 3.8764 | 3.8391 | 3.799 | 3.774 | 3.7022 | 3.2765 | 3.1077 | 2.9761 | 5.7803 | 5.7793 | 5.7779 | 5.7755 | 5.7662 | 5.7557 | 5.7463 | 5.7359 | 5.7223 | 5.7178 | 5.7054 | 3.6101 | 3.5329 | 3.4927
| ST MARYS | SP |  |  | 6.7234 | 6.7227 | 6.722 | 6.7211 | 6.7184 | 6.7153 | 6.7129 | 6.7105 | 6.7071 | 6.7038 | 6.6931 | 6.6809 | 6.6213 | 6.5785 | 5.9498 | 5.9494 | 5.9489 | 5.9485 | 5.9478 | 5.9471 | 5.9465 | 5.9457 | 5.9445 | 5.9426 | 3.9756 | 3.9315 | 3.8416 | 3.7701 | 5.7807 | 5.7802 | 5.7796 | 5.779 | 5.7775 | 5.7758 | 5.7744 | 5.773 | 5.7709 | 5.7684 | 5.7602 | 5.752 | 5.6961 | 5.6568
WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | 29.4337 | 29.4285 | 29.4201 | 29.3993 | 29.3944 | 29.3905 | 29.3866 | 29.3829 | 29.3793 | 29.3753 | 29.3637 | 29.3449 | 29.326 | 29.3072 | 26.2263 | 26.2215 | 26.214 | 26.1953 | 26.1744 | 26.154 | 26.134 | 26.1144 | 26.0953 | 26.0747 | 26.0135 | 25.915 | 25.8159 | 25.7177 | 25.7543 | 25.7502 | 25.7435 | 25.7269 | 25.7085 | 25.6905 | 25.6741 | 25.6741 | 25.672 | 25.6717 | 25.6708 | 25.6688 | 25.6653 | 25.6587
| ST NICHOLAS | CT |  |  | 29.434 | 29.4297 | 29.4233 | 29.4081 | 29.3966 | 29.3936 | 29.3905 | 29.3874 | 29.3843 | 29.3811 | 29.3718 | 29.356 | 29.3388 | 29.3185 | 26.2265 | 26.2226 | 26.2168 | 26.2031 | 26.1883 | 26.1737 | 26.1593 | 26.1447 | 26.1303 | 26.115 | 26.0697 | 25.996 | 25.9205 | 25.8424 | 25.7546 | 25.7511 | 25.746 | 25.7339 | 25.7207 | 25.7078 | 25.695 | 25.6821 | 25.672 | 25.6717 | 25.6708 | 25.6688 | 25.6653 | 25.6587
| ST NICHOLAS | LW |  |  | 29.4337 | 29.4285 | 29.4201 | 29.3993 | 29.3944 | 29.3905 | 29.3866 | 29.3829 | 29.3793 | 29.3753 | 29.3637 | 29.3449 | 29.326 | 29.3072 | 26.2263 | 26.2215 | 26.214 | 26.1953 | 26.1744 | 26.154 | 26.134 | 26.1144 | 26.0953 | 26.0747 | 26.0135 | 25.915 | 25.8159 | 25.7177 | 25.7543 | 25.7502 | 25.7435 | 25.7269 | 25.7085 | 25.6905 | 25.6741 | 25.6741 | 25.6741 | 25.6741 | 25.6741 | 25.6741 | 25.6741 | 25.6741
| ST NICHOLAS | ST |  |  | 29.4346 | 29.431 | 29.4262 | 29.4169 | 29.4043 | 29.3964 | 29.3921 | 29.3879 | 29.3838 | 29.3819 | 29.3762 | 29.3672 | 29.3573 | 29.348 | 26.2271 | 26.2238 | 26.2194 | 26.2111 | 26.1997 | 26.1861 | 26.1643 | 26.1429 | 26.122 | 26.112 | 26.083 | 26.037 | 25.991 | 25.9455 | 25.7551 | 25.7522 | 25.7483 | 25.7409 | 25.7309 | 25.7189 | 25.6995 | 25.6806 | 25.6734 | 25.6734 | 25.6732 | 25.6729 | 25.6715 | 25.6707
| ST NICHOLAS | SP |  |  | 29.4381 | 29.4376 | 29.4371 | 29.4365 | 29.433 | 29.4289 | 29.4216 | 29.4144 | 29.4052 | 29.4007 | 29.3964 | 29.3929 | 29.3897 | 29.3867 | 26.2303 | 26.2298 | 26.2293 | 26.2287 | 26.2256 | 26.2219 | 26.2154 | 26.2089 | 26.2006 | 26.1965 | 26.1849 | 26.1666 | 26.1498 | 26.1342 | 25.7579 | 25.7575 | 25.757 | 25.7565 | 25.7538 | 25.7505 | 25.7447 | 25.739 | 25.7316 | 25.7281 | 25.7178 | 25.7017 | 25.6868 | 25.6741
ARDMORE | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | 1.418 | 1.4172 | 1.4161 | 1.4138 | 1.3908 | 1.3673 | 1.3422 | 1.3157 | 1.2789 | 1.2718 | 1.2553 | 0.90581 | 0.77206 | 0.66562 | 1.3897 | 1.3889 | 1.3878 | 1.3853 | 1.3612 | 1.3355 | 0.99001 | 0.96358 | 0.92675 | 0.91966 | 0.90318 | 0.78314 | 0.63913 | 0.52259 | 1.6268 | 1.6264 | 1.6261 | 1.6254 | 1.6033 | 1.5794 | 1.554 | 0.98414 | 0.94731 | 0.94023 | 0.92375 | 0.82256 | 0.74523 | 0.62889
| STOCKINISH | CT |  |  | 1.418 | 1.4172 | 1.4161 | 1.4138 | 1.3908 | 1.3673 | 1.3422 | 1.3157 | 1.2789 | 1.2718 | 1.2553 | 0.90581 | 0.77206 | 0.66562 | 1.3897 | 1.3889 | 1.3878 | 1.3853 | 1.3612 | 1.3355 | 0.99001 | 0.96358 | 0.92675 | 0.91966 | 0.90318 | 0.78314 | 0.63913 | 0.52259 | 1.6268 | 1.6264 | 1.6261 | 1.6254 | 1.6033 | 1.5794 | 1.554 | 0.98414 | 0.94731 | 0.94023 | 0.92375 | 0.82256 | 0.74523 | 0.62889
| STOCKINISH | LW |  |  | 1.4184 | 1.4177 | 1.4167 | 1.4141 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.39 | 1.3894 | 1.3883 | 1.3856 | 1.3825 | 1.3796 | 1.3767 | 1.3739 | 1.3711 | 1.3681 | 1.3592 | 1.345 | 1.3306 | 1.3164 | 1.6271 | 1.627 | 1.6269 | 1.6265 | 1.6261 | 1.6257 | 1.6252 | 1.6249 | 1.6245 | 1.624 | 1.6228 | 1.6208 | 1.6188 | 1.6168
| STOCKINISH | ST |  |  | 1.4186 | 1.4183 | 1.4178 | 1.417 | 1.4024 | 1.3867 | 1.3722 | 1.3567 | 1.3318 | 1.3266 | 1.3138 | 1.2638 | 0.96515 | 0.90527 | 1.3903 | 1.3899 | 1.3895 | 1.3886 | 1.374 | 1.3582 | 1.3422 | 1.3244 | 0.97959 | 0.97444 | 0.96161 | 0.9116 | 0.83922 | 0.7801 | 1.6271 | 1.6271 | 1.627 | 1.6268 | 1.6132 | 1.5987 | 1.5846 | 1.5688 | 1.5435 | 0.99501 | 0.98217 | 0.93216 | 0.85979 | 0.83608
| STOCKINISH | SP |  |  | 1.4189 | 1.4189 | 1.4188 | 1.4188 | 1.4185 | 1.4181 | 1.4174 | 1.4166 | 1.4157 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.3906 | 1.3906 | 1.3905 | 1.3905 | 1.3902 | 1.3898 | 1.389 | 1.3882 | 1.3873 | 1.3849 | 1.3782 | 1.3677 | 1.3579 | 1.3486 | 1.6272 | 1.6272 | 1.6272 | 1.6272 | 1.6271 | 1.6271 | 1.627 | 1.6269 | 1.6267 | 1.6264 | 1.6255 | 1.624 | 1.6226 | 1.6213
PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | 0.19517 | 0.049586 | -0.097715 | -0.2917 | -0.49443 | -0.70575 | -0.92849 | -1.1675 | -1.4742 | -1.599 | -1.8099 | -2.9137 | -5.2564 | -7.3988 | 0.21723 | 0.1003 | -0.015979 | -0.16948 | -0.33298 | -0.50573 | -0.69111 | -0.89401 | -1.1617 | -1.2641 | -1.4414 | -2.292 | -4.3141 | -6.0118 | 0.18716 | 0.040061 | -0.1094 | -0.30555 | -0.51046 | -0.72418 | -0.94934 | -1.1908 | -1.5001 | -1.6272 | -1.8422 | -2.9371 | -5.2873 | -7.4418
| STONEFIELD | CT |  |  | 0.19517 | 0.049586 | -0.097715 | -0.2917 | -0.49443 | -0.70575 | -0.92849 | -1.1675 | -1.4742 | -1.599 | -1.8099 | -2.5801 | -3.1866 | -3.574 | 0.21723 | 0.1003 | -0.015979 | -0.16948 | -0.33298 | -0.50573 | -0.69111 | -0.89401 | -1.1617 | -1.2641 | -1.4414 | -2.1555 | -2.7032 | -3.0305 | 0.18716 | 0.040061 | -0.1094 | -0.30555 | -0.51046 | -0.72418 | -0.94934 | -1.1908 | -1.5001 | -1.6272 | -1.8422 | -2.619 | -3.2318 | -3.6253
| STONEFIELD | LW |  |  | 0.33143 | 0.31228 | 0.302 | 0.28855 | 0.27252 | 0.25496 | 0.23601 | 0.19939 | 0.12863 | 0.091639 | -0.045653 | -0.3879 | -0.75323 | -1.0397 | 0.32753 | 0.31321 | 0.30348 | 0.2918 | 0.27865 | 0.26428 | 0.24881 | 0.21591 | 0.14963 | 0.11731 | -0.0052892 | -0.32113 | -0.65406 | -0.90254 | 0.3222 | 0.30727 | 0.29537 | 0.28112 | 0.2651 | 0.24757 | 0.22868 | 0.19196 | 0.121 | 0.083813 | -0.054102 | -0.39745 | -0.76414 | -1.0524
| STONEFIELD | ST |  |  | 0.33567 | 0.32835 | 0.31286 | 0.3034 | 0.29372 | 0.28316 | 0.27009 | 0.24932 | 0.19847 | 0.17579 | 0.097559 | -0.76582 | -3.7871 | -7.3988 | 0.33002 | 0.3258 | 0.3138 | 0.30489 | 0.29613 | 0.28752 | 0.2768 | 0.25832 | 0.20977 | 0.18935 | 0.11882 | -0.6187 | -3.1034 | -6.0118 | 0.32664 | 0.31902 | 0.30799 | 0.29707 | 0.28635 | 0.27583 | 0.26277 | 0.242 | 0.19117 | 0.1685 | 0.089925 | -0.77953 | -3.8136 | -7.4418
| STONEFIELD | SP |  |  | 0.33082 | 0.31286 | 0.30344 | 0.29397 | 0.27832 | 0.26252 | 0.2468 | 0.22996 | 0.20838 | 0.18484 | 0.091471 | -2.9137 | -5.2564 | -7.2423 | 0.32718 | 0.31414 | 0.30552 | 0.29687 | 0.284 | 0.27128 | 0.25858 | 0.24472 | 0.22607 | 0.20543 | 0.12051 | -2.292 | -4.3141 | -5.9476 | 0.3216 | 0.30835 | 0.29776 | 0.28712 | 0.27119 | 0.25523 | 0.23937 | 0.22239 | 0.20067 | 0.177 | 0.08322 | -2.9371 | -5.2873 | -7.2814
FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | YES | 31.5187 | 31.5133 | 31.5068 | 31.4976 | 31.0103 | 30.3435 | 29.6421 | 28.8771 | 28.8771 | 28.6821 | 23.6105 | 19.6638 | 17.1192 | 15.321 | 30.4374 | 30.4265 | 30.4118 | 30.3829 | 29.9256 | 29.2554 | 28.5506 | 23.5815 | 23.0372 | 22.7237 | 21.8786 | 16.9269 | 14.2084 | 12.2391 | 29.2141 | 29.1992 | 29.1784 | 29.135 | 28.6998 | 28.027 | 23.8068 | 23.0418 | 23.0418 | 22.8468 | 22.2681 | 17.2352 | 14.5273 | 12.5683
| STONEHAVEN | CT |  |  | 31.5187 | 31.5133 | 31.5068 | 31.4976 | 31.1358 | 30.7401 | 30.2221 | 29.6717 | 28.8993 | 28.7481 | 23.8913 | 19.6638 | 17.1192 | 15.321 | 30.4374 | 30.4265 | 30.4118 | 30.3829 | 30 | 29.5834 | 29.0449 | 23.9595 | 23.0372 | 22.7237 | 21.8786 | 16.9269 | 14.2084 | 12.2391 | 29.2141 | 29.1992 | 29.1784 | 29.135 | 28.7366 | 28.3047 | 27.7511 | 23.8364 | 23.064 | 22.9128 | 22.4761 | 17.2352 | 14.5273 | 12.5683
| STONEHAVEN | LW |  |  | 31.5267 | 31.5267 | 31.5267 | 31.5267 | 31.0103 | 30.3435 | 29.6421 | 28.8771 | 28.8771 | 28.6821 | 23.6105 | 20.862 | 19.5796 | 19.1106 | 30.4509 | 30.45 | 30.4488 | 30.4456 | 29.9256 | 29.2554 | 28.5506 | 23.5815 | 23.5815 | 23.3866 | 22.8079 | 20.4791 | 19.0092 | 17.7612 | 29.2315 | 29.2301 | 29.2279 | 29.2224 | 28.6998 | 28.027 | 23.8068 | 23.0418 | 23.0418 | 22.8468 | 22.2681 | 19.6142 | 18.3318 | 17.8628
| STONEHAVEN | ST |  |  | 31.5244 | 31.523 | 31.5215 | 31.5197 | 31.2743 | 31.0081 | 30.7498 | 30.4539 | 29.983 | 29.8819 | 29.6197 | 23.4048 | 20.2889 | 19.217 | 30.444 | 30.438 | 30.4304 | 30.4169 | 30.1555 | 29.8703 | 29.6004 | 29.2932 | 28.8113 | 28.7006 | 23.7028 | 21.0386 | 17.7374 | 16.5567 | 29.2213 | 29.212 | 29.2 | 29.1778 | 28.9047 | 28.6055 | 28.3271 | 28.0116 | 27.5216 | 27.4038 | 23.7844 | 21.4885 | 17.9497 | 16.7756
| STONEHAVEN | SP |  |  | 31.5218 | 31.5192 | 31.5165 | 31.5137 | 31.4874 | 31.4617 | 31.4352 | 31.4054 | 31.3563 | 31.2999 | 31.0934 | 30.9045 | 22.8021 | 19.7446 | 30.4458 | 30.4426 | 30.4392 | 30.4357 | 30.3712 | 30.3019 | 30.2124 | 30.1208 | 23.679 | 23.5805 | 23.253 | 22.8748 | 19.4481 | 15.9242 | 29.2264 | 29.2228 | 29.2189 | 29.2148 | 29.1224 | 29.0209 | 28.9492 | 28.9194 | 28.8703 | 28.8139 | 23.8683 | 23.4927 | 20.0793 | 16.5896
STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 67734109 | NO | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.6344 | 8.6343 | 8.6343 | 8.6342 | 8.6341 | 8.6339 | 8.6338 | 8.6337 | 8.6336 | 8.6334 | 8.6331 | 8.6325 | 8.6319 | 8.6312 | 8.8412 | 8.8412 | 8.8411 | 8.841 | 8.8409 | 8.8408 | 8.8407 | 8.8406 | 8.8405 | 8.8404 | 8.8401 | 8.8397 | 8.8392 | 8.8387
| STONEYHILL | CT |  |  | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.6344 | 8.6343 | 8.6343 | 8.6342 | 8.6341 | 8.6341 | 8.634 | 8.6339 | 8.6338 | 8.6337 | 8.6335 | 8.633 | 8.6326 | 8.6322 | 8.8412 | 8.8412 | 8.8411 | 8.8411 | 8.841 | 8.8409 | 8.8409 | 8.8408 | 8.8407 | 8.8407 | 8.8404 | 8.8401 | 8.8398 | 8.8394
| STONEYHILL | LW |  |  | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.6344 | 8.6343 | 8.6343 | 8.6342 | 8.6341 | 8.6339 | 8.6338 | 8.6337 | 8.6336 | 8.6334 | 8.6331 | 8.6325 | 8.6319 | 8.6312 | 8.8412 | 8.8412 | 8.8411 | 8.841 | 8.8409 | 8.8408 | 8.8407 | 8.8406 | 8.8405 | 8.8404 | 8.8401 | 8.8397 | 8.8392 | 8.8387
| STONEYHILL | ST |  |  | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.6344 | 8.6344 | 8.6344 | 8.6343 | 8.6343 | 8.6342 | 8.6341 | 8.6341 | 8.634 | 8.634 | 8.6338 | 8.6335 | 8.6333 | 8.633 | 8.8412 | 8.8412 | 8.8412 | 8.8411 | 8.8411 | 8.841 | 8.841 | 8.841 | 8.8409 | 8.8409 | 8.8407 | 8.8405 | 8.8403 | 8.8401
| STONEYHILL | SP |  |  | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.9411 | 8.6344 | 8.6344 | 8.6344 | 8.6344 | 8.6344 | 8.6344 | 8.6343 | 8.6343 | 8.6343 | 8.6343 | 8.6342 | 8.6341 | 8.634 | 8.6339 | 8.8412 | 8.8412 | 8.8412 | 8.8412 | 8.8412 | 8.8412 | 8.8412 | 8.8411 | 8.8411 | 8.8411 | 8.841 | 8.841 | 8.8409 | 8.8408
PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | 30.4124 | 30.3759 | 30.339 | 30.168 | 30.0104 | 22.8254 | 22.3156 | 21.7878 | 21.2419 | 21.0326 | 20.4048 | 19.0153 | 17.4072 | 16.7644 | 32.0044 | 31.9648 | 31.923 | 31.7613 | 31.5683 | 31.0612 | 30.5364 | 29.9939 | 29.4336 | 29.2088 | 28.535 | 27.0343 | 21.6034 | 20.8656 | 31.7939 | 31.7525 | 31.708 | 31.5514 | 31.3386 | 30.8239 | 22.0794 | 21.5516 | 21.0057 | 20.7964 | 20.1686 | 18.7792 | 17.171 | 16.5283
| STONEYWOOD T1&T2 | CT |  |  | 30.5188 | 30.49 | 30.4606 | 30.4558 | 30.3123 | 30.0457 | 23.1211 | 22.8804 | 22.5656 | 22.4089 | 21.9372 | 19.1729 | 17.4072 | 16.7644 | 32.1068 | 32.0716 | 32.0326 | 32.0052 | 31.8372 | 31.5467 | 31.2802 | 31.0132 | 30.6725 | 30.4878 | 29.9331 | 27.0343 | 21.6034 | 20.8656 | 31.8939 | 31.8552 | 31.8109 | 31.7706 | 31.5889 | 31.2849 | 31.0052 | 30.7252 | 30.3718 | 30.1907 | 21.7011 | 18.9367 | 17.171 | 16.5283
| STONEYWOOD T1&T2 | LW |  |  | 30.4124 | 30.3759 | 30.339 | 30.3373 | 30.0104 | 22.8254 | 22.3156 | 21.7878 | 21.2419 | 21.0326 | 20.4048 | 19.0153 | 17.4901 | 16.8413 | 32.0044 | 31.9648 | 31.923 | 31.9089 | 31.5683 | 31.0612 | 30.5364 | 29.9939 | 29.4336 | 29.2088 | 28.535 | 27.0714 | 21.7085 | 21.0533 | 31.7939 | 31.7525 | 31.708 | 31.6869 | 31.3386 | 30.8239 | 22.0794 | 21.5516 | 21.0057 | 20.7964 | 20.1686 | 18.7792 | 17.2539 | 16.6051
| STONEYWOOD T1&T2 | ST |  |  | 30.6288 | 30.6101 | 30.5914 | 30.5902 | 30.4969 | 30.4029 | 22.9266 | 22.1436 | 22.0501 | 21.7422 | 20.8186 | 19.2433 | 18.172 | 17.6268 | 32.2209 | 32.1997 | 32.1775 | 32.1699 | 32.0676 | 31.9631 | 31.1563 | 30.3497 | 30.233 | 29.9067 | 28.9294 | 27.2679 | 26.1117 | 21.8342 | 32.0103 | 31.9877 | 31.9637 | 31.9523 | 31.8451 | 31.7346 | 30.916 | 21.9074 | 21.8139 | 21.506 | 20.5825 | 19.0071 | 17.9358 | 17.3906
| STONEYWOOD T1&T2 | SP |  |  | 30.7373 | 30.7281 | 30.7188 | 30.168 | 30.1224 | 30.0768 | 30.0307 | 29.9845 | 23.2438 | 22.9978 | 22.26 | 20.9761 | 20.1249 | 19.8157 | 32.3319 | 32.3222 | 32.3125 | 31.7613 | 31.7132 | 31.6645 | 31.6115 | 31.5586 | 31.5036 | 31.2503 | 30.4913 | 29.1743 | 28.2923 | 27.9541 | 32.1227 | 32.1129 | 32.103 | 31.5514 | 31.5019 | 31.4515 | 31.3947 | 31.338 | 31.278 | 31.0212 | 22.0238 | 20.7399 | 19.8888 | 19.5795
PERSLEY | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | 9.6355 | 9.6175 | 9.5994 | 9.5132 | 9.437 | 9.1911 | 8.9362 | 8.6723 | 8.3994 | 8.2947 | 7.9808 | 7.2861 | 6.482 | 9.1443 | 8.9269 | 8.9089 | 8.8908 | 8.8046 | 8.7284 | 8.4825 | 8.2276 | 7.9637 | 7.6908 | 7.5861 | 7.2722 | 6.5775 | 5.7734 | 8.4357 | 11.0883 | 11.0702 | 11.0522 | 10.966 | 10.875 | 10.6181 | 10.3524 | 10.0779 | 9.7947 | 9.6789 | 9.332 | 8.5232 | 7.543 | 10.5665
| STONEYWOOD T3 | CT |  |  | 9.6891 | 9.6751 | 9.6611 | 9.6603 | 9.5903 | 9.4588 | 9.339 | 9.2186 | 9.0612 | 8.9829 | 8.7471 | 7.3649 | 6.482 | 9.3508 | 8.9804 | 8.9665 | 8.9525 | 8.9517 | 8.8817 | 8.7502 | 8.6304 | 8.51 | 8.3526 | 8.2743 | 8.0384 | 6.6563 | 5.7734 | 8.6422 | 11.1418 | 11.1278 | 11.1106 | 11.0913 | 11.0012 | 10.85 | 10.7109 | 10.5716 | 10.3957 | 10.2972 | 10.0018 | 8.5232 | 7.543 | 10.735
| STONEYWOOD T3 | LW |  |  | 9.6355 | 9.6175 | 9.5994 | 9.5994 | 9.437 | 9.1911 | 8.9362 | 8.6723 | 8.3994 | 8.2947 | 7.9808 | 7.2861 | 6.5235 | 9.1443 | 8.9269 | 8.9089 | 8.8908 | 8.8908 | 8.7284 | 8.4825 | 8.2276 | 7.9637 | 7.6908 | 7.5861 | 7.2722 | 6.5775 | 5.8149 | 8.4357 | 11.0883 | 11.0702 | 11.0522 | 11.0487 | 10.875 | 10.6181 | 10.3524 | 10.0779 | 9.7947 | 9.6789 | 9.332 | 8.5841 | 7.768 | 10.5665
| STONEYWOOD T3 | ST |  |  | 9.7437 | 9.7346 | 9.7255 | 9.7254 | 9.6793 | 9.6331 | 9.2418 | 8.8502 | 8.8035 | 8.6495 | 8.1878 | 7.4001 | 6.8644 | 9.1932 | 9.0351 | 9.026 | 9.0169 | 9.0168 | 8.9707 | 8.9245 | 8.5331 | 8.1416 | 8.0949 | 7.9409 | 7.4791 | 6.6915 | 6.1558 | 8.4846 | 11.1964 | 11.1873 | 11.1782 | 11.1781 | 11.1278 | 11.0729 | 10.6643 | 10.2558 | 10.1925 | 10.0253 | 9.525 | 8.6755 | 8.0789 | 10.6097
| STONEYWOOD T3 | SP |  |  | 9.7978 | 9.7932 | 9.7886 | 9.5132 | 9.4907 | 9.4681 | 9.4455 | 9.4229 | 9.4003 | 9.2774 | 8.9084 | 8.2665 | 7.8409 | 9.4533 | 9.0892 | 9.0846 | 9.08 | 8.8046 | 8.782 | 8.7595 | 8.7369 | 8.7143 | 8.6917 | 8.5687 | 8.1998 | 7.5579 | 7.1323 | 8.7447 | 11.2505 | 11.2459 | 11.2413 | 10.966 | 10.9434 | 10.9208 | 10.8982 | 10.8741 | 10.8444 | 10.7162 | 10.3321 | 9.6665 | 9.2187 | 10.9037
CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | 1.5771 | 1.5764 | 1.5612 | 1.5457 | 1.5271 | 1.5048 | 1.4149 | 0.94928 | 0.81421 | 0.76227 | 0.63872 | -0.57417 | -0.89515 | -1.152 | 1.2634 | 1.2627 | 1.2529 | 1.2427 | 1.2296 | 0.96847 | 0.8592 | 0.75797 | 0.6272 | 0.57954 | 0.46022 | -0.6082 | -0.92028 | -1.1687 | 1.4026 | 1.3989 | 1.3819 | 1.3655 | 1.3461 | 1.3227 | 0.905 | 0.79553 | 0.6556 | 0.59849 | 0.46149 | -0.75554 | -1.0955 | -1.371
| STRACHUR | CT |  |  | 1.5771 | 1.5764 | 1.5612 | 1.5457 | 1.5271 | 1.5048 | 1.4149 | 0.94928 | 0.81421 | 0.76227 | 0.63872 | -0.57417 | -0.89515 | -1.152 | 1.2634 | 1.2627 | 1.2529 | 1.2427 | 1.2296 | 0.96847 | 0.8592 | 0.75797 | 0.6272 | 0.57954 | 0.46022 | -0.6082 | -0.92028 | -1.1687 | 1.4026 | 1.3989 | 1.3819 | 1.3655 | 1.3461 | 1.3227 | 0.905 | 0.79553 | 0.6556 | 0.59849 | 0.46149 | -0.75554 | -1.0955 | -1.371
| STRACHUR | LW |  |  | 1.5781 | 1.5781 | 1.5781 | 1.5781 | 1.5781 | 1.5781 | 1.4837 | 1.3824 | 0.85758 | 0.83248 | 0.76061 | -0.14158 | -0.28744 | -0.35595 | 1.2645 | 1.2645 | 1.2645 | 1.2645 | 1.2645 | 1.2645 | 0.94301 | 0.8417 | 0.69596 | 0.67087 | 0.599 | -0.23147 | -0.37997 | -0.45108 | 1.4065 | 1.406 | 1.4051 | 1.4031 | 1.4009 | 1.3996 | 0.97166 | 0.87035 | 0.72461 | 0.69952 | 0.62765 | -0.26356 | -0.41094 | -0.48376
| STRACHUR | ST |  |  | 1.5779 | 1.5777 | 1.5775 | 1.5773 | 1.5754 | 1.5732 | 1.5707 | 1.5678 | 1.5645 | 1.5634 | 1.5601 | 0.72877 | 0.64672 | 0.57715 | 1.2642 | 1.264 | 1.2638 | 1.2636 | 1.2617 | 1.2595 | 1.257 | 1.2541 | 1.2508 | 0.99854 | 0.95803 | 0.56147 | 0.47409 | 0.39922 | 1.4046 | 1.4026 | 1.4 | 1.3988 | 1.3969 | 1.3947 | 1.3922 | 1.3892 | 1.386 | 1.3849 | 1.3816 | 0.58465 | 0.49522 | 0.41832
| STRACHUR | SP |  |  | 1.5775 | 1.5772 | 1.5769 | 1.5766 | 1.5765 | 1.5764 | 1.5764 | 1.5763 | 1.5762 | 1.5757 | 1.5741 | 1.5728 | 1.5646 | 1.5468 | 1.2639 | 1.2635 | 1.2632 | 1.2629 | 1.2628 | 1.2628 | 1.2627 | 1.2626 | 1.2625 | 1.2621 | 1.2604 | 1.2591 | 1.2509 | 0.98497 | 1.406 | 1.4054 | 1.4048 | 1.4041 | 1.4022 | 1.3999 | 1.3985 | 1.3978 | 1.3977 | 1.3972 | 1.3956 | 1.3943 | 1.3861 | 1.3683
TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | NO | 3.4156 | 3.3006 | 3.1898 | 3.0448 | 2.8913 | 2.4338 | 2.2461 | 2.0416 | 1.7824 | 1.6789 | 1.4966 | -0.053066 | -3.21 | -7.6853 | 3.001 | 2.9283 | 2.8581 | 2.4411 | 2.2992 | 2.1497 | 1.9892 | 1.8092 | 1.5763 | 1.4849 | 1.3151 | -0.034501 | -2.6346 | -6.2477 | 2.3743 | 2.2457 | 2.1212 | 1.9565 | 1.7837 | 1.6043 | 1.4151 | 1.2083 | 0.94672 | 0.8406 | 0.65009 | -0.914 | -4.0888 | -8.5927
| STRATHDON | CT |  |  | 3.4156 | 3.3006 | 3.1898 | 3.0448 | 2.8913 | 2.4338 | 2.2461 | 2.0416 | 1.7824 | 1.6789 | 1.4966 | -0.053066 | -3.21 | -7.6853 | 3.001 | 2.9283 | 2.8581 | 2.4411 | 2.2992 | 2.1497 | 1.9892 | 1.8092 | 1.5763 | 1.4849 | 1.3151 | -0.034501 | -2.6346 | -6.2477 | 2.3743 | 2.2457 | 2.1212 | 1.9565 | 1.7837 | 1.6043 | 1.4151 | 1.2083 | 0.94672 | 0.8406 | 0.65009 | -0.914 | -4.0888 | -8.5927
| STRATHDON | LW |  |  | 3.52 | 3.5104 | 3.5012 | 3.4905 | 3.4785 | 3.4653 | 3.451 | 3.4209 | 3.3618 | 3.3327 | 3.2229 | 2.8753 | 2.2337 | 1.9718 | 3.0669 | 3.0607 | 3.0546 | 3.0473 | 3.039 | 3.03 | 3.0203 | 2.9953 | 2.9421 | 2.9192 | 2.829 | 2.149 | 1.8378 | 1.605 | 2.4896 | 2.4775 | 2.4646 | 2.4462 | 2.4254 | 2.4035 | 2.3805 | 2.3419 | 2.2742 | 2.2359 | 2.0983 | 1.6989 | 1.3567 | 1.0884
| STRATHDON | ST |  |  | 3.5236 | 3.5173 | 3.5109 | 3.5024 | 3.4942 | 3.4861 | 3.4763 | 3.4596 | 3.4165 | 3.3982 | 3.3348 | 0.54955 | -2.0431 | -5.0478 | 3.0693 | 3.0652 | 3.0611 | 3.0555 | 3.05 | 3.0447 | 3.0379 | 3.0241 | 2.984 | 2.9684 | 2.9148 | 0.56696 | -1.5794 | -4.0131 | 2.4944 | 2.4866 | 2.4785 | 2.467 | 2.4551 | 2.4428 | 2.4259 | 2.4022 | 2.3521 | 2.3263 | 2.2407 | -0.29903 | -2.9075 | -5.9308
| STRATHDON | SP |  |  | 3.5194 | 3.5109 | 3.5025 | 3.494 | 3.4814 | 3.469 | 3.4568 | 3.4435 | 3.426 | 3.4067 | 3.3282 | 0.3981 | -1.6831 | -3.4425 | 3.0667 | 3.0613 | 3.056 | 3.0506 | 3.0426 | 3.0347 | 3.0268 | 3.0178 | 3.0045 | 2.9892 | 2.9226 | 0.50512 | -1.2971 | -2.7493 | 2.4905 | 2.481 | 2.4715 | 2.4619 | 2.4474 | 2.4328 | 2.4175 | 2.4011 | 2.38 | 2.357 | 2.2677 | -0.44222 | -2.5319 | -4.3002
STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | 6.6433 | 6.6316 | 6.6144 | 6.5743 | 6.1961 | 5.8703 | 5.545 | 5.1681 | 4.6094 | 4.571 | 3.0582 | 1.088 | 0.65002 | -0.11089 | 4.8942 | 4.8793 | 4.8572 | 4.8056 | 4.3186 | 3.9006 | 3.4841 | 3.0014 | 2.2855 | 2.2388 | 0.92108 | -0.91638 | -1.381 | -2.3942 | 4.8943 | 4.8819 | 4.8636 | 4.8209 | 4.4182 | 4.0717 | 3.7258 | 3.2167 | 2.4607 | 2.4119 | 0.84982 | -1.2552 | -1.7446 | -2.8222
| STRICHEN | CT |  |  | 6.6433 | 6.6316 | 6.6144 | 6.5743 | 6.1961 | 5.8703 | 5.545 | 5.1681 | 4.6094 | 4.571 | 3.0582 | 1.088 | 0.65002 | 0.36166 | 4.8942 | 4.8793 | 4.8572 | 4.8056 | 4.3186 | 3.9006 | 3.4841 | 3.0014 | 2.2855 | 2.2388 | 0.92108 | -0.91638 | -1.381 | -1.7088 | 4.8943 | 4.8819 | 4.8636 | 4.8209 | 4.4182 | 4.0717 | 3.7258 | 3.2167 | 2.4607 | 2.4119 | 0.84982 | -1.2552 | -1.7446 | -2.0825
| STRICHEN | LW |  |  | 6.6547 | 6.6527 | 6.6495 | 6.6415 | 6.613 | 6.5805 | 6.5435 | 6.5004 | 6.4349 | 6.4149 | 4.9493 | 2.9288 | 2.6449 | -0.11089 | 4.9086 | 4.906 | 4.9018 | 4.8914 | 4.8602 | 4.8251 | 4.7855 | 4.74 | 4.672 | 4.6494 | 3.3955 | 1.4562 | 1.173 | -2.3942 | 4.9064 | 4.9042 | 4.9008 | 4.8923 | 4.8632 | 4.8301 | 4.7925 | 4.7489 | 4.6828 | 4.6622 | 3.1095 | 0.96916 | 0.67716 | -2.8222
| STRICHEN | ST |  |  | 6.6519 | 6.6479 | 6.6425 | 6.6323 | 6.3254 | 6.0325 | 5.733 | 5.3553 | 4.8113 | 4.7871 | 4.0166 | 2.9395 | 2.5955 | 2.4644 | 4.905 | 4.8999 | 4.8929 | 4.8798 | 4.4833 | 4.1056 | 3.7195 | 3.2324 | 2.5315 | 2.5019 | 1.8253 | 0.78291 | 0.42048 | 0.2643 | 4.9034 | 4.8991 | 4.8934 | 4.8825 | 4.5555 | 4.2435 | 3.9245 | 3.4588 | 2.718 | 2.687 | 1.8873 | 0.703 | 0.32687 | 0.16431
| STRICHEN | SP |  |  | 6.6552 | 6.6543 | 6.6531 | 6.6519 | 6.5719 | 6.4806 | 6.3424 | 6.2051 | 6.0223 | 5.7789 | 4.7438 | 3.4473 | 2.167 | 1.0986 | 4.9094 | 4.9084 | 4.9069 | 4.9054 | 4.8018 | 4.6832 | 4.5034 | 4.3251 | 4.0879 | 3.772 | 2.4286 | 0.74522 | -0.86735 | -2.2472 | 4.9069 | 4.906 | 4.9048 | 4.9035 | 4.8182 | 4.7207 | 4.5732 | 4.4266 | 4.2316 | 3.9718 | 2.606 | 0.82398 | -0.87331 | -2.3326
THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | YES | 19.4311 | 19.4128 | 19.3864 | 19.3172 | 19.2226 | 19.118 | 18.9726 | 18.8191 | 18.6197 | 18.5631 | 18.4061 | 17.6194 | 14.1726 | 13.6484 | 18.3029 | 18.2838 | 18.2563 | 18.1728 | 18.0122 | 17.8432 | 17.6687 | 17.4877 | 13.616 | 13.5594 | 13.4024 | 12.2166 | 11.507 | 10.813 | 13.32 | 13.3182 | 13.3164 | 13.2944 | 13.1782 | 13.0527 | 12.9239 | 12.7868 | 12.5969 | 12.5403 | 12.3833 | 11.6422 | 11.3266 | 11.021
| STROMNESS | CT |  |  | 19.4311 | 19.4128 | 19.3864 | 19.3172 | 19.2226 | 19.1184 | 19.0077 | 18.89 | 18.7396 | 18.686 | 18.545 | 17.6194 | 14.1726 | 13.6484 | 18.3029 | 18.2838 | 18.2563 | 18.1728 | 18.0122 | 17.8432 | 17.6687 | 17.4877 | 13.736 | 13.6824 | 13.4547 | 12.2166 | 11.507 | 10.813 | 13.32 | 13.3182 | 13.3164 | 13.2944 | 13.1998 | 13.0957 | 12.985 | 12.8673 | 12.7169 | 12.6633 | 12.5223 | 11.6422 | 11.3266 | 11.021
| STROMNESS | LW |  |  | 19.4479 | 19.4439 | 19.4377 | 19.4005 | 19.2605 | 19.118 | 18.9726 | 18.8191 | 18.6197 | 18.5631 | 18.4061 | 17.6402 | 17.4448 | 17.336 | 18.3204 | 18.3162 | 18.3097 | 18.2718 | 18.131 | 17.9877 | 17.8414 | 17.6872 | 13.616 | 13.5594 | 13.4024 | 12.8688 | 12.6734 | 12.5646 | 13.3224 | 13.3224 | 13.3224 | 13.3008 | 13.1782 | 13.0527 | 12.9239 | 12.7868 | 12.5969 | 12.5403 | 12.3833 | 11.663 | 11.4676 | 11.3588
| STROMNESS | ST |  |  | 19.4491 | 19.4469 | 19.444 | 19.4268 | 19.3593 | 19.2862 | 19.1854 | 19.079 | 18.9692 | 18.9367 | 18.8653 | 18.4386 | 18.1403 | 18.0316 | 18.3216 | 18.3193 | 18.3164 | 18.2989 | 18.2311 | 18.1576 | 18.0551 | 17.9469 | 17.8061 | 17.7292 | 17.5285 | 13.551 | 13.0672 | 12.712 | 13.322 | 13.3217 | 13.3214 | 13.3091 | 13.2483 | 13.1832 | 13.1198 | 13.0499 | 12.9465 | 12.914 | 12.8425 | 12.4386 | 12.1404 | 12.0316
| STROMNESS | SP |  |  | 19.4506 | 19.4499 | 19.4491 | 19.4447 | 19.4392 | 19.4333 | 19.417 | 19.4008 | 19.3827 | 19.362 | 19.3144 | 19.3035 | 19.2892 | 19.2621 | 18.3232 | 18.3225 | 18.3217 | 18.3173 | 18.3117 | 18.3057 | 18.2889 | 18.272 | 18.2532 | 18.2317 | 18.1774 | 18.0882 | 18.0001 | 17.9035 | 13.3216 | 13.3212 | 13.3208 | 13.3167 | 13.3131 | 13.3095 | 13.3059 | 13.3021 | 13.2997 | 13.2958 | 13.2916 | 13.2808 | 13.2664 | 13.2394
THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | 1.3528 | 1.3527 | 1.3526 | 1.3524 | 1.2534 | 1.1519 | 0.89866 | 0.78609 | 0.62417 | 0.59629 | 0.51643 | 0.33489 | 0.20235 | 0.15548 | 1.2296 | 1.2293 | 1.2289 | 1.228 | 1.1273 | 0.94406 | 0.8391 | 0.72654 | 0.56461 | 0.53673 | 0.45687 | 0.27533 | 0.14279 | 0.095921 | 1.1939 | 1.1937 | 1.1934 | 1.193 | 1.0933 | 0.93052 | 0.82557 | 0.713 | 0.55107 | 0.52319 | 0.44334 | 0.2618 | 0.12925 | 0.077262
| STRONSAY | CT |  |  | 1.3528 | 1.3527 | 1.3526 | 1.3524 | 1.2872 | 1.2169 | 0.99435 | 0.91658 | 0.80653 | 0.78792 | 0.74794 | 0.45654 | 0.28586 | 0.22936 | 1.2296 | 1.2293 | 1.2289 | 1.228 | 1.1619 | 1.0908 | 0.9348 | 0.85703 | 0.74698 | 0.72836 | 0.68838 | 0.39698 | 0.2085 | 0.13155 | 1.1939 | 1.1937 | 1.1934 | 1.193 | 1.1274 | 0.99554 | 0.92126 | 0.84349 | 0.73344 | 0.71482 | 0.67485 | 0.37384 | 0.18297 | 0.10655
| STRONSAY | LW |  |  | 1.353 | 1.353 | 1.353 | 1.353 | 1.2534 | 1.1519 | 0.89866 | 0.78609 | 0.62417 | 0.59629 | 0.51643 | 0.33489 | 0.20235 | 0.15548 | 1.2298 | 1.2295 | 1.2291 | 1.228 | 1.1273 | 0.94406 | 0.8391 | 0.72654 | 0.56461 | 0.53673 | 0.45687 | 0.27533 | 0.14279 | 0.095921 | 1.194 | 1.1939 | 1.1937 | 1.1933 | 1.0933 | 0.93052 | 0.82557 | 0.713 | 0.55107 | 0.52319 | 0.44334 | 0.2618 | 0.12925 | 0.077262
| STRONSAY | ST |  |  | 1.3529 | 1.3529 | 1.3529 | 1.3529 | 1.3526 | 1.3524 | 1.3521 | 1.3518 | 1.3514 | 1.3513 | 1.351 | 1.3504 | 1.3472 | 1.3454 | 1.2298 | 1.2297 | 1.2295 | 1.2291 | 1.2285 | 1.2277 | 1.226 | 1.2243 | 1.2226 | 1.2207 | 1.2156 | 1.2085 | 1.2017 | 1.1989 | 1.194 | 1.1939 | 1.1938 | 1.1937 | 1.1933 | 1.1929 | 1.192 | 1.1911 | 1.1903 | 1.1895 | 1.1871 | 1.1843 | 1.1793 | 1.1775
| STRONSAY | SP |  |  | 1.3529 | 1.3528 | 1.3528 | 1.3527 | 1.3527 | 1.3527 | 1.3527 | 1.3527 | 1.3527 | 1.3526 | 1.3524 | 1.3522 | 1.351 | 1.3485 | 1.2299 | 1.2298 | 1.2298 | 1.2297 | 1.2296 | 1.2294 | 1.2289 | 1.2285 | 1.2279 | 1.2271 | 1.2249 | 1.2217 | 1.2177 | 1.2128 | 1.194 | 1.1939 | 1.1939 | 1.1938 | 1.1938 | 1.1937 | 1.1935 | 1.1933 | 1.1931 | 1.1927 | 1.1917 | 1.1904 | 1.1881 | 1.1845
FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | 2.9268 | 2.9222 | 2.8598 | 2.7884 | 2.7133 | 2.4668 | 2.3616 | 2.2436 | 2.0763 | 2.0206 | 1.8216 | 1.4734 | 1.1602 | 0.83834 | 2.8324 | 2.8321 | 2.7828 | 2.7333 | 2.4695 | 2.3842 | 2.2842 | 2.1825 | 2.0207 | 1.9656 | 1.7812 | 1.4322 | 1.1162 | 0.79119 | 2.8056 | 2.8023 | 2.7244 | 2.6438 | 2.4197 | 2.3141 | 2.2062 | 2.1072 | 1.9663 | 1.8936 | 1.6823 | 1.3197 | 0.99204 | 0.6559
| STRONTIAN | CT |  |  | 2.9268 | 2.9222 | 2.8598 | 2.7884 | 2.7133 | 2.4668 | 2.3694 | 2.265 | 2.1503 | 2.0336 | 1.8216 | 1.4734 | 1.1602 | 0.83834 | 2.8324 | 2.8321 | 2.7828 | 2.7333 | 2.4695 | 2.3842 | 2.2842 | 2.1872 | 2.0872 | 1.9853 | 1.7812 | 1.4322 | 1.1162 | 0.79119 | 2.8056 | 2.8023 | 2.7244 | 2.6438 | 2.4197 | 2.3141 | 2.2062 | 2.1072 | 2.0017 | 1.8936 | 1.6823 | 1.3197 | 0.99204 | 0.6559
| STRONTIAN | LW |  |  | 2.9314 | 2.9309 | 2.9053 | 2.8785 | 2.7685 | 2.4694 | 2.3616 | 2.2436 | 2.0763 | 2.0206 | 1.8888 | 1.6272 | 1.3898 | 1.2195 | 2.8328 | 2.8328 | 2.811 | 2.7893 | 2.4914 | 2.3958 | 2.2923 | 2.1825 | 2.0207 | 1.9656 | 1.8332 | 1.5711 | 1.3476 | 1.193 | 2.8089 | 2.8085 | 2.7755 | 2.7416 | 2.4896 | 2.379 | 2.2623 | 2.1348 | 1.9663 | 1.9092 | 1.7726 | 1.5034 | 1.2727 | 1.1057
| STRONTIAN | ST |  |  | 2.9316 | 2.9313 | 2.9145 | 2.8973 | 2.8797 | 2.8619 | 2.8401 | 2.8182 | 2.7965 | 2.7745 | 2.7088 | 2.4344 | 2.3116 | 2.177 | 2.8327 | 2.8327 | 2.8182 | 2.8037 | 2.789 | 2.7743 | 2.7595 | 2.7446 | 2.7298 | 2.7151 | 2.4734 | 2.3514 | 2.2249 | 2.0972 | 2.809 | 2.8088 | 2.7869 | 2.7648 | 2.7424 | 2.7198 | 2.6943 | 2.6688 | 2.6433 | 2.4928 | 2.4143 | 2.2814 | 2.1423 | 2.0022
| STRONTIAN | SP |  |  | 2.9318 | 2.9317 | 2.9316 | 2.9315 | 2.9313 | 2.931 | 2.9293 | 2.9276 | 2.9255 | 2.9234 | 2.9172 | 2.9076 | 2.8977 | 2.8885 | 2.8327 | 2.8326 | 2.8326 | 2.8325 | 2.8325 | 2.8325 | 2.8325 | 2.8325 | 2.8325 | 2.8324 | 2.8322 | 2.832 | 2.8308 | 2.8282 | 2.8091 | 2.8091 | 2.809 | 2.8089 | 2.8087 | 2.8085 | 2.8073 | 2.8062 | 2.8047 | 2.8032 | 2.7988 | 2.7938 | 2.7926 | 2.79
SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | 5.9253 | 5.9241 | 5.9225 | 5.921 | 5.9171 | 5.9126 | 5.9071 | 5.901 | 5.894 | 5.8899 | 5.8767 | 5.8459 | 5.7952 | 5.6967 | 5.2315 | 5.2293 | 5.2266 | 5.2235 | 5.2174 | 5.2108 | 5.2033 | 5.1955 | 5.1869 | 5.1811 | 5.1627 | 5.1235 | 5.0643 | 4.9603 | 3.9912 | 3.9836 | 3.9724 | 3.9465 | 3.916 | 3.8853 | 3.8541 | 3.8273 | 3.8001 | 3.7742 | 3.696 | 3.5597 | 3.4024 | 3.1992
| SUMBURGH | CT |  |  | 5.9253 | 5.9241 | 5.9225 | 5.921 | 5.9171 | 5.9126 | 5.9071 | 5.901 | 5.894 | 5.8899 | 5.8767 | 5.8459 | 5.7952 | 5.6967 | 5.2315 | 5.2293 | 5.2266 | 5.2235 | 5.2174 | 5.2108 | 5.2033 | 5.1955 | 5.1869 | 5.1811 | 5.1627 | 5.1235 | 5.0643 | 4.9603 | 3.9912 | 3.9836 | 3.9724 | 3.9465 | 3.916 | 3.8853 | 3.8541 | 3.8273 | 3.8001 | 3.7742 | 3.696 | 3.5597 | 3.4024 | 3.1992
| SUMBURGH | LW |  |  | 5.9268 | 5.9268 | 5.9267 | 5.9266 | 5.9264 | 5.9263 | 5.9261 | 5.9259 | 5.9258 | 5.9256 | 5.9251 | 5.9247 | 5.9247 | 5.9247 | 5.234 | 5.2339 | 5.2338 | 5.2333 | 5.2328 | 5.2324 | 5.2319 | 5.2315 | 5.231 | 5.2306 | 5.2292 | 5.2284 | 5.2275 | 5.2267 | 3.9995 | 3.999 | 3.9982 | 3.9961 | 3.9938 | 3.9916 | 3.9895 | 3.9873 | 3.9853 | 3.983 | 3.9764 | 3.9656 | 3.9549 | 3.9442
| SUMBURGH | ST |  |  | 5.9263 | 5.9258 | 5.9253 | 5.9243 | 5.9224 | 5.9205 | 5.9183 | 5.9159 | 5.9131 | 5.9122 | 5.9094 | 5.9047 | 5.8807 | 5.8671 | 5.2329 | 5.2319 | 5.2306 | 5.2284 | 5.2257 | 5.2225 | 5.2194 | 5.216 | 5.2123 | 5.2103 | 5.2041 | 5.1942 | 5.1648 | 5.1458 | 3.995 | 3.9908 | 3.9852 | 3.9746 | 3.9588 | 3.94 | 3.9262 | 3.9125 | 3.8986 | 3.8833 | 3.8385 | 3.7664 | 3.6754 | 3.595
| SUMBURGH | SP |  |  | 5.9264 | 5.9262 | 5.9259 | 5.9256 | 5.9253 | 5.9249 | 5.9246 | 5.9242 | 5.9238 | 5.9231 | 5.922 | 5.9212 | 5.9157 | 5.9038 | 5.2336 | 5.2332 | 5.2329 | 5.2325 | 5.2316 | 5.2305 | 5.2297 | 5.2288 | 5.2279 | 5.2271 | 5.2247 | 5.2219 | 5.2145 | 5.2008 | 3.9987 | 3.9979 | 3.997 | 3.996 | 3.9919 | 3.9869 | 3.9831 | 3.9794 | 3.9745 | 3.9685 | 3.9512 | 3.925 | 3.8957 | 3.8611
ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | YES | 18.2418 | 18.1384 | 18.0372 | 17.9075 | 17.7129 | 17.516 | 17.3178 | 17.1157 | 16.8992 | 16.8192 | 16.659 | 14.5347 | 13.9917 | 13.2995 | 16.3878 | 16.2954 | 16.2015 | 16.0755 | 15.9097 | 15.759 | 15.6054 | 15.4492 | 15.2714 | 15.2144 | 15.0959 | 13.1114 | 12.3502 | 11.6534 | 16.7165 | 16.5991 | 16.4862 | 16.3584 | 16.1655 | 15.97 | 15.7732 | 15.5701 | 15.3522 | 15.2691 | 15.0985 | 13.1957 | 12.4354 | 11.7383
| TAIN | CT |  |  | 18.2418 | 18.1384 | 18.0372 | 17.9075 | 17.7129 | 17.516 | 17.3178 | 17.1157 | 16.8992 | 16.8192 | 16.659 | 14.5347 | 13.9917 | 13.2995 | 16.3878 | 16.2954 | 16.2015 | 16.0755 | 15.9097 | 15.759 | 15.6054 | 15.4492 | 15.2714 | 15.2144 | 15.0959 | 13.1114 | 12.3502 | 11.6534 | 16.7165 | 16.5991 | 16.4862 | 16.3584 | 16.1655 | 15.97 | 15.7732 | 15.5701 | 15.3522 | 15.2691 | 15.0985 | 13.1957 | 12.4354 | 11.7383
| TAIN | LW |  |  | 18.3363 | 18.3276 | 18.319 | 18.3085 | 18.2005 | 18.0896 | 17.9744 | 17.851 | 17.6811 | 17.6402 | 17.5074 | 17.1841 | 16.933 | 16.7925 | 16.4758 | 16.4644 | 16.4513 | 16.4286 | 16.3069 | 16.1827 | 16.0546 | 15.9214 | 15.7435 | 15.6938 | 15.5596 | 15.2696 | 15.0495 | 14.942 | 16.8228 | 16.8115 | 16.7993 | 16.781 | 16.6642 | 16.5446 | 16.4207 | 16.2903 | 16.12 | 16.0786 | 15.9444 | 15.619 | 15.3657 | 15.2231
| TAIN | ST |  |  | 18.3389 | 18.3327 | 18.3264 | 18.3177 | 18.2619 | 18.2024 | 18.1423 | 18.0758 | 17.9779 | 17.9477 | 17.8599 | 17.5903 | 17.197 | 17.0956 | 16.4773 | 16.4681 | 16.4575 | 16.4405 | 16.3732 | 16.2997 | 16.2156 | 16.1317 | 16.0178 | 15.9715 | 15.9039 | 15.6651 | 15.3011 | 15.2272 | 16.8253 | 16.8167 | 16.8073 | 16.7931 | 16.7302 | 16.6622 | 16.5882 | 16.5133 | 16.4142 | 16.3818 | 16.2873 | 16.0069 | 15.6171 | 15.5303
| TAIN | SP |  |  | 18.3348 | 18.3266 | 18.3185 | 18.3103 | 18.2922 | 18.2745 | 18.2563 | 18.2376 | 18.2141 | 18.1886 | 18.1053 | 18.0634 | 17.4196 | 17.1522 | 16.4769 | 16.4688 | 16.4606 | 16.4524 | 16.4317 | 16.4107 | 16.3851 | 16.3595 | 16.327 | 16.2867 | 16.1671 | 16.1317 | 15.5127 | 15.2687 | 16.8226 | 16.8134 | 16.8042 | 16.7948 | 16.7738 | 16.7527 | 16.7291 | 16.7049 | 16.6747 | 16.6396 | 16.5448 | 16.5002 | 15.8537 | 15.5836
ARDMORE | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | YES | 2.984 | 2.9762 | 2.968 | 2.9669 | 2.9635 | 2.9595 | 2.9547 | 2.9492 | 2.9431 | 2.9396 | 2.9279 | 2.4697 | 2.3086 | 2.1074 | 2.9457 | 2.9424 | 2.9393 | 2.9383 | 2.9348 | 2.9308 | 2.9261 | 2.9206 | 2.9145 | 2.911 | 2.4798 | 2.3207 | 2.1429 | 1.9251 | 2.8701 | 2.8643 | 2.8559 | 2.8472 | 2.8437 | 2.8397 | 2.835 | 2.8295 | 2.8234 | 2.8199 | 2.4457 | 2.2874 | 2.1104 | 1.8934
| TARBERT | CT |  |  | 2.984 | 2.9762 | 2.968 | 2.9669 | 2.9635 | 2.9595 | 2.9547 | 2.9492 | 2.9431 | 2.9396 | 2.9279 | 2.4697 | 2.3086 | 2.1074 | 2.9457 | 2.9424 | 2.9393 | 2.9383 | 2.9348 | 2.9308 | 2.9261 | 2.9206 | 2.9145 | 2.911 | 2.4798 | 2.3207 | 2.1429 | 1.9251 | 2.8701 | 2.8643 | 2.8559 | 2.8472 | 2.8437 | 2.8397 | 2.835 | 2.8295 | 2.8234 | 2.8199 | 2.4457 | 2.2874 | 2.1104 | 1.8934
| TARBERT | LW |  |  | 2.9915 | 2.9901 | 2.9879 | 2.9824 | 2.9763 | 2.9702 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 2.9491 | 2.9486 | 2.9477 | 2.9457 | 2.9434 | 2.9415 | 2.9415 | 2.9415 | 2.9415 | 2.9415 | 2.9415 | 2.9415 | 2.9415 | 2.9415 | 2.8759 | 2.8748 | 2.8732 | 2.8692 | 2.8648 | 2.8604 | 2.8562 | 2.852 | 2.8504 | 2.8504 | 2.8504 | 2.8504 | 2.8504 | 2.8504
| TARBERT | ST |  |  | 2.992 | 2.9913 | 2.9903 | 2.9885 | 2.9857 | 2.9823 | 2.9705 | 2.9674 | 2.9665 | 2.9662 | 2.9654 | 2.964 | 2.9565 | 2.9523 | 2.9492 | 2.9489 | 2.9485 | 2.9478 | 2.9465 | 2.9448 | 2.9401 | 2.9387 | 2.9379 | 2.9376 | 2.9367 | 2.9353 | 2.9278 | 2.4453 | 2.8762 | 2.8757 | 2.8749 | 2.8736 | 2.8714 | 2.8688 | 2.8601 | 2.8514 | 2.8468 | 2.8465 | 2.8456 | 2.8442 | 2.4985 | 2.4115
| TARBERT | SP |  |  | 2.9926 | 2.9924 | 2.9922 | 2.992 | 2.9913 | 2.9905 | 2.9863 | 2.9821 | 2.977 | 2.9705 | 2.969 | 2.9686 | 2.9663 | 2.9613 | 2.9494 | 2.9492 | 2.9491 | 2.949 | 2.9487 | 2.9484 | 2.9468 | 2.9453 | 2.9434 | 2.9409 | 2.9404 | 2.94 | 2.9377 | 2.9326 | 2.8766 | 2.8764 | 2.8762 | 2.8761 | 2.8756 | 2.875 | 2.8719 | 2.8689 | 2.8651 | 2.8604 | 2.8493 | 2.8489 | 2.8466 | 2.8415
PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | 0.1621 | 0.16209 | 0.1577 | 0.1498 | 0.14417 | 0.13714 | 0.12989 | 0.12233 | 0.11452 | 0.10651 | 0.092015 | 0.06836 | 0.047446 | 0.026735 | 0.15892 | 0.15877 | 0.1554 | 0.1474 | 0.14159 | 0.13462 | 0.12745 | 0.11982 | 0.11196 | 0.10388 | 0.088752 | 0.064105 | 0.042022 | 0.019821 | 0.15789 | 0.15783 | 0.15282 | 0.14571 | 0.13982 | 0.13259 | 0.12511 | 0.11718 | 0.10901 | 0.10062 | 0.084982 | 0.059503 | 0.036525 | 0.013728
| TARBERT JURA | CT |  |  | 0.1621 | 0.16209 | 0.1577 | 0.1498 | 0.14417 | 0.13714 | 0.12989 | 0.12233 | 0.11452 | 0.10651 | 0.092015 | 0.06836 | 0.047446 | 0.026735 | 0.15892 | 0.15879 | 0.1554 | 0.1474 | 0.14159 | 0.13462 | 0.12745 | 0.11982 | 0.11196 | 0.10388 | 0.088752 | 0.064105 | 0.042022 | 0.019821 | 0.15789 | 0.15783 | 0.15282 | 0.14571 | 0.13982 | 0.13259 | 0.12511 | 0.11718 | 0.10901 | 0.10062 | 0.084982 | 0.059503 | 0.036525 | 0.013728
| TARBERT JURA | LW |  |  | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.1469 | 0.14275 | 0.13864 | 0.15892 | 0.15877 | 0.15856 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.14708 | 0.14223 | 0.13735 | 0.13252 | 0.1579 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.14919 | 0.14616 | 0.1413 | 0.13639 | 0.13154
| TARBERT JURA | ST |  |  | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.14873 | 0.14504 | 0.14134 | 0.15897 | 0.1589 | 0.15881 | 0.15863 | 0.15844 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.14884 | 0.14438 | 0.14004 | 0.1357 | 0.15792 | 0.15789 | 0.15786 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.14793 | 0.14345 | 0.13909 | 0.13473
| TARBERT JURA | SP |  |  | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.16211 | 0.15904 | 0.15903 | 0.15902 | 0.15901 | 0.15894 | 0.15886 | 0.15862 | 0.15842 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.15837 | 0.14981 | 0.158 | 0.15798 | 0.15797 | 0.15795 | 0.15791 | 0.15787 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.15785 | 0.1489
PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | YES | 5.6324 | 5.6298 | 5.6259 | 5.6159 | 5.4269 | 3.6182 | 3.2068 | 2.7431 | 2.1515 | 1.5717 | -0.6076 | -2.5687 | -3.1621 | -4.8922 | 3.7895 | 3.787 | 3.7835 | 3.7727 | 3.2485 | 2.7083 | 2.1715 | 1.6376 | 0.95096 | 0.26937 | -2.2923 | -4.5905 | -5.2783 | -7.3094 | 3.8801 | 3.877 | 3.8725 | 3.86 | 3.3475 | 2.8178 | 2.2914 | 1.7679 | 1.1006 | 0.44499 | -2.11 | -4.404 | -5.0906 | -7.1179
| TARBERT LOCH FYNE | CT |  |  | 5.6324 | 5.6298 | 5.6259 | 5.6173 | 5.4429 | 5.4198 | 3.9329 | 3.7431 | 3.4616 | 3.0594 | 1.5502 | -0.54221 | -1.881 | -4.6092 | 3.7895 | 3.787 | 3.7835 | 3.7744 | 3.5521 | 3.3474 | 3.1437 | 2.8852 | 2.502 | 2.0045 | 0.2448 | -2.2046 | -3.7662 | -6.9624 | 3.8801 | 3.877 | 3.8725 | 3.8622 | 3.6451 | 3.4443 | 3.2445 | 2.991 | 2.6151 | 2.1274 | 0.4212 | -2.0226 | -3.5814 | -6.7717
| TARBERT LOCH FYNE | LW |  |  | 5.6329 | 5.6303 | 5.6262 | 5.6159 | 5.4269 | 3.6182 | 3.2068 | 2.7431 | 2.1515 | 1.5717 | -0.6076 | -2.5687 | -3.1621 | -4.8922 | 3.79 | 3.7876 | 3.7837 | 3.7727 | 3.2485 | 2.7083 | 2.1715 | 1.6376 | 0.95096 | 0.26937 | -2.2923 | -4.5905 | -5.2783 | -7.3094 | 3.8806 | 3.8775 | 3.8725 | 3.86 | 3.3475 | 2.8178 | 2.2914 | 1.7679 | 1.1006 | 0.44499 | -2.11 | -4.404 | -5.0906 | -7.1179
| TARBERT LOCH FYNE | ST |  |  | 5.6338 | 5.6323 | 5.6304 | 5.6268 | 5.4763 | 5.4249 | 3.9735 | 3.7857 | 3.514 | 3.1274 | 1.6434 | -0.37872 | -3.0342 | -4.561 | 3.7908 | 3.7894 | 3.7877 | 3.7844 | 3.5975 | 3.3985 | 3.1967 | 2.9399 | 2.5688 | 2.0806 | 0.35075 | -2.0227 | -5.1326 | -6.9226 | 3.8817 | 3.8799 | 3.8777 | 3.8734 | 3.6897 | 3.4945 | 3.2966 | 3.0448 | 2.6809 | 2.2022 | 0.5239 | -1.8409 | -4.9451 | -6.7318
| TARBERT LOCH FYNE | SP |  |  | 5.6349 | 5.6345 | 5.6341 | 5.6337 | 5.5944 | 5.5495 | 5.4805 | 5.4329 | 5.4274 | 3.9836 | 3.4482 | 2.6706 | 1.9338 | 1.266 | 3.7918 | 3.7915 | 3.7911 | 3.7907 | 3.7499 | 3.6997 | 3.6031 | 3.508 | 3.3814 | 3.2087 | 2.4744 | 1.552 | 0.69915 | -0.08179 | 3.8831 | 3.8827 | 3.8822 | 3.8818 | 3.8342 | 3.7799 | 3.6951 | 3.6019 | 3.4778 | 3.3085 | 2.5886 | 1.6842 | 0.85748 | 0.096216
TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | YES | 3.0418 | 3.0404 | 3.0126 | 2.9828 | 2.9503 | 2.9119 | 2.8722 | 2.8195 | 2.7655 | 2.7112 | 2.5918 | 2.4463 | 1.7183 | 1.4816 | 2.3481 | 2.347 | 2.3124 | 2.2762 | 2.2437 | 2.2096 | 2.1846 | 2.1438 | 2.1023 | 2.0783 | 1.7736 | 1.5633 | 1.3563 | 1.1237 | 2.4794 | 2.4778 | 2.4448 | 2.4093 | 2.371 | 2.3258 | 2.279 | 2.2162 | 2.152 | 2.087 | 2.009 | 1.6064 | 1.3682 | 1.105
| TAYNUILT | CT |  |  | 3.0418 | 3.0404 | 3.0126 | 2.9828 | 2.9503 | 2.9119 | 2.8722 | 2.8195 | 2.7655 | 2.7112 | 2.5918 | 2.4463 | 1.7183 | 1.4816 | 2.3481 | 2.347 | 2.3124 | 2.2762 | 2.2437 | 2.2096 | 2.1846 | 2.1438 | 2.1023 | 2.0783 | 1.7736 | 1.5633 | 1.3563 | 1.1237 | 2.4794 | 2.4778 | 2.4448 | 2.4093 | 2.371 | 2.3258 | 2.279 | 2.2162 | 2.152 | 2.087 | 2.009 | 1.6064 | 1.3682 | 1.105
| TAYNUILT | LW |  |  | 3.0423 | 3.0412 | 3.0394 | 3.0351 | 3.0302 | 3.0254 | 3.0207 | 3.0162 | 3.0117 | 3.0069 | 2.9926 | 2.9696 | 2.9464 | 2.9234 | 2.3487 | 2.3478 | 2.3465 | 2.343 | 2.3392 | 2.3355 | 2.3318 | 2.3283 | 2.3248 | 2.3215 | 2.3125 | 2.3081 | 2.3081 | 2.3081 | 2.4799 | 2.4785 | 2.4763 | 2.4727 | 2.4712 | 2.4697 | 2.4683 | 2.4669 | 2.4668 | 2.4668 | 2.4668 | 2.4668 | 2.4668 | 2.4668
| TAYNUILT | ST |  |  | 3.0426 | 3.0419 | 3.0411 | 3.0396 | 3.0366 | 3.0331 | 3.0214 | 3.0096 | 2.9978 | 2.9868 | 2.9548 | 2.9032 | 2.8385 | 2.7812 | 2.3489 | 2.3483 | 2.3477 | 2.3464 | 2.3439 | 2.3409 | 2.3314 | 2.3218 | 2.3128 | 2.3056 | 2.2974 | 2.2942 | 2.2774 | 2.2679 | 2.4803 | 2.4795 | 2.4785 | 2.4766 | 2.4732 | 2.4701 | 2.4654 | 2.4606 | 2.4587 | 2.458 | 2.4561 | 2.4529 | 2.4361 | 2.4266
| TAYNUILT | SP |  |  | 3.043 | 3.0427 | 3.0425 | 3.0422 | 3.0416 | 3.041 | 3.0378 | 3.0347 | 3.0307 | 3.0263 | 3.0137 | 2.9947 | 2.9731 | 2.9474 | 2.3491 | 2.3489 | 2.3487 | 2.3484 | 2.348 | 2.3474 | 2.345 | 2.3425 | 2.3394 | 2.3359 | 2.3258 | 2.3128 | 2.3008 | 2.2913 | 2.4808 | 2.4806 | 2.4803 | 2.48 | 2.4793 | 2.4785 | 2.4745 | 2.4719 | 2.4707 | 2.4691 | 2.4646 | 2.4639 | 2.4596 | 2.45
BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | YES | 27.913 | 27.775 | 27.6251 | 27.1109 | 26.971 | 26.2115 | 25.5924 | 24.9788 | 24.0117 | 23.7751 | 19.8706 | 18.7134 | 17.888 | 17.4476 | 25.7457 | 25.6292 | 25.4931 | 24.9183 | 24.7694 | 23.9989 | 23.3339 | 22.6704 | 18.8197 | 18.5964 | 17.9254 | 16.7864 | 15.9769 | 15.5529 | 24.5127 | 24.4045 | 24.2935 | 23.7704 | 23.6799 | 22.9796 | 22.3965 | 21.8132 | 18.8501 | 18.6244 | 17.9451 | 16.7921 | 15.9111 | 14.5234
| THIMBLEROW | CT |  |  | 27.913 | 27.775 | 27.6251 | 27.4151 | 27.1178 | 26.7806 | 26.4895 | 26.2045 | 25.871 | 25.6951 | 25.2284 | 19.9324 | 18.487 | 17.594 | 25.7499 | 25.6292 | 25.4931 | 25.2908 | 24.9712 | 24.5691 | 24.1874 | 23.8386 | 23.4671 | 23.2434 | 22.6126 | 18.4471 | 17.0498 | 15.9255 | 24.5156 | 24.4045 | 24.2935 | 24.1736 | 23.9451 | 23.6327 | 23.3395 | 23.0528 | 22.7177 | 22.5403 | 22.0693 | 17.8427 | 15.9111 | 14.5234
| THIMBLEROW | LW |  |  | 27.9262 | 27.8744 | 27.813 | 27.7384 | 27.4042 | 26.9626 | 26.5291 | 26.0817 | 25.6308 | 25.453 | 24.9182 | 23.795 | 19.518 | 18.7799 | 25.7457 | 25.6928 | 25.6285 | 25.5444 | 25.1996 | 24.7373 | 24.2622 | 23.7745 | 23.2743 | 23.0255 | 22.281 | 18.7915 | 17.6703 | 16.9693 | 24.5127 | 24.4748 | 24.4353 | 24.4154 | 24.142 | 23.7492 | 23.342 | 22.9204 | 22.4847 | 22.3057 | 21.7674 | 18.765 | 17.5362 | 16.398
| THIMBLEROW | ST |  |  | 28.092 | 28.0556 | 28.0133 | 27.1109 | 26.971 | 26.2115 | 25.5924 | 24.9788 | 24.0117 | 23.7751 | 19.8706 | 18.7134 | 17.888 | 17.4476 | 25.9101 | 25.8719 | 25.8268 | 24.9183 | 24.7694 | 23.9989 | 23.3339 | 22.6704 | 18.8197 | 18.5964 | 17.9254 | 16.7864 | 15.9769 | 15.5529 | 24.6816 | 24.6595 | 24.6363 | 23.7704 | 23.6799 | 22.9796 | 22.3965 | 21.8132 | 18.8501 | 18.6244 | 17.9451 | 16.7921 | 15.9705 | 15.4374
| THIMBLEROW | SP |  |  | 28.1886 | 28.1721 | 28.1552 | 27.7194 | 27.6569 | 26.6792 | 26.6094 | 26.5401 | 25.5517 | 25.3446 | 24.7263 | 23.696 | 19.7396 | 19.4496 | 26.0104 | 25.9952 | 25.9794 | 25.5446 | 25.4815 | 24.5024 | 24.4306 | 24.3591 | 23.3673 | 23.1585 | 22.5351 | 18.4918 | 17.8565 | 17.5901 | 24.7647 | 24.7505 | 24.7363 | 24.3033 | 24.2559 | 23.296 | 23.2474 | 23.199 | 22.2374 | 22.0496 | 21.4868 | 18.4829 | 17.8286 | 17.5442
TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | 0.077429 | 0.17743 | 0.1757 | 0.17398 | 0.17221 | 0.17007 | 0.16856 | 0.16736 | 0.16611 | 0.16483 | 0.14624 | 0.13475 | 0.12389 | 0.11326 | 0.069168 | 0.169 | 0.16728 | 0.1657 | 0.16459 | 0.16325 | 0.16186 | 0.1607 | 0.14994 | 0.14685 | 0.14017 | 0.12933 | 0.11908 | 0.109 | 0.071194 | 0.17113 | 0.16924 | 0.16734 | 0.16547 | 0.1632 | 0.16087 | 0.15913 | 0.14953 | 0.14596 | 0.13778 | 0.12449 | 0.11192 | 0.0996
| TIRORAN BRIDGE | CT |  |  | 0.077429 | 0.17743 | 0.1757 | 0.17398 | 0.17221 | 0.17007 | 0.16856 | 0.16736 | 0.16611 | 0.16483 | 0.14624 | 0.13475 | 0.12389 | 0.11326 | 0.06918 | 0.16904 | 0.16728 | 0.1657 | 0.16459 | 0.16325 | 0.16186 | 0.1607 | 0.14994 | 0.14685 | 0.14017 | 0.12933 | 0.11908 | 0.109 | 0.0712 | 0.17114 | 0.16924 | 0.16734 | 0.16547 | 0.1632 | 0.16087 | 0.15913 | 0.14953 | 0.14596 | 0.13778 | 0.12449 | 0.11192 | 0.0996
| TIRORAN BRIDGE | LW |  |  | 0.077429 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.14715 | 0.069168 | 0.169 | 0.16873 | 0.16812 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.14796 | 0.1421 | 0.1363 | 0.071194 | 0.17113 | 0.17102 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.14974 | 0.14386 | 0.13804
| TIRORAN BRIDGE | ST |  |  | 0.077429 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.069237 | 0.16915 | 0.16904 | 0.16883 | 0.16854 | 0.16824 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.14752 | 0.14289 | 0.071291 | 0.17119 | 0.17114 | 0.17106 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.1493 | 0.14465
| TIRORAN BRIDGE | SP |  |  | 0.077429 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.17743 | 0.069319 | 0.16931 | 0.16929 | 0.16928 | 0.1692 | 0.1691 | 0.16882 | 0.16854 | 0.16824 | 0.16803 | 0.16788 | 0.16788 | 0.16788 | 0.16788 | 0.071422 | 0.1714 | 0.17138 | 0.17136 | 0.17123 | 0.17117 | 0.17106 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099 | 0.17099
BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | 2.6981 | 2.6979 | 2.6828 | 2.6676 | 2.6508 | 1.7494 | 1.3244 | 0.90131 | 0.35834 | -0.17271 | -2.1776 | -3.9586 | -4.4604 | -7.3414 | 2.4945 | 2.4941 | 2.4808 | 2.4669 | 1.9227 | 1.4218 | 0.9239 | 0.42854 | -0.20626 | -0.82917 | -3.1817 | -5.2709 | -5.8522 | -9.2493 | 2.4121 | 2.4118 | 2.3984 | 2.3846 | 1.7867 | 1.2856 | 0.78757 | 0.29205 | -0.34296 | -0.96607 | -3.3182 | -5.4013 | -5.981 | -9.3677
| TOMATIN | CT |  |  | 2.6981 | 2.6979 | 2.6828 | 2.6676 | 2.6508 | 2.6302 | 2.6084 | 1.8356 | 1.5218 | 1.1156 | -0.28622 | -2.2247 | -4.1844 | -6.6876 | 2.4945 | 2.4941 | 2.4808 | 2.4669 | 2.4113 | 2.3967 | 1.8113 | 1.5722 | 1.2144 | 0.74769 | -0.87941 | -3.1173 | -5.3909 | -8.3085 | 2.4121 | 2.4118 | 2.3984 | 2.3846 | 2.3194 | 1.8364 | 1.6387 | 1.3909 | 1.0241 | 0.54802 | -1.096 | -3.361 | -5.6511 | -8.5824
| TOMATIN | LW |  |  | 2.6983 | 2.6983 | 2.6983 | 2.6983 | 2.6965 | 1.7494 | 1.3244 | 0.90131 | 0.35834 | -0.17271 | -2.1776 | -3.9586 | -4.4604 | -6.0255 | 2.4947 | 2.4944 | 2.4939 | 2.4927 | 1.9227 | 1.4218 | 0.9239 | 0.42854 | -0.20626 | -0.82917 | -3.1817 | -5.2709 | -5.8522 | -7.6916 | 2.4123 | 2.4122 | 2.412 | 2.4116 | 1.7867 | 1.2856 | 0.78757 | 0.29205 | -0.34296 | -0.96607 | -3.3182 | -5.4013 | -5.981 | -7.8148
| TOMATIN | ST |  |  | 2.6983 | 2.6982 | 2.6982 | 2.6981 | 2.6976 | 2.6965 | 2.6952 | 1.9274 | 1.632 | 1.2437 | -0.12255 | -1.9793 | -4.4197 | -7.3414 | 2.4948 | 2.4946 | 2.4944 | 2.494 | 2.4435 | 2.4425 | 1.8679 | 1.6307 | 1.2847 | 0.82887 | -0.7743 | -2.9494 | -5.8125 | -9.2493 | 2.4123 | 2.4122 | 2.4121 | 2.412 | 2.3677 | 1.9169 | 1.7319 | 1.4946 | 1.1484 | 0.69251 | -0.91119 | -3.0867 | -5.9413 | -9.3677
| TOMATIN | SP |  |  | 2.6982 | 2.6982 | 2.6982 | 2.6982 | 2.6981 | 2.6981 | 2.6981 | 2.698 | 2.6978 | 2.6975 | 1.5406 | 0.80608 | 0.13239 | -0.47346 | 2.4949 | 2.4949 | 2.4948 | 2.4948 | 2.4651 | 2.445 | 2.444 | 2.4439 | 2.4437 | 1.8644 | 1.1762 | 0.31433 | -0.46855 | -1.1768 | 2.4124 | 2.4123 | 2.4123 | 2.4123 | 2.4008 | 2.3877 | 2.3673 | 2.3473 | 1.8892 | 1.7284 | 1.0399 | 0.17779 | -0.60532 | -1.3138
LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | 0.10333 | 0.10333 | 0.097454 | 0.091784 | 0.08595 | 0.078906 | 0.071652 | 0.064187 | 0.056488 | 0.04857 | 0.0344 | 0.011353 | -0.0087107 | -0.028077 | 0.10169 | 0.10168 | 0.096204 | 0.09076 | 0.085179 | 0.078444 | 0.07151 | 0.064374 | 0.057015 | 0.049447 | 0.035912 | 0.013912 | -0.0052514 | -0.023751 | 0.10167 | 0.10167 | 0.095883 | 0.090138 | 0.084232 | 0.077103 | 0.069762 | 0.062207 | 0.054415 | 0.046402 | 0.032085 | 0.008814 | -0.011449 | -0.031009
| TORBOLL | CT |  |  | 0.10333 | 0.10333 | 0.097454 | 0.091784 | 0.08595 | 0.078906 | 0.071652 | 0.064187 | 0.056488 | 0.04857 | 0.0344 | 0.011353 | -0.0087107 | -0.028077 | 0.10169 | 0.10168 | 0.096204 | 0.09076 | 0.085179 | 0.078444 | 0.07151 | 0.064374 | 0.057015 | 0.049447 | 0.035912 | 0.013912 | -0.0052514 | -0.023751 | 0.10167 | 0.10167 | 0.095883 | 0.090138 | 0.084232 | 0.077103 | 0.069762 | 0.062207 | 0.054415 | 0.046402 | 0.032085 | 0.008814 | -0.011449 | -0.031009
| TORBOLL | LW |  |  | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10169 | 0.10168 | 0.10166 | 0.10162 | 0.10159 | 0.10156 | 0.10154 | 0.10153 | 0.10152 | 0.10152 | 0.10152 | 0.10152 | 0.10152 | 0.099784 | 0.10167 | 0.10167 | 0.10166 | 0.10165 | 0.10163 | 0.10162 | 0.10161 | 0.1016 | 0.1016 | 0.1016 | 0.1016 | 0.1016 | 0.1016 | 0.099844
| TORBOLL | ST |  |  | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10169 | 0.10169 | 0.10168 | 0.10167 | 0.10165 | 0.10163 | 0.10158 | 0.10154 | 0.10153 | 0.10152 | 0.10152 | 0.10152 | 0.10152 | 0.10152 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 0.10166 | 0.10165 | 0.10163 | 0.10161 | 0.1016 | 0.1016 | 0.1016 | 0.1016 | 0.1016 | 0.1016
| TORBOLL | SP |  |  | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.1017 | 0.10169 | 0.10169 | 0.10169 | 0.10169 | 0.10168 | 0.10167 | 0.10165 | 0.10162 | 0.10162 | 0.1016 | 0.10157 | 0.10155 | 0.10153 | 0.10168 | 0.10168 | 0.10168 | 0.10168 | 0.10167 | 0.10167 | 0.10166 | 0.10166 | 0.10165 | 0.10165 | 0.10164 | 0.10162 | 0.10162 | 0.10161
KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | YES | 32.9223 | 32.8142 | 32.6969 | 32.5096 | 32.1457 | 31.7813 | 31.5455 | 31.1584 | 30.4967 | 30.3412 | 29.8702 | 22.2385 | 17.5988 | 14.8591 | 29.1071 | 29.0026 | 28.8836 | 28.677 | 28.2227 | 27.7426 | 27.2293 | 26.6646 | 25.7874 | 25.3833 | 19.5386 | 17.0889 | 11.7739 | 8.7436 | 30.5431 | 30.4442 | 30.3422 | 30.1946 | 29.9546 | 29.6627 | 29.3783 | 28.8879 | 28.0867 | 27.757 | 20.1418 | 17.6349 | 12.2573 | 9.1582
| TORRYBURN | CT |  |  | 32.9223 | 32.8142 | 32.6969 | 32.5096 | 32.1457 | 31.7813 | 31.607 | 31.43 | 31.2078 | 31.0871 | 30.7811 | 22.439 | 19.7681 | 14.8591 | 29.1071 | 29.0026 | 28.8836 | 28.677 | 28.2227 | 27.7426 | 27.4156 | 27.1447 | 26.776 | 26.436 | 20.2516 | 17.4759 | 14.7068 | 9.0394 | 30.5431 | 30.4442 | 30.3422 | 30.1946 | 29.9546 | 29.6627 | 29.3824 | 29.0992 | 28.7312 | 28.4251 | 20.6533 | 17.7562 | 14.8545 | 9.1582
| TORRYBURN | LW |  |  | 33.0244 | 33.0142 | 33.0022 | 32.9808 | 32.5954 | 32.3124 | 32.2166 | 32.1167 | 32.0055 | 31.9268 | 31.6828 | 30.5822 | 22.2092 | 19.449 | 29.2064 | 29.1958 | 29.1825 | 29.1563 | 28.6098 | 27.9881 | 27.6062 | 27.2452 | 26.9456 | 26.825 | 26.5912 | 19.2187 | 17.1646 | 13.9596 | 30.636 | 30.6274 | 30.618 | 30.6036 | 30.4123 | 30.1417 | 29.8693 | 29.5946 | 29.2631 | 28.9635 | 28.6963 | 19.6964 | 17.5168 | 14.2908
| TORRYBURN | ST |  |  | 33.0014 | 32.9725 | 32.9358 | 32.8686 | 32.6312 | 31.9348 | 31.5455 | 31.1584 | 30.4967 | 30.3412 | 29.8702 | 22.2385 | 17.5988 | 15.0076 | 29.1726 | 29.1344 | 29.085 | 28.9929 | 28.6613 | 27.8675 | 27.2293 | 26.6646 | 25.7874 | 25.3833 | 19.5386 | 17.0889 | 11.7739 | 8.7436 | 30.6254 | 30.6085 | 30.5876 | 30.5513 | 30.4275 | 29.8484 | 29.3783 | 28.8879 | 28.0867 | 27.757 | 20.1418 | 17.6349 | 12.2573 | 9.2176
| TORRYBURN | SP |  |  | 33.019 | 33.008 | 32.9963 | 32.9843 | 32.9177 | 32.1673 | 32.079 | 31.9919 | 31.2049 | 30.9455 | 30.489 | 29.7892 | 29.204 | 28.8849 | 29.2006 | 29.1893 | 29.1771 | 29.1644 | 29.0744 | 28.2967 | 28.1754 | 28.0559 | 27.2255 | 26.9115 | 25.9458 | 21.7599 | 20.0031 | 18.5849 | 30.6311 | 30.6214 | 30.6114 | 30.6011 | 30.5641 | 29.8479 | 29.8004 | 29.7536 | 29.0198 | 28.8271 | 28.177 | 27.1488 | 20.5771 | 19.1472
LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | 0.66567 | 1.6655 | 1.6576 | 1.6497 | 1.6408 | 1.6302 | 1.6191 | 1.6076 | 1.5955 | 1.5839 | 1.5652 | 1.4425 | 1.371 | 1.2897 | 0.58389 | 1.5834 | 1.5763 | 1.569 | 1.5635 | 1.5573 | 1.5509 | 1.5434 | 1.4998 | 1.4838 | 1.4462 | 1.3828 | 1.3153 | 1.2381 | 0.58312 | 1.5828 | 1.5748 | 1.5665 | 1.5572 | 1.5462 | 1.5364 | 1.5261 | 1.4903 | 1.4713 | 1.4246 | 1.3466 | 1.2662 | 1.1756
| TRESSADY | CT |  |  | 0.66567 | 1.6655 | 1.6576 | 1.6497 | 1.6408 | 1.6302 | 1.6191 | 1.6076 | 1.5955 | 1.5839 | 1.5652 | 1.4425 | 1.371 | 1.2897 | 0.58389 | 1.5834 | 1.5763 | 1.569 | 1.5635 | 1.5573 | 1.5509 | 1.5434 | 1.4998 | 1.4838 | 1.4462 | 1.3828 | 1.3153 | 1.2381 | 0.58312 | 1.5828 | 1.5748 | 1.5665 | 1.5572 | 1.5462 | 1.5364 | 1.5261 | 1.4903 | 1.4713 | 1.4246 | 1.3466 | 1.2662 | 1.1756
| TRESSADY | LW |  |  | 0.66593 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 0.58411 | 1.5838 | 1.5832 | 1.5818 | 1.5802 | 1.5789 | 1.5777 | 1.5769 | 1.5763 | 1.5759 | 1.5758 | 1.5758 | 1.5758 | 1.5758 | 0.58336 | 1.5832 | 1.583 | 1.5824 | 1.5818 | 1.5812 | 1.5808 | 1.5804 | 1.58 | 1.5796 | 1.5796 | 1.5796 | 1.5796 | 1.5796
| TRESSADY | ST |  |  | 0.66588 | 1.6658 | 1.6658 | 1.6658 | 1.6655 | 1.6652 | 1.6648 | 1.6643 | 1.6638 | 1.6636 | 1.6631 | 1.6622 | 1.6578 | 1.6553 | 0.58422 | 1.584 | 1.5838 | 1.5833 | 1.5824 | 1.5813 | 1.577 | 1.5744 | 1.5737 | 1.5735 | 1.573 | 1.4889 | 1.4544 | 1.4219 | 0.58338 | 1.5833 | 1.5832 | 1.5829 | 1.5824 | 1.5818 | 1.5797 | 1.5782 | 1.5774 | 1.5773 | 1.5768 | 1.4918 | 1.4581 | 1.4262
| TRESSADY | SP |  |  | 0.66593 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 1.6659 | 0.58443 | 1.5844 | 1.5844 | 1.5843 | 1.5842 | 1.584 | 1.5825 | 1.581 | 1.5794 | 1.5781 | 1.576 | 1.5758 | 1.5758 | 1.5758 | 0.58349 | 1.5835 | 1.5835 | 1.5835 | 1.5834 | 1.5833 | 1.5827 | 1.5821 | 1.5814 | 1.5809 | 1.5798 | 1.5796 | 1.5796 | 1.5796
SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | 8.4466 | 8.3817 | 8.3191 | 8.2428 | 8.1672 | 8.0938 | 8.0225 | 7.9516 | 7.8847 | 7.8483 | 7.7868 | 7.685 | 7.5718 | 5.8399 | 7.23 | 7.1977 | 7.1667 | 7.1285 | 7.0898 | 7.052 | 7.0149 | 6.9766 | 6.9401 | 6.9195 | 6.8809 | 5.861 | 5.6279 | 5.3591 | 7.6755 | 7.6121 | 7.551 | 7.4765 | 7.4026 | 7.3308 | 7.2611 | 7.1914 | 7.1258 | 7.0898 | 7.0286 | 5.8142 | 5.5744 | 5.3012
| TUMBLIN | CT |  |  | 8.4466 | 8.3817 | 8.3191 | 8.2428 | 8.1672 | 8.0938 | 8.0225 | 7.9516 | 7.8847 | 7.8483 | 7.7868 | 7.685 | 7.5718 | 5.8399 | 7.23 | 7.1977 | 7.1667 | 7.1285 | 7.0898 | 7.052 | 7.0149 | 6.9766 | 6.9401 | 6.9195 | 6.8809 | 5.861 | 5.6279 | 5.3591 | 7.6755 | 7.6121 | 7.551 | 7.4765 | 7.4026 | 7.3308 | 7.2611 | 7.1914 | 7.1258 | 7.0898 | 7.0286 | 5.8142 | 5.5744 | 5.3012
| TUMBLIN | LW |  |  | 8.5057 | 8.5002 | 8.4949 | 8.4887 | 8.4816 | 8.4738 | 8.4655 | 8.4566 | 8.4475 | 8.438 | 8.4082 | 8.355 | 8.2989 | 8.2437 | 7.2594 | 7.2567 | 7.254 | 7.2507 | 7.247 | 7.243 | 7.2386 | 7.234 | 7.2293 | 7.2244 | 7.2091 | 7.1819 | 7.1531 | 7.1249 | 7.7332 | 7.7279 | 7.7227 | 7.7165 | 7.7095 | 7.7019 | 7.6937 | 7.6849 | 7.676 | 7.6667 | 7.6375 | 7.5853 | 7.5302 | 7.476
| TUMBLIN | ST |  |  | 8.5076 | 8.504 | 8.5002 | 8.4953 | 8.4896 | 8.4839 | 8.4762 | 8.4685 | 8.4611 | 8.4545 | 8.4328 | 8.3969 | 8.3538 | 8.3163 | 7.2603 | 7.2585 | 7.2566 | 7.254 | 7.2507 | 7.2472 | 7.2422 | 7.237 | 7.232 | 7.2276 | 7.2136 | 7.1906 | 7.1586 | 7.1323 | 7.7351 | 7.7315 | 7.7279 | 7.723 | 7.7174 | 7.7118 | 7.7041 | 7.6964 | 7.6889 | 7.6822 | 7.6604 | 7.6242 | 7.5808 | 7.543
| TUMBLIN | SP |  |  | 8.5052 | 8.5003 | 8.4954 | 8.4905 | 8.4834 | 8.4764 | 8.4692 | 8.4621 | 8.455 | 8.4477 | 8.4264 | 8.3859 | 8.3433 | 8.299 | 7.2591 | 7.2567 | 7.2542 | 7.2517 | 7.2482 | 7.2447 | 7.2409 | 7.2372 | 7.2334 | 7.2293 | 7.2176 | 7.1958 | 7.1718 | 7.1451 | 7.7327 | 7.728 | 7.7232 | 7.7184 | 7.7115 | 7.7046 | 7.6975 | 7.6905 | 7.6835 | 7.6763 | 7.6552 | 7.6153 | 7.5733 | 7.5295
TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | 2.9922 | 2.8333 | 2.478 | 2.2881 | 2.0611 | 1.8206 | 1.5666 | 1.291 | 0.93989 | 0.80057 | 0.55677 | -0.33678 | -1.917 | -4.3424 | 2.8842 | 2.4891 | 2.3614 | 2.1923 | 2.0103 | 1.8155 | 1.605 | 1.3701 | 1.0628 | 0.9449 | 0.72843 | -0.12386 | -1.3608 | -3.3636 | 2.9156 | 2.3985 | 2.2296 | 2.0072 | 1.7738 | 1.5317 | 1.2761 | 0.99831 | 0.64506 | 0.5038 | 0.25483 | -0.64712 | -2.2185 | -4.6532
| TUMMEL BRIDGE | CT |  |  | 2.9922 | 2.8333 | 2.478 | 2.2881 | 2.0611 | 1.8206 | 1.5666 | 1.291 | 0.93989 | 0.80057 | 0.55677 | -0.33678 | -1.0368 | -1.4836 | 2.8842 | 2.4891 | 2.3614 | 2.1923 | 2.0103 | 1.8155 | 1.605 | 1.3701 | 1.0628 | 0.9449 | 0.72843 | -0.12386 | -0.77892 | -1.1778 | 2.9156 | 2.3985 | 2.2296 | 2.0072 | 1.7738 | 1.5317 | 1.2761 | 0.99831 | 0.64506 | 0.5038 | 0.25483 | -0.64712 | -1.3557 | -1.811
| TUMMEL BRIDGE | LW |  |  | 3.1355 | 3.1214 | 3.1071 | 3.0884 | 3.0675 | 3.045 | 3.021 | 2.9756 | 2.8903 | 2.8458 | 2.6814 | 2.0832 | 1.6301 | 1.2802 | 2.9667 | 2.9581 | 2.949 | 2.9363 | 2.9219 | 2.9068 | 2.8908 | 2.8561 | 2.4903 | 2.4459 | 2.2827 | 1.8798 | 1.4622 | 1.1541 | 3.0732 | 3.0572 | 3.0408 | 3.0185 | 2.9935 | 2.9669 | 2.9387 | 2.889 | 2.4423 | 2.3914 | 2.2079 | 1.7684 | 1.3068 | 0.94867
| TUMMEL BRIDGE | ST |  |  | 3.141 | 3.1318 | 3.1223 | 3.1094 | 3.0962 | 3.0831 | 3.0665 | 3.0405 | 2.9787 | 2.9504 | 2.8541 | 1.6575 | -0.85793 | -3.9714 | 2.9701 | 2.9645 | 2.9587 | 2.9506 | 2.9422 | 2.9335 | 2.9224 | 2.9017 | 2.8452 | 2.8219 | 2.4546 | 1.5843 | -0.48727 | -3.0184 | 3.0794 | 3.069 | 3.0584 | 3.0436 | 3.0284 | 3.013 | 2.9935 | 2.9646 | 2.9 | 2.8686 | 2.4065 | 1.3594 | -1.1681 | -4.2969
| TUMMEL BRIDGE | SP |  |  | 3.1357 | 3.1239 | 3.1122 | 3.1004 | 3.0827 | 3.0651 | 3.0472 | 3.028 | 3.0028 | 2.9749 | 2.8634 | 0.94737 | -1.917 | -4.3424 | 2.9673 | 2.9604 | 2.9537 | 2.9468 | 2.9364 | 2.9259 | 2.9152 | 2.9029 | 2.8845 | 2.8633 | 2.4902 | 1.1185 | -1.3608 | -3.3636 | 3.0738 | 3.0608 | 3.0479 | 3.0349 | 3.0151 | 2.9955 | 2.9755 | 2.9541 | 2.9265 | 2.8963 | 2.4315 | 0.65454 | -2.2185 | -4.6532
MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | YES | 24.6775 | 24.6745 | 24.671 | 24.6498 | 24.5877 | 24.5062 | 24.4191 | 24.3225 | 24.4435 | 24.4192 | 23.7065 | 22.185 | 13.3556 | 12.8453 | 21.4877 | 21.46 | 21.4196 | 21.3102 | 20.8776 | 20.4856 | 20.1462 | 13.7445 | 13.3437 | 12.3591 | 11.2781 | 9.8801 | 7.5713 | 6.2525 | 21.1034 | 21.1004 | 21.0969 | 21.0758 | 21.0136 | 20.9322 | 20.845 | 20.7484 | 20.8694 | 20.8451 | 13.2074 | 11.7525 | 9.0453 | 7.6862
| TURRIFF | CT |  |  | 24.6775 | 24.6745 | 24.671 | 24.6498 | 24.5905 | 24.5225 | 24.4482 | 24.3662 | 24.6864 | 24.6384 | 23.7838 | 23.0902 | 22.2321 | 14.2811 | 21.4877 | 21.46 | 21.4196 | 21.3102 | 20.8776 | 20.4856 | 20.1462 | 13.7445 | 13.3437 | 12.3591 | 11.2781 | 9.8801 | 8.5569 | 7.5349 | 21.1034 | 21.1004 | 21.0969 | 21.0758 | 21.0164 | 20.9485 | 20.8741 | 20.7922 | 21.1124 | 21.0644 | 13.2074 | 11.7525 | 10.3489 | 9.3094
| TURRIFF | LW |  |  | 24.6819 | 24.6819 | 24.6819 | 24.6636 | 24.5877 | 24.5062 | 24.4191 | 24.3225 | 24.6036 | 24.558 | 23.7065 | 23.1499 | 22.4538 | 22.31 | 21.5146 | 21.5095 | 21.5013 | 21.4627 | 21.3641 | 21.2605 | 21.1517 | 21.0338 | 21.2943 | 21.2262 | 20.5876 | 19.6288 | 13.0371 | 9.4159 | 21.1078 | 21.1078 | 21.1078 | 21.0896 | 21.0136 | 20.9322 | 20.845 | 20.7484 | 21.0296 | 20.984 | 20.1342 | 19.578 | 18.8829 | 11.235
| TURRIFF | ST |  |  | 24.6808 | 24.68 | 24.6793 | 24.6683 | 24.6326 | 24.5931 | 24.5524 | 24.507 | 24.4435 | 24.4192 | 24.004 | 22.185 | 13.3556 | 12.8453 | 21.5126 | 21.5068 | 21.4993 | 21.4753 | 21.1754 | 20.8841 | 20.5749 | 20.205 | 13.7174 | 12.7927 | 12.2179 | 10.0579 | 7.5713 | 6.2525 | 21.1067 | 21.106 | 21.1052 | 21.0942 | 21.0585 | 21.019 | 20.9783 | 20.9329 | 20.8694 | 20.8451 | 20.4308 | 11.8046 | 9.0453 | 7.6862
| TURRIFF | SP |  |  | 24.6797 | 24.6785 | 24.6773 | 24.673 | 24.6672 | 24.6615 | 24.6556 | 24.6492 | 24.6419 | 24.6318 | 24.6027 | 24.5691 | 24.2671 | 24.1104 | 21.5164 | 21.5145 | 21.5124 | 21.5071 | 21.4312 | 21.3452 | 21.2123 | 21.0809 | 20.9079 | 20.6757 | 13.7304 | 12.0024 | 10.239 | 8.7118 | 21.1056 | 21.1044 | 21.1032 | 21.0989 | 21.0931 | 21.0874 | 21.0815 | 21.0752 | 21.0678 | 21.0577 | 21.0286 | 20.9951 | 12.225 | 10.6505
RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | 3.229 | 3.2287 | 3.1762 | 3.1268 | 2.485 | 2.3157 | 2.1292 | 1.9361 | 1.7119 | 1.5608 | 1.2829 | 0.6406 | 0.14528 | -0.25282 | 2.915 | 2.9147 | 2.8438 | 2.8065 | 2.4184 | 2.3236 | 2.1631 | 1.9839 | 1.7744 | 1.6381 | 1.3719 | 0.7356 | 0.24385 | -0.15106 | 2.2431 | 2.2428 | 2.1662 | 2.0894 | 1.9559 | 1.8018 | 1.6414 | 1.4751 | 1.2786 | 1.156 | 0.93015 | 0.33931 | -0.14448 | -0.54063
| TYNDRUM | CT |  |  | 3.229 | 3.2287 | 3.1762 | 3.1268 | 2.485 | 2.3157 | 2.1292 | 1.9361 | 1.7119 | 1.5608 | 1.2829 | 0.6406 | 0.14528 | -0.25282 | 2.915 | 2.9147 | 2.8438 | 2.8065 | 2.4184 | 2.3236 | 2.1631 | 1.9839 | 1.7744 | 1.6381 | 1.3719 | 0.7356 | 0.24385 | -0.15106 | 2.2431 | 2.2428 | 2.1662 | 2.0894 | 1.9559 | 1.8018 | 1.6414 | 1.4751 | 1.2786 | 1.156 | 0.93015 | 0.33931 | -0.14448 | -0.54063
| TYNDRUM | LW |  |  | 3.2293 | 3.2292 | 3.2143 | 3.2027 | 3.1911 | 3.1795 | 3.1678 | 3.1561 | 3.1445 | 3.1328 | 3.1093 | 2.4981 | 2.4288 | 2.3544 | 2.9153 | 2.9152 | 2.8974 | 2.8794 | 2.8618 | 2.8462 | 2.8306 | 2.815 | 2.7994 | 2.7863 | 2.4909 | 2.4669 | 2.4255 | 2.3438 | 2.2434 | 2.2434 | 2.2252 | 2.207 | 2.189 | 2.1708 | 2.1526 | 2.1344 | 2.1162 | 2.098 | 2.0613 | 1.9994 | 1.9361 | 1.8713
| TYNDRUM | ST |  |  | 3.2292 | 3.2291 | 3.218 | 3.2102 | 3.2019 | 3.1935 | 3.185 | 3.1763 | 3.1676 | 3.1595 | 3.135 | 3.0937 | 2.4549 | 2.3707 | 2.9152 | 2.9151 | 2.9032 | 2.8912 | 2.8788 | 2.8662 | 2.8544 | 2.8431 | 2.8317 | 2.8209 | 2.7885 | 2.478 | 2.4448 | 2.37 | 2.2433 | 2.2432 | 2.2311 | 2.2189 | 2.2063 | 2.1935 | 2.1807 | 2.1676 | 2.1546 | 2.1421 | 2.1044 | 2.0409 | 1.9693 | 1.8997
| TYNDRUM | SP |  |  | 3.2293 | 3.2292 | 3.2292 | 3.2292 | 3.2291 | 3.2291 | 3.229 | 3.229 | 3.2289 | 3.2287 | 3.228 | 3.227 | 3.2254 | 3.2228 | 2.9153 | 2.9152 | 2.9152 | 2.9151 | 2.9151 | 2.9151 | 2.915 | 2.915 | 2.915 | 2.9148 | 2.9143 | 2.9137 | 2.9123 | 2.91 | 2.2433 | 2.2433 | 2.2432 | 2.2432 | 2.2432 | 2.2432 | 2.2432 | 2.2432 | 2.2432 | 2.2431 | 2.243 | 2.2428 | 2.2419 | 2.2401
DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | 3.2712 | 3.1682 | 3.0507 | 2.9093 | 2.3871 | 2.2284 | 2.0553 | 1.8864 | 1.7391 | 1.6349 | 1.4313 | 1.0949 | 0.77425 | 0.41463 | 3.0686 | 2.9939 | 2.893 | 2.7695 | 2.381 | 2.2366 | 2.0954 | 1.9578 | 1.8383 | 1.7541 | 1.5807 | 1.2932 | 1.0123 | 0.69224 | 2.972 | 2.8665 | 2.735 | 2.3604 | 2.1761 | 1.9914 | 1.8102 | 1.6332 | 1.478 | 1.3657 | 1.1426 | 0.77484 | 0.42416 | 0.035073
| UIG | CT |  |  | 3.2712 | 3.1682 | 3.0507 | 2.9093 | 2.3871 | 2.2284 | 2.0553 | 1.8864 | 1.7391 | 1.6349 | 1.4313 | 1.0949 | 0.77425 | 0.41463 | 3.0686 | 2.9939 | 2.893 | 2.7695 | 2.381 | 2.2366 | 2.0954 | 1.9578 | 1.8383 | 1.7541 | 1.5807 | 1.2932 | 1.0123 | 0.69224 | 2.972 | 2.8665 | 2.735 | 2.3604 | 2.1761 | 1.9914 | 1.8102 | 1.6332 | 1.478 | 1.3657 | 1.1426 | 0.77484 | 0.42416 | 0.035073
| UIG | LW |  |  | 3.3649 | 3.3564 | 3.3482 | 3.3387 | 3.328 | 3.3162 | 3.3034 | 3.2898 | 3.2777 | 3.2652 | 3.2257 | 3.1549 | 3.095 | 3.032 | 3.1365 | 3.1299 | 3.1232 | 3.1142 | 3.1042 | 3.0934 | 3.0819 | 3.07 | 3.0591 | 3.0478 | 3.0125 | 2.9506 | 2.8945 | 2.4474 | 3.068 | 3.0592 | 3.0508 | 3.0411 | 3.0301 | 3.0181 | 3.005 | 2.991 | 2.9787 | 2.9658 | 2.9253 | 2.8528 | 2.4256 | 2.309
| UIG | ST |  |  | 3.3681 | 3.3623 | 3.3566 | 3.349 | 3.3409 | 3.3329 | 3.3232 | 3.3135 | 3.3042 | 3.2959 | 3.2677 | 3.2283 | 3.1837 | 3.1492 | 3.138 | 3.1328 | 3.1273 | 3.1191 | 3.1093 | 3.0988 | 3.0882 | 3.0775 | 3.0672 | 3.0564 | 3.0223 | 2.9717 | 2.4885 | 2.3793 | 3.0712 | 3.0653 | 3.0595 | 3.0516 | 3.0434 | 3.0352 | 3.0253 | 3.0154 | 3.0059 | 2.9974 | 2.9685 | 2.9282 | 2.3787 | 2.2581
| UIG | SP |  |  | 3.3644 | 3.3568 | 3.3492 | 3.3416 | 3.3304 | 3.3194 | 3.3085 | 3.2977 | 3.2871 | 3.2767 | 3.2461 | 3.186 | 3.1366 | 3.0909 | 3.1365 | 3.1309 | 3.1254 | 3.1199 | 3.1108 | 3.1017 | 3.0929 | 3.0841 | 3.0751 | 3.0658 | 3.0389 | 2.9881 | 2.9448 | 2.9032 | 3.0674 | 3.0596 | 3.0519 | 3.0441 | 3.0326 | 3.0213 | 3.0101 | 2.9991 | 2.9883 | 2.9775 | 2.9462 | 2.8846 | 2.8336 | 2.4684
GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | YES | 4.1883 | 4.1875 | 4.1864 | 4.1849 | 4.1801 | 4.1744 | 4.1676 | 4.1599 | 4.1511 | 4.1462 | 4.1296 | 4.0911 | 4.0276 | 3.9046 | 3.5843 | 3.578 | 3.5689 | 3.5481 | 3.5226 | 3.4964 | 3.471 | 3.4492 | 3.4267 | 3.4068 | 3.3527 | 3.3069 | 2.4608 | 2.1934 | 3.3137 | 3.3085 | 3.301 | 3.284 | 3.2625 | 3.2404 | 3.2259 | 3.2181 | 3.2094 | 3.2044 | 3.1878 | 3.1493 | 2.3659 | 2.109
| ULLAPOOL | CT |  |  | 4.1883 | 4.1875 | 4.1864 | 4.1849 | 4.1801 | 4.1744 | 4.1676 | 4.1599 | 4.1511 | 4.1462 | 4.1296 | 4.0911 | 4.0276 | 3.9046 | 3.5843 | 3.578 | 3.5689 | 3.5481 | 3.5226 | 3.4964 | 3.471 | 3.4492 | 3.4267 | 3.4068 | 3.3527 | 3.3069 | 2.4608 | 2.1934 | 3.3137 | 3.3085 | 3.301 | 3.284 | 3.2625 | 3.2404 | 3.2259 | 3.2181 | 3.2094 | 3.2044 | 3.1878 | 3.1493 | 2.3659 | 2.109
| ULLAPOOL | LW |  |  | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 4.1896 | 3.5904 | 3.5892 | 3.5872 | 3.5822 | 3.5768 | 3.5714 | 3.5662 | 3.561 | 3.556 | 3.5506 | 3.5345 | 3.5086 | 3.4857 | 3.4648 | 3.3188 | 3.3178 | 3.3163 | 3.3123 | 3.3079 | 3.3036 | 3.2994 | 3.2952 | 3.2912 | 3.2869 | 3.274 | 3.2532 | 3.2478 | 3.2478
| ULLAPOOL | ST |  |  | 4.1892 | 4.1889 | 4.1886 | 4.1883 | 4.1857 | 4.1826 | 4.1789 | 4.1747 | 4.17 | 4.1685 | 4.1638 | 4.156 | 4.1157 | 4.0927 | 3.587 | 3.5832 | 3.5782 | 3.5687 | 3.5537 | 3.5357 | 3.5204 | 3.5047 | 3.4888 | 3.4756 | 3.4423 | 3.3886 | 3.3358 | 3.3082 | 3.3161 | 3.3129 | 3.3088 | 3.3012 | 3.2886 | 3.2736 | 3.2605 | 3.2471 | 3.2334 | 3.2267 | 3.2221 | 3.2143 | 3.1739 | 3.151
| ULLAPOOL | SP |  |  | 4.1887 | 4.1883 | 4.1878 | 4.1873 | 4.1872 | 4.1871 | 4.187 | 4.1869 | 4.1868 | 4.1861 | 4.1837 | 4.1818 | 4.1698 | 4.1437 | 3.59 | 3.589 | 3.5879 | 3.5868 | 3.5832 | 3.5789 | 3.5748 | 3.5709 | 3.5658 | 3.5603 | 3.5442 | 3.5208 | 3.4886 | 3.4453 | 3.3183 | 3.3175 | 3.3165 | 3.3155 | 3.3126 | 3.3091 | 3.3058 | 3.3026 | 3.2985 | 3.294 | 3.2806 | 3.2614 | 3.2332 | 3.202
SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | 5.7242 | 5.7237 | 5.7233 | 5.7225 | 5.7201 | 5.7172 | 5.7138 | 5.71 | 5.7056 | 5.7031 | 5.6948 | 5.6754 | 5.6436 | 5.1106 | 4.9881 | 4.9876 | 4.987 | 4.9861 | 4.9834 | 4.9803 | 4.9768 | 4.9704 | 4.9635 | 4.9583 | 4.9419 | 4.9095 | 4.8646 | 3.9706 | 5.2261 | 5.2256 | 5.2251 | 5.2243 | 5.2218 | 5.2188 | 5.2153 | 5.2104 | 5.2049 | 5.2012 | 5.1894 | 5.1643 | 5.1267 | 4.6094
| UNST | CT |  |  | 5.7242 | 5.7237 | 5.7233 | 5.7225 | 5.7201 | 5.7172 | 5.7138 | 5.71 | 5.7056 | 5.7031 | 5.6948 | 5.6754 | 5.6436 | 5.5819 | 4.9881 | 4.9876 | 4.987 | 4.9861 | 4.9834 | 4.9803 | 4.9768 | 4.9704 | 4.9635 | 4.9583 | 4.9419 | 4.9095 | 4.8646 | 4.7921 | 5.2261 | 5.2256 | 5.2251 | 5.2243 | 5.2218 | 5.2188 | 5.2153 | 5.2104 | 5.2049 | 5.2012 | 5.1894 | 5.1643 | 5.1267 | 5.0594
| UNST | LW |  |  | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.7249 | 5.1106 | 4.9887 | 4.9886 | 4.9885 | 4.9883 | 4.988 | 4.9877 | 4.9874 | 4.9871 | 4.9869 | 4.9866 | 4.9857 | 4.9843 | 4.983 | 3.9706 | 5.2268 | 5.2267 | 5.2267 | 5.2266 | 5.2264 | 5.2263 | 5.2262 | 5.2261 | 5.226 | 5.2258 | 5.2255 | 5.2248 | 5.2242 | 4.6094
| UNST | ST |  |  | 5.7247 | 5.7246 | 5.7245 | 5.7243 | 5.7233 | 5.722 | 5.7205 | 5.7189 | 5.7169 | 5.7164 | 5.7145 | 5.7113 | 5.6951 | 5.6858 | 4.9886 | 4.9884 | 4.9883 | 4.9881 | 4.9869 | 4.9855 | 4.9834 | 4.9811 | 4.9786 | 4.9762 | 4.9691 | 4.9577 | 4.9331 | 4.9157 | 5.2266 | 5.2265 | 5.2263 | 5.2262 | 5.2251 | 5.2238 | 5.222 | 5.2201 | 5.2179 | 5.2165 | 5.2124 | 5.2056 | 5.1857 | 5.1729
| UNST | SP |  |  | 5.7246 | 5.7245 | 5.7243 | 5.7242 | 5.7242 | 5.7242 | 5.7241 | 5.7241 | 5.7241 | 5.7239 | 5.7232 | 5.7227 | 5.7193 | 5.7119 | 4.9885 | 4.9884 | 4.9882 | 4.9881 | 4.988 | 4.988 | 4.9878 | 4.9875 | 4.9872 | 4.9863 | 4.9836 | 4.98 | 4.9737 | 4.9635 | 5.2265 | 5.2264 | 5.2263 | 5.2261 | 5.2261 | 5.2261 | 5.2259 | 5.2258 | 5.2257 | 5.2252 | 5.2236 | 5.2217 | 5.217 | 5.2085
SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | 11.8359 | 11.8331 | 11.8294 | 11.8223 | 11.8117 | 11.802 | 11.7907 | 11.7775 | 11.7628 | 11.7543 | 11.7262 | 11.6609 | 11.5536 | 11.3453 | 10.3442 | 10.3387 | 10.3312 | 10.3236 | 10.3113 | 10.2977 | 10.2824 | 10.2665 | 10.2491 | 10.2376 | 10.2008 | 10.1214 | 9.9998 | 7.7531 | 11.2151 | 11.2072 | 11.196 | 11.1707 | 11.138 | 11.1042 | 11.0692 | 11.0392 | 11.0081 | 10.9818 | 10.9009 | 10.7498 | 10.5789 | 10.354
| VOE | CT |  |  | 11.8359 | 11.8331 | 11.8294 | 11.8223 | 11.8117 | 11.802 | 11.7907 | 11.7775 | 11.7628 | 11.7543 | 11.7262 | 11.6609 | 11.5536 | 11.3453 | 10.3442 | 10.3387 | 10.3312 | 10.3236 | 10.3113 | 10.2977 | 10.2824 | 10.2665 | 10.2491 | 10.2376 | 10.2008 | 10.1214 | 9.9998 | 7.7531 | 11.2151 | 11.2072 | 11.196 | 11.1707 | 11.138 | 11.1042 | 11.0692 | 11.0392 | 11.0081 | 10.9818 | 10.9009 | 10.7498 | 10.5789 | 10.354
| VOE | LW |  |  | 11.8395 | 11.8394 | 11.8392 | 11.8389 | 11.8385 | 11.8382 | 11.8378 | 11.8375 | 11.8372 | 11.8368 | 11.8357 | 11.834 | 11.8323 | 11.8306 | 10.3505 | 10.3502 | 10.3498 | 10.3489 | 10.3478 | 10.3467 | 10.3456 | 10.3446 | 10.3436 | 10.3425 | 10.3393 | 10.3345 | 10.3331 | 10.3317 | 11.224 | 11.2236 | 11.223 | 11.2214 | 11.2196 | 11.2178 | 11.2161 | 11.2145 | 11.2128 | 11.211 | 11.2058 | 11.1974 | 11.1889 | 11.1805
| VOE | ST |  |  | 11.8385 | 11.8378 | 11.8368 | 11.8352 | 11.8307 | 11.8253 | 11.8195 | 11.8133 | 11.8078 | 11.8063 | 11.8015 | 11.7936 | 11.7524 | 11.7292 | 10.3485 | 10.3467 | 10.3444 | 10.3401 | 10.332 | 10.3262 | 10.3208 | 10.3149 | 10.3085 | 10.305 | 10.2946 | 10.2777 | 10.2275 | 10.1953 | 11.2211 | 11.2183 | 11.2147 | 11.2079 | 11.1964 | 11.1827 | 11.169 | 11.155 | 11.1406 | 11.1273 | 11.0884 | 11.0255 | 10.9298 | 10.8522
| VOE | SP |  |  | 11.8386 | 11.838 | 11.8375 | 11.8369 | 11.8341 | 11.8313 | 11.8284 | 11.8252 | 11.8203 | 11.8144 | 11.7943 | 11.775 | 11.6132 | 11.5406 | 10.3495 | 10.3489 | 10.3481 | 10.3474 | 10.3436 | 10.3395 | 10.3352 | 10.3306 | 10.3238 | 10.3161 | 10.2952 | 10.2767 | 10.1118 | 10.0362 | 11.223 | 11.2222 | 11.2213 | 11.2203 | 11.2156 | 11.2104 | 11.2047 | 11.1987 | 11.1903 | 11.1808 | 11.1502 | 11.1146 | 10.9335 | 10.8424
GLENAGNES | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | 26.7041 | 26.6601 | 26.616 | 26.4067 | 26.2194 | 25.6253 | 22.6276 | 21.7036 | 21.5735 | 21.2252 | 20.1305 | 18.2668 | 17.0234 | 15.9654 | 24.1148 | 24.0695 | 24.0234 | 23.818 | 23.6165 | 21.5795 | 20.7173 | 19.7888 | 19.6575 | 19.3088 | 18.2135 | 16.3487 | 15.1044 | 14.0434 | 24.3069 | 24.2553 | 24.1993 | 24.0138 | 23.7397 | 21.7847 | 20.9223 | 19.9949 | 19.8645 | 19.5165 | 18.4224 | 16.5597 | 15.3173 | 14.2622
| WALTON | CT |  |  | 26.836 | 26.8027 | 26.7693 | 26.7689 | 26.6022 | 26.2912 | 26.0088 | 25.726 | 23.2215 | 23.0371 | 22.4812 | 19.1678 | 17.1018 | 16.0976 | 24.2467 | 24.2124 | 24.1775 | 24.1735 | 24.003 | 23.6883 | 21.9638 | 21.6785 | 21.3066 | 21.1211 | 20.5642 | 17.2493 | 15.1817 | 14.1759 | 24.4392 | 24.3998 | 24.3574 | 24.3353 | 24.1454 | 23.8117 | 23.507 | 21.8841 | 21.5127 | 21.3279 | 20.773 | 17.4612 | 15.3968 | 14.3942
| WALTON | LW |  |  | 26.7041 | 26.6601 | 26.616 | 26.616 | 26.2194 | 25.6253 | 22.8741 | 22.2359 | 21.5735 | 21.3206 | 20.5621 | 18.9009 | 17.0815 | 15.9654 | 24.1148 | 24.0695 | 24.0234 | 24.0185 | 23.6165 | 21.5795 | 20.9608 | 20.3201 | 19.6575 | 19.4043 | 18.6448 | 16.9821 | 15.161 | 14.0434 | 24.3069 | 24.2553 | 24.1993 | 24.1695 | 23.7397 | 21.7847 | 21.1666 | 20.5265 | 19.8645 | 19.6119 | 18.8543 | 17.1947 | 15.3768 | 14.2622
| WALTON | ST |  |  | 26.9685 | 26.9465 | 26.9244 | 26.9244 | 26.8141 | 25.6867 | 22.6276 | 21.7036 | 21.5901 | 21.2252 | 20.1305 | 18.2668 | 17.0234 | 16.3872 | 24.3795 | 24.3567 | 24.3336 | 24.3317 | 24.2187 | 21.6458 | 20.7173 | 19.7888 | 19.674 | 19.3088 | 18.2135 | 16.3487 | 15.1044 | 14.4672 | 24.5733 | 24.5466 | 24.5185 | 24.5067 | 24.3806 | 21.8498 | 20.9223 | 19.9949 | 19.8812 | 19.5165 | 18.4224 | 16.5597 | 15.3173 | 14.6821
| WALTON | SP |  |  | 27.1007 | 27.0897 | 27.0787 | 26.4067 | 26.3516 | 26.2965 | 26.2414 | 26.1864 | 26.1313 | 25.8408 | 22.8344 | 21.3189 | 20.3191 | 19.9635 | 24.5124 | 24.5013 | 24.4902 | 23.818 | 23.7622 | 23.7063 | 23.6487 | 23.5911 | 23.5328 | 21.7992 | 20.9258 | 19.4071 | 18.4042 | 18.0475 | 24.7099 | 24.6983 | 24.6866 | 24.0138 | 23.9543 | 23.894 | 23.8237 | 23.7535 | 23.679 | 22.0033 | 21.1304 | 19.6125 | 18.6103 | 18.2543
INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | 36.8461 | 36.8049 | 36.7574 | 36.0432 | 35.948 | 35.8493 | 35.7041 | 35.3384 | 34.9583 | 34.8353 | 34.4681 | 33.9895 | 33.2676 | 32.9553 | 32.7189 | 32.6749 | 32.623 | 31.9105 | 31.8107 | 31.7065 | 31.5236 | 31.1466 | 30.7555 | 30.6206 | 30.2181 | 29.7102 | 28.9077 | 28.436 | 30.328 | 30.2844 | 30.2333 | 29.5205 | 29.4214 | 29.3181 | 29.1412 | 28.766 | 28.3766 | 28.2436 | 27.8467 | 27.402 | 26.8099 | 26.5495
| WATERLOO PLACE | CT |  |  | 36.9385 | 36.9066 | 36.8704 | 36.8393 | 36.6902 | 36.5414 | 36.393 | 36.2374 | 36.0822 | 35.9941 | 35.7308 | 33.9895 | 33.2676 | 32.9553 | 32.8114 | 32.7773 | 32.7379 | 32.6989 | 32.5413 | 32.3843 | 32.2278 | 32.0623 | 31.8975 | 31.799 | 31.5048 | 29.7135 | 28.9077 | 28.436 | 30.4205 | 30.3868 | 30.3478 | 30.3101 | 30.1539 | 29.9981 | 29.843 | 29.679 | 29.5158 | 29.4188 | 29.1295 | 27.402 | 26.8099 | 26.5495
| WATERLOO PLACE | LW |  |  | 36.8461 | 36.8049 | 36.7574 | 36.7152 | 36.3925 | 36.0555 | 35.7041 | 35.3384 | 34.9583 | 34.8353 | 34.4681 | 34.017 | 33.7199 | 33.4329 | 32.7189 | 32.6749 | 32.623 | 32.5701 | 32.2353 | 31.8865 | 31.5236 | 31.1466 | 30.7555 | 30.6206 | 30.2181 | 29.7102 | 29.2389 | 28.7702 | 30.328 | 30.2844 | 30.2333 | 30.182 | 29.8492 | 29.5022 | 29.1412 | 28.766 | 28.3766 | 28.2436 | 27.8467 | 27.5299 | 27.3017 | 27.0739
| WATERLOO PLACE | ST |  |  | 37.0343 | 37.0137 | 36.9914 | 36.0432 | 35.948 | 35.8493 | 35.7481 | 35.6474 | 35.5471 | 35.4893 | 35.3184 | 35.1009 | 34.8947 | 34.6919 | 32.9082 | 32.8862 | 32.8621 | 31.9105 | 31.8107 | 31.7065 | 31.5992 | 31.4925 | 31.3863 | 31.3216 | 31.1307 | 30.8813 | 30.6439 | 30.4099 | 30.5171 | 30.4954 | 30.4716 | 29.5205 | 29.4214 | 29.3181 | 29.2117 | 29.106 | 29.0008 | 28.9372 | 28.7494 | 28.5051 | 28.2726 | 28.1242
| WATERLOO PLACE | SP |  |  | 37.1312 | 37.1227 | 37.1141 | 36.6457 | 36.6023 | 36.5579 | 36.5117 | 36.4656 | 36.4173 | 36.391 | 36.3132 | 36.2178 | 36.1315 | 36.0455 | 33.0064 | 32.9977 | 32.9889 | 32.5202 | 32.4755 | 32.4296 | 32.3814 | 32.3333 | 32.2824 | 32.2533 | 32.1675 | 32.0595 | 31.9615 | 31.8648 | 30.6151 | 30.6065 | 30.5977 | 30.129 | 30.0845 | 30.0389 | 29.991 | 29.9432 | 29.8927 | 29.8641 | 29.7795 | 29.6736 | 29.5774 | 29.4824
LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | 30.3669 | 30.363 | 30.3586 | 30.3524 | 30.3241 | 30.2915 | 30.2541 | 30.212 | 30.162 | 30.1387 | 30.063 | 29.8314 | 29.5219 | 28.9857 | 27.9557 | 27.9374 | 27.9114 | 27.8535 | 27.7697 | 27.6824 | 27.5912 | 27.4876 | 27.3771 | 27.2883 | 27.0865 | 26.7522 | 26.3389 | 25.7008 | 27.2644 | 27.2506 | 27.2312 | 27.1891 | 27.1223 | 27.0518 | 26.9771 | 26.8924 | 26.8004 | 26.7317 | 26.5213 | 26.0711 | 25.6602 | 25.0252
| WEST KIRKTON | CT |  |  | 30.3669 | 30.363 | 30.3586 | 30.3524 | 30.3241 | 30.2915 | 30.2541 | 30.212 | 30.162 | 30.1387 | 30.063 | 29.8314 | 29.5219 | 28.9857 | 27.9557 | 27.9374 | 27.9114 | 27.8535 | 27.7697 | 27.6824 | 27.5912 | 27.4876 | 27.3771 | 27.2883 | 27.0865 | 26.7522 | 26.3389 | 25.7008 | 27.2644 | 27.2506 | 27.2312 | 27.1891 | 27.1223 | 27.0518 | 26.9771 | 26.8924 | 26.8004 | 26.7317 | 26.5213 | 26.0711 | 25.6602 | 25.0252
| WEST KIRKTON | LW |  |  | 30.3723 | 30.3723 | 30.3723 | 30.3723 | 30.3607 | 30.3488 | 30.3366 | 30.3235 | 30.3046 | 30.3013 | 30.292 | 30.2496 | 30.2187 | 30.2078 | 27.9756 | 27.9738 | 27.971 | 27.9639 | 27.9444 | 27.9249 | 27.9051 | 27.8846 | 27.8585 | 27.8475 | 27.8151 | 27.7356 | 27.6673 | 27.6194 | 27.2799 | 27.2786 | 27.2767 | 27.2718 | 27.2547 | 27.2375 | 27.22 | 27.2018 | 27.1779 | 27.1693 | 27.144 | 27.0759 | 27.019 | 26.9824
| WEST KIRKTON | ST |  |  | 30.3713 | 30.3706 | 30.3699 | 30.3691 | 30.357 | 30.3432 | 30.3285 | 30.3117 | 30.2898 | 30.2838 | 30.2668 | 30.2172 | 30.0717 | 29.9995 | 27.9701 | 27.9642 | 27.9564 | 27.9421 | 27.9116 | 27.8757 | 27.8276 | 27.778 | 27.724 | 27.6748 | 27.5322 | 27.2806 | 27.065 | 26.928 | 27.2757 | 27.2714 | 27.2658 | 27.2556 | 27.2308 | 27.2017 | 27.1639 | 27.1243 | 27.0801 | 27.0442 | 26.9401 | 26.7504 | 26.4659 | 26.2555
| WEST KIRKTON | SP |  |  | 30.3705 | 30.3696 | 30.3687 | 30.3677 | 30.3667 | 30.3658 | 30.3648 | 30.3637 | 30.362 | 30.3591 | 30.3487 | 30.3401 | 30.2609 | 30.1915 | 27.9742 | 27.9724 | 27.9703 | 27.9681 | 27.9607 | 27.952 | 27.9401 | 27.9283 | 27.9128 | 27.893 | 27.834 | 27.7494 | 27.5986 | 27.4614 | 27.2784 | 27.2768 | 27.2751 | 27.2733 | 27.2678 | 27.2615 | 27.253 | 27.2444 | 27.2331 | 27.2185 | 27.1745 | 27.1132 | 26.9843 | 26.8679
KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | 0.0046615 | -0.10297 | -0.31794 | -0.57497 | -0.83176 | -1.114 | -1.3976 | -1.6826 | -1.9513 | -2.1863 | -2.594 | -3.2562 | -3.8278 | -4.3945 | 0.022517 | -0.063661 | -0.25569 | -0.48113 | -0.70701 | -0.95676 | -1.208 | -1.4621 | -1.7038 | -1.919 | -2.2992 | -2.9203 | -3.4592 | -3.993 | 0.0013923 | -0.10683 | -0.33229 | -0.59504 | -0.85748 | -1.145 | -1.4333 | -1.7236 | -1.9968 | -2.2347 | -2.6489 | -3.3213 | -3.9024 | -4.4786
| WESTER DRUMMOND | CT |  |  | 0.0046615 | -0.10297 | -0.31794 | -0.57497 | -0.83176 | -1.114 | -1.3976 | -1.6826 | -1.9513 | -2.1863 | -2.594 | -3.2562 | -3.8278 | -4.3945 | 0.022517 | -0.063661 | -0.25569 | -0.48113 | -0.70701 | -0.95676 | -1.208 | -1.4621 | -1.7038 | -1.919 | -2.2992 | -2.9203 | -3.4592 | -3.993 | 0.0013923 | -0.10683 | -0.33229 | -0.59504 | -0.85748 | -1.145 | -1.4333 | -1.7236 | -1.9968 | -2.2347 | -2.6489 | -3.3213 | -3.9024 | -4.4786
| WESTER DRUMMOND | LW |  |  | 0.10537 | 0.092849 | 0.027429 | -0.042888 | -0.11413 | -0.18666 | -0.26014 | -0.33472 | -0.4073 | -0.48063 | -0.64173 | -0.91766 | -1.1884 | -1.4669 | 0.10297 | 0.092717 | 0.03077 | -0.035308 | -0.10213 | -0.16998 | -0.23855 | -0.308 | -0.37584 | -0.44436 | -0.59341 | -0.84794 | -1.0993 | -1.3575 | 0.098975 | 0.089581 | 0.022158 | -0.049095 | -0.12138 | -0.19499 | -0.26956 | -0.34525 | -0.41887 | -0.4933 | -0.65773 | -0.93928 | -1.2153 | -1.4992
| WESTER DRUMMOND | ST |  |  | 0.10849 | 0.097987 | 0.055887 | 0.0076415 | -0.040398 | -0.088508 | -0.13795 | -0.18736 | -0.23619 | -0.28493 | -0.43483 | -0.67968 | -0.92621 | -1.1716 | 0.10477 | 0.096162 | 0.055621 | 0.0099138 | -0.035998 | -0.082282 | -0.12895 | -0.17559 | -0.22175 | -0.26787 | -0.40907 | -0.64084 | -0.87487 | -1.1089 | 0.1039 | 0.094395 | 0.050254 | 0.00083774 | -0.048683 | -0.098505 | -0.14917 | -0.19976 | -0.24976 | -0.29968 | -0.45311 | -0.70338 | -0.95515 | -1.2056
| WESTER DRUMMOND | SP |  |  | 0.10492 | 0.093408 | 0.085706 | 0.07763 | 0.065083 | 0.052477 | 0.040305 | 0.02829 | 0.01616 | 0.0042164 | -0.030627 | -0.097891 | -0.15297 | -0.20525 | 0.10279 | 0.093717 | 0.0872 | 0.08064 | 0.070093 | 0.059445 | 0.049291 | 0.039264 | 0.029114 | 0.019174 | -0.0097996 | -0.06534 | -0.11101 | -0.15438 | 0.098712 | 0.090631 | 0.08253 | 0.074379 | 0.061547 | 0.048664 | 0.036277 | 0.024049 | 0.011747 | -0.0003191 | -0.0356 | -0.10357 | -0.15929 | -0.21219
CARRADALE | WESTPARK FERGUS | MINIMUM HEADROOM | NR 66116 20950 | YES | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 3.4402 | 4.6007 | 4.6005 | 4.6002 | 4.5996 | 4.5988 | 4.5981 | 4.5973 | 4.5966 | 4.596 | 4.5952 | 4.593 | 4.5894 | 4.5859 | 3.7823 | 4.3748 | 4.3745 | 4.3741 | 4.373 | 4.3718 | 4.3707 | 4.3704 | 4.3701 | 4.3698 | 4.3695 | 4.3687 | 4.3673 | 4.3671 | 3.6455
| WESTPARK FERGUS | CT |  |  | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.6007 | 4.6006 | 4.6003 | 4.5999 | 4.5993 | 4.5988 | 4.5983 | 4.5978 | 4.5973 | 4.5968 | 4.5953 | 4.5928 | 4.5903 | 4.5878 | 4.3748 | 4.3746 | 4.3743 | 4.3735 | 4.3726 | 4.3718 | 4.371 | 4.3706 | 4.3704 | 4.3702 | 4.3695 | 4.3686 | 4.3676 | 4.3671
| WESTPARK FERGUS | LW |  |  | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 3.4402 | 4.6007 | 4.6005 | 4.6002 | 4.5996 | 4.5988 | 4.5981 | 4.5973 | 4.5966 | 4.596 | 4.5952 | 4.593 | 4.5894 | 4.5859 | 3.7823 | 4.3748 | 4.3745 | 4.3741 | 4.373 | 4.3718 | 4.3707 | 4.3704 | 4.3701 | 4.3698 | 4.3695 | 4.3687 | 4.3673 | 4.3671 | 3.6455
| WESTPARK FERGUS | ST |  |  | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.6007 | 4.6007 | 4.6006 | 4.6003 | 4.6 | 4.5997 | 4.5994 | 4.599 | 4.5987 | 4.5984 | 4.5974 | 4.5958 | 4.5942 | 4.5927 | 4.3749 | 4.3748 | 4.3746 | 4.3742 | 4.3738 | 4.3732 | 4.3727 | 4.3722 | 4.3716 | 4.3711 | 4.3704 | 4.3698 | 4.3691 | 4.3685
| WESTPARK FERGUS | SP |  |  | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.0968 | 4.6008 | 4.6008 | 4.6008 | 4.6008 | 4.6007 | 4.6006 | 4.6005 | 4.6004 | 4.6002 | 4.6001 | 4.5997 | 4.5991 | 4.5985 | 4.5979 | 4.375 | 4.375 | 4.375 | 4.375 | 4.3748 | 4.3747 | 4.3745 | 4.3743 | 4.3741 | 4.3739 | 4.3732 | 4.3722 | 4.3713 | 4.3706
THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | 3.4286 | 3.4286 | 3.4285 | 3.4284 | 3.3232 | 3.2156 | 3.1043 | 2.985 | 2.8134 | 2.7838 | 2.6992 | 0.96572 | 0.81728 | 0.76478 | 3.5091 | 3.5087 | 3.5082 | 3.507 | 3.4026 | 3.2945 | 3.1828 | 3.063 | 2.8908 | 2.8608 | 2.7746 | 1.5718 | 1.4208 | 1.3659 | 2.5008 | 2.4974 | 2.4923 | 2.48 | 2.384 | 2.2709 | 2.1542 | 2.0296 | 1.8528 | 1.8177 | 1.7166 | -0.24659 | -0.42176 | -0.50072
| WESTRAY | CT |  |  | 3.4286 | 3.4286 | 3.4285 | 3.4284 | 3.4242 | 3.3499 | 3.2715 | 3.1894 | 3.0731 | 3.0536 | 3.0119 | 1.1578 | 0.96986 | 0.91277 | 3.5091 | 3.5087 | 3.5082 | 3.507 | 3.5015 | 3.4261 | 3.3465 | 3.2639 | 3.1471 | 3.1271 | 3.0839 | 1.7603 | 1.5698 | 1.5102 | 2.5008 | 2.4974 | 2.4923 | 2.48 | 2.4626 | 2.3755 | 2.2845 | 2.197 | 2.0755 | 2.0502 | 1.9917 | -0.092859 | -0.30832 | -0.39258
| WESTRAY | LW |  |  | 3.4287 | 3.4287 | 3.4287 | 3.4287 | 3.3232 | 3.2156 | 3.1043 | 2.985 | 2.8134 | 2.7838 | 2.6992 | 0.96572 | 0.81728 | 0.76478 | 3.5094 | 3.5093 | 3.5091 | 3.5087 | 3.4026 | 3.2945 | 3.1828 | 3.063 | 2.8908 | 2.8608 | 2.7746 | 1.5718 | 1.4208 | 1.3659 | 2.5035 | 2.5022 | 2.5002 | 2.4951 | 2.384 | 2.2709 | 2.1542 | 2.0296 | 1.8528 | 1.8177 | 1.7166 | -0.24659 | -0.42176 | -0.50072
| WESTRAY | ST |  |  | 3.4287 | 3.4287 | 3.4287 | 3.4287 | 3.4259 | 3.3742 | 3.325 | 3.2693 | 3.1794 | 3.161 | 3.1152 | 1.4368 | 1.1738 | 1.0894 | 3.5093 | 3.5091 | 3.5089 | 3.5084 | 3.505 | 3.4525 | 3.4029 | 3.3468 | 3.2565 | 3.2377 | 3.1909 | 2.03 | 1.7653 | 1.6793 | 2.5025 | 2.5005 | 2.4979 | 2.4928 | 2.483 | 2.4228 | 2.3692 | 2.309 | 2.2147 | 2.1925 | 2.1358 | 0.24215 | -0.038074 | -0.13958
| WESTRAY | SP |  |  | 3.4287 | 3.4287 | 3.4287 | 3.4287 | 3.4283 | 3.4279 | 3.4275 | 3.4271 | 3.4263 | 3.4255 | 3.4227 | 3.4202 | 3.3918 | 3.3829 | 3.5095 | 3.5095 | 3.5095 | 3.5094 | 3.5088 | 3.5082 | 3.5077 | 3.5071 | 3.5061 | 3.5052 | 3.5019 | 3.4988 | 3.4698 | 3.4604 | 2.5044 | 2.5042 | 2.5038 | 2.5034 | 2.501 | 2.4982 | 2.4961 | 2.4941 | 2.4914 | 2.4891 | 2.4819 | 2.4725 | 2.4378 | 2.423
TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | 12.5032 | 12.5007 | 12.498 | 12.4939 | 12.4803 | 12.4639 | 12.4445 | 12.4218 | 12.395 | 12.3807 | 12.3328 | 7.1927 | 4.5782 | 2.8447 | 10.0969 | 10.0803 | 10.0564 | 10.0016 | 9.8676 | 9.7429 | 9.6166 | 9.5388 | 9.4871 | 7.2362 | 5.7663 | 3.81 | 0.65566 | -1.2807 | 10.2275 | 10.2194 | 10.21 | 10.1909 | 10.1774 | 10.1609 | 10.1415 | 10.1189 | 7.3285 | 6.9565 | 5.5652 | 3.6462 | 0.50128 | -1.4315
| WHITEHOUSE | CT |  |  | 12.5032 | 12.5007 | 12.498 | 12.4939 | 12.4803 | 12.4639 | 12.4445 | 12.4218 | 12.395 | 12.3807 | 12.3328 | 7.7193 | 4.9304 | 2.8447 | 10.0969 | 10.0803 | 10.0564 | 10.0016 | 9.8676 | 9.7429 | 9.6166 | 9.5388 | 9.4871 | 9.4412 | 6.31 | 4.4986 | 1.1683 | -1.2807 | 10.2275 | 10.2194 | 10.21 | 10.1909 | 10.1774 | 10.1609 | 10.1415 | 10.1189 | 10.092 | 7.2164 | 6.0568 | 4.3319 | 1.0111 | -1.4315
| WHITEHOUSE | LW |  |  | 12.5067 | 12.5067 | 12.5067 | 12.5067 | 12.5056 | 12.5033 | 12.4998 | 12.4947 | 12.4853 | 12.4833 | 12.4746 | 7.1927 | 4.5782 | 3.5709 | 10.1142 | 10.1122 | 10.1089 | 10.1007 | 9.9385 | 9.7768 | 9.625 | 9.5917 | 9.5466 | 7.2362 | 5.7663 | 3.81 | 0.65566 | -0.55921 | 10.2377 | 10.2367 | 10.2351 | 10.2312 | 10.2026 | 10.2003 | 10.1968 | 10.1918 | 7.3285 | 6.9565 | 5.5652 | 3.6462 | 0.50128 | -0.70994
| WHITEHOUSE | ST |  |  | 12.5058 | 12.5051 | 12.5045 | 12.5038 | 12.4976 | 12.4901 | 12.4813 | 12.4709 | 12.4581 | 12.4539 | 12.4408 | 12.4058 | 6.6475 | 4.6645 | 10.1067 | 10.0988 | 10.0883 | 10.0688 | 9.9786 | 9.8858 | 9.7946 | 9.6867 | 9.578 | 9.5446 | 6.8345 | 5.2552 | 3.1859 | 0.80225 | 10.2336 | 10.2294 | 10.2246 | 10.2179 | 10.1947 | 10.1872 | 10.1783 | 10.1679 | 10.1551 | 10.151 | 6.5496 | 5.0868 | 3.0234 | 0.6468
| WHITEHOUSE | SP |  |  | 12.5049 | 12.504 | 12.5031 | 12.5021 | 12.5019 | 12.5017 | 12.5015 | 12.5013 | 12.5009 | 12.4994 | 12.4935 | 12.4882 | 12.4362 | 12.3745 | 10.1129 | 10.1109 | 10.1086 | 10.1061 | 10.0826 | 10.0554 | 10.0192 | 9.9835 | 9.9364 | 9.8771 | 9.6367 | 9.5636 | 7.2128 | 6.6889 | 10.2362 | 10.2347 | 10.2331 | 10.2314 | 10.221 | 10.2123 | 10.2007 | 10.1983 | 10.198 | 10.1964 | 10.1906 | 10.1852 | 6.9338 | 6.41
PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | 21.2589 | 21.1406 | 21.025 | 20.8732 | 20.6878 | 20.4883 | 20.2713 | 20.0322 | 19.734 | 19.6091 | 19.3341 | 12.8966 | 8.8567 | 3.2104 | 18.9914 | 18.8323 | 18.6447 | 18.2989 | 17.9128 | 17.5487 | 17.1793 | 16.9406 | 16.6649 | 13.7181 | 13.0289 | 10.8831 | 7.3586 | 2.5306 | 19.9021 | 19.7557 | 19.6001 | 19.3566 | 19.0732 | 18.7774 | 18.4656 | 18.1895 | 17.8546 | 17.6924 | 13.3583 | 10.9918 | 6.8642 | 1.1499
| WHITESTRIPES | CT |  |  | 21.2589 | 21.1406 | 21.025 | 20.8732 | 20.6878 | 20.4883 | 20.2713 | 20.0322 | 19.734 | 19.6091 | 19.3341 | 12.8966 | 8.8567 | 3.2104 | 18.9914 | 18.8323 | 18.6447 | 18.2989 | 17.9128 | 17.5487 | 17.1793 | 16.9406 | 16.6649 | 13.7181 | 13.0289 | 10.8831 | 7.3586 | 2.5306 | 19.9021 | 19.7557 | 19.6001 | 19.3566 | 19.0732 | 18.7774 | 18.4656 | 18.1895 | 17.8546 | 17.6924 | 13.3583 | 10.9918 | 6.8642 | 1.1499
| WHITESTRIPES | LW |  |  | 21.3702 | 21.3609 | 21.352 | 21.3416 | 21.33 | 21.3171 | 21.3032 | 21.274 | 21.2168 | 21.1887 | 21.0825 | 20.8955 | 20.6118 | 20.4012 | 19.1516 | 19.1428 | 19.1334 | 19.12 | 19.105 | 19.0891 | 19.0724 | 19.0408 | 18.9817 | 18.9514 | 18.8395 | 18.6452 | 18.3576 | 18.1467 | 20.0437 | 20.0336 | 20.0235 | 20.0108 | 19.9965 | 19.9811 | 19.9646 | 19.9328 | 19.873 | 19.8421 | 19.7275 | 19.5266 | 19.2281 | 19.0023
| WHITESTRIPES | ST |  |  | 21.3705 | 21.3623 | 21.3538 | 21.343 | 21.3138 | 21.2806 | 21.2416 | 21.1917 | 21.1121 | 21.0819 | 20.9829 | 18.7216 | 11.7886 | 8.4855 | 19.1042 | 19.0561 | 18.9941 | 18.8793 | 18.7084 | 18.5048 | 18.3926 | 18.281 | 18.1409 | 18.065 | 17.8338 | 13.1451 | 10.4123 | 7.658 | 20.0256 | 20.001 | 19.9708 | 19.9182 | 19.8324 | 19.7312 | 19.6605 | 19.5795 | 19.4694 | 19.4159 | 19.2488 | 13.2694 | 10.06 | 6.7087
| WHITESTRIPES | SP |  |  | 21.362 | 21.3496 | 21.3372 | 21.3246 | 21.3117 | 21.2989 | 21.2861 | 21.2724 | 21.2543 | 21.2294 | 21.132 | 18.7287 | 13.1203 | 11.4023 | 19.136 | 19.1195 | 19.1019 | 19.0835 | 19.0325 | 18.974 | 18.9379 | 18.9011 | 18.8527 | 18.8072 | 18.6503 | 16.5787 | 12.735 | 11.0048 | 20.0325 | 20.0176 | 20.0023 | 19.9865 | 19.9573 | 19.9251 | 19.9019 | 19.8778 | 19.8466 | 19.8123 | 19.6879 | 13.7787 | 11.8959 | 10.2237
CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | 9.4164 | 9.4154 | 9.4072 | 9.3985 | 9.386 | 9.371 | 9.3546 | 9.337 | 9.3178 | 9.3025 | 9.2668 | 9.1962 | 9.1021 | 7.86 | 8.8415 | 8.8402 | 8.8312 | 8.8209 | 8.8067 | 8.79 | 8.7718 | 8.7439 | 8.7146 | 8.6883 | 8.6208 | 7.8245 | 7.5563 | 7.2267 | 8.7743 | 8.7734 | 8.7647 | 8.7555 | 8.7424 | 8.7268 | 8.7097 | 8.6914 | 8.6716 | 8.6556 | 8.6186 | 7.766 | 7.4794 | 7.1319
| WHITING BAY | CT |  |  | 9.4164 | 9.4154 | 9.4072 | 9.3985 | 9.386 | 9.371 | 9.3546 | 9.337 | 9.3178 | 9.3025 | 9.2668 | 9.1962 | 9.1021 | 7.86 | 8.8415 | 8.8402 | 8.8312 | 8.8209 | 8.8067 | 8.79 | 8.7718 | 8.7439 | 8.7146 | 8.6883 | 8.6208 | 7.8245 | 7.5563 | 7.2267 | 8.7743 | 8.7734 | 8.7647 | 8.7555 | 8.7424 | 8.7268 | 8.7097 | 8.6914 | 8.6716 | 8.6556 | 8.6186 | 7.766 | 7.4794 | 7.1319
| WHITING BAY | LW |  |  | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 9.4178 | 8.8429 | 8.8425 | 8.8419 | 8.8402 | 8.8384 | 8.8366 | 8.8349 | 8.8332 | 8.8315 | 8.8297 | 8.8243 | 8.8158 | 8.8071 | 8.7985 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757 | 8.7757
| WHITING BAY | ST |  |  | 9.4175 | 9.4173 | 9.4171 | 9.4168 | 9.4149 | 9.4126 | 9.4099 | 9.4068 | 9.4033 | 9.4021 | 9.3986 | 9.3929 | 9.3629 | 9.3459 | 8.8428 | 8.8424 | 8.8419 | 8.8411 | 8.8385 | 8.8353 | 8.829 | 8.8223 | 8.8152 | 8.8072 | 8.7838 | 8.746 | 7.9843 | 7.8511 | 8.7754 | 8.7752 | 8.775 | 8.7748 | 8.7729 | 8.7705 | 8.7678 | 8.7647 | 8.7612 | 8.7601 | 8.7566 | 8.7509 | 7.9694 | 7.8303
| WHITING BAY | SP |  |  | 9.4172 | 9.4169 | 9.4166 | 9.4162 | 9.4162 | 9.4161 | 9.416 | 9.416 | 9.4159 | 9.4154 | 9.4138 | 9.4125 | 9.4044 | 9.3868 | 8.8427 | 8.8423 | 8.842 | 8.8416 | 8.8414 | 8.8411 | 8.8398 | 8.8385 | 8.8368 | 8.8337 | 8.8243 | 8.811 | 8.7915 | 8.7631 | 8.7751 | 8.7748 | 8.7745 | 8.7742 | 8.7741 | 8.7741 | 8.774 | 8.7739 | 8.7739 | 8.7734 | 8.7718 | 8.7705 | 8.7624 | 8.7447
MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | YES | 31.565 | 31.5648 | 31.5645 | 31.5641 | 30.9129 | 30.2457 | 29.5535 | 28.7367 | 28.7367 | 28.5329 | 22.9416 | 20.0858 | 16.8986 | 13.6787 | 28.457 | 28.4516 | 28.4431 | 28.4216 | 27.3801 | 26.3277 | 25.2545 | 21.3278 | 20.5594 | 19.5844 | 17.9881 | 14.9111 | 11.283 | 7.7948 | 27.4825 | 27.4796 | 27.4748 | 27.4628 | 26.5918 | 25.7083 | 24.8517 | 21.3148 | 20.5578 | 19.5941 | 18.0126 | 14.9591 | 11.3779 | 7.9182
| WICK | CT |  |  | 31.565 | 31.5648 | 31.5645 | 31.5641 | 31.1397 | 30.6822 | 30.1986 | 29.6301 | 28.8229 | 28.6879 | 28.398 | 20.0858 | 17.1136 | 13.6787 | 28.4571 | 28.4525 | 28.4456 | 28.4296 | 27.8296 | 27.2241 | 26.5941 | 25.8485 | 24.7795 | 21.7458 | 19.4961 | 14.9111 | 11.7095 | 7.7948 | 27.4825 | 27.4798 | 27.4759 | 27.4667 | 26.9437 | 26.4031 | 25.8372 | 25.1693 | 24.2216 | 21.726 | 19.5052 | 14.9591 | 11.7819 | 7.9182
| WICK | LW |  |  | 31.5653 | 31.5653 | 31.5653 | 31.5653 | 30.9129 | 30.2457 | 29.5535 | 28.7367 | 28.7367 | 28.5329 | 22.9416 | 20.4989 | 18.6105 | 16.1757 | 28.457 | 28.4516 | 28.4431 | 28.4216 | 27.3801 | 26.3277 | 25.2545 | 21.3278 | 20.5594 | 19.5844 | 17.9881 | 15.3132 | 13.315 | 10.5595 | 27.4826 | 27.4796 | 27.4748 | 27.4628 | 26.5918 | 25.7083 | 24.8517 | 21.3148 | 20.5578 | 19.5941 | 18.0126 | 15.3624 | 13.3758 | 10.6544
| WICK | ST |  |  | 31.5652 | 31.5651 | 31.565 | 31.5649 | 31.266 | 30.9461 | 30.6418 | 30.2755 | 29.6831 | 29.5611 | 29.2552 | 21.7585 | 16.8986 | 15.0386 | 28.4591 | 28.4564 | 28.4528 | 28.4459 | 27.9972 | 27.5349 | 27.0893 | 26.5441 | 25.6952 | 25.2337 | 20.4812 | 16.608 | 11.283 | 9.1532 | 27.4838 | 27.4822 | 27.4801 | 27.4763 | 27.0932 | 26.6933 | 26.3097 | 25.8429 | 25.1064 | 24.8481 | 20.4884 | 16.6534 | 11.3779 | 9.2767
| WICK | SP |  |  | 31.565 | 31.5649 | 31.5647 | 31.5645 | 31.5286 | 31.4938 | 31.4581 | 31.4181 | 31.3524 | 31.2817 | 31.0221 | 30.7813 | 27.8732 | 22.5875 | 28.4615 | 28.461 | 28.4604 | 28.4598 | 28.3843 | 28.3043 | 28.2006 | 28.0937 | 27.9389 | 27.748 | 26.9782 | 26.4491 | 19.5549 | 17.7439 | 27.485 | 27.4847 | 27.4843 | 27.4839 | 27.4257 | 27.3655 | 27.2916 | 27.2141 | 27.0983 | 26.9601 | 26.4206 | 26.0449 | 19.5553 | 17.7567
WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | 37.7306 | 37.7287 | 37.7263 | 37.7226 | 37.6893 | 37.6445 | 37.6003 | 37.5504 | 37.4732 | 37.4538 | 37.4036 | 37.2386 | 37.373 | 37.2702 | 35.5983 | 35.5936 | 35.5872 | 35.5737 | 35.5398 | 35.4862 | 35.4228 | 35.3541 | 35.2584 | 35.206 | 35.0595 | 34.7402 | 34.7219 | 34.4008 | 21.3059 | 21.3011 | 21.2946 | 21.2808 | 21.2469 | 21.1931 | 21.1292 | 21.06 | 20.9638 | 20.9105 | 20.7615 | 20.4382 | 20.4158 | 19.969
| WOODHILL | CT |  |  | 37.7306 | 37.7287 | 37.7263 | 37.7226 | 37.7126 | 37.7008 | 37.6872 | 37.668 | 37.6471 | 37.6328 | 37.5869 | 37.4909 | 37.7397 | 37.4858 | 35.5983 | 35.5936 | 35.5872 | 35.5737 | 35.5532 | 35.5313 | 35.5076 | 35.4413 | 35.374 | 35.3096 | 35.1151 | 34.778 | 34.7876 | 34.4008 | 21.3059 | 21.3011 | 21.2946 | 21.2808 | 21.2601 | 21.2379 | 21.2139 | 21.1464 | 21.0779 | 21.0121 | 20.8138 | 20.4703 | 20.4692 | 19.969
| WOODHILL | LW |  |  | 37.733 | 37.7326 | 37.7321 | 37.7308 | 37.7293 | 37.7279 | 37.7265 | 37.7251 | 37.7238 | 37.7223 | 37.718 | 37.9343 | 37.9273 | 37.9204 | 35.6005 | 35.5968 | 35.591 | 35.5764 | 35.5602 | 35.5443 | 35.5288 | 35.5136 | 35.4988 | 35.4828 | 35.4353 | 35.5819 | 35.5049 | 35.4287 | 21.308 | 21.3043 | 21.2983 | 21.2834 | 21.2668 | 21.2506 | 21.2347 | 21.2191 | 21.2039 | 21.1875 | 21.1389 | 21.2837 | 21.2049 | 21.1268
| WOODHILL | ST |  |  | 37.7326 | 37.7321 | 37.7316 | 37.7307 | 37.6893 | 37.6445 | 37.6003 | 37.5504 | 37.4732 | 37.4538 | 37.4036 | 37.2386 | 37.373 | 37.2702 | 35.6009 | 35.5983 | 35.5949 | 35.5886 | 35.5398 | 35.4862 | 35.4228 | 35.3541 | 35.2584 | 35.206 | 35.0595 | 34.7402 | 34.7219 | 34.4667 | 21.3085 | 21.3058 | 21.3024 | 21.2959 | 21.2469 | 21.1931 | 21.1292 | 21.06 | 20.9638 | 20.9105 | 20.7615 | 20.4382 | 20.4158 | 20.1567
| WOODHILL | SP |  |  | 37.7325 | 37.732 | 37.7315 | 37.731 | 37.7308 | 37.7304 | 37.7297 | 37.729 | 37.7281 | 37.7262 | 37.7203 | 37.7128 | 37.6964 | 38.6737 | 35.6028 | 35.6021 | 35.6013 | 35.6004 | 35.5981 | 35.5953 | 35.5884 | 35.5816 | 35.5728 | 35.5579 | 35.5146 | 35.4484 | 35.3769 | 36.3026 | 21.3105 | 21.3097 | 21.3089 | 21.308 | 21.3056 | 21.3028 | 21.2957 | 21.2887 | 21.2798 | 21.2646 | 21.2202 | 21.1525 | 21.0796 | 22.0039

## Local Authority Reference
Local Authority | Grid Supply Point | Primary Substation
Aberdeen City | CLAYHILLS | BALNAGASK
Aberdeen City | CLAYHILLS | CLAYHILLS
Aberdeen City | CLAYHILLS | COMMERCE STREET
Aberdeen City | CLAYHILLS | CRAIGINCHES
Aberdeen City | CRAIGIEBUCKLER | CRAIGIEBUCKLER
Aberdeen City | CRAIGIEBUCKLER | CRAIGTON
Aberdeen City | CRAIGIEBUCKLER | CULTER
Aberdeen City | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeen City | DYCE | DYCE NORTH
Aberdeen City | KINTORE | PARK
Aberdeen City | KINTORE | SKENE
Aberdeen City | KINTORE | TORRYBURN
Aberdeen City | PERSLEY | BRIDGE OF DON
Aberdeen City | PERSLEY | HAUDAGAIN
Aberdeen City | PERSLEY | NORTHFIELD
Aberdeen City | PERSLEY | ST MACHAR
Aberdeen City | PERSLEY | STONEYWOOD T1&T2
Aberdeen City | PERSLEY | STONEYWOOD T3
Aberdeen City | PERSLEY | WHITESTRIPES
Aberdeen City | REDMOSS | KINCORTH
Aberdeen City | REDMOSS | REDMOSS
Aberdeen City | WILLOWDALE | DENBURN
Aberdeen City | WILLOWDALE | GREYFRIARS
Aberdeen City | WILLOWDALE | HAYTON
Aberdeen City | WILLOWDALE | ST NICHOLAS
Aberdeen City | WOODHILL | QUEENS LANE NORTH
Aberdeen City | WOODHILL | SPRINGHILL
Aberdeen City | WOODHILL | WOODHILL
Aberdeenshire | BOAT OF GARTEN | AVIEMORE
Aberdeenshire | BOAT OF GARTEN | BALLINDALLOCH
Aberdeenshire | BRIDGE OF DUN | INCHBARE
Aberdeenshire | BRIDGE OF DUN | LOGIE PERT
Aberdeenshire | BRIDGE OF DUN | MONTROSE NORTH
Aberdeenshire | BRIDGE OF DUN | ST CYRUS
Aberdeenshire | COUPAR ANGUS | DALRULZION
Aberdeenshire | CRAIGIEBUCKLER | CRAIGTON
Aberdeenshire | CRAIGIEBUCKLER | CULTER
Aberdeenshire | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeenshire | DYCE | BALMEDIE
Aberdeenshire | DYCE | DYCE NORTH
Aberdeenshire | DYCE | ELLON 11 kV
Aberdeenshire | DYCE | KINGSEAT
Aberdeenshire | FIDDES | EDZELL
Aberdeenshire | FIDDES | INVERBERVIE
Aberdeenshire | FIDDES | LAURENCEKIRK
Aberdeenshire | FIDDES | STONEHAVEN
Aberdeenshire | FRASERBURGH | FRASERBURGH
Aberdeenshire | KEITH | CULLEN
Aberdeenshire | KEITH | DUFFTOWN
Aberdeenshire | KEITH | HUNTLY
Aberdeenshire | KEITH | INSCH
Aberdeenshire | KEITH | KEITH
Aberdeenshire | KEITH | LIMEHILLOCKS
Aberdeenshire | KEITH | MARNOCH
Aberdeenshire | KINTORE | BANCHORY
Aberdeenshire | KINTORE | FYVIE
Aberdeenshire | KINTORE | INVERURIE
Aberdeenshire | KINTORE | KEMNAY
Aberdeenshire | KINTORE | METHLICK
Aberdeenshire | KINTORE | MIDMAR
Aberdeenshire | KINTORE | OLDMELDRUM
Aberdeenshire | KINTORE | PARK
Aberdeenshire | KINTORE | SKENE
Aberdeenshire | KINTORE | TORRYBURN
Aberdeenshire | LUNANHEAD | MARYTON
Aberdeenshire | MACDUFF | MACDUFF
Aberdeenshire | MACDUFF | PORTSOY
Aberdeenshire | MACDUFF | TURRIFF
Aberdeenshire | PERSLEY | BRIDGE OF DON
Aberdeenshire | PERSLEY | WHITESTRIPES
Aberdeenshire | PETERHEAD GRANGE | PETERHEAD GRANGE 11kV
Aberdeenshire | PETERHEAD GRANGE | PHEAD NORTH ST
Aberdeenshire | PETERHEAD SHELL | BODDAM
Aberdeenshire | REDMOSS | KINCORTH
Aberdeenshire | REDMOSS | NEWTONHILL
Aberdeenshire | REDMOSS | REDMOSS
Aberdeenshire | ST FERGUS GAS | ST FERGUS GAS TERM
Aberdeenshire | STRICHEN | HATTON
Aberdeenshire | STRICHEN | MAUD
Aberdeenshire | STRICHEN | MINTLAW
Aberdeenshire | STRICHEN | NEW PITSLIGO
Aberdeenshire | STRICHEN | STONEYHILL
Aberdeenshire | STRICHEN | STRICHEN
Aberdeenshire | TARLAND | ABOYNE
Aberdeenshire | TARLAND | BALLATER
Aberdeenshire | TARLAND | MOSSAT
Aberdeenshire | TARLAND | STRATHDON
Aberdeenshire | TARLAND | WHITEHOUSE
Aberdeenshire | TUMMEL BRIDGE | BONSKEID
Aberdeenshire | WOODHILL | SPRINGHILL
Angus | ABERNETHY | BALBEGGIE
Angus | ARBROATH | CARNOUSTIE
Angus | ARBROATH | CHARLES AVENUE
Angus | ARBROATH | ELLIOT DEPOT
Angus | ARBROATH | HUME STREET
Angus | ARBROATH | REDFORD
Angus | BRIDGE OF DUN | BRECHIN
Angus | BRIDGE OF DUN | BRIDGE OF DUN 11kV
Angus | BRIDGE OF DUN | INCHBARE
Angus | BRIDGE OF DUN | LOGIE PERT
Angus | BRIDGE OF DUN | MILL RD MONTROSE
Angus | BRIDGE OF DUN | MONTROSE NORTH
Angus | BRIDGE OF DUN | ST CYRUS
Angus | CHARLESTON | GOURDIE
Angus | COUPAR ANGUS | ALYTH
Angus | COUPAR ANGUS | COUPAR ANGUS
Angus | COUPAR ANGUS | DALRULZION
Angus | COUPAR ANGUS | LEOCH
Angus | FIDDES | EDZELL
Angus | FIDDES | LAURENCEKIRK
Angus | KINTORE | BANCHORY
Angus | LUNANHEAD | FRIOCKHEIM
Angus | LUNANHEAD | INVERARITY
Angus | LUNANHEAD | LOCHSIDE
Angus | LUNANHEAD | LUNANHEAD
Angus | LUNANHEAD | MARYTON
Angus | LYNDHURST | MACALPINE ROAD
Angus | LYNDHURST | WEST KIRKTON
Angus | MILTON OF CRAIGIE | ASHLUDIE
Angus | MILTON OF CRAIGIE | BALDOVIE
Angus | MILTON OF CRAIGIE | BROUGHTY FERRY
Angus | MILTON OF CRAIGIE | EDZELL STREET
Angus | MILTON OF CRAIGIE | LONGHAUGH
Angus | TARLAND | BALLATER
Argyll and Bute | CARRADALE | BALLURE
Argyll and Bute | CARRADALE | CAMPBELTOWN
Argyll and Bute | CARRADALE | CLAONAIG
Argyll and Bute | CARRADALE | DIPPEN
Argyll and Bute | CARRADALE | WESTPARK FERGUS
Argyll and Bute | CLACHAN | BUTTERBRIDGE
Argyll and Bute | CLACHAN | DOUGLAS PIER
Argyll and Bute | CLACHAN | INVERARAY
Argyll and Bute | CLACHAN | LOCHGOILHEAD
Argyll and Bute | CLACHAN | STRACHUR
Argyll and Bute | DUNOON | BRUCHAG
Argyll and Bute | DUNOON | COLINTRAIVE
Argyll and Bute | DUNOON | DUNOON
Argyll and Bute | DUNOON | GLENDARUEL
Argyll and Bute | DUNOON | INNELLAN
Argyll and Bute | DUNOON | KAMES
Argyll and Bute | DUNOON | NEWTON
Argyll and Bute | DUNOON | OTTER FERRY
Argyll and Bute | DUNOON | ROTHESAY
Argyll and Bute | DUNOON | SANDBANK
Argyll and Bute | FORT WILLIAM | SALEN
Argyll and Bute | KILLIN | CASHLIE
Argyll and Bute | PORT ANN | AIRIGH-NA-BRODAIG
Argyll and Bute | PORT ANN | BOWMORE
Argyll and Bute | PORT ANN | CRINAN
Argyll and Bute | PORT ANN | CROMALT
Argyll and Bute | PORT ANN | INVERNEIL
Argyll and Bute | PORT ANN | LOCHGILPHEAD
Argyll and Bute | PORT ANN | LUSSAGIVEN
Argyll and Bute | PORT ANN | PORT ASKAIG
Argyll and Bute | PORT ANN | PORT ELLEN
Argyll and Bute | PORT ANN | STONEFIELD
Argyll and Bute | PORT ANN | TARBERT JURA
Argyll and Bute | PORT ANN | TARBERT LOCH FYNE
Argyll and Bute | RANNOCH | BLACKMOUNT
Argyll and Bute | RANNOCH | GLENETIVE
Argyll and Bute | RANNOCH | TYNDRUM
Argyll and Bute | STRATHLEVEN | DRYMEN
Argyll and Bute | TAYNUILT | BARCALDINE
Argyll and Bute | TAYNUILT | CONNEL
Argyll and Bute | TAYNUILT | DALMALLY
Argyll and Bute | TAYNUILT | DERVAIG
Argyll and Bute | TAYNUILT | EREDINE
Argyll and Bute | TAYNUILT | KENMORE
Argyll and Bute | TAYNUILT | KERRERA
Argyll and Bute | TAYNUILT | KILCHRENAN
Argyll and Bute | TAYNUILT | KILMELFORD PS
Argyll and Bute | TAYNUILT | KILNINVER
Argyll and Bute | TAYNUILT | KINLOCH
Argyll and Bute | TAYNUILT | LOCHDONHEAD
Argyll and Bute | TAYNUILT | OBAN
Argyll and Bute | TAYNUILT | SCAMMADALE
Argyll and Bute | TAYNUILT | TAYNUILT
Argyll and Bute | TAYNUILT | TIRORAN BRIDGE
Argyll and Bute | TUMMEL BRIDGE | KINLOCH RANNOCH
Clackmannanshire | ABERNETHY | GLENDEVON
Clackmannanshire | ABERNETHY | MILNATHORT
Clackmannanshire | BRACO | GLENEAGLES
Dundee City | CHARLESTON | CHARLESTON
Dundee City | CHARLESTON | GOURDIE
Dundee City | CHARLESTON | MENZIESHILL
Dundee City | CHARLESTON | NINEWELLS
Dundee City | COUPAR ANGUS | LEOCH
Dundee City | DUDHOPE | CONSTABLE STREET
Dundee City | DUDHOPE | ROSEBANK STREET
Dundee City | GLENAGNES | OVERGATE
Dundee City | GLENAGNES | WALTON
Dundee City | LYNDHURST | LOCHEE
Dundee City | LYNDHURST | LYNDHURST
Dundee City | LYNDHURST | MACALPINE ROAD
Dundee City | LYNDHURST | WEST KIRKTON
Dundee City | MILTON OF CRAIGIE | ASHLUDIE
Dundee City | MILTON OF CRAIGIE | BALDOVIE
Dundee City | MILTON OF CRAIGIE | BROUGHTY FERRY
Dundee City | MILTON OF CRAIGIE | EDZELL STREET
Dundee City | MILTON OF CRAIGIE | LONGHAUGH
Dundee City | MILTON OF CRAIGIE | MILTON OF CRAIGIE
Dundee City | MILTON OF CRAIGIE | OLD CRAIGIE ROAD
East Dunbartonshire | BRACO | KIPPEN
East Dunbartonshire | STRATHLEVEN | KEPCULLOCH
East Dunbartonshire | STRATHLEVEN | KILLEARN
Eilean Siar | ARDMORE | AIRD
Eilean Siar | ARDMORE | CLACHAN
Eilean Siar | ARDMORE | DRIMORE
Eilean Siar | ARDMORE | LOCH CARNAN
Eilean Siar | ARDMORE | POLLACHAR
Eilean Siar | ARDMORE | STOCKINISH
Eilean Siar | ARDMORE | TARBERT
Eilean Siar | STORNOWAY | ARNISH
Eilean Siar | STORNOWAY | BARVAS
Eilean Siar | STORNOWAY | BATTERY POINT
Eilean Siar | STORNOWAY | CALLANISH
Eilean Siar | STORNOWAY | COLL
Eilean Siar | STORNOWAY | GISLA
Eilean Siar | STORNOWAY | HARRIS GRID
Eilean Siar | STORNOWAY | LAXAY
Eilean Siar | STORNOWAY | MAARUIG
Fife | ABERNETHY | ABERNETHY
Fife | ABERNETHY | BRIDGE OF EARN
Fife | ABERNETHY | GLENDEVON
Fife | ABERNETHY | MILNATHORT
Highland | ALNESS | BALALDIE
Highland | ALNESS | CONTULLICH
Highland | ALNESS | CROSSHILLS
Highland | ALNESS | GLASTULLICH
Highland | ALNESS | INVERGORDON
Highland | ALNESS | NIGG
Highland | ALNESS | PEDDIESTON
Highland | ALNESS | TAIN
Highland | BEAULY | AIGAS
Highland | BEAULY | BLACKSTAND
Highland | BEAULY | CONON BRIDGE
Highland | BEAULY | DINGWALL
Highland | BEAULY | KILTARLITY
Highland | BEAULY | MARYBANK
Highland | BEAULY | MUIR OF ORD
Highland | BEAULY | MUIREND
Highland | BOAT OF GARTEN | AVIEMORE
Highland | BOAT OF GARTEN | BALLINDALLOCH
Highland | BOAT OF GARTEN | BOAT OF GARTEN 11 kV
Highland | BOAT OF GARTEN | DALWHINNIE
Highland | BOAT OF GARTEN | GRANTOWN
Highland | BOAT OF GARTEN | KINGUSSIE
Highland | BOAT OF GARTEN | TOMATIN
Highland | BROADFORD | ACHINTEE
Highland | BROADFORD | BROADFORD
Highland | BROADFORD | KISHORNHILL
Highland | BROADFORD | KYLE
Highland | BROADFORD | LOWER OLLACH
Highland | BROADFORD | NOSTIE BRIDGE
Highland | BROADFORD | SHIELDAIG
Highland | BROADFORD | SKULAMUS
Highland | BRORA | BRORA
Highland | BRORA | DORNOCH
Highland | BRORA | GOLSPIE
Highland | BRORA | HELMSDALE
Highland | CASSLEY | OVERSCAIG
Highland | CASSLEY | RHICONICH
Highland | CEANNACROC | DRUMNADROCHIT
Highland | DOUNREAY | BETTYHILL
Highland | DOUNREAY | COLDBACKIE
Highland | DOUNREAY | DOUNREAY
Highland | DOUNREAY | FORSS
Highland | DUNOON | DUNOON
Highland | DUNVEGAN | DRYNOCH
Highland | DUNVEGAN | DUNVEGAN GRID
Highland | DUNVEGAN | PORTREE
Highland | DUNVEGAN | UIG
Highland | FORT AUGUSTUS | ABERCHALDER
Highland | FORT AUGUSTUS | BUNOICH
Highland | FORT AUGUSTUS | GLEN LAOGH
Highland | FORT AUGUSTUS | GLENDOE PRIMARY
Highland | FORT AUGUSTUS | INVERGARRY
Highland | FORT WILLIAM | ANNAT
Highland | FORT WILLIAM | ARISAIG
Highland | FORT WILLIAM | CORRAN
Highland | FORT WILLIAM | GLENUIG
Highland | FORT WILLIAM | INVERLOCHY
Highland | FORT WILLIAM | KINGAIRLOCH
Highland | FORT WILLIAM | KINLOCHMOIDART
Highland | FORT WILLIAM | LIDDESDALE
Highland | FORT WILLIAM | LOCHALINE
Highland | FORT WILLIAM | MALLAIG
Highland | FORT WILLIAM | PINEGROVE
Highland | FORT WILLIAM | POOR HOUSE
Highland | FORT WILLIAM | RAHOY
Highland | FORT WILLIAM | SHONA BEAG
Highland | FORT WILLIAM | STRONTIAN
Highland | GRUDIE BRIDGE | ACHILTIBUIE
Highland | GRUDIE BRIDGE | AULTBEA
Highland | GRUDIE BRIDGE | CONON FALLS
Highland | GRUDIE BRIDGE | DRUMRUNIE
Highland | GRUDIE BRIDGE | GARBAT FOREST
Highland | GRUDIE BRIDGE | GRUDIE BRIDGE
Highland | GRUDIE BRIDGE | INVERBROOM
Highland | GRUDIE BRIDGE | KERRY FALLS
Highland | GRUDIE BRIDGE | KINLOCHEWE
Highland | GRUDIE BRIDGE | LETTEREWE
Highland | GRUDIE BRIDGE | LOCH GLASCARNOCH
Highland | GRUDIE BRIDGE | LOCHINVER
Highland | GRUDIE BRIDGE | ULLAPOOL
Highland | INVERNESS | CULLODEN
Highland | INVERNESS | DALNEIGH
Highland | INVERNESS | ERROGIE
Highland | INVERNESS | FOYERS
Highland | INVERNESS | HILTON
Highland | INVERNESS | INVERARNIE
Highland | INVERNESS | INVERNESS 11 kV
Highland | INVERNESS | RAIGMORE
Highland | INVERNESS | WATERLOO PLACE
Highland | KEITH | ABERLOUR
Highland | KILLIN | WESTER DRUMMOND
Highland | KINLOCHLEVEN | GLENCOE
Highland | KINLOCHLEVEN | KINLOCHLEVEN
Highland | LAIRG | LAIRG GRID
Highland | LAIRG | TORBOLL
Highland | LAIRG | TRESSADY
Highland | MYBSTER | LATHERON
Highland | MYBSTER | MELVICH
Highland | MYBSTER | WICK
Highland | NAIRN | ARDERSIER
Highland | NAIRN | DALCROSS
Highland | NAIRN | FORRES
Highland | NAIRN | LETHEN
Highland | NAIRN | NAIRN CENTRAL
Highland | QUOICH | QUOICH PRIMARY
Highland | RANNOCH | BLACKMOUNT
Highland | RANNOCH | BRIDGE OF GAUR
Highland | RANNOCH | GLENETIVE
Highland | SHIN | GLEDFIELD
Highland | SHIN | SHIN
Highland | ST FILLANS | COMRIE
Highland | TAYNUILT | BARCALDINE
Highland | TAYNUILT | SALEN 2
Highland | THURSO | HALKIRK
Highland | THURSO | HASTIGROW
Highland | THURSO | MOUNT PLEASANT
Highland | THURSO | ORMLIE
Highland | TUMMEL BRIDGE | BONSKEID
Highland | TUMMEL BRIDGE | CALVINE
Highland | TUMMEL BRIDGE | KINLOCH RANNOCH
Moray | BOAT OF GARTEN | AVIEMORE
Moray | BOAT OF GARTEN | BALLINDALLOCH
Moray | BOAT OF GARTEN | GRANTOWN
Moray | ELGIN | ASHGROVE
Moray | ELGIN | BILBOHALL
Moray | ELGIN | BURGHEAD
Moray | ELGIN | CUMMING STREET
Moray | ELGIN | ELGIN
Moray | ELGIN | FOCHABERS
Moray | ELGIN | KINLOSS
Moray | ELGIN | LHANBRYDE
Moray | ELGIN | LOSSIEMOUTH
Moray | KEITH | ABERLOUR
Moray | KEITH | BUCKIE
Moray | KEITH | CULLEN
Moray | KEITH | DUFFTOWN
Moray | KEITH | HUNTLY
Moray | KEITH | KEITH
Moray | KEITH | LIMEHILLOCKS
Moray | KEITH | MARNOCH
Moray | KEITH | ROTHES
Moray | MACDUFF | PORTSOY
Moray | NAIRN | FORRES
Moray | NAIRN | LETHEN
Moray | NAIRN | NAIRN CENTRAL
Moray | TARLAND | BALLATER
Moray | TARLAND | MOSSAT
Moray | TARLAND | STRATHDON
North Ayrshire | CARRADALE | BALLIEKINE
North Ayrshire | CARRADALE | BRODICK
North Ayrshire | CARRADALE | MACHRIE
North Ayrshire | CARRADALE | WHITING BAY
North Ayrshire | DUNOON | BRUCHAG
North Lanarkshire | BRACO | KIPPEN
Orkney Islands | THURSO | BURGARHILL
Orkney Islands | THURSO | EDAY
Orkney Islands | THURSO | FLOTTA
Orkney Islands | THURSO | KIRKWALL
Orkney Islands | THURSO | LYNESS
Orkney Islands | THURSO | NORTH HOY
Orkney Islands | THURSO | ROUSAY
Orkney Islands | THURSO | SANDAY
Orkney Islands | THURSO | SHAPINSAY
Orkney Islands | THURSO | ST MARYS
Orkney Islands | THURSO | STROMNESS
Orkney Islands | THURSO | STRONSAY
Orkney Islands | THURSO | WESTRAY
Perth and Kinross | ABERNETHY | ABERNETHY
Perth and Kinross | ABERNETHY | BALBEGGIE
Perth and Kinross | ABERNETHY | BRIDGE OF EARN
Perth and Kinross | ABERNETHY | ERROL
Perth and Kinross | ABERNETHY | GLENDEVON
Perth and Kinross | ABERNETHY | HARBOUR
Perth and Kinross | ABERNETHY | MILNATHORT
Perth and Kinross | ABERNETHY | SCONE
Perth and Kinross | BOAT OF GARTEN | AVIEMORE
Perth and Kinross | BOAT OF GARTEN | DALWHINNIE
Perth and Kinross | BOAT OF GARTEN | KINGUSSIE
Perth and Kinross | BRACO | CALLANDER
Perth and Kinross | BRACO | CRIEFF
Perth and Kinross | BRACO | DUNBLANE
Perth and Kinross | BRACO | FORTEVIOT
Perth and Kinross | BRACO | GLENEAGLES
Perth and Kinross | BURGHMUIR | BURGHMUIR
Perth and Kinross | BURGHMUIR | GOODLYBURN
Perth and Kinross | BURGHMUIR | INVERALMOND
Perth and Kinross | BURGHMUIR | REDGORTON
Perth and Kinross | BURGHMUIR | THIMBLEROW
Perth and Kinross | CHARLESTON | GOURDIE
Perth and Kinross | CHARLESTON | NINEWELLS
Perth and Kinross | COUPAR ANGUS | ALYTH
Perth and Kinross | COUPAR ANGUS | BLAIRGOWRIE
Perth and Kinross | COUPAR ANGUS | CAPUTH
Perth and Kinross | COUPAR ANGUS | COUPAR ANGUS
Perth and Kinross | COUPAR ANGUS | DALRULZION
Perth and Kinross | COUPAR ANGUS | LEOCH
Perth and Kinross | FORT WILLIAM | INVERLOCHY
Perth and Kinross | KILLIN | CASHLIE
Perth and Kinross | KILLIN | CHAORACH
Perth and Kinross | KILLIN | COSHIEVILLE
Perth and Kinross | KILLIN | KILLIN TOWN
Perth and Kinross | KILLIN | LOCHEARNHEAD
Perth and Kinross | LUNANHEAD | MARYTON
Perth and Kinross | RANNOCH | BLACKMOUNT
Perth and Kinross | RANNOCH | BRIDGE OF GAUR
Perth and Kinross | RANNOCH | GLENETIVE
Perth and Kinross | RANNOCH | TYNDRUM
Perth and Kinross | ST FILLANS | DALCHONZIE
Perth and Kinross | ST FILLANS | ST FILLANS P S
Perth and Kinross | TARLAND | BALLATER
Perth and Kinross | TUMMEL BRIDGE | ABERFELDY
Perth and Kinross | TUMMEL BRIDGE | BONSKEID
Perth and Kinross | TUMMEL BRIDGE | CALVINE
Perth and Kinross | TUMMEL BRIDGE | FINCASTLE
Perth and Kinross | TUMMEL BRIDGE | KINLOCH RANNOCH
Perth and Kinross | TUMMEL BRIDGE | PITLOCHRY
Shetland Islands | SHETLAND | FIRTH
Shetland Islands | SHETLAND | GUTCHER
Shetland Islands | SHETLAND | MID YELL
Shetland Islands | SHETLAND | SANDWICK
Shetland Islands | SHETLAND | SCALLOWAY
Shetland Islands | SHETLAND | SUMBURGH
Shetland Islands | SHETLAND | TUMBLIN
Shetland Islands | SHETLAND | UNST
Shetland Islands | SHETLAND | VOE
Shetland Islands | WOODHILL | BRAE
Stirling | BRACO | CALLANDER
Stirling | BRACO | DUNBLANE
Stirling | BRACO | GLENEAGLES
Stirling | BRACO | KIPPEN
Stirling | KILLIN | CASHLIE
Stirling | KILLIN | CHAORACH
Stirling | KILLIN | COSHIEVILLE
Stirling | KILLIN | KILLIN TOWN
Stirling | KILLIN | LOCHEARNHEAD
Stirling | KILLIN | LUBNAIG
Stirling | RANNOCH | TYNDRUM
Stirling | ST FILLANS | DALCHONZIE
Stirling | ST FILLANS | ST FILLANS P S
Stirling | STRATHLEVEN | ABERFOYLE
Stirling | STRATHLEVEN | DRYMEN
Stirling | STRATHLEVEN | KEPCULLOCH
Stirling | STRATHLEVEN | KILLEARN
Stirling | TAYNUILT | DALMALLY
West Dunbartonshire | STRATHLEVEN | BLAIRLINNANS
West Dunbartonshire | STRATHLEVEN | DRYMEN
West Dunbartonshire | STRATHLEVEN | KILLEARN