## Disclaimer
Disclaimer
The information in this table should be read in conjunction with the explanatory notes in the main text.
The information contained in this statement is provided for the sole purpose of allowing existing and potential customers to assess the capabilities of the electricity network and opportunities for changes
in their use of the network or for connecting to it.
While all reasonable effort has been made to ensure the accuracy of the information, Electricity North West will accept no liability for any loss or damage caused by the information not being accurate.
Actual changes in supply capacity for existing customers or new connections are subject to detailed assessment and approval by Electricity North West, and payment of appropriate charges.
The information contained in this statement is the Copyright of Electricity North West, All Rights Reserved.

## Pry Load Table
33kV SUBSTATION MAXIMUM LOAD INFORMATION
[5 empty] | Forecast Load Information MVA |  |  |  |  | Firm Capacity Data
Substation Group | Substation or Busbar Name | Voltage Level (kV) | 2022/23 Weather corrected Maximum Demand (MVA) | Power Factor | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | Capacity Based on Network Assets only (MVA) | Estimated Distributed Generation contribution to Capacity (MVA) | Notes
Lower Darwen | ALBION ST | 33 | 11.7205 | 0.99871 | 14.2892 | 15.1537 | 15.3099 | 15.6978 | 15.9211 | 22.863 | 0
Moss Nook | ALDERLEY & CHELFORD | 33 | 17.0031 | 0.9756 | 18.6741 | 19.2532 | 19.8136 | 20.2998 | 20.8224 | 28.31 | 0.068 | Demand group comprising 2 primary substation sites that are paralled on the HV side
Penrith & Shap | ALSTON | 33 | 1.5316 | 0.98575 | 1.5694 | 1.6416 | 1.6888 | 1.7311 | 1.7977 | 1.7 | 0.01206
Kendal (Parkside Rd) | AMBLESIDE | 33 | 9.1925 | 0.99317 | 9.5741 | 9.8601 | 10.0652 | 10.3718 | 10.6342 | 17.8 | 0.0483
Red Bank | ANCOATS NORTH T11 & T12 | 33 | 17.3471 | 0.99286 | 19.1662 | 19.8162 | 20.4522 | 21.1269 | 21.6313 | 22.863 | 0.006
Red Bank | ANCOATS NORTH T14 | 33 | 10.0676 | 0.99286 | 11.2662 | 11.7937 | 12.2484 | 12.6475 | 12.8979 | 13.25 | 0
Stainburn & Siddick | ANNIE PIT | 33 | 16.2322 | 0.99255 | 16.8816 | 17.2983 | 17.374 | 17.7987 | 18.0976 | 21.5 | 1.02
Lytham | ANSDELL | 33 | 7.7875 | 0.99123 | 9.2793 | 9.826 | 10.0796 | 10.3804 | 10.6323 | 16 | 0.0044
Stuart Street | ARDWICK | 33 | 16.2197 | 0.9993 | 16.4006 | 16.7229 | 17.0142 | 17.4551 | 17.7601 | 16 | 0
Kendal (Parkside Rd) | ARNSIDE | 33 | 3.7882 | 0.99737 | 4.2767 | 4.5612 | 4.6019 | 4.7662 | 4.9156 | 15 | 0
Orrel / Wigan | ASHTON (GOLBORNE) | 33 | 14.583 | 0.9981 | 15.0272 | 15.5975 | 15.8684 | 16.3524 | 16.7227 | 21.2 | 0
Ribble | ASHTON (RIBBLE) | 33 | 5.7158 | 0.99751 | 7.4869 | 8.1042 | 8.181 | 8.4289 | 8.6598 | 10.5 | 0
Sale | ASHTON ON MERSEY | 33 | 11.7623 | 0.99569 | 14.9011 | 15.5393 | 15.6766 | 16.0748 | 16.3905 | 22.86 | 0.01986
Hartshead-Heyrod | ASHTON UNDER LYNE T11 & T12 | 33 | 17.3251 | 0.99857 | 17.8796 | 18.2519 | 18.592 | 18.931 | 19.3374 | 22.863 | 0
Hartshead-Heyrod | ASHTON UNDER LYNE T13 | 33 | 6.5313 | 0.99857 | 6.6548 | 6.7847 | 6.8088 | 6.9593 | 7.0652 | 13.25 | 0
Buxton | ASHWOOD DALE | 33 | 13.5684 | 0.99676 | 14.2334 | 14.5494 | 14.6651 | 14.9966 | 15.2383 | 19.719 | 0.0045
Ulverston | ASKAM & DALTON | 33 | 15.9288 | 0.9083 | 16.8366 | 17.4678 | 17.6404 | 18.1755 | 18.6083 | 20.02 | 1.5888 | Demand group comprising 2 primary substation sites that are paralled on the HV side
Spadeadam | ASKERTON CASTLE | 33 | 1.3389 | 0.99228 | 1.2784 | 1.3256 | 1.3699 | 1.4203 | 1.4707 | 2.3 | 0
Stainburn & Siddick | ASPATRIA | 33 | 7.1055 | 0.99609 | 7.6692 | 7.9746 | 8.1263 | 8.3746 | 8.6074 | 13 | 0.42415
Atherton | ATHERTON TOWN CENTRE | 33 | 24.6294 | 0.99605 | 27.5917 | 29.2342 | 30.1 | 32.4676 | 34.4806 | 33.24 | 0
Burnley | ATHLETIC ST | 33 | 9.5803 | 0.99857 | 10.3794 | 10.5273 | 10.752 | 11.0332 | 11.3441 | 17.5 | 0.119
Preston East | AVENHAM | 33 | 10.6827 | 0.97272 | 11.0784 | 11.2807 | 11.6427 | 11.9098 | 12.1019 | 22.863 | 0
Sale | BAGULEY | 33 | 15.8873 | 0.99742 | 16.6401 | 16.7694 | 17.5181 | 18.4913 | 19.2956 | 22.863 | 0.04052
Ribble | BAMBER BRIDGE | 33 | 13.2165 | 0.99731 | 16.3258 | 17.1216 | 17.3027 | 17.6507 | 17.9842 | 22.863 | 0
Bolton | BARBARA ST | 33 | 11.7362 | 0.99593 | 14.4505 | 15.0733 | 15.1449 | 15.4922 | 15.6326 | 15.6 | 0
Barrow & Sandgate | BARROW | 33 | 10.8644 | 0.97393 | 11.73 | 12.0902 | 12.2521 | 12.5459 | 12.8144 | 23 | 0.0825
Barton | BARTON DOCK RD | 33 | 8.7767 | 0.99866 | 9.1984 | 9.3547 | 9.5279 | 9.8067 | 9.8974 | 12.5 | 0
Atherton | BEDFORD | 33 | 17.5887 | 0.99779 | 18.2173 | 18.9704 | 19.1404 | 19.7739 | 20.2391 | 23 | 0.15468
Greenhill | BELGRAVE | 33 | 8.9362 | 0.99711 | 9.5768 | 9.8378 | 10.0211 | 10.236 | 10.3671 | 17.5 | 0
West Didsbury | BENCHILL | 33 | 3.6941 | 0.9998 | 3.9606 | 4.0053 | 4.5828 | 5.1517 | 5.7144 | 12 | 0
Kendal (Parkside Rd) | BENTHAM | 33 | 3.967 | 0.95 | 3.9148 | 4.0272 | 4.1501 | 4.2233 | 4.3391 | 5.5 | 0.08
Bispham | BISPHAM | 33 | 16.3377 | 0.99925 | 17.9598 | 18.6089 | 18.8496 | 19.2425 | 19.4769 | 22.863 | 3.4
Ribble | BLACKBULL | 33 | 13.3501 | 0.99707 | 16.892 | 17.7874 | 18.1667 | 18.4931 | 18.861 | 22.863 | 0
Blackburn | BLACKBURN | 33 | 13.4206 | 0.99275 | 15.8644 | 16.7102 | 16.8314 | 17.218 | 17.3562 | 22.863 | 0
Huncoat | BLACKBURN RD CLAYTON | 33 | 7.7205 | 0.97701 | 8.4931 | 8.8352 | 9.0836 | 9.2776 | 9.4412 | 19.32 | 0.017
Frederick Rd | BLACKFRIARS | 33 | 12.8435 | 0.99768 | 13.4949 | 14.0002 | 14.0502 | 14.5061 | 14.8984 | 17.8 | 0
Red Bank | BLACKLEY | 33 | 11.0733 | 0.99912 | 13.3318 | 13.8611 | 16.8647 | 21.3601 | 21.4863 | 22.863 | 0.018236
Blackpool | BLACKPOOL | 33 | 11.1292 | 0.99698 | 11.5417 | 12.3404 | 13.001 | 13.7482 | 13.8769 | 23.75 | 0
Macclesfield | BOLLINGTON | 33 | 8.666 | 0.99795 | 9.244 | 9.468 | 9.8571 | 10.0816 | 10.3296 | 13 | 0.2064
Padiham | BOLTON BY BOWLAND | 33 | 2.9627 | 0.95 | 3.0213 | 3.1186 | 3.2287 | 3.32 | 3.4028 | 3 | 0.0188
Lancaster | BOLTON LE SANDS | 33 | 10.6018 | 0.98262 | 11.2537 | 11.638 | 12.0526 | 12.3492 | 12.6745 | 17.5 | 0.055
Leyland | BOTANY BAY | 33 | 7.5324 | 0.98855 | 8.7383 | 9.1537 | 9.4151 | 9.7408 | 10.0101 | 10 | 0
Leyland | BOW LANE | 33 | 16.2405 | 0.99388 | 18.4501 | 19.2393 | 19.6715 | 20.2271 | 20.698 | 22.863 | 0.00424
Barrow & Sandgate | BOWATERS | 33 | 17.7887 | 0.92095 | 17.276 | 17.4906 | 17.8273 | 18.3543 | 18.5265 | 34.5 | 0.08
Altrincham | BOWDON | 33 | 14.8026 | 0.99152 | 15.4457 | 15.8278 | 15.9903 | 16.3549 | 16.6337 | 22.863 | 0
Stuart Street | BRADFORD | 33 | 13.0277 | 0.99328 | 13.4953 | 13.8268 | 13.9801 | 14.3224 | 14.5469 | 22.863 | 0.017103
Bolton | BRADSHAWGATE | 33 | 9.6549 | 0.99852 | 10.5643 | 11.7656 | 12.6875 | 13.3235 | 13.552 | 20.86 | 0.09095
Hazel Grove | BRAMHALL | 33 | 10.7456 | 0.97535 | 11.8723 | 12.2105 | 12.256 | 12.4136 | 12.6498 | 17.5 | 0
Bloom Street | BRIDGEWATER | 33 | 14.1658 | 0.99859 | 15.2902 | 15.5947 | 15.9542 | 16.256 | 16.5478 | 20.5 | 0.010754
Adswood | BRINKSWAY | 33 | 9.162 | 0.99866 | 13.0579 | 14.0436 | 14.3088 | 14.7989 | 15.3654 | 22.863 | 0
Altrincham | BROADHEATH | 33 | 24.9908 | 0.99568 | 27.3017 | 27.728 | 28.2539 | 29.1232 | 29.74 | 40.1 | 0.025705
Lancaster | BROADWAY | 33 | 10.0308 | 0.99837 | 10.8745 | 11.1696 | 11.5075 | 11.6459 | 11.8523 | 22.863 | 0.326
Leyland | BUCKSHAW | 33 | 9.0519 | 0.97607 | 10.4298 | 10.9443 | 11.2127 | 11.5056 | 11.7586 | 23 | 0.39715
Burnley | BURNLEY | 33 | 9.8848 | 0.99713 | 11.4035 | 11.6305 | 11.8029 | 12.1544 | 12.4491 | 22.863 | 1.0398
Burnley | BURNLEY CENTRE | 33 | 11.8202 | 0.97325 | 12.9231 | 13.2337 | 13.6723 | 14.0044 | 14.2405 | 22.863 | 0
Burnley | BURNLEY NORTH | 33 | 6.7332 | 0.99989 | 7.5711 | 7.7989 | 8.0636 | 8.4229 | 8.743 | 12 | 0.016
Lancaster | BURROW BECK | 33 | 15.2861 | 0.99246 | 17.7897 | 18.6065 | 18.9645 | 19.3245 | 19.6655 | 23 | 0.50808
Wrightington | BURSCOUGH BRIDGE | 33 | 12.0475 | 0.9951 | 12.6917 | 12.9851 | 13.2911 | 13.6645 | 13.9427 | 17.5 | 0.04
Bury | BURY TOWN CENTRE | 33 | 11.7971 | 0.99879 | 14.4287 | 15.1521 | 15.3091 | 15.6361 | 15.9535 | 22.863 | 0
Kearsley (Local) | CAMPBELL ST | 33 | 11.584 | 0.9964 | 11.9112 | 12.172 | 12.2259 | 12.5242 | 12.7019 | 17.5 | 0.02734
Red Bank | CANNON ST | 33 | 23.3544 | 0.98506 | 24.6699 | 25.3387 | 25.8349 | 26.4019 | 26.6396 | 36 | 0
Carlisle | CAPONTREE | 33 | 6.257 | 0.95695 | 7.1687 | 7.5328 | 7.7241 | 7.9693 | 8.2046 | 22.863 | 0.12262
Egremont | CARLETON | 33 | 1.9686 | 0.99382 | 2.0159 | 2.1354 | 2.2278 | 2.3276 | 2.4184 | 5 | 0.003
Harker | CARLISLE NORTH | 132 | 14.0735 | 0.9816 | 15.453 | 16.4058 | 16.8043 | 16.7242 | 17.1056 | 24.5 | 1.6386
Kearsley (Local) | CARR ST | 33 | 11.8879 | 0.99475 | 13.3567 | 13.7314 | 13.9452 | 14.2616 | 14.4903 | 22.863 | 0
Castleton | CASTLETON | 33 | 12.8806 | 0.99823 | 14.2674 | 14.4947 | 14.7322 | 15.1323 | 15.4823 | 22.863 | 0.0476
Ribble | CATTERALL WATERWORKS | 33 | 8.2664 | 0.93916 | 8.2495 | 8.4802 | 8.6116 | 8.7051 | 8.8586 | 5 | 0.136
Blackpool | CECIL ST | 33 | 12.5448 | 0.9993 | 13.5788 | 13.9829 | 14.1184 | 14.3983 | 14.5952 | 22.31 | 0
Stuart Street | CENTRAL MANCHESTER | 33 | 13.2626 | 0.99916 | 15.2613 | 15.8111 | 16.0839 | 16.4512 | 16.7027 | 29 | 0
Chadderton | CHADDERTON | 33 | 10.468 | 0.99465 | 12.858 | 13.4311 | 13.6765 | 14.013 | 14.1472 | 38 | 0.48843
Bury | CHAMBERHALL | 33 | 17.6385 | 0.99904 | 18.8002 | 19.7788 | 20.0271 | 20.8419 | 21.0824 | 21.68 | 0.086673
Frederick Rd | CHAPEL WHARF | 33 | 9.4937 | 0.99752 | 12.3605 | 13.1598 | 13.2429 | 13.6298 | 13.8646 | 22.863 | 0
Barton | CHASSEN RD | 33 | 13.0133 | 0.99621 | 14.0208 | 14.2915 | 14.3503 | 14.7131 | 14.9775 | 16.6 | 0.02734
Barrow & Sandgate | CHATSWORTH ST | 33 | 11.9211 | 0.99551 | 12.2154 | 12.6541 | 12.8972 | 13.3487 | 13.6709 | 20.1 | 0.125
Adswood | CHEADLE HEATH | 33 | 10.0482 | 0.99644 | 10.8094 | 11.0565 | 11.2769 | 11.4594 | 11.8428 | 17.5 | 0.07144
Adswood | CHEADLE HULME | 33 | 14.137 | 0.99182 | 15.3476 | 16.0935 | 15.9888 | 16.349 | 16.7697 | 22.863 | 0
Agecroft | CHEETHAM HILL | 33 | 15.5968 | 0.99879 | 16.7635 | 17.3214 | 17.4409 | 17.7869 | 18.0305 | 18.2905 | 0
Stretford | CHESTER RD T11 & T12 | 33 | 10.6839 | 0.99924 | 11.4425 | 11.6826 | 11.9971 | 12.2679 | 12.555 | 16 | 0
Stretford | CHESTER RD T13 | 33 | 3.0838 | 0.99924 | 3.5609 | 3.7788 | 3.9712 | 4.2165 | 4.5356 | 13.25 | 0
Wrightington | CHORLEY SOUTH | 33 | 13.9242 | 0.98234 | 16.3415 | 17.2068 | 17.7128 | 18.3253 | 18.8532 | 17.5 | 0
West Didsbury | CHORLTON | 33 | 7.1153 | 0.99309 | 7.6017 | 7.7366 | 7.9581 | 8.1509 | 8.3642 | 12 | 0
Huncoat | CHURCH | 33 | 5.9673 | 0.97778 | 6.3467 | 6.4423 | 6.5623 | 6.6716 | 6.7755 | 7 | 0
Longsight | CIRCLE SQUARE | 33 | 5.0527 | 0.94874 | 5.3117 | 5.4319 | 5.5713 | 5.6866 | 5.7794 | 22.86 | 0
Blackburn | CLARENDON RD | 33 | 12.2275 | 0.99274 | 14.1188 | 14.9272 | 15.0154 | 15.48 | 15.674 | 22.863 | 0
Lancaster | CLAUGHTON | 33 | 3.5358 | 0.9949 | 3.6028 | 3.6781 | 3.7819 | 3.8778 | 3.947 | 4 | 0
Bispham | CLEVELEYS | 33 | 12.0257 | 0.99812 | 12.5994 | 12.9517 | 13.1038 | 13.3979 | 13.5932 | 17.5 | 0
Kearsley (Local) | CLIFTON JUNCTION | 33 | 10.3277 | 0.98533 | 10.382 | 10.5928 | 10.7417 | 10.9988 | 11.1746 | 17.5 | 0.3942
Nelson | CLOVER HILL | 33 | 8.1542 | 0.99756 | 8.7098 | 8.894 | 9.1007 | 9.2803 | 9.4498 | 19.4 | 0.02475
Huncoat | COG LANE | 33 | 18.4229 | 0.99187 | 19.6183 | 19.9638 | 20.331 | 20.6452 | 20.9284 | 27.0751 | 0
Ulverston | CONISTON | 33 | 2.2732 | 0.99632 | 2.3739 | 2.4535 | 2.5508 | 2.6111 | 2.7125 | 1.8 | 0.00945
Thornton | COPSE RD | 33 | 15.3502 | 0.9971 | 15.8339 | 16.2863 | 16.5934 | 17.0279 | 17.3528 | 22.863 | 0.36
Bolton | COX GREEN | 33 | 10.9933 | 0.99757 | 11.3422 | 11.8909 | 11.7224 | 12.1202 | 12.2574 | 16.7 | 0.0064
Ribble | CRAGGS ROW & BUSHELL ST | 33 | 17.0242 | 0.99519 | 19.5876 | 20.5243 | 20.627 | 21.1487 | 21.3771 | 22.86 | 0 | Demand group comprising 2 primary substation sites that are paralled on the HV side
Westhoughton | CROWN LANE | 33 | 15.833 | 0.99813 | 17.2288 | 17.9054 | 18.239 | 18.8428 | 19.2473 | 22.863 | 1.0395
Golborne | CULCHETH | 33 | 8.1359 | 0.99909 | 9.0859 | 9.4474 | 9.5403 | 9.8604 | 10.1213 | 12 | 0.01
Kearsley (Local) | CUTACRE | 33 | 4.9224 | 0.99945 | 9.0313 | 10.104 | 10.6736 | 11.2824 | 11.8444 | 23 | 0.03236
Bloom Street | DEANSGATE | 33 | 11.0359 | 0.99855 | 12.1279 | 12.3654 | 12.6436 | 12.8668 | 13.1013 | 20.17 | 0
Droylsden | DENTON EAST | 33 | 12.6251 | 0.99855 | 13.4484 | 13.7378 | 13.8762 | 14.1484 | 14.3659 | 22.863 | 0.003
Droylsden | DENTON WEST | 33 | 13.4891 | 0.99419 | 15.9697 | 16.5073 | 16.6489 | 16.9793 | 17.5032 | 22.863 | 0
Bloom Street | DICKINSON ST | 33 | 24.8321 | 0.99903 | 25.1754 | 25.4218 | 26.0564 | 26.6139 | 27.2417 | 31.5 | 0
West Didsbury | DIDSBURY | 33 | 14.6837 | 0.99771 | 15.1385 | 15.4477 | 15.8658 | 16.2209 | 16.6248 | 22.863 | 0
Preston East | DODGSON RD | 33 | 7.456 | 0.99864 | 9.4103 | 9.8964 | 9.8963 | 10.066 | 10.2372 | 22.863 | 0
Ribble | DOUGLAS ST | 33 | 10.8386 | 0.99801 | 12.0053 | 12.5061 | 12.6422 | 12.9756 | 13.185 | 20.84 | 0.01
Droylsden | DROYLSDEN EAST | 33 | 14.1683 | 0.99849 | 15.4203 | 15.8106 | 16.0026 | 16.4024 | 16.7018 | 22.86 | 0
Hyde | DUKINFIELD | 33 | 10.5236 | 0.95 | 10.7006 | 11.0223 | 11.2465 | 11.5975 | 11.8862 | 22.863 | 1.0326
Bury | DUMERS LANE | 33 | 9.853 | 0.9874 | 10.6729 | 11.3402 | 11.7007 | 12.0517 | 12.1657 | 20.5 | 0.33256
Barton | DUMPLINGTON | 33 | 16.7017 | 0.99804 | 18.2032 | 18.4724 | 18.793 | 19.1764 | 19.5227 | 34 | 0
Stuart Street | EASTLANDS | 33 | 11.5721 | 0.99796 | 16.6718 | 22.2324 | 27.4716 | 32.8285 | 38.0944 | 22.863 | 0
Spadeadam | EASTON | 33 | 1.5151 | 0.99727 | 1.5817 | 1.6575 | 1.6329 | 1.6897 | 1.7407 | 1.7 | 0
Egremont | EGREMONT | 33 | 11.2474 | 0.99496 | 12.5473 | 13.2978 | 13.2275 | 13.7295 | 14.2472 | 15 | 0.22431
Stainburn & Siddick | EMBLETON | 33 | 11.9321 | 0.99472 | 12.9211 | 13.3909 | 13.7803 | 14.083 | 14.4475 | 15.242 | 0.059
Lower Darwen | EXCHANGE ST | 33 | 9.6428 | 0.9955 | 12.0897 | 12.7977 | 12.8822 | 13.2055 | 13.3325 | 17.5 | 0
Chadderton | FAILSWORTH | 33 | 12.8521 | 0.99836 | 14.1189 | 14.5062 | 14.7585 | 15.0627 | 15.245 | 22.863 | 0.567
West Didsbury | FALLOWFIELD | 33 | 15.6101 | 0.99899 | 16.5512 | 16.9265 | 17.3486 | 17.7057 | 18.0865 | 22.863 | 0
Kearsley (Local) | FARNWORTH | 33 | 12.9635 | 0.99517 | 14.5495 | 14.9606 | 15.0947 | 15.4428 | 15.6623 | 23 | 0
Lower Darwen | FENISCOWLES | 33 | 2.6403 | 0.99849 | 2.949 | 3.0914 | 3.1358 | 3.2201 | 3.2977 | 5.7 | 0
Buxton / New Mills | FERODO | 33 | 9.7884 | 0.99371 | 10.4797 | 10.8516 | 11.1359 | 11.4748 | 11.7797 | 16.54 | 0
Nelson | FLAT LANE | 33 | 3.8041 | 0.95 | 4.1087 | 4.2583 | 4.3961 | 4.5205 | 4.6429 | 4.5 | 0.0588
Frederick Rd | FREDERICK RD | 33 | 15.0956 | 0.99945 | 16.7452 | 17.5277 | 17.9663 | 18.7746 | 19.2721 | 20.5 | 0
Carlisle | FUSEHILL | 33 | 16.2435 | 0.99618 | 16.8205 | 17.2426 | 17.3589 | 17.7795 | 18.0584 | 20.5 | 0.011
Belfield | GALE | 33 | 8.4282 | 0.99833 | 9.1187 | 9.2687 | 9.4826 | 9.7799 | 10.0129 | 22.863 | 0
Thornton | GARSTANG | 33 | 10.219 | 0.9406 | 12.8468 | 13.8315 | 14.2718 | 14.8239 | 15.3028 | 19.6 | 0.25025
Moss Nook | GATLEY | 33 | 7.652 | 0.92508 | 8.0043 | 8.0831 | 8.2452 | 8.3859 | 8.5517 | 10 | 0
Wigan | GIDLOW | 33 | 14.1662 | 0.9976 | 16.5726 | 17.1461 | 17.6078 | 18.037 | 18.434 | 22.863 | 0
Penrith & Shap | GILLSROW | 33 | 3.7172 | 0.99785 | 4.0586 | 4.2006 | 4.3292 | 4.4463 | 4.5452 | 5.3 | 0.02259
Ulverston | GLAXO | 33 | 2.4145 | 0.99406 | 2.4878 | 2.5658 | 2.5682 | 2.6235 | 2.6602 | 12.05 | 0
Hyde | GLOSSOP | 33 | 13.7285 | 0.99627 | 14.5078 | 14.8907 | 15.0917 | 15.5322 | 15.8453 | 22.863 | 0
Golborne | GOLBORNE | 33 | 28.4534 | 0.99423 | 31.4704 | 33.0115 | 33.3193 | 34.9452 | 36.0489 | 43 | 0.005
New Mills | GOWHOLE | 33 | 15.1755 | 0.99509 | 15.6831 | 16.214 | 16.6504 | 17.0666 | 17.5262 | 22.863 | 0.2817
Rossendale | GRANE RD & PRINNY HILL | 33 | 10.3351 | 0.9924 | 11.0439 | 11.2827 | 11.4826 | 11.6738 | 11.8529 | 17.5 | 0.01024 | Demand group comprising 2 primary substation sites that are paralled on the HV side
Ulverston | GRANGE | 33 | 7.3561 | 0.99471 | 8.0225 | 8.3539 | 8.5 | 8.8177 | 9.0898 | 13 | 0
Huncoat | GREAT HARWOOD | 33 | 6.6199 | 0.89855 | 8.6126 | 9.1809 | 9.4309 | 9.6245 | 9.7944 | 18.88 | 0.01
Altrincham | GREEN LANE (ALTRINCHAM) | 33 | 15.1856 | 0.99012 | 16.5405 | 16.8135 | 16.9411 | 17.3281 | 17.5735 | 22.863 | 0
Hazel Grove | GREEN LANE (HAZEL GROVE) | 33 | 16.3495 | 0.99465 | 17.7211 | 18.3374 | 18.4446 | 18.8257 | 19.2993 | 22.863 | 0
Wigan | GREEN ST T11 | 33 | 9.5207 | 0.9949 | 10.1602 | 10.4109 | 10.6857 | 10.9183 | 11.1112 | 13.25 | 0.544
Wigan | GREEN ST T12 & T13 | 33 | 16.5112 | 0.9949 | 17.9457 | 18.3128 | 18.6848 | 19.0145 | 19.3409 | 21.46 | 0.544
Hartshead-Heyrod | GREENFIELD | 33 | 9.6225 | 0.994 | 10.2086 | 10.5696 | 10.6989 | 11.0573 | 11.3776 | 23 | 0
Greenhill | GREENHILL | 33 | 24.1352 | 0.95 | 25.9123 | 26.1072 | 26.9422 | 27.6246 | 27.9244 | 42 | 0
Lower Darwen | GRIFFIN | 33 | 13.5338 | 0.99878 | 14.6004 | 15.3452 | 15.4029 | 15.8866 | 16.1693 | 22.86 | 0
Hyde | HADFIELD | 33 | 9.4607 | 0.95 | 9.8411 | 10.1461 | 10.4011 | 10.6619 | 10.9737 | 22.863 | 2.0801
Peel | HALL CROSS | 33 | 18.9276 | 0.98285 | 22.294 | 23.5097 | 24.0909 | 24.7785 | 25.3424 | 22.863 | 0.4916
Moss Nook | HANDFORTH | 33 | 12.0169 | 0.99454 | 14.188 | 14.6917 | 15.1337 | 15.5364 | 15.949 | 22.863 | 0.08568
Wrightington | HANGING BRIDGE | 33 | 5.1558 | 0.9931 | 5.7456 | 6.0445 | 6.2281 | 6.4538 | 6.6575 | 8 | 0.2475
Rossendale | HAREHOLME | 33 | 13.6586 | 0.99788 | 14.6882 | 15.1741 | 15.6065 | 16.0695 | 16.4769 | 22.863 | 0.11198
Red Bank | HARPURHEY | 33 | 11.3906 | 0.99874 | 12.5727 | 12.9419 | 13.1765 | 13.4628 | 13.6459 | 22.86 | 0
Bolton | HARWOOD | 33 | 12.7075 | 0.99262 | 13.5819 | 14.0756 | 14.2221 | 14.7525 | 14.9843 | 16.7 | 0
Hyde | HATTERSLEY | 33 | 9.7699 | 0.98202 | 11.2308 | 12.2705 | 13.1213 | 14.0639 | 14.9476 | 17.5 | 1.1743
Ulverston | HAVERTHWAITE | 33 | 4.2999 | 0.99863 | 4.855 | 5.1054 | 4.9734 | 5.1336 | 5.2621 | 9.5 | 0.01388
Hazel Grove | HAWK GREEN | 33 | 10.1268 | 0.98408 | 10.8517 | 11.2225 | 11.3168 | 11.6399 | 11.9486 | 23 | 0
Golborne | HAYDOCK | 33 | 17.8517 | 0.99268 | 21.8684 | 23.0733 | 23.2388 | 23.4629 | 24.0233 | 32 | 3.4735
Stainburn & Siddick | HDA NO1 & HDA NO2 | 33 | 6.9663 | 0.99906 | 6.947 | 7.6798 | 7.8411 | 7.8885 | 8.3543 | 20.78 | 2.8587 | Estimated demand
Castleton | HEADY HILL | 33 | 9.8174 | 0.99692 | 11.5223 | 11.7978 | 12.0309 | 12.3974 | 12.7334 | 17.5 | 0
Bury | HEAP BRIDGE | 33 | 7.3568 | 0.95 | 7.7574 | 8.0498 | 8.249 | 8.4934 | 8.6915 | 16.75 | 2.8226
Burnley | HEASANDFORD | 33 | 8.0478 | 0.997 | 8.6454 | 8.8184 | 8.9561 | 9.2104 | 9.3729 | 18.29 | 4.4185
Vernon Park | HEATON MOOR | 33 | 11.7377 | 0.99521 | 13.4666 | 14.0286 | 14.474 | 14.9309 | 15.6061 | 17.5 | 0
Vernon Park | HEATON NORRIS | 33 | 13.5745 | 0.97831 | 14.8363 | 15.2569 | 15.4624 | 15.8722 | 16.5585 | 20.5 | 0
Nelson | HELWITH BRIDGE | 33 | 3.2503 | 0.95 | 3.215 | 3.2827 | 3.3847 | 3.4574 | 3.5367 | 4 | 0
Egremont | HENSINGHAM | 33 | 8.3562 | 0.96687 | 11.0272 | 11.6681 | 11.6829 | 11.9131 | 12.091 | 22.863 | 0
Hartshead-Heyrod | HEYROD | 33 | 13.0595 | 0.99556 | 13.7725 | 14.0426 | 14.1973 | 14.4845 | 14.7137 | 22.863 | 0
Royton | HEYSIDE | 33 | 9.3798 | 0.98919 | 10.1041 | 10.4108 | 10.6592 | 10.9106 | 11.0837 | 22.863 | 0
Castleton | HEYWOOD | 33 | 12.014 | 0.99461 | 12.9271 | 13.082 | 13.5075 | 13.6902 | 14.1607 | 20.291 | 0
Moss Nook | HIGHER MILL | 33 | 12.6742 | 0.99723 | 13.9971 | 14.3192 | 14.6925 | 15.0379 | 15.4274 | 20 | 0
Leyland | HIGHER WALTON | 33 | 15.3125 | 0.98893 | 15.7994 | 17.3099 | 18.7536 | 21.6027 | 24.4845 | 22.863 | 1.0205
Kearsley (Local) | HILL TOP T11 & T12 | 33 | 15.9256 | 0.98893 | 17.8236 | 18.4063 | 18.9055 | 19.412 | 19.8666 | 22.86 | 0.92173
Kearsley (Local) | HILL TOP T13 | 33 | 6.5033 | 0.98893 | 7.8588 | 8.1642 | 8.3633 | 8.5718 | 8.7245 | 13.25 | 0.54
Atherton | HINDLEY GREEN | 33 | 20.5053 | 0.99579 | 24.7636 | 25.8619 | 26.2087 | 27.0988 | 27.5541 | 35 | 0.2897
Chadderton | HOLLINWOOD | 33 | 8.7733 | 0.99476 | 9.0522 | 9.2931 | 9.4683 | 9.6914 | 9.8108 | 22.863 | 0.00588
Ribble | HOLME RD | 33 | 13.6291 | 0.98638 | 14.9691 | 15.5039 | 15.6765 | 16.027 | 16.3524 | 22.863 | 0.34
Bury | HOLT ST | 33 | 11.1449 | 0.98949 | 12.0663 | 12.5473 | 12.857 | 13.2841 | 13.5813 | 17.5 | 0
Hartshead-Heyrod | HURST | 33 | 10.299 | 0.99781 | 10.9497 | 11.2556 | 11.4161 | 11.69 | 11.9093 | 17.5 | 0.0036
Penrith & Shap | HUTTON END & SKELTON C | 33 | 6.0513 | 1 | 6.3336 | 6.5647 | 6.7473 | 6.8567 | 7.024 | 17.36 | 0.44074 | Demand group comprising 2 primary substation sites that are paralled on the HV side
Hyde | HYDE | 33 | 15.3054 | 0.9937 | 16.2516 | 16.6859 | 17.1387 | 17.6869 | 18.1384 | 22.863 | 0.0192
Huncoat | HYNDBURN RD | 33 | 10.1222 | 0.9971 | 10.1653 | 10.3031 | 10.494 | 10.6608 | 10.797 | 14.7 | 0.0032
Lower Darwen | INDIA ST | 33 | 8.3853 | 0.99791 | 9.1349 | 9.4502 | 9.6059 | 9.8583 | 10.1017 | 22.863 | 0
Kendal (Parkside Rd) | INGLETON | 33 | 2.2437 | 0.94502 | 2.3653 | 2.4739 | 2.5513 | 2.6544 | 2.7536 | 4 | 0
Carrington BSP | IRLAM | 33 | 15.94 | 0.99506 | 18.9312 | 19.1804 | 19.2707 | 19.6348 | 19.8853 | 22.86 | 0.2817
Carlisle | JAMES ST | 33 | 19.2493 | 0.9984 | 22.3373 | 23.3974 | 23.6712 | 24.3093 | 24.7313 | 22.863 | 0
Huncoat | KAY ST | 33 | 8.8826 | 0.99863 | 9.4538 | 9.7348 | 10.0271 | 10.2793 | 10.5056 | 22.863 | 0.002
Kendal (Parkside Rd) | KENDAL | 33 | 18.4186 | 0.99785 | 20.3796 | 21.1691 | 21.3721 | 22.0054 | 22.5307 | 22.86 | 0.08
Stainburn & Siddick | KESWICK | 33 | 11.6845 | 0.98941 | 12.7255 | 13.0581 | 13.2608 | 13.5676 | 13.7725 | 15 | 0.0252
Belfield | KINGSWAY | 33 | 4.3887 | 0.99178 | 8.1961 | 8.6512 | 8.7303 | 8.8929 | 9.0201 | 30 | 0
Spadeadam | KINKRY HILL | 33 | 0.67694 | 0.99083 | 0.6837 | 0.71223 | 0.74036 | 0.76605 | 0.79403 | 1.5 | 0
Kendal (Parkside Rd) | KIRKBY LONSDALE | 33 | 4.7116 | 0.98684 | 4.8501 | 5.0358 | 5.1984 | 5.3136 | 5.4956 | 8 | 0.0032
Ulverston | KIRKBY MOOR | 33 | 1.7549 | 0.92592 | 1.7491 | 1.8481 | 1.9113 | 2.0174 | 2.0975 | 4 | 0.5483
Penrith & Shap | KIRKBY STEPHEN | 33 | 6.0619 | 0.99672 | 6.4445 | 6.718 | 6.8431 | 7.0412 | 7.2276 | 15 | 0
Penrith & Shap | KIRKBY THORE | 33 | 8.9514 | 0.94487 | 9.1177 | 9.4038 | 9.7506 | 9.7832 | 10.0315 | 15.75 | 0
Atherton | KIRKHALL LANE | 33 | 10.066 | 0.99762 | 11.1691 | 11.6265 | 11.6902 | 12.082 | 12.3812 | 16.65 | 0
Orrell | KITT GREEN | 33 | 14.4308 | 0.99411 | 15.7473 | 16.065 | 16.343 | 16.5563 | 16.7049 | 20.5 | 0
Bloom Street | KNOTT MILL | 33 | 13.1087 | 0.99943 | 14.1001 | 14.4866 | 14.9568 | 15.4006 | 15.8705 | 22.863 | 0
Orrell | LAMBERHEAD | 33 | 10.1638 | 0.99017 | 12.9337 | 13.6043 | 14.0518 | 14.4364 | 14.764 | 22.86 | 1.02
Lancaster | LANCASTER | 33 | 18.6561 | 0.961 | 19.7867 | 20.3576 | 22.4702 | 22.9508 | 23.1912 | 22.863 | 1.1524
Chadderton | LANGLEY | 33 | 13.5899 | 0.99466 | 14.8928 | 15.2182 | 15.7549 | 16.2023 | 16.5755 | 22.863 | 0.0048
Nelson | LANGROYD RD | 33 | 11.7348 | 0.99751 | 12.3621 | 12.7095 | 13.0357 | 13.3242 | 13.5796 | 22.86 | 0
Atherton | LEIGH | 33 | 5.9398 | 0.94995 | 6.5582 | 6.7918 | 6.7967 | 6.9144 | 6.9986 | 10 | 0.0884
Longsight | LEVENSHULME | 33 | 15.9195 | 0.99911 | 17.1403 | 17.4414 | 17.6081 | 17.963 | 18.4902 | 17.5 | 0
Stainburn & Siddick | LEYLAND NATIONAL | 33 | 4.3296 | 0.95 | 4.7265 | 4.8944 | 5.1176 | 5.2211 | 5.3483 | 22.863 | 2.5418 | Estimated demand
Kearsley (Local) | LITTLE HULTON | 33 | 12.9176 | 0.98988 | 14.2938 | 15.0971 | 15.8713 | 17.2569 | 18.6092 | 16.95 | 0.0368
Penrith & Shap | LITTLE SALKELD | 33 | 5.8545 | 0.84114 | 5.9305 | 6.0644 | 6.2602 | 6.3951 | 6.4457 | 13 | 0.00496
Belfield | LITTLEBOROUGH | 33 | 12.153 | 0.99411 | 13.239 | 13.5085 | 13.8524 | 14.2386 | 14.6088 | 17.5 | 0
Stretford | LONGFORD BRIDGE | 33 | 11.3433 | 0.9973 | 12.5385 | 12.7614 | 13.0276 | 13.2719 | 13.5724 | 22.863 | 0
Preston East | LONGRIDGE | 33 | 11.0202 | 0.99856 | 13.4985 | 14.2754 | 14.6435 | 14.9417 | 15.3269 | 22.863 | 0
Longsight | LONGSIGHT | 33 | 18.094 | 0.99802 | 19.0224 | 19.6338 | 20.7005 | 21.1813 | 21.6438 | 22.863 | 0
Westhoughton | LOSTOCK | 33 | 21.6475 | 0.99774 | 24.1924 | 25.0296 | 25.6098 | 25.9325 | 26.3279 | 32 | 0.64697
Lower Darwen | LOWER DARWEN | 33 | 9.1448 | 0.97114 | 10.3405 | 10.7513 | 10.9663 | 11.0061 | 11.1855 | 20.5 | 0.0084
Barton | LYONS RD | 33 | 7.9235 | 0.98278 | 9.5316 | 9.6327 | 9.6711 | 9.9275 | 10.0245 | 22.863 | 0
Longsight | MANCHESTER UNIVERSITY | 33 | 13.6919 | 0.9958 | 13.2587 | 13.4308 | 13.7425 | 13.9452 | 14.189 | 22.863 | 0
Hazel Grove | MARPLE | 33 | 4.461 | 0.99966 | 4.9492 | 5.1609 | 5.2202 | 5.3398 | 5.5096 | 6 | 0
Blackpool | MARTON | 33 | 13.7285 | 0.98528 | 14.567 | 15.0551 | 15.3158 | 15.5346 | 15.7807 | 22.9 | 0.008656
Stainburn & Siddick | MARYPORT | 33 | 9.3038 | 0.9871 | 9.7911 | 10.2398 | 10.5973 | 11.0183 | 11.4142 | 23 | 0.12143 | Estimated demand
Altrincham | MEDIPARK | 33 | 3.982 | 0.95 | 3.9199 | 3.9686 | 4.0593 | 4.1231 | 4.1662 | 32 | 0
Kendal (Parkside Rd) | MELLING | 33 | 2.2452 | 0.9995 | 2.297 | 2.4112 | 2.4571 | 2.5526 | 2.6427 | 4 | 0
Peel | MERESIDE | 33 | 8.417 | 0.99772 | 10.7323 | 11.4101 | 11.7113 | 11.9518 | 12.1265 | 16.24 | 0.247
Chadderton | MIDDLETON JUNCTION | 33 | 14.2803 | 0.9912 | 14.7832 | 15.1799 | 15.5154 | 15.8327 | 16.0376 | 23 | 0
Egremont | MIDWAY | 33 | 5.2795 | 0.98156 | 5.4401 | 5.6757 | 5.8322 | 6.0659 | 6.2571 | 15 | 0.17275
Belfield / Castleton | MILNROW | 33 | 10.4658 | 0.99753 | 11.431 | 11.5759 | 11.7751 | 12.0481 | 12.3321 | 22.86 | 0.0146
Kendal (Parkside Rd) | MINTSFEET | 33 | 14.2642 | 0.98909 | 15.2992 | 15.8489 | 16.1819 | 16.5336 | 16.8797 | 21 | 0.3382
Stuart Street | MONSALL | 33 | 10.6504 | 0.95 | 12.703 | 13.0012 | 13.0603 | 13.2144 | 13.3003 | 18 | 0
Barton | MONTON | 33 | 10.3788 | 0.9983 | 12.1851 | 12.5428 | 12.8091 | 13.1153 | 13.4491 | 17.5 | 0.0025
Ribble | MOORSIDE | 33 | 8.5302 | 0.99755 | 13.0966 | 14.3839 | 14.4979 | 14.865 | 15.2155 | 17.5 | 0.25198
Carlisle | MORTON PARK & PIRELLI | 33 | 18.0784 | 0.9926 | 27.0813 | 32.1716 | 35.2897 | 38.7925 | 42.2706 | 28.2 | 1.0725 | Demand group comprising 2 primary substation sites that are paralled on the HV side
Stretford | MOSLEY RD | 33 | 11.5514 | 0.97923 | 11.7566 | 11.8349 | 12.1438 | 12.4148 | 12.5632 | 22.863 | 0.002
Kearsley (Local) | MOSS LANE | 33 | 19.8165 | 0.99913 | 21.6226 | 22.3551 | 22.8141 | 23.455 | 23.8975 | 22.863 | 0
Moss Nook | MOSS NOOK PRIMARY | 132 | 12.7095 | 0.99256 | 14.5659 | 14.9694 | 15.3762 | 15.7395 | 16.1077 | 32 | 0.414
Leyland | MOSS SIDE (Leyland) & SEVEN STARS | 33 | 16.4895 | 0.9807 | 20.6695 | 21.8988 | 22.194 | 22.642 | 22.9637 | 21.15 | 0.27 | Demand group comprising 2 primary substation sites that are paralled on the HV side
Longsight | MOSS SIDE (Longsight) | 33 | 18.4582 | 0.98902 | 23.5686 | 24.699 | 24.8078 | 25.2722 | 25.7549 | 20.5 | 0
Hartshead-Heyrod | MOSSLEY | 33 | 11.337 | 0.98947 | 12.759 | 13.167 | 13.3805 | 13.7278 | 14.031 | 22.863 | 1.2533
Barton | MOUNT ST | 33 | 10.2457 | 0.99729 | 13.1762 | 13.6553 | 13.8235 | 14.2535 | 14.6116 | 22.8631 | 0.00474
Bolton | MUSGRAVE RD | 33 | 11.7998 | 0.99601 | 12.5478 | 12.8816 | 13.0432 | 13.4147 | 13.5932 | 21.88 | 0
Nelson | NELSON | 33 | 14.9704 | 0.9916 | 15.8648 | 16.2277 | 16.4872 | 16.7516 | 16.9815 | 22.86 | 0.00216
Chadderton | NEW MOSTON | 33 | 11.1686 | 0.99874 | 11.7783 | 12.1278 | 12.3677 | 12.6866 | 12.861 | 22.863 | 0
Penrith & Shap | NEWBIGGIN ON LUNE | 33 | 0.9759 | 0.94996 | 1.0242 | 1.0715 | 1.1146 | 1.1519 | 1.1972 | 1.5 | 0
Penrith & Shap | NEWBY | 33 | 5.4909 | 0.97436 | 6.1204 | 6.3001 | 6.495 | 6.6466 | 6.7467 | 7 | 0
Hyde | NEWTON | 33 | 4.344 | 0.96409 | 4.4526 | 4.618 | 4.7798 | 4.9451 | 5.1238 | 16 | 0
Chadderton | NEWTON HEATH | 33 | 7.6567 | 0.95259 | 8.6902 | 8.9266 | 9.0546 | 9.2049 | 9.2919 | 12 | 0
Golborne | NEWTON LE WILLOWS | 33 | 13.4388 | 0.97741 | 14.1075 | 14.5358 | 15.0205 | 15.5501 | 16.0181 | 22.863 | 0.59265
Penrith & Shap | NEWTONGATE T11 & T12 | 33 | 16.8592 | 0.95 | 18.3592 | 19.1724 | 19.1129 | 19.6265 | 19.9926 | 23 | 0.16114
Penrith & Shap | NEWTONGATE T13 | 33 | 6.766 | 0.97523 | 7.8125 | 8.1426 | 8.2791 | 8.4832 | 8.6815 | 13.25 | 0
Bispham | NORBRECK | 33 | 4.1688 | 0.97655 | 4.3134 | 4.4386 | 4.4791 | 4.5914 | 4.654 | 22.863 | 0
Hazel Grove | NORBURY | 33 | 11.9085 | 0.99145 | 13.7451 | 14.2022 | 14.4148 | 14.7871 | 14.9934 | 22.863 | 0
West Didsbury | NORTHENDEN | 33 | 9.0788 | 0.99536 | 9.9601 | 10.2174 | 10.4704 | 10.7024 | 10.9808 | 17.5 | 0.5913
Carrington BSP | NWGB PARTINGTON | 33 | 4.2518 | 0.9988 | 7.3489 | 7.7802 | 7.8638 | 7.9872 | 8.0793 | 16.06 | 0.002
Vernon Park | OFFERTON | 33 | 7.4825 | 0.99083 | 8.9165 | 9.4202 | 9.8541 | 10.2927 | 10.8189 | 17.5 | 0
Droylsden | OPENSHAW | 33 | 14.3868 | 0.99608 | 16.2683 | 16.7113 | 17.099 | 17.4779 | 17.8607 | 17.5 | 0.0032
Skelmersdale | ORMSKIRK | 33 | 13.5357 | 0.99863 | 14.2659 | 14.6407 | 14.9963 | 15.3317 | 15.6338 | 22.863 | 0.025
Padiham | PADIHAM | 33 | 18.938 | 0.9891 | 21.9891 | 22.8907 | 23.3813 | 23.7484 | 24.0828 | 38 | 0.02212
Padiham | PEEL ST | 33 | 6.83 | 0.99558 | 7.7433 | 8.1485 | 8.4888 | 8.8036 | 9.1108 | 8.2 | 0
Padiham | PEEL ST | 33 | 6.83 | 0.9957 | 7.7433 | 8.1485 | 8.4888 | 8.8036 | 9.1108 | 8.2 | 0
Frederick Rd | PENDLETON | 33 | 13.9025 | 0.99661 | 14.404 | 15.1921 | 15.5969 | 16.1596 | 16.632 | 22.863 | 0
Carlisle | PETTERIL BANK | 33 | 13.9598 | 0.99228 | 14.844 | 15.2562 | 15.437 | 15.8506 | 16.2445 | 22.863 | 0.005
Nelson | PHILLIPS LANE | 33 | 5.3979 | 0.95 | 6.3059 | 6.563 | 6.6959 | 6.8289 | 6.9528 | 9 | 0
Bloom Street | PICCADILLY | 33 | 10.0272 | 0.9885 | 10.7433 | 11.0051 | 11.266 | 11.5239 | 11.7322 | 22.863 | 0
Skelmersdale | PIMBO | 33 | 20.5493 | 0.98467 | 20.9291 | 21.2039 | 21.6176 | 22.177 | 22.4205 | 30 | 0.253
Vernon Park | PORTWOOD | 33 | 12.1185 | 0.99853 | 14.828 | 15.7592 | 16.0493 | 16.6493 | 17.3336 | 22.863 | 0.0058
Bispham | POULTON | 33 | 11.3012 | 0.90849 | 11.9224 | 12.3965 | 12.8396 | 13.2379 | 13.6274 | 20.96 | 1.0862
Hazel Grove | POYNTON | 33 | 8.6063 | 0.9917 | 9.2175 | 9.5151 | 9.5559 | 9.7737 | 10.008 | 17.5 | 0.003
Thornton | PREESALL | 33 | 9.4984 | 0.9978 | 10.4026 | 10.9521 | 11.241 | 11.6765 | 12.047 | 23 | 0
Preston East | PRESTON EAST | 33 | 15.3428 | 0.9412 | 20.8641 | 22.647 | 22.7101 | 22.865 | 23.346 | 32 | 0.25932
Blackpool | PRESTON OLD RD | 33 | 11.0185 | 0.9977 | 11.6189 | 11.8287 | 11.9379 | 12.1204 | 12.244 | 22.863 | 0
Agecroft | PRESTWICH | 33 | 15.019 | 0.99936 | 15.8847 | 16.5952 | 16.5214 | 16.9603 | 17.2453 | 22.863 | 0
Blackburn | PRINGLE ST | 33 | 10.3717 | 0.99845 | 11.2774 | 11.7955 | 11.8217 | 12.1658 | 12.3166 | 19.94 | 0
Stuart Street | QUEENS PARK | 33 | 8.3081 | 0.9726 | 13.2001 | 18.8048 | 24.0647 | 29.2757 | 34.6367 | 19.2 | 0
Kearsley GSP | RADCLIFFE | 132 | 28.1506 | 0.99304 | 31.0487 | 32.3472 | 32.808 | 33.8735 | 34.487 | 38 | 0.0033
Blackburn | RANDAL ST | 33 | 12.4489 | 0.99894 | 13.2064 | 13.8994 | 13.9745 | 14.3668 | 14.5497 | 18.8 | 0
Rossendale | RAWTENSTALL RD | 33 | 11.7553 | 0.99217 | 12.5333 | 12.7539 | 13.0153 | 13.2379 | 13.4505 | 22.863 | 0.015
Vernon Park | REDDISH VALE | 33 | 10.1828 | 0.99721 | 11.5094 | 11.9846 | 12.1305 | 12.4669 | 12.842 | 18.5 | 0
Padiham | RIBBLESDALE T13 & T14 | 33 | 12.6658 | 0.9491 | 13.7245 | 14.1129 | 14.4885 | 14.8059 | 15.0913 | 16 | 0
Padiham | RIBBLESDALE T13 & T14 | 33 | 12.6658 | 0.9897 | 13.7245 | 14.1129 | 14.4885 | 14.8059 | 15.0913 | 16 | 0
Preston East | RIBBLETON | 33 | 8.9758 | 0.99851 | 9.5602 | 10.8928 | 11.9645 | 14.7476 | 17.3911 | 22.863 | 0.05984
Kearsley (Local) | RINGLEY | 33 | 6.4981 | 0.95657 | 7.6058 | 7.8505 | 7.9307 | 8.1225 | 8.2278 | 23 | 0.1028
Risley | RISLEY | 132 | 14.8296 | 0.95 | 16.4599 | 17.21 | 17.3791 | 17.863 | 17.9053 | 19.3 | 1.2947
Frederick Rd | ROBERT HALL ST | 33 | 13.452 | 0.99509 | 14.6689 | 15.5944 | 16.0667 | 16.7761 | 17.4265 | 20.5 | 0
Rochdale Central | ROCHDALE CENTRAL | 33 | 18.3476 | 0.98865 | 19.8963 | 20.1299 | 20.5018 | 21.1334 | 21.6611 | 42 | 0.0452
Lower Darwen | ROMAN RD | 33 | 14.018 | 0.99084 | 14.8501 | 15.2545 | 15.5336 | 15.809 | 15.9525 | 20.5 | 0.0064
Vernon Park | ROMILEY | 33 | 13.1304 | 0.99309 | 14.2009 | 14.4951 | 14.7995 | 15.0496 | 15.5581 | 17.5 | 0.03328
Thornton | ROSSALL | 33 | 3.891 | 0.98501 | 3.7974 | 3.9087 | 3.9909 | 4.0957 | 4.1797 | 3.5 | 3.0312 | Estimated demand
Royton | ROYTON | 33 | 11.0779 | 0.99737 | 12.1117 | 12.4577 | 12.6829 | 12.9687 | 13.1318 | 22.863 | 0
Macclesfield | S.E. MACCLESFIELD | 33 | 11.5468 | 0.99551 | 13.7822 | 14.265 | 14.7877 | 15.1596 | 15.5467 | 22.863 | 0
Macclesfield | S.W. MACCLESFIELD | 33 | 17.0746 | 0.9993 | 19.8504 | 20.4889 | 21.3353 | 21.7882 | 22.3226 | 22.863 | 1.3686
Sale | SALE | 33 | 11.9892 | 0.99904 | 13.4199 | 13.6112 | 13.8519 | 14.4065 | 14.7057 | 22.86 | 0.081
Sale | SALE MOOR | 33 | 7.4305 | 0.99738 | 7.9617 | 8.1196 | 8.1354 | 8.3229 | 8.4629 | 10 | 0
Frederick Rd | SALFORD QUAYS | 33 | 9.4884 | 0.99902 | 11.0585 | 11.3623 | 11.7546 | 12.3001 | 12.6129 | 20.5 | 0
Blackburn | SAMLESBURY ENTERPRISE ZONE | 33 | 1 | 0.95 | 1 | 1 | 1 | 1 | 1 | 23 | 0 | New substation, no demand in 2021/22
Barrow & Sandgate | SANDGATE | 33 | 12.7125 | 0.99284 | 14.1655 | 14.5599 | 14.6969 | 15.0125 | 15.3154 | 23 | 0.2278
Skelmersdale | SCARISBRICK | 33 | 3.7496 | 0.99461 | 3.8566 | 3.9344 | 4.0499 | 4.1489 | 4.2514 | 6 | 0.04
Carlisle | SEBERGHAM | 33 | 3.9209 | 0.98228 | 3.9345 | 3.9961 | 4.1584 | 4.2457 | 4.3474 | 4 | 0.08 | Estimated demand
Kendal (Parkside Rd) | SEDBERGH | 33 | 4.1071 | 0.99913 | 4.6604 | 4.9438 | 4.9992 | 5.1692 | 5.3356 | 7.6208 | 0
Penrith & Shap | SELSMIRE | 33 | 2.2806 | 0.99396 | 2.4756 | 2.5954 | 2.639 | 2.7176 | 2.7845 | 4 | 0
Nelson | SETTLE | 33 | 4.4229 | 0.99495 | 5.3687 | 5.5853 | 5.6925 | 5.7925 | 5.8801 | 5 | 0
Blackpool | SHANNON ST SOUTH | 33 | 15.2268 | 0.9972 | 17.1241 | 17.7118 | 17.8682 | 18.1973 | 18.4104 | 22 | 0
Penrith & Shap | SHAP | 33 | 4.8615 | 0.97157 | 4.8036 | 4.9124 | 4.9959 | 5.0441 | 5.132 | 8.5 | 0
Royton | SHAW | 33 | 11.3408 | 0.99824 | 12.3098 | 12.6744 | 12.9499 | 13.2218 | 13.3469 | 22.863 | 0
Stainburn & Siddick | SIDDICK | 33 | 3.1909 | 0.98575 | 2.9068 | 3.0113 | 3.2218 | 3.3671 | 3.465 | 20.5 | 2.2858 | Estimated demand
Carlisle | SILLOTH | 33 | 6.1097 | 0.73806 | 6.2097 | 6.2784 | 6.5097 | 6.6721 | 6.8164 | 30.69 | 0.052
Skelmersdale | SKELMERSDALE | 33 | 12.7905 | 0.99265 | 14.0218 | 14.3568 | 14.6254 | 14.8846 | 15.1221 | 22.863 | 5.1394
Egremont | SLIPWAY | 33 | 8.2938 | 0.99349 | 8.5719 | 8.7129 | 8.8572 | 9.0567 | 9.2246 | 13 | 0
Droylsden | SNIPE | 33 | 12.7679 | 0.99563 | 13.3615 | 13.6047 | 13.9354 | 14.6357 | 15.2602 | 22.86 | 0
Lytham | SOUTH PARK | 33 | 7.8159 | 0.99601 | 8.9169 | 9.3453 | 9.4217 | 9.6486 | 9.7929 | 23 | 0
Bolton | SPA RD | 33 | 23.5238 | 0.97314 | 24.071 | 25.1257 | 25.5481 | 26.18 | 26.6483 | 31.5 | 0.0035
Spadeadam | SPADEADAM 11/33KV | 33 | 0 | 0.9488 | 0 | 0 | 0 | 0 | 0 | 9.5 | 0
Spadeadam | SPADEADAM 132/11KV | 132 | 11.5425 | 0.99927 | 12.0476 | 12.4616 | 12.3659 | 12.9628 | 13.0328 | 38 | 0
Rochdale Central | SPOTLAND | 33 | 9.5707 | 0.99625 | 10.065 | 10.1367 | 10.4372 | 10.798 | 11.2505 | 17.5 | 0.055
Nelson | SPRING COTTAGE | 33 | 8.7391 | 0.98102 | 8.7606 | 8.8756 | 9.0318 | 9.1684 | 9.2765 | 13.72 | 0
Lancaster | SPRING GARDEN ST 11kV | 33 | 9.3384 | 0.99585 | 12.9159 | 13.7382 | 14.0492 | 14.2767 | 14.4857 | 29 | 0
Lancaster | SPRING GARDEN ST 6.6KV | 33 | 11.3267 | 0.99585 | 13.4611 | 14.12 | 14.5806 | 14.9575 | 15.3127 | 22.863 | 0.0096
Blackpool | SQUIRES GATE | 33 | 12.0406 | 0.95 | 15.2485 | 16.188 | 16.3958 | 16.7539 | 16.9789 | 22.9 | 1.1985
Lytham | ST ANNES | 33 | 6.4543 | 0.99157 | 7.2843 | 7.5942 | 7.7728 | 7.968 | 8.1273 | 17.5 | 0
Frederick Rd | ST JOHNS | 33 | 7.6134 | 0.95 | 11.6233 | 12.1069 | 12.1101 | 12.1141 | 12.1188 | 22.9 | 0
Greenhill | ST MARYS | 33 | 7.6708 | 0.99657 | 9.1878 | 10.483 | 11.7835 | 13.0184 | 13.1683 | 22.863 | 0
Ribble | ST MARYS ST | 33 | 10.2926 | 0.99448 | 11.7846 | 12.3651 | 12.3926 | 12.6817 | 12.8611 | 17.5 | 0
Lytham | ST THOMAS RD | 33 | 9.8253 | 0.99695 | 10.123 | 10.4906 | 10.7143 | 11.0105 | 11.2554 | 22.863 | 0
Stainburn & Siddick | STAINBURN | 33 | 5.7913 | 0.99989 | 5.8227 | 6.0009 | 6.312 | 6.5461 | 6.7453 | 15 | 0.002
Wrightington | STANDISH | 33 | 15.6991 | 0.98955 | 16.8477 | 17.4865 | 17.9441 | 18.5325 | 19.0545 | 23 | 1.2486
Frederick Rd | STRANGEWAYS | 33 | 14.0561 | 0.99891 | 15.387 | 15.8278 | 16.5038 | 16.8602 | 17.0097 | 20.5 | 0
Huncoat | STRAWBERRY BANK | 33 | 9.0606 | 0.95 | 11.274 | 11.9705 | 13.3316 | 14.6609 | 15.9269 | 22.863 | 2.4712
Stuart Street | STUART ST | 33 | 11.0976 | 0.98912 | 11.4277 | 11.5795 | 11.8011 | 12.0283 | 12.194 | 20.5 | 0
Rossendale | STUBBINS | 33 | 15.5795 | 0.93136 | 15.7563 | 15.9969 | 16.3425 | 16.5981 | 16.7726 | 28 | 0
Agecroft | SWINTON | 33 | 9.9268 | 0.99761 | 10.6094 | 10.9138 | 11.0269 | 11.34 | 11.4689 | 23 | 0
Hartshead-Heyrod | TAME VALLEY | 33 | 14.6066 | 0.99685 | 15.2776 | 15.8678 | 16.5144 | 17.1097 | 17.6147 | 22.863 | 0.00858
Ribble | TARDY GATE | 33 | 11.4484 | 0.99522 | 14.0534 | 14.9236 | 15.0525 | 15.4511 | 15.7303 | 22.863 | 0.001
Wrightington | TARLETON | 33 | 16.2475 | 0.97766 | 18.1021 | 18.8753 | 19.3078 | 19.8177 | 20.2321 | 22.863 | 0.923
Agecroft | THE HEIGHT | 33 | 10.6509 | 0.99687 | 11.4661 | 11.9409 | 12.0624 | 12.4048 | 12.6785 | 16.8 | 0.2025
Moss Nook | THORLEY LANE | 33 | 0.43821 | 0.95 | 0.64937 | 0.67467 | 0.67467 | 0.67467 | 0.67467 | 32 | 0 | New substation, no demand in 2021/22
Bispham | THORNTON | 33 | 11.6556 | 0.9952 | 12.9969 | 13.4455 | 13.7034 | 14.0194 | 14.2793 | 22.863 | 0.00098
Chadderton | TOWNLEY ST | 33 | 8.2703 | 0.99764 | 10.0033 | 10.4032 | 10.5618 | 10.7535 | 10.8691 | 15.242 | 0
Stretford | TRAFFORD | 33 | 14.898 | 0.99352 | 14.7524 | 15.0229 | 15.4388 | 15.8729 | 16.2981 | 20.5 | 3.579
Barton | TRAFFORD PARK NORTH | 33 | 10.6233 | 0.88083 | 10.7276 | 10.8129 | 11.0142 | 11.0681 | 11.099 | 15.75 | 0.56
Heysham | TRIMPELL | 132 | 3.2848 | 0.95 | 3.9876 | 4.2347 | 4.3593 | 4.4295 | 4.5037 | 23.815 | 0.88
Frederick Rd | TRINITY | 33 | 13.4275 | 0.97233 | 19.9693 | 21.2828 | 21.8009 | 22.3268 | 22.8146 | 42 | 0
Ribble | TULKETH | 33 | 13.7635 | 0.99577 | 14.0934 | 14.636 | 14.8615 | 15.3005 | 15.5829 | 22.863 | 0
Ulverston | ULVERSTON | 33 | 8.8847 | 0.90362 | 10.2956 | 10.7426 | 10.9562 | 11.2471 | 11.5008 | 15 | 0.51634
Bolton | UNION RD | 33 | 15.3648 | 0.99673 | 15.7829 | 16.2455 | 16.4653 | 16.823 | 17.1756 | 22.863 | 0
Orrell | UPHOLLAND | 33 | 12.1162 | 0.98986 | 13.0501 | 13.4536 | 13.8991 | 14.3157 | 14.6897 | 17.5 | 0.65135
Stretford | URMSTON | 33 | 11.063 | 0.9977 | 12.3259 | 12.6112 | 12.9195 | 13.2049 | 13.5261 | 22.863 | 0
Longsight | VICTORIA PARK | 33 | 13.9071 | 0.99038 | 13.4278 | 13.6268 | 14.0162 | 14.2829 | 14.4318 | 20.5 | 0.0028
Bispham | WARBRECK | 33 | 9.1567 | 0.95 | 9.6792 | 9.9005 | 10.0194 | 10.1969 | 10.34 | 17.5 | 0.001
Belfield | WARDLEWORTH | 33 | 11.8471 | 0.98232 | 12.8566 | 12.9186 | 13.1278 | 13.5639 | 13.9496 | 22.863 | 0.00856
Peel | WARTON | 33 | 9.7323 | 0.99685 | 10.5771 | 10.8988 | 11.2918 | 11.5749 | 11.8708 | 22.863 | 0.27
Greenhill | WATERHEAD | 33 | 7.2232 | 0.99626 | 7.7108 | 7.8559 | 8.1149 | 8.3165 | 8.4712 | 22.863 | 0
Buxton | WATERSWALLOWS | 33 | 10.0637 | 0.97673 | 10.1348 | 10.332 | 10.5008 | 10.7971 | 10.9776 | 22.863 | 0
Frederick Rd | WEASTE | 33 | 14.0739 | 0.997 | 15.1301 | 15.6035 | 15.8213 | 16.3286 | 16.4605 | 20.5 | 0
Greenhill | WERNETH | 33 | 8.6537 | 0.99999 | 9.3964 | 9.7065 | 9.9047 | 10.1701 | 10.3374 | 22.863 | 0
Rossendale | WESLEY PLACE BACUP | 33 | 9.8643 | 0.99688 | 10.5824 | 10.8302 | 11.1094 | 11.3726 | 11.6337 | 22.863 | 0.0867
West Didsbury | WEST DIDSBURY | 33 | 11.8101 | 0.99499 | 14.1078 | 14.6055 | 15.0113 | 15.3609 | 15.7283 | 20.5 | 0
Lancaster | WESTGATE | 33 | 14.9478 | 0.9959 | 15.3669 | 15.8118 | 16.4358 | 16.7367 | 17.1174 | 22.863 | 0.605
Westhoughton | WESTHOUGHTON | 33 | 17.798 | 0.99499 | 19.2323 | 20.1029 | 19.9986 | 20.5703 | 20.9113 | 22.863 | 0.01298
Carlisle | WESTLINTON | 33 | 6.9289 | 0.9994 | 12.1458 | 13.5261 | 13.039 | 13.3188 | 13.4801 | 15 | 0.06248 | Estimated demand
Padiham | WHALLEY | 33 | 12.2036 | 0.98832 | 12.8961 | 13.407 | 13.9831 | 14.5061 | 14.9493 | 22.863 | 0.0234
West Didsbury | WHALLEY RANGE | 33 | 17.113 | 0.99828 | 17.8581 | 18.2194 | 18.7495 | 19.1904 | 19.6991 | 22.863 | 0
Kendal (Parkside Rd) | WHASSET | 33 | 12.5055 | 0.96874 | 12.3399 | 12.69 | 12.8386 | 13.3813 | 16.2691 | 16 | 0.00828
Leyland | WHITTLE LE WOODS | 33 | 9.5813 | 0.99959 | 11.1048 | 11.6681 | 11.9629 | 12.389 | 12.7081 | 17.5 | 0
Rochdale Central | WHITWORTH | 33 | 2.6635 | 0.92921 | 2.7645 | 2.799 | 2.8735 | 3.0275 | 3.1518 | 8 | 0
Carlisle | WIGTON | 33 | 20.0688 | 0.97895 | 20.656 | 21.1385 | 21.5643 | 22.0235 | 22.4154 | 22.863 | 0.65824
Skelmersdale | WILLOW HEY | 33 | 10.5967 | 0.99177 | 11.4853 | 11.7663 | 12.0133 | 12.2202 | 12.4417 | 22.863 | 0.00264
Greenhill | WILLOWBANK | 33 | 12.9354 | 0.99742 | 13.9101 | 14.1194 | 14.5314 | 14.8679 | 15.0005 | 17.5 | 0.001
Carlisle | WILLOWHOLME | 33 | 10.8514 | 0.99758 | 12.6607 | 13.2606 | 13.5587 | 13.7362 | 14.052 | 22.863 | 0.0198
Moss Nook | WILMSLOW | 33 | 13.035 | 0.99493 | 13.782 | 13.9989 | 14.3339 | 14.6399 | 14.9588 | 17.5 | 0
Kendal (Parkside Rd) | WINDERMERE | 33 | 13.0489 | 0.99737 | 13.8838 | 14.3931 | 14.517 | 14.9898 | 15.352 | 23 | 0.00698
Adswood | WINIFRED RD | 33 | 12.0488 | 0.99496 | 13.2325 | 13.7942 | 13.8443 | 14.1713 | 14.4887 | 17.5 | 0.00048
West Didsbury | WITHINGTON | 33 | 14.8687 | 0.99736 | 15.7343 | 16.1109 | 16.5011 | 16.8288 | 17.1872 | 17.5 | 0.007
Macclesfield | WITHYFOLD DRIVE | 33 | 17.0556 | 0.99898 | 18.6111 | 19.0053 | 19.764 | 20.1674 | 20.6298 | 35 | 0
Castleton | WOODBINE ST | 33 | 11.7191 | 0.99497 | 12.829 | 13.0686 | 13.3688 | 13.7641 | 14.1693 | 17.5 | 0.00044
Wrightington | WOODFIELD RD | 33 | 15.3727 | 0.99784 | 18.3735 | 19.2776 | 19.4698 | 19.8687 | 20.119 | 22.863 | 0.0022
Lancaster | WOODHILL LANE | 33 | 6.3676 | 0.99436 | 6.6567 | 7.8028 | 9.0308 | 10.105 | 11.2323 | 9 | 0
Moss Nook | WOODHOUSE PARK | 33 | 11.4479 | 0.99584 | 12.9571 | 13.2007 | 13.4685 | 13.741 | 13.998 | 17.5 | 0.04
Vernon Park | WOODLEY | 33 | 12.0958 | 0.99581 | 12.5813 | 12.9433 | 13.2145 | 13.3547 | 13.7634 | 22.863 | 1.0501
Bury | WOOLFOLD | 33 | 10.6123 | 0.99138 | 10.9561 | 11.3797 | 11.6058 | 12.0295 | 12.2807 | 23 | 0
Bolton | WORDSWORTH ST | 33 | 12.9451 | 0.99916 | 13.3713 | 13.7669 | 14.0071 | 14.5334 | 14.7295 | 22.863 | 0.01634
Wigan | WORSLEY MESNES | 33 | 8.3907 | 0.99514 | 9.1093 | 10.1609 | 11.241 | 13.5048 | 15.7303 | 22.863 | 0
Wrightington | WRIGHTINGTON | 33 | 10.7097 | 0.98496 | 12.2648 | 13.0215 | 13.4833 | 14.0058 | 14.4571 | 22.863 | 0
Kendal (Parkside Rd) | YEALAND | 33 | 2.9296 | 0.97999 | 3.147 | 3.2934 | 3.4028 | 3.5311 | 3.655 | 4 | 0
The information in this table should be read in conjunction with the explanatory notes in the main text.
The information contained in this statement is provided for the sole purpose of allowing existing and potential customers to assess the capabilities of the electricity network and opportunities for changes
in their use of the network or for connecting to it.
While all reasonable effort has been made to ensure the accuracy of the information, Electricity North West will accept no liability for any loss or damage caused by the information not being accurate.
Actual changes in supply capacity for existing customers or new connections are subject to detailed assessment and approval by Electricity North West, and payment of appropriate charges.
The information contained in this statement is the Copyright of Electricity North West, All Rights Reserved.

## BSP Load Table
132kV SUBSTATION MAXIMUM LOAD INFORMATION
[6 empty] | Forecast Demand (MVA) |  |  |  |  | Firm Capacity Data
Substation Group | Substation | 132kV Schematic Number | Voltage Level (kV) | 2022/23 Weather corrected Maximum Demand (MVA) | Power Factor | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | Capacity Based on Network Assets only (MVA) | Estimated Distributed Generation contribution to Capacity (MVA) | Comment
BREDBURY | ADSWOOD | Sheet 1 | 132 | 47.92 | 0.99233 | 55.1012 | 56.7923 | 58.0542 | 59.2152 | 60.3418 | 117 | 0.07144
KEARSLEY | AGECROFT | Sheet 1 | 132 | 56.28 | 0.90067 | 60.1899 | 61.5307 | 62.9655 | 64.1608 | 65.243 | 78 | 0.2025
CARRINGTON | ALTRINCHAM | Sheet 1 | 132 | 50.52 | 0.96694 | 54.6102 | 56.199 | 57.763 | 59.084 | 60.2829 | 117 | 0.025705
KEARSLEY | ATHERTON | Sheet 2 | 132 | 82.25 | 0.9976 | 91.7581 | 94.8824 | 97.9257 | 107.0516 | 116.0292 | 117 | 0.53278
HUTTON | BARROW & SANDGATE | Sheet 3 | 132 | 61.93 | 0.98529 | 50.3972 | 51.4586 | 52.9366 | 53.8895 | 54.7369 | 126 | 0.5153 | Barrow & Sandgate run in parallel on the 33kV system.
CARRINGTON | BARTON | Sheet 1 | 132 | 76.84 | 0.9904 | 80.6928 | 82.9045 | 85.0693 | 94.9562 | 104.6135 | 150 | 3.8616
ROCHDALE | BELFIELD | Sheet 3 | 132 | 44.1 | 0.9943 | 50.1635 | 51.5204 | 52.7293 | 53.7722 | 54.7283 | 117 | 4.0016
STANAH | BISPHAM | Sheet 2 | 132 | 64.15 | 0.97651 | 70.296 | 72.0676 | 73.7079 | 75.132 | 76.4874 | 117 | 4.4862
PENWORTHAM EAST | BLACKBURN | Sheet 2 | 132 | 47.15 | 0.95132 | 53.1761 | 55.0362 | 56.2449 | 57.2835 | 58.2506 | 117 | 2.7612
STANAH | BLACKPOOL | Sheet 2 | 132 | 68.74 | 0.97627 | 71.0584 | 77.3167 | 82.9377 | 89.0547 | 103.5366 | 117 | 1.2072
SOUTH MANCHESTER | BLOOM ST | Sheet 1 | 132 | 67.91 | 0.99592 | 70.9039 | 72.377 | 74.0846 | 75.4741 | 76.5902 | 93.2 | 0.010754
KEARSLEY | BOLTON | Sheet 2 | 132 | 100.37 | 0.99252 | 109.692 | 113.0501 | 116.377 | 118.9722 | 121.0387 | 124 | 0.11719
ROCHDALE | BURNLEY | Sheet 2 | 132 | 49.09 | 0.972 | 52.815 | 54.2511 | 55.631 | 56.7956 | 57.8218 | 117 | 5.5933
KEARSLEY | BURY | Sheet 2 | 132 | 79.89 | 0.96892 | 86.6858 | 89.3294 | 91.9545 | 94.0198 | 95.7187 | 117 | 9.7618
STALYBRIDGE | BUXTON | Sheet 1 | 132 | 58.05 | 0.94566 | 58.2506 | 58.7839 | 59.6805 | 60.3385 | 60.8579 | 103.5 | 5.1045
HARKER | CARLISLE | Sheet 3 | 132 | 116.29 | 0.99886 | 135.0376 | 143.754 | 149.8917 | 155.4702 | 160.8061 | 150 | 8.9261
HARKER | CARLISLE NORTH | Sheet 3 | 133 | 14.02 | 0.9964 | 15.3969 | 15.9169 | 16.29 | 16.575 | 16.8111 | 24.5 | 1.6386
CARRINGTON | CARRINGTON BSP | Sheet 1 | 132 | 31.86 | 0.9985 | 37.8792 | 38.8066 | 39.1799 | 47.1343 | 55.0822 | 69 | 6.7437
ROCHDALE | CASTLETON | Sheet 1 | 132 | 49.89 | 0.9951 | 51.7727 | 57.9744 | 64.4658 | 75.704 | 78.7776 | 117 | 0.4222
WHITEGATE | CHADDERTON | Sheet 1 | 132 | 81.88 | 0.99424 | 91.6254 | 94.211 | 96.6573 | 98.6767 | 100.5481 | 117 | 4.645
STALYBRIDGE | DROYLSDEN | Sheet 1 | 132 | 68.77 | 0.9939 | 76.1415 | 77.835 | 79.5877 | 81.4276 | 83.4196 | 117 | 0.0062
HARKER | EGREMONT | Sheet 3 | 132 | 34.07 | 0.96477 | 39.0773 | 40.582 | 41.666 | 51.5084 | 61.2766 | 117 | 0.59166
KEARSLEY | FREDERICK RD | Sheet 1 | 132 | 108.51 | 0.99707 | 123.3786 | 128.5634 | 133.5573 | 144.1795 | 154.469 | 138 | 0
BOLD | GOLBORNE | Sheet 2 | 132 | 65.28 | 0.9969 | 74.501 | 77.0632 | 79.4136 | 81.7306 | 83.8977 | 117 | 7.66
WHITEGATE | GREENHILL | Sheet 1 | 132 | 69.1 | 0.97665 | 74.5366 | 76.9437 | 79.8154 | 82.3939 | 83.9258 | 117 | 0
STALYBRIDGE | HARTSHEAD-HEYROD | Sheet 1 | 132 | 86.76 | 0.99344 | 91.7701 | 94.0724 | 96.7195 | 98.8553 | 100.8436 | 118 | 1.2691
BREDBURY | HAZEL GROVE | Sheet 1 | 132 | 63.1 | 0.97844 | 68.8235 | 70.4562 | 73.6108 | 76.4956 | 77.591 | 117 | 0.003
PADIHAM | HUNCOAT | Sheet 2 | 132 | 60.7 | 0.9891 | 64.5908 | 66.5121 | 68.8557 | 70.8944 | 72.7417 | 117 | 7.4241
STALYBRIDGE | HYDE | Sheet 1 | 132 | 56.18 | 0.91852 | 59.7646 | 62.1223 | 64.9463 | 67.3737 | 69.6514 | 117 | 7.7062
HUTTON | KENDAL (PARKSIDE RD) | Sheet 3 | 132 | 89.94 | 0.9873 | 93.4676 | 96.5233 | 99.415 | 101.9265 | 106.88 | 117 | 3.1557
HEYSHAM | LANCASTER | Sheet 3 | 132 | 105.53 | 0.96237 | 111.2388 | 116.2572 | 124.0241 | 129.6839 | 135.1286 | 135 | 4.4251
PENWORTHAM WEST | LEYLAND | Sheet 2 | 132 | 77.61 | 0.95198 | 88.1575 | 92.3224 | 96.5621 | 102.0828 | 107.4856 | 117 | 1.6919
BREDBURY | LONGSIGHT | Sheet 1 | 132 | 74.38 | 0.99753 | 83.4575 | 91.4615 | 99.6372 | 108.7512 | 118.4216 | 117 | 0.0028
ROCHDALE | LOWER DARWEN | Sheet 2 | 132 | 76.79 | 0.99429 | 84.6833 | 87.2331 | 89.3458 | 91.0955 | 92.6916 | 85 | 6.7772
PENWORTHAM WEST | LYTHAM | Sheet 2 | 132 | 30.98 | 1 | 35.239 | 36.5158 | 37.4475 | 38.2649 | 39.0293 | 78 | 0.0044
SOUTH MANCHESTER | MOSS NOOK | Sheet 1 | 132 | 88.48 | 0.95498 | 96.2966 | 98.5124 | 100.5336 | 102.2715 | 103.8508 | 146 | 0.19368
SOUTH MANCHESTER | MOSS NOOK PRIMARY | Sheet 1 | 132 | 12.73 | 0.9453 | 14.5126 | 14.9791 | 15.3987 | 15.741 | 16.0335 | 32 | 0.414
PADIHAM | NELSON | Sheet 2 | 132 | 54.39 | 0.99064 | 58.4882 | 59.9618 | 61.3662 | 62.5925 | 63.7271 | 68.5872 | 0.14451
STALYBRIDGE | NEW MILLS | Sheet 1 | 132 | 26.68 | 0.9488 | 28.3398 | 29.0431 | 29.992 | 30.6656 | 31.4472 | 58.5 | 0.2817
WASHWAY FARM / KIRKBY | ORRELL | Sheet 2 | 132 | 49.31 | 0.99596 | 50.5699 | 51.9579 | 53.4819 | 54.6877 | 55.698 | 78 | 1.9234
PADIHAM | PADIHAM | Sheet 2 | 132 | 71.62 | 0.98312 | 76.0082 | 78.3083 | 81.7484 | 83.6687 | 85.3304 | 103.5 | 0.12312
PENWORTHAM WEST | PEEL | Sheet 2 | 132 | 39.73 | 0.92887 | 44.4894 | 46.1573 | 47.3779 | 48.3887 | 49.2829 | 58.5 | 3.0215
HARKER | PENRITH & SHAP | Sheet 3 | 132 | 61.96 | 0.98957 | 67.5087 | 69.8508 | 71.7389 | 73.286 | 74.7233 | 118.2 | 0.64149 | Penrith & Shap run in parallel on the 33kV system.
PENWORTHAM EAST | PRESTON EAST | Sheet 2 | 132 | 66.4 | 0.9958 | 72.6223 | 76.0294 | 78.366 | 83.6731 | 97.8257 | 117 | 1.4192
KEARSLEY | RADCLIFFE | Sheet 2 | 132 | 28.15 | 0.9564 | 31.0884 | 32.0813 | 32.9858 | 33.7579 | 34.4612 | 38 | 0.0033
WHITEGATE | RED BANK | Sheet 1 | 132 | 64.88 | 0.98089 | 75.8717 | 80.2646 | 85.2124 | 90.1273 | 91.8004 | 117 | 0.024236
PENWORTHAM EAST | RIBBLE | Sheet 2 | 132 | 126.01 | 0.96572 | 143.4907 | 149.6723 | 154.1381 | 160.569 | 168.1728 | 234 | 0.83782
FIDLERS FERRY | RISLEY | Sheet 2 | 132 | 15.04 | 0.99045 | 17.0062 | 17.495 | 17.896 | 18.2187 | 18.4909 | 19.3 | 1.2947
ROCHDALE | ROCHDALE CENTRAL | Sheet 1 | 132 | 30.95 | 0.99499 | 32.6983 | 33.3569 | 34.2468 | 35.0181 | 35.7399 | 78 | 0.1002
PADIHAM | ROSSENDALE | Sheet 2 | 132 | 59.32 | 0.92061 | 62.1037 | 63.442 | 65.0013 | 66.281 | 67.406 | 117 | 1.405
WHITEGATE | ROYTON | Sheet 1 | 132 | 33.3 | 0.9488 | 35.9172 | 36.7577 | 37.6735 | 38.4453 | 39.1519 | 68.5872 | 3.4
CARRINGTON | SALE | Sheet 1 | 132 | 46.97 | 0.95069 | 53.476 | 55.1243 | 56.9408 | 58.5657 | 60.1022 | 78 | 0.14138
WASHWAY FARM | SKELMERSDALE | Sheet 2 | 132 | 57.63 | 0.91901 | 61.0048 | 62.2871 | 63.6781 | 65.0545 | 66.0236 | 117 | 9.0389
HARKER | SPADEADAM 11/33kV | Sheet 3 | 33 | 4.64 | 0.94738 | 4.6464 | 4.7496 | 4.8842 | 4.9943 | 5.0855 | 9.5 | 0
HARKER | SPADEADAM 132/11kV | Sheet 3 | 132 | 10.66 | 0.95566 | 11.0893 | 11.3041 | 11.4989 | 11.6221 | 11.6966 | 38 | 0
HARKER | STAINBURN & SIDDICK | Sheet 3 | 132 | 112.64 | 0.987 | 116.0167 | 118.758 | 122.0129 | 124.5742 | 126.8377 | 131.9 | 15.8295 | Stainburn & Siddick run in parallel on the 33kV system. Estimated demand.
SOUTH MANCHESTER | STRETFORD | Sheet 1 | 132 | 63.98 | 0.94424 | 64.5461 | 65.9566 | 68.2571 | 69.6183 | 71.0176 | 103.5 | 3.661
STALYBRIDGE | STUART ST | Sheet 1 | 132 | 70.49 | 0.93922 | 83.0766 | 96.1245 | 113.0313 | 131.5947 | 150.029 | 207 | 0.017103
STANAH | THORNTON | Sheet 2 | 132 | 53.95 | 0.966 | 58.6284 | 60.3957 | 61.956 | 63.4062 | 64.7398 | 75 | 5.0424
HEYSHAM | TRIMPELL | Sheet 3 | 132 | 4.7 | 0.9488 | 5.4221 | 5.6539 | 5.7782 | 5.8682 | 5.9417 | 23.815 | 0.88
HUTTON | ULVERSTON | Sheet 3 | 132 | 40.97 | 0.9964 | 45.1989 | 46.76 | 48.0879 | 49.2587 | 50.3619 | 117 | 3.9439
BREDBURY | VERNON PARK | Sheet 1 | 132 | 74.54 | 0.99326 | 84.0847 | 86.851 | 89.4794 | 91.8454 | 94.1172 | 117 | 1.0892
SOUTH MANCHESTER | WEST DIDSBURY | Sheet 1 | 132 | 90.17 | 0.98528 | 98.1316 | 100.6497 | 103.6894 | 106.3 | 108.7581 | 124 | 0.6191
KEARSLEY | WESTHOUGHTON | Sheet 2 | 132 | 56.35 | 0.9488 | 62.2627 | 63.957 | 65.5765 | 69.1891 | 72.7414 | 117 | 1.6994
WASHWAY FARM / KIRKBY | WIGAN | Sheet 2 | 132 | 55.26 | 0.99441 | 62.3403 | 64.7572 | 66.9634 | 70.193 | 73.3738 | 72 | 1.088
PENWORTHAM WEST | WRIGHTINGTON | Sheet 2 | 132 | 87.98 | 0.98105 | 99.2898 | 103.28 | 106.6727 | 109.6884 | 112.5354 | 117 | 2.4613
The information contained in this statement is provided for the sole purpose of allowing existing and potential and opportunities for changes in their use of the network or for connecting to it customers to assess the capabilities of the electricity network. While all reasonable effort has been made to ensure the accuracy of the information, Electricity North West Limited will accept no liability for any loss or damage caused by the information not being accurate. Actual changes in supply capacity for existing customers or new connections are subject to detailed assessment and approval by Electricity North West Limited, and payment of appropriate charges. The information contained in this statement is the Copyright of Electricity North West Limited, All Rights Reserved.