## Table 3 - System Loads_HV
TABLE 3 - LOAD INFORMATION
(1) Group Maximum Demand increased by measured distribution generation to provide true system demand.
Substations |  | Voltage Level | Transformer flows at group maximum demand - previous year (2022/2023) |  |  | Forecast Load Information |  |  |  |  | Group Firm Capacity | Minimum load scaling factor | Comments
[6 empty] | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028
S/S Group | S/S Name | kV | MW | MVAr | MVA(1) | MVA | MVA | MVA | MVA | MVA | MVA | %
BR BROMBOROUGH | BR BROMBOROUGH | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
BXL BROMBOROUGH T1 / TULIP T1 | BXL BROMBOROUGH T1 | 11 | 3.2126 | 0.23142 | 6.612 | 6.5274 | 6.5245 | 6.8654 | 7.0648 | 7.3813 | 10 | 39%
| TULIP T1 |  | 3.3789 | 0.28856
CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | CEREAL PARTNERS T1 | 11 | 0 | 0 | 9.1912 | 9.0146 | 8.9823 | 9.3069 | 9.4868 | 9.81 | 30 | 39% | CEREAL PARTNERS T1 not operating at time of group peak demand
| LEVER GEORGIA AVE T1 |  | 2.9856 | 1.0853
| POOL LA T1 |  | 2.9709 | 0.81815
| UML LEVER BROMBOROUGH T2 |  | 2.9764 | 0.26086
DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | DIBBINSDALE T1 | 11 | 3.6429 | -0.28974 | 10.9866 | 10.8774 | 11.0212 | 11.7712 | 12.4646 | 13.3855 | 20 | 39%
| PLYMYARD T1 |  | 3.6263 | 0.40107
| WIBP HARDKNOTT RD T1 |  | 3.7137 | -0.39526
LEVER SUNLIGHT T1 / LEVER SUNLIGHT T2 | LEVER SUNLIGHT T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| LEVER SUNLIGHT T2 |  | - | -
LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | LOWER BEBINGTON T1 | 11 | 3.6791 | 0.38941 | 14.4803 | 14.2805 | 14.6565 | 15.9901 | 17.301 | 19.0231 | 30 | 39%
| NEW FERRY T1 |  | 3.4446 | -0.57415
| SPITAL T1 |  | 3.755 | 0.5792
| UNILEVER RESEARCH T1 |  | 3.4035 | -0.63795
NWWA BROMBOROUGH T1 / NWWA BROMBOROUGH T2 | NWWA BROMBOROUGH T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| NWWA BROMBOROUGH T2 |  | - | -
ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | ARROWE PK HOSP T1 | 11 | 2.5355 | -0.058709 | 9.89 | 9.1101 | 9.1106 | 9.4874 | 9.7229 | 10.0816 | 30 | 39%
| CHAMPION PLUGS T1 |  | 2.3959 | -0.3672
| CHAMPION PLUGS T2 |  | 2.4785 | 0.5897
| WOODCHURCH T1 |  | 2.4793 | -0.03644
BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | BARNSTON T1 | 11 | 4.358 | -0.19346 | 17.4854 | 17.1164 | 17.4193 | 18.9705 | 20.5944 | 22.6926 | 30 | 39%
| GAYTON T1 |  | 5.1255 | 0.93036
| IRBY T1 |  | 3.7033 | -1.4301
| THINGWALL T1 |  | 4.2733 | -0.24575
CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | CALDY T1 | 11 | 4.516 | -0.74377 | 15.037 | 14.6455 | 14.8107 | 16.107 | 17.2557 | 18.86 | 30 | 39% | Meols T1 not operating at time of group peak
| HOYLAKE T1 |  | 5.58 | 0.388
| MEOLS T1 |  | 0 | 0
| WEST KIRBY SOUTH T1 |  | 4.9225 | -0.38967
BUILDWAS RD T1 / MORGAN REFRACTORIES T1 / NESTON MAIN T1 | BUILDWAS RD T1 | 11 | 2.701 | -0.85572 | 8.6482 | 8.6301 | 8.844 | 9.7109 | 10.65 | 11.8209 | 20 | 39%
| MORGAN REFRACTORIES T1 |  | 2.9274 | 0.21248
| NESTON MAIN T1 |  | 3.003 | 0.10517
GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | GREASBY T1 | 11 | 3.946 | -1.7151 | 12.5055 | 12.0704 | 12.1889 | 12.9988 | 13.789 | 14.8654 | 20 | 39%
| SAUGHALL MASSIE T1 |  | 2.2143 | no good data
| UPTON T1 |  | 6.3444 | 1.862
BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST (BIRKENHEAD) T1 | BENTINCK ST T1 | 6.6 | 0 | 0 | 7.7773 | 7.8105 | 7.9447 | 8.5434 | 9.0839 | 9.7471 | 18.2 | 39% | Bentink ST T1 on Open Standby
| BENTINCK ST T2 |  | 4.3399 | 1.0771
| CHESTER ST T1 |  | 3.4334 | -0.82525
BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | BIRKENHEAD CENTRAL T1 | 6.6 | 3.616 | 2.176 | 8.4631 | 8.3221 | 8.3726 | 8.8238 | 9.3617 | 9.8549 | 18.2 | 39%
| SINGLETON AVE T1 |  | 1.677 | -1.14
| TRANMERE T1 |  | 3.1677 | -0.83766
BR SHORE ROAD | BR SHORE ROAD T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| BR SHORE ROAD T2 |  | - | -
CAMMELL LAIRD NORTH -CAMMELL LAIRD SOUTH T1 T2 | CAMMELL LAIRD NORTH | 6.6 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| CAMMELL LAIRD SOUTH T1 |  | - | -
| CAMMELL LAIRD SOUTH T2 |  | - | -
EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | EGERTON T1 | 11 | 4.5552 | 0.13139 | 14.1063 | 13.7887 | 13.8524 | 14.5415 | 15.0519 | 15.7722 | 20 | 39%
| ROCK FERRY T1 |  | 4.7183 | 0.3325
| SHELL TRANMERE T1 |  | 4.7289 | 1.2444
FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | FORD T1 | 11 | 3.7134 | -1.7677 | 17.6177 | 16.5216 | 16.737 | 17.8517 | 19.1883 | 21.061 | 30 | 39%
| OXTON T1 |  | 5.3718 | 1.5551
| PRENTON LOCAL T1 |  | 4.84 | -0.5287
| SINGLETON AVE T2 |  | 3.675 | -0.04191
MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | MDHB EGERTON DOCK T1 | 6.6 | 2.5642 | 0.54763 | 5.4405 | 5.0511 | 5.1335 | 5.6973 | 6.2935 | 7.065 | 9.1 | 39%
| MDHB EGERTON DOCK T2 |  | 2.7639 | 0.55252
NWW WOODSIDE T1 / NWW WOODSIDE T2 | NWW WOODSIDE T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| NWW WOODSIDE T2 |  | - | -
CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | CADBURYS T1 | 11 | 3.675 | -0.04815 | 11.0228 | 10.6273 | 10.6122 | 11.0417 | 11.2871 | 11.7097 | 20 | 39%
| CADBURYS T2 |  | 3.537 | -0.0651
| HOPFIELD RD T1 |  | 3.7999 | 0.60175
EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | EGREMONT T1 | 11 | 4.2144 | -0.147 | 16.3766 | 15.5844 | 15.4202 | 15.8038 | 15.989 | 16.4144 | 30 | 39%
| LISCARD T1 |  | 3.885 | -0.1092
| POULTON T1 |  | 4.2146 | -0.374
| STONE MANGANESE T1 |  | 4.06 | 0.3352
GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | GILBROOK DOCK T1 | 6.6 | 4.7309 | 1.531 | 8.5324 | 7.9631 | 7.893 | 8.1965 | 8.4392 | 8.8274 | 18.2 | 39% | HILL RD T1 not operating at time of group peak demand
| HILL RD T1 |  | -0.00026068 | 0.0002546
| MOBIL OIL (WALLASEY) T1 |  | 3.7338 | -0.45759
NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | NEW BRIGHTON T1 | 11 | 3.9061 | 0.68127 | 14.2625 | 13.2345 | 13.2208 | 14.0376 | 14.7781 | 15.8439 | 30 | 39%
| SEAVIEW RD T2 |  | 3.6895 | 0.52623
| WALLASEY VILLAGE T1 |  | 3.4821 | -0.25058
| WALLASEY T1 |  | 3.1821 | -1.2359
BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY MAIN T1 | BOWATER CONTAINERS T1 | 11 | 3.1283 | -0.533 | 18.225 | 17.7566 | 17.8078 | 18.7159 | 19.3039 | 20.2294 | 25.5 | 39%
| ELLESMERE PORT LOCAL T1 |  | 4.0892 | 1.0643
| HH ROBERTSONS T1 |  | 3.8435 | 0.45643
| MOBIL OIL (E PORT) T1 |  | 3.2336 | No good data
| WHITBY T1 |  | 3.8257 | 0.96318
CHESTER GATES T1 / UNILEVER DUNKIRK T1 | CHESTER GATES T1 | 11 | 2.7736 | 0.373 | 5.6646 | 5.5709 | 5.5631 | 5.8166 | 5.9778 | 6.2423 | 10 | 39%
| UNILEVER DUNKIRK T1 |  | 2.8908 | -0.4213
GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | GREAT SUTTON T1 | 11 | 0 | 0 | 22.5397 | 21.397 | 21.4748 | 22.6856 | 23.8635 | 25.5627 | 26.42 | 39% | GREAT SUTTON T1 not operating at time of group peak demand
| LITTLE SUTTON T1 |  | 6.1319 | 0.34572
| STRAWBERRY ROUNDABOUT T1 |  | 5.976 | 1.0059
| SUTTON HALL WWB T1 |  | 5.0742 | -1.1342
| WHITBY T2 |  | 5.3575 | -0.14937
HOOTON MAIN T1 | HOOTON MAIN T1 | 11 | 4.5193 | 0.028601 | 4.5194 | 4.5754 | 4.685 | 5.1724 | 5.6441 | 6.2329 | 7.5 | 39%
MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | MORGANITE CERAMICS T1 | 11 | 1.6275 | -0.32075 | 6.7571 | 6.7391 | 6.8828 | 7.4881 | 8.0912 | 8.8834 | 15 | 39% | Previously two separate groups MORGANITE CERAMICS T1 / PLYMYARD T2 and VAUXHALL NORTH RD T1
| PLYMYARD T2 |  | 1.6054 | 0.49215
| VAUXHALL NORTH RD T1 |  | 1.2735 | 0.35704
ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | ASSOCIATED LEAD T1 | 11 | 4.1124 | -0.20495 | 12.2591 | 11.9179 | 12.1954 | 13.2445 | 14.4203 | 15.9421 | 20 | 39%
| GREAT BOUGHTON T1 |  | 4.0066 | -0.068573
| PIPERS ASH T1 |  | 4.1352 | -0.06982
BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | BLACON T1 | 11 | 2.8177 | -0.076495 | 20.8541 | 20.2225 | 20.2688 | 21.2383 | 22.0483 | 23.2859 | 37.5 | 39%
| COCOA BARRY T1 |  | 4.2701 | -0.11095
| CRANE BANK T1 |  | 4.4557 | -0.218
| KNUTSFORD WAY T1 |  | 4.568 | -0.0089715
| TOWER WHARF T1 |  | 4.74 | 0.7402
BODFARI PRODUCERS T1 | BODFARI PRODUCERS T1 | 11 | 2.4051 | 0.52966 | 2.8251 | 2.7529 | 2.7379 | 2.8226 | 2.8594 | 2.9428 | 7.5 | 39%
BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | BROOK LA T1 | 11 | 4.4118 | -0.2627 | 17.508 | 16.7865 | 16.9349 | 17.9018 | 18.8028 | 20.1173 | 30 | 39%
| MANNINGS LA T1 |  | 4.49 | -0.29725
| NEWTOWN CHESTER T1 |  | 4.2822 | -0.355
| UPTON HEATH T1 |  | 4.3223 | 0.6752
CHESTER WTW T1 - CHESTER WTW T2 | CHESTER WTW T1 | 6.6 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| CHESTER WTW T2 |  | - | -
DUDDON T1 | DUDDON T1 | 11 | 2.1437 | 0.20174 | 2.1532 | 2.1044 | 2.1148 | 2.2628 | 2.3898 | 2.556 | 7.5 | 39%
GOWY LANDFILL GEN T1 | GOWY LANDFILL GEN | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | GROSVENOR ST T1 | 11 | 4.5576 | 0.75283 | 21.4226 | 20.2496 | 20.0983 | 20.7416 | 21.0474 | 21.7537 | 30 | 39%
| LINENHALL ST T1 |  | 4.1464 | 1.4402
| NORTHGATE TERRACE T1 |  | 4.2809 | -1.187
| STATION VIEW T1 |  | 4.2172 | -1.4266
| TOMULAR PLACE T1 |  | 4.2191 | 0.65296
HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | HERONS WAY T1 | 11 | 2.2455 | -0.43009 | 10.5802 | 10.2376 | 10.265 | 10.8315 | 11.3358 | 12.08 | 30 | 39%
| LACHE T1 |  | 3.485 | 1.472
| MBNA T1 |  | 2.5554 | 0.46545
| SMFS KINGSMEADOW T1 |  | 2.2865 | -1.9139
SALTNEY GRID T1 | SALTNEY T1 | 11 | 2.484 | 0.35098 | 2.5086 | 2.5148 | 2.5493 | 2.7034 | 2.8504 | 3.039 | 7.5 | 39%
LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | LCWW HUNTINGTON T1 | 6.6 | 0 | 0 | 4.461 | 4.3469 | 4.3504 | 4.5556 | 4.7025 | 4.9338 | 9.1 | 39% | LCWW HUNTINGTON T1 not operating at time of group peak demand
| LCWW HUNTINGTON T2 |  | 4.4246 | 0.56906
TARVIN T1 | TARVIN T1 | 11 | 5.8561 | -0.14944 | 5.858 | 5.6648 | 5.7076 | 6.0928 | 6.5017 | 7.0269 | 7.5 | 39%
WERVIN T1 | WERVIN T1 | 11 | 3.1494 | 0.146 | 3.1528 | 3.1744 | 3.2716 | 3.5691 | 3.9287 | 4.3435 | 7.5 | 39%
BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | BARBAULD ST T1 | 11 | 2.7955 | -0.96399 | 8.6409 | 8.5882 | 8.657 | 9.0905 | 9.4506 | 9.9224 | 20 | 39%
| HORROCKS LA T1 |  | 2.7419 | 0.16275
| WARRINGTON CENTRAL T1 |  | 3.1012 | 1.0011
BATTERSBY LA T1 / RYLANDS ELDON ST T2 | BATTERSBY LA T1 | 6.3 | 0.48037 | -0.057817 | 0.97158 | 0.9313 | 0.95607 | 1.0135 | 1.0516 | 1.0918 | 9.1 | 39%
| RYLANDS ELDON ST T2 |  | 0.48664 | -0.036317
BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | BEWSEY T1 | 11 | 4.1344 | -0.90169 | 15.8651 | 15.5186 | 15.5413 | 16.2836 | 16.8677 | 17.6973 | 30 | 39%
| OWEN ST T1 |  | 4.5377 | 0.92757
| RODNEY ST T1 |  | 3.6066 | 0.70027
| RYLANDS ELDON ST T1 |  | 3.4788 | -0.15247
BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | BOULEVARD T1 | 11 | 4.1542 | 0.35121 | 20.7909 | 20.2535 | 20.2809 | 21.2746 | 22.0639 | 23.2372 | 37.5 | 39%
| CHAPELFORD T1 |  | 3.6309 | -1.0288
| HAWLEYS LA T1 |  | 4.5153 | 0.31936
| WESTBROOK T1 |  | 4.2635 | -0.59453
| WINWICK QUAY T1 |  | 4.1901 | -0.28505
BRITISH ALUMINIUM LATCHFORD T1 / GREENHALL WHITLEY T1 / LATCHFORD T1 / LATCHFORD T2 / THAMES BOARD MILL T1 | BRITISH ALUMINIUM LATCHFORD T1 | 11 | 3.0364 | -0.12291 | 17.8012 | 17.1104 | 17.022 | 17.6472 | 18.0367 | 18.6961 | 30 | 39%
| GREENHALL WHITLEY T1 |  | 3.1411 | 3.1411
| LATCHFORD T1 |  | 3.1518 | 3.1518
| LATCHFORD T2 |  | 2.9471 | -0.22146
| THAMES BOARD MILL T1 |  | 2.9882 | 2.9882
CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | CROSSFIELDS T1 | 11 | 2.323 | 1.2033 | 8.2153 | 7.8622 | 7.7911 | 7.9984 | 8.1028 | 8.3291 | 30 | 39%
| CROSSFIELDS T2 |  | 2.3476 | 1.2902
| CROSSFIELDS T3 |  | 1.2587 | -0.72381
| GATEWARTH SEWAGE T1 |  | 2.0065 | 0.35502
GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | GIGG LA THELWALL T1 | 11 | 4.9875 | 0.16851 | 19.3446 | 18.5825 | 18.6327 | 19.6585 | 20.5591 | 21.8618 | 30 | 39%
| HILLCLIFFE T1 |  | 4.976 | 0.26263
| STOCKTON HEATH T1 |  | 5.0675 | -0.66958
| STRETTON IND EST T1 |  | 4.2704 | -1.0524
GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | GREAT SANKEY T1 | 11 | 3.5831 | 0.19935 | 10.6029 | 10.4466 | 10.6195 | 11.5125 | 12.4154 | 13.5958 | 20 | 39%
| PENKETH T1 |  | 3.7722 | 0.88416
| WIDNES RD T1 |  | 3.2284 | -1.7184
KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | KINGSLAND 33 T1 | 11 | 4.0018 | 0.27889 | 16.8719 | 15.7049 | 15.5107 | 15.8529 | 16.0853 | 16.5911 | 30 | 39%
| SAFEWAY T1 |  | 4.1622 | 0.29918
| WOOLSTON T1 |  | 4.1711 | 1.0111
| WOOLSTON T2 |  | 4.0245 | 0.028456
LYMM T1 / WHITELEGGS LA T1 | LYMM T1 | 11 | 4.5878 | 0.038338 | 8.8742 | 8.6297 | 8.776 | 9.4492 | 10.2326 | 11.2368 | 10 | 39%
| WHITELEGGS LA T1 |  | 4.2852 | -0.1828
NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | NORTH WEST WATER CAMPUS T1 | 11 | 4.0611 | 0.38812 | 14.8158 | 14.0391 | 13.9045 | 14.2382 | 14.3923 | 14.7594 | 40 | 39% | NORTH WEST WATER CAMPUS T2 not operating at time of group peak demand
| NORTH WEST WATER CAMPUS T2 |  | 0 | 0
| OMEGA T1 |  | 3.6045 | -0.035929
| OMEGA T2 |  | 3.4686 | -0.037608
| ORION BOULEVARD T1 |  | 3.6741 | 0.15863
ORFORD T1 / PADGATE T1 | ORFORD T1 | 11 | 4.5319 | 0.25212 | 8.7672 | 9.1099 | 10.0664 | 11.6696 | 12.9508 | 14.627 | 10 | 39% | Proposed reinforcement to install an auto close between adjacent HV groups
| PADGATE T1 |  | 4.2295 | -0.5713
SOLVAY INTEROX T1 / SOLVAY INTEROX T2 / SOLVAY INTEROX T3 | SOLVAY INTEROX T1 | 6.3 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| SOLVAY INTEROX T2 |  | - | -
| SOLVAY INTEROX T3 |  | - | -
CLEDFORD T1 | CLEDFORD T1 | 11 | 5.9328 | 0.5415 | 5.9574 | 5.6123 | 5.5815 | 5.8036 | 6.0061 | 6.3147 | 7.5 | 39%
FISONS T1 | FISONS T1 | 11 | 2.7102 | 0.12477 | 2.7131 | 2.6752 | 2.6785 | 2.824 | 2.916 | 3.0526 | 7.5 | 39%
HOLMES CHAPEL T1 | HOLMES CHAPEL T1 | 11 | 5.614 | 0.024767 | 5.6918 | 5.6443 | 5.7123 | 6.1483 | 6.5509 | 7.0835 | 7.5 | 39%
ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | ILFORDS T1 | 11 | 3.7169 | 0.011891 | 14.4224 | 14.1038 | 14.1806 | 14.886 | 15.5908 | 16.5237 | 30 | 39%
| KNUTSFORD T1 |  | 4.2022 | 1.4848
| MOBBERLEY T1 |  | 3.4075 | 0.034588
| RADBROKE HALL T1 |  | 3.0949 | -1.692
KNUTSFORD T2 | KNUTSFORD T2 | 11 | 5.447 | 0.038425 | 5.4471 | 5.3736 | 5.4123 | 5.6804 | 5.9414 | 6.2829 | 7.5 | 39%
LOSTOCK T1 | LOSTOCK T1 | 11 | 4.2628 | -0.11198 | 4.2643 | 4.2058 | 4.2923 | 4.6162 | 4.9742 | 5.4071 | 7.5 | 39%
LOSTOCK TRIANGLE T1 | LOSTOCK TRIANGLE T1 | 11 | 3.6545 | 0.085596 | 3.6555 | 2.8614 | 2.9317 | 3.108 | 3.3467 | 3.6085 | 7.5 | 39%
MERE T1 | MERE T1 | 11 | 4.6368 | 0.10722 | 4.638 | 4.71 | 4.8816 | 5.5375 | 6.2396 | 7.0827 | 7.5 | 39%
MIDDLEWICH T1 | MIDDLEWICH T1 | 11 | 4.5415 | No good data | 4.638 | 4.5999 | 4.6815 | 5.094 | 5.4625 | 5.9715 | 7.5 | 39%
MIDPOINT POCHIN WAY T1 | MIDPOINT POCHIN WAY T1 | 11 | 1.6908 | 0.080474 | 1.6927 | 1.6559 | 1.6604 | 1.7224 | 1.7591 | 1.8273 | 7.5 | 39%
MORRISONS T1 | MORRISONS T1 | 11 | 5.2071 | 1.0273 | 5.3075 | 5.2085 | 5.2199 | 5.4718 | 5.6767 | 5.9652 | 7.5 | 39%
PRIMROSE HALL T1 | PRIMROSE HALL T1 | 11 | 2.624 | No good data | 2.624 | 2.5796 | 2.5866 | 2.739 | 2.8635 | 3.0393 | 7.5 | 39%
RHM FOODS LTD T1 | RHM FOODS LTD T1 | 11 | 1.2079 | 0.26018 | 1.2356 | 1.216 | 1.2119 | 1.2601 | 1.2815 | 1.3215 | 7.5 | 39%
RINGWAY T1 / RINGWAY T2 | RINGWAY T1 | 11 | 2.731 | -0.1232 | 2.7916 | 2.6977 | 2.7405 | 2.9578 | 3.2522 | 3.5946 | 2.8 | 39% | Work ongoing in year to commission T2, causing issues with tags. Unclear when group peak demand was or what transformer flows are.
| RINGWAY T2 |  | - | -
ANDERTON T1 | ANDERTON T1 | 11 | 5.119 | 0.204 | 2.6068 | 3.8652 | 4.0474 | 4.5587 | 5.1796 | 5.9133 | 7.5 | 39%
CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | CASTLE BEESTON ST T1 | 11 | 4.3796 | 0.089138 | 20.1254 | 19.3952 | 19.3545 | 20.4188 | 21.2278 | 22.4283 | 37.5 | 39%
| HARTFORD T2 |  | 4.082 | -0.17021
| LEICESTER ST T1 |  | 3.6031 | -0.82696
| NORTHWICH TOWN T1 |  | 3.452 | -0.6622
| WINNINGTON T1 |  | 4.5709 | 0.338
CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | CHURCH ST WINSFORD T1 | 11 | 4.4617 | 0.33714 | 17.8256 | 17.2229 | 17.2939 | 18.3678 | 19.37 | 20.7886 | 30 | 39%
| OVER T1 |  | 4.8492 | 1.0425
| WHARTON PK T1 |  | 4.4598 | 0.18379
| WOODFORD PK T1 |  | 4.0348 | -0.71786
EDEN VALE T1 | EDEN VALE T1 | 11 | 4.3793 | -0.11619 | 4.3808 | 4.2132 | 4.2181 | 4.431 | 4.6414 | 4.9282 | 7.5 | 39%
GADBROOK T1 | GADBROOK T1 | 11 | 3.7497 | -0.15819 | 3.753 | 3.6474 | 3.6834 | 3.9339 | 4.1744 | 4.4729 | 7.5 | 39%
GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | GRAVEL T1 | 11 | 1.9829 | 0.073619 | 6.4041 | 6.2687 | 6.276 | 6.5325 | 6.7421 | 7.0522 | 20 | 39%
| WCB PLASTICS T1 |  | 2.0699 | 0.7971
| WHARTON T1 |  | 2.2644 | -0.01489
HARTFORD T1 | HARTFORD T1 | 11 | 6.131 | -0.2059 | 6.1345 | 5.7902 | 5.8236 | 6.3078 | 6.803 | 7.4596 | 7.5 | 39%
TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | TACO PLASTICS T1 | 11 | 3.6674 | 3.1107 | 10.8699 | 10.7346 | 10.7574 | 11.4038 | 11.6863 | 12.2059 | 20 | 39%
| TACO PLASTICS T2 |  | 3.3233 | 0.08497
| UNITED PERIPHERALS T1 |  | 3.3988 | No good data
WINCHAM T1 | WINCHAM T1 | 11 | 2.3137 | 0.20206 | 2.3225 | 2.3041 | 2.3288 | 2.455 | 2.5737 | 2.7292 | 7.5 | 39%
ACER AVE T1 | ACER AVE T1 | 11 | 6.5652 | -0.25862 | 6.5703 | 6.8438 | 6.9622 | 7.4501 | 7.8945 | 8.5288 | 7.5 | 39%
ACTON T1 | ACTON T1 | 11 | 4.9479 | 0.62624 | 4.9885 | 4.8257 | 4.8479 | 5.0867 | 5.3115 | 5.6366 | 7.5 | 39%
AUDLEM T1 | AUDLEM T1 | 11 | 3.5585 | 0.13264 | 3.561 | 3.4667 | 3.5422 | 3.7802 | 4.0651 | 4.3991 | 7.5 | 39%
BAE RADWAY T1 / BAE RADWAY T2 | BAE RADWAY T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| BAE RADWAY T2 |  | - | -
CHURCH LAWTON T1 | CHURCH LAWTON T1 | 11 | 3.6867 | 0.07716 | 3.6875 | 3.569 | 3.6657 | 3.9996 | 4.2894 | 4.704 | 7.5 | 39%
CIVIC CENTRE T1 / CLAUGHTON AVE T1 / CHESTER ST CREWE T1/ CHESTER ST CREWE T2 | CIVIC CENTRE T1 | 11 | 4.6788 | -0.44964 | 14.4677 | 14.3076 | 14.7034 | 15.815 | 16.3724 | 17.2335 | 19.18 | 39% | Previously CIVIC CENTRE T1 / CLAUGHTON AVE T1 / ELECTRICITY ST T1. ELECTRICITY ST T1 decommissioned at time of group peak demand.
| CHESTER ST CREWE T1 |  | 0 | 0
| CHESTER ST CREWE T2 |  | 0 | 0
| CLAUGHTON AVE T1 |  | 4.7954 | 0.29361
| ELECTRICITY ST T1 |  | 4.9904 | 0.45708
BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | CREWE STATION T1 | 11 | 3.2587 | -0.083874 | 24.2674 | 23.8532 | 28.8612 | 30.058 | 30.8223 | 36.0508 | 37.5 | 39%
| DUCHY RD T1 |  | 5.2319 | 0.68881
| ELECTRA WAY T1 |  | 5.4329 | 0.88211
| MIDLAND ROLLMAKERS 1A |  | 4.9397 | 0.93802
| NORTH WESTERN MILLS T1 |  | 5.1759 | 0.89595
CREWE T1 | CREWE T1 | 11 | 4.9116 | 0.91755 | 5.0541 | 4.5399 | 10.4293 | 10.4265 | 10.4026 | 10.4555 | 7.5 | 39%
LEIGHTON HOSPITAL T1 | LEIGHTON HOSPITAL T1 | 11 | 3.4486 | -0.13455 | 3.4512 | 3.1959 | 3.1694 | 3.213 | 3.276 | 3.3607 | 7.5 | 39%
DUCKINGTON T1 / DUCKINGTON T2 | DUCKINGTON T1 | 11 | 4.3316 | -0.066476 | 4.8122 | 4.7478 | 4.8441 | 5.2487 | 5.6792 | 6.1958 | 9.75 | 39% | DUCKINGTON T2 on Open Standby
| DUCKINGTON T2 |  | 0.4801 | No good data
FODENS T1 | FODENS T1 | 11 | 4.8991 | -0.0913 | 4.9 | 4.8733 | 4.9333 | 5.3124 | 5.587 | 5.9723 | 7.5 | 39%
HATHERTON T1 | HATHERTON T1 | 11 | 1.6903 | 0.479 | 1.7568 | 2.1308 | 2.1555 | 2.2715 | 2.3579 | 2.4848 | 4 | 39%
MAW GREEN GEN T1 | MAW GREEN GEN T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
NANTWICH T1 | NANTWICH T1 | 11 | 5.5746 | 0.047959 | 5.5748 | 5.536 | 5.6794 | 6.1234 | 6.4788 | 6.9332 | 7.5 | 39%
NEWHALL T1 / NEWHALL T2 | NEWHALL T1 | 11 | 1.9421 | 0.71742 | 3.9246 | 3.8533 | 3.8522 | 4.0207 | 4.1263 | 4.2843 | 10 | 39%
| NEWHALL T2 |  | 1.8766 | 0.18845
CHESHIRE GREEN T1 / NWF T1 | CHESHIRE GREEN T1 | 11 | 2.6028 | 0.82142 | 5.5638 | 5.5076 | 5.5662 | 5.8983 | 6.1129 | 6.4343 | 10 | 39%
NWF T1 / CHESHIRE GREEN | NWF T1 | 11 | 2.8949 | 0.03364 | 5.5638 | 5.5076 | 5.5662 | 5.8983 | 6.1129 | 6.4343 | 10 | 0%
RADWAY GREEN T1 | RADWAY GREEN T1 | 11 | 6.0279 | -0.2324 | 6.0324 | 5.9066 | 5.9608 | 6.3618 | 6.7173 | 7.196 | 7.5 | 39%
ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | ROLLS ROYCE T1 | 11 | 5.402 | 1.116 | 11.6376 | 10.8496 | 10.7396 | 10.9449 | 11.0281 | 11.2623 | 15 | 39% | ROLLS ROYCE T2 not operating at time of group peak demand
| ROLLS ROYCE T2 |  | 0 | 0
| ROLLS ROYCE T3 |  | 5.56 | 0.1658
SANDBACH T1 | SANDBACH T1 | 11 | 7.4964 | 0.40659 | 7.5074 | 7.2446 | 7.263 | 7.6859 | 8.0418 | 8.5761 | 7.5 | 39%
SMALLWOOD T1 | SMALLWOOD T1 | 11 | 5.6067 | 0.44102 | 5.624 | 5.7375 | 6.0716 | 6.752 | 7.3632 | 8.1026 | 7.5 | 39%
SNOWHILL T1 | SNOWHILL T1 | 11 | 5.4638 | 0.15096 | 5.4659 | 5.3913 | 5.4841 | 5.8715 | 6.2393 | 6.7138 | 7.5 | 39%
STAPELEY T1 | STAPELEY T1 | 11 | 4.9399 | -0.1114 | 4.9412 | 4.9935 | 5.3296 | 5.9621 | 6.3006 | 6.7934 | 7.5 | 39%
TWYFORDS T1 | TWYFORDS T1 | 11 | 2.9867 | -0.232 | 2.9957 | 2.8608 | 2.8878 | 3.055 | 3.2079 | 3.435 | 7.5 | 39%
WESTON T1 | WESTON T1 | 11 | 6.9856 | -0.070716 | 6.986 | 6.8136 | 6.9049 | 7.3517 | 7.7916 | 8.3682 | 10 | 39%
WHEELOCK T1 | WHEELOCK T1 | 11 | 4.9721 | -0.14134 | 4.9741 | 4.8075 | 4.8622 | 5.2215 | 5.6005 | 6.0861 | 7.5 | 39%
WISTASTON HALL T1 | WISTASTON HALL T1 | 11 | 4.3761 | -0.26658 | 4.3842 | 4.112 | 4.0928 | 4.2945 | 4.458 | 4.6871 | 7.5 | 39%
WRENBURY FRITH T1 | WRENBURY FRITH T1 | 11 | 3.1979 | 0.38599 | 3.2211 | 3.1257 | 3.1426 | 3.2958 | 3.4402 | 3.6378 | 4 | 39%
BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | BROMFIELD T1 | 11 | 2.578 | -0.50189 | 15.071 | 14.6102 | 14.6884 | 15.7019 | 16.6009 | 17.8512 | 37.5 | 39%
| BROMFIELD T2 |  | 2.4402 | -0.47966
| PONTERWYL T1 |  | 2.7877 | -0.24354
| RHYD-Y-GOLEU T1 |  | 3.6809 | 1.079
| SYNTHITE T1 |  | 3.5549 | 1.0869
CEFN MAWR T1 | CEFN MAWR T1 | 11 | 3.4909 | -0.031801 | 3.4911 | 3.4723 | 3.6043 | 4.0291 | 4.5274 | 5.1149 | 7.5 | 39%
FLINT T1 / FLINT T2 | FLINT T1 | 11 | -0.3305 | -0.114 | 5.931 | 5.7378 | 5.7256 | 10.0212 | 10.2345 | 10.5591 | 10 | 39%
| FLINT T2 |  | -0.39908 | -0.981
NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | NORTH WALES PAPER T1 | 11 | 3.7966 | 0.018614 | 12.354 | 12.0412 | 12.0494 | 12.5766 | 12.9383 | 13.5165 | 20 | 39%
| NORTH WALES PAPER T2 |  | 3.8551 | 1.5465
| WOODFIELD AVE T1 |  | 4.2207 | 1.8502
GREENFIELD T1 / GREENFIELD T2 | GREENFIELD T1 | 11 | 3.1441 | 0.60018 | 5.9306 | 5.8914 | 5.9839 | 6.3905 | 6.7975 | 7.325 | 10 | 39%
| GREENFIELD T2 |  | 2.776 | -0.24724
HOLWAY RD T1 | HOLWAY RD T1 | 11 | 4.2036 | -0.08715 | 4.2045 | 4.1313 | 4.1755 | 4.4945 | 4.7626 | 5.1301 | 7.5 | 39%
WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | WIMPEYS PANT QUARRY T1 | 11 | 2.0467 | -0.25206 | 4.0487 | 3.8658 | 3.8852 | 4.077 | 4.2959 | 4.561 | 5.2 | 39%
| WIMPEYS PANT QUARRY T2 |  | 1.8771 | 1.25
AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | AIRBUS T1 | 11 | 1.7264 | 0.78955 | 7.013 | 6.8726 | 6.9054 | 7.2962 | 7.626 | 8.102 | 20 | 39%
| BROUGHTON RETAIL PARK T1 |  | 1.8975 | 0.90617
| MIXALLOY T1 |  | 0.99613 | -1.597
BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | BUCKLEY CROSS T1 | 11 | 3.987 | -0.44539 | 11.3013 | 10.9171 | 11.0134 | 11.8232 | 12.6074 | 13.6662 | 20 | 39%
| BUCKLEY T1 |  | 3.653 | -0.18678
| BUCKLEY T2 |  | 3.5209 | 0.65097
CAERGWRLE T1 | CAERGWRLE T1 | 11 | 5.4866 | 0.003975 | 5.4866 | 5.663 | 5.7481 | 6.2413 | 6.8468 | 7.6081 | 7.5 | 39%
CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | CONNAHS QUAY LOCAL T1 | 11 | 3.922 | -0.002366 | 16.6652 | 15.9605 | 16.0504 | 17.0525 | 18.0231 | 19.4088 | 30 | 39%
| CONNAHS QUAY LOCAL T2 |  | 3.995 | 0.02104
| HAWARDEN T1 |  | 4.5202 | -0.2442
| KING GEORGE ST T1 |  | 4.2104 | -0.5402
ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | ENGINEER PK T1 | 11 | 2.6184 | 0.5158 | 14.0666 | 13.7777 | 13.7663 | 14.3657 | 14.7427 | 15.3589 | 20 | 39%
| PILKINGTONS QUEENSFERRY T1 |  | 3.3865 | 1.8041
| QUEENSFERRY T1 |  | 3.3246 | 0.12181
KINNERTON T1 | KINNERTON T1 | 11 | 3.237 | 0.16028 | 3.241 | 3.3442 | 3.4636 | 3.7885 | 4.1774 | 4.6072 | 7.5 | 39%
DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | DEESIDE IND PK 6TH AVE T1 | 11 | 4.419 | 1.6288 | 12.5417 | 12.3322 | 12.3758 | 12.9178 | 13.3753 | 14.0241 | 20 | 39%
| DEESIDE IND PK T1 |  | 4.0543 | -0.25102
| RAF SEALAND T1 |  | 3.9057 | 0.63618
OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | OPTICAL FIBRES T1 | 11 | 4.1464 | 0.7072 | 12.5369 | 12.2994 | 12.2452 | 12.6697 | 12.8692 | 13.2393 | 20 | 39%
| SHOTWICK T1 |  | 3.9279 | 0.34457
| WALBRO T1 |  | 4.1259 | 1.5734
ABERGELE T1 / PENSARN T1 | ABERGELE T1 | 11 | 3.5684 | -0.5062 | 7.9635 | 7.8362 | 8.0178 | 8.7379 | 9.5831 | 10.6175 | 10 | 39%
| PENSARN T1 |  | 4.3121 | 0.3462
BRYN STANLEY T1 / DENBIGH T1 | BRYN STANLEY T1 | 11 | 2.8124 | 0.40767 | 5.6001 | 5.5008 | 5.5609 | 5.9737 | 6.3503 | 6.8676 | 10 | 39% | Previously two separate groups BRYN STANLEY T1 and DENBIGH T1
| DENBIGH T1 |  | 2.7062 | -0.35306
CHURCH LANE T1 / NANT HALL T1 / PRESTATYN T1 | CHURCH LA T1 | 11 | 3.3122 | 0.43506 | 9.3036 | 9.0427 | 9.18 | 9.9269 | 10.715 | 11.7571 | 20 | 39%
| NANT HALL T1 |  | 2.9485 | -0.23392
| PRESTATYN T1 |  | 3.0428 | -0.21187
DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | DYSERTH RD T1 | 11 | 2.5484 | -0.58021 | 18.7092 | 17.2417 | 17.0984 | 17.7352 | 18.367 | 19.4444 | 30 | 39%
| FFORDD LAS T1 |  | 5.1881 | -0.19884
| FFORDD LAS T2 |  | 5.5091 | 0.72137
| WESTBOURNE AVE T1 |  | 5.4634 | -0.020625
EGA ELECTRIC T1 | EGA ELECTRIC T1 | 11 | 2.7464 | -0.2481 | 3.4274 | 3.4047 | 3.4632 | 3.7356 | 3.9975 | 4.3237 | 7.5 | 39%
GRAIG FAWR T1 / GRAIG FAWR T2 | GRAIG FAWR T1 | 11 | 5.6826 | 0.02422 | 5.6827 | 5.7912 | 5.9926 | 6.586 | 7.259 | 8.0545 | 4.34 | 39% | Work ongoing in year to commission T2, causing issues with tags. Unclear when group peak demand was or what transformer flows are.
| GRAIG FAWR T2 |  | - | -
HOLYWELL T1 | HOLYWELL T1 | 11 | 4.0678 | 0.040272 | 4.068 | 4.0511 | 4.1471 | 4.5539 | 5.001 | 5.5391 | 7.5 | 39%
LLANARMON T1 | LLANARMON T1 | 11 | 1.5422 | 0.011276 | 1.5423 | 1.4917 | 1.5037 | 1.5828 | 1.6739 | 1.7849 | 7.5 | 39%
LLANDYRNOG T1 | LLANDYRNOG T1 | 11 | 3.0224 | 0.12003 | 3.0248 | 2.891 | 2.8879 | 3.0111 | 3.1214 | 3.2806 | 5 | 39%
LLANFWROG T1 / RUTHIN T1 | LLANFWROG T1 | 11 | 4.2355 | -0.066946 | 9.0243 | 8.7019 | 8.7516 | 9.2663 | 9.7709 | 10.4556 | 15 | 39%
| RUTHIN T1 |  | 4.7568 | 0.41203
LLANSANNAN T1 | LLANSANNAN T1 | 11 | 2.503 | 0.19052 | 2.6961 | 2.7054 | 2.7774 | 3.0726 | 3.3789 | 3.7555 | 7.5 | 39%
PILKINGTONS T1 / PILKINGTONS T2 | PILKINGTONS T1 | 11 | 1.5272 | 0.030579 | 3.4654 | 3.3492 | 3.3426 | 3.4937 | 3.6106 | 3.796 | 10 | 39%
| PILKINGTONS T2 |  | 1.9365 | 0.07738
ST ASAPH BUSINESS PK T1 | ST ASAPH BUSINESS PK T1 | 11 | 3.9091 | -0.0077521 | 3.9091 | 4.5583 | 4.7524 | 5.1777 | 5.489 | 5.9437 | 7.5 | 39%
YSBYTY GLAN CLWYD T1 | YSBYTY GLAN CLWYD T1 | 11 | 3.7675 | 0.65949 | 3.8248 | 3.7473 | 3.7605 | 3.9621 | 4.1149 | 4.3384 | 7.5 | 39%
POINT OF AYR COLLIERY T1 | POINT OF AYR COLLIERY T1 | 11 | 5.0374 | 0.8955 | 5.1164 | 5.067 | 5.1176 | 5.4282 | 5.7262 | 6.1258 | 7.5 | 39%
RHUDDLAN T1 | RHUDDLAN T1 | 11 | 4.1259 | 0.014107 | 4.126 | 3.8937 | 3.9265 | 4.1462 | 4.4226 | 4.7778 | 7.5 | 39%
ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | ASTMOOR IND EST T1 | 11 | 2.7948 | 0.94136 | 11.0793 | 10.8473 | 10.9136 | 11.3982 | 11.6211 | 12.0251 | 30 | 39%
| MACKAMAX T1 |  | 2.7311 | 0.94478
| MERSEY RD T1 |  | 2.3795 | -1.11
| PICOW FARM RD T1 |  | 2.9186 | 1.5886
BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | BASS CHARRINGTON T1 | 11 | 3.734 | 0.97947 | 15.8104 | 15.3713 | 15.3433 | 15.9816 | 16.4341 | 17.1583 | 30 | 39%
| BASS CHARRINGTON T2 |  | 3.8579 | 1.0234
| CLIFTON T1 |  | 4.3049 | 0.72724
| YKK T1 |  | 3.7315 | -0.70006
DARESBURY NPL T2/T2/T3 | DARESBURY NPL T2 | 11 | 0 | 0.020551 | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| DARESBURY NPL T3 |  | - | -
| DARESBURY NPL T4 |  | - | -
DARESBURY NPL T1 / DARESBURY PK T1 | DARESBURY NPL T1 | 11 | 2.5398 | -0.80752 | 5.1787 | 5.1261 | 5.1799 | 5.4791 | 5.7602 | 6.1262 | 10 | 39%
| DARESBURY PK T1 |  | 2.6357 | 0.60595
HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | HALTON RD T1 | 11 | 2.5015 | -2.1441 | 18.1494 | 16.575 | 16.2942 | 16.5255 | 16.6309 | 16.9723 | 25 | 39%
| MURDISHAW T1 |  | 3.3506 | -0.045665
| PERCIVAL LA T4 |  | 3.5629 | 0.028372
| RUNCORN CENTRAL T1 |  | 3.7404 | 0.84687
MANOR PK T1 / NORTON CHAINS T1 | MANOR PK T1 | 11 | 4.532 | 0.94228 | 8.9679 | 9.2348 | 9.9787 | 11.0861 | 11.4853 | 12.0671 | 10 | 39%
| NORTON CHAINS T1 |  | 4.3797 | 0.060165
DUFFRYN | DUFFRYN T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| DUFFRYN T2 |  | - | -
MERES EDGE T1 / MERES EDGE T2 | MERES EDGE T1 | 11 | 2.1874 | -0.53169 | 4.4385 | 4.4595 | 4.6052 | 5.0725 | 5.599 | 6.2481 | 10 | 39% | Previously BICC HELSBY T1 / BICC HELSBY T2 / EVC T1
| MERES EDGE T2 |  | 2.2192 | 0.00053873
BRITISH PIPE ASSOCIATION T1 | BRITISH PIPE ASSOCIATION T1 | 11 | 3.4401 | 0.5787 | 3.4884 | 3.4291 | 3.4329 | 3.5685 | 3.6638 | 3.8317 | 7.5 | 39%
BURMAH OIL T1 / VAN LEER NO 1 T1 | BURMAH OIL T1 | 6.6 | 0 | 0 | 4.5375 | 4.4499 | 4.4318 | 4.572 | 4.6469 | 4.7843 | 6.4 | 39% | BURMAH OIL T1 not operating at time of group peak demand
| VAN LEER NO 1 T1 |  | 1.7906 | 1.4103
CROWTON T1 | CROWTON T1 | 11 | 3.77 | -0.0083805 | 3.77 | 3.6251 | 3.6345 | 3.8539 | 4.0729 | 4.3574 | 7.5 | 39%
ELTON T1 | ELTON T1 | 11 | 2.6683 | 0.01464 | 2.6683 | 2.7594 | 2.8954 | 3.2301 | 3.5932 | 4.028 | 7.5 | 39%
FRODSHAM LOCAL T1 | FRODSHAM LOCAL T1 | 11 | 5.9984 | -0.2592 | 6.004 | 5.968 | 6.2356 | 6.902 | 7.473 | 8.2115 | 8.17 | 39%
ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | ALMONDS TURN T1 | 11 | 2.9984 | 0.59193 | 14.5336 | 14.3172 | 14.5956 | 15.6129 | 16.7311 | 18.2478 | 37.5 | 39%
| ATLANTIC COMPLEX T1 |  | 3.0938 | 0.341
| GIRO T1 |  | 2.865 | 0.30016
| MIDLAND BANK T1 |  | 2.9894 | 0.40445
| NETHERTON T1 |  | 2.5819 | -1.2542
ALTMOUTH T1 | ALTMOUTH T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | BLUNDELLSANDS (NORTH) T1 | 11 | 4.0883 | -0.5687 | 21.0777 | 20.4181 | 20.7432 | 22.2308 | 23.8982 | 26.1383 | 37.5 | 39%
| BLUNDELLSANDS (SOUTH) T1 |  | 4.3057 | 0.31412
| CROSBY T1 |  | 4.2533 | -0.4422
| KERSHAW AVE T1 |  | 4.3402 | 0.4367
| WATERLOO T2 |  | 4.0771 | -0.48314
BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | BURLINGTON AVE T1 | 11 | 3.5681 | 0.44113 | 14.6994 | 14.2548 | 14.405 | 15.4694 | 16.5055 | 17.8895 | 28 | 39%
| FRESHFIELD T1 |  | 3.4455 | -1.1299
| MARSH BROWS T1 |  | 4.093 | 0.7693
| SOUTHPORT RD T1 |  | 3.5858 | -0.53159
DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | DODDS LA T1 | 11 | 4.4744 | -0.80814 | 23.532 | 21.9195 | 21.9822 | 23.2671 | 24.691 | 26.6687 | 37.5 | 39% | ROBBINS BRIDGE T1 out of service at time of group MD
| HOLBORN HILL T1 |  | 4.4259 | -0.072299
| MAGHULL T1 |  | 5.1789 | 0.3262
| MAGHULL T2 |  | 5.139 | 0.31291
| ROBBINS BRIDGE T1 |  | 4.2867 | -0.88864
HASKAYNE T1 | HASKAYNE T1 | 11 | 2.0657 | 0.24896 | 2.0806 | 2.0094 | 2.0277 | 2.1717 | 2.3189 | 2.5159 | 7.5 | 39%
AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | AINTREE LOCAL T1 | 11 | 3.8064 | -0.43332 | 11.6686 | 11.4489 | 11.5126 | 12.2795 | 12.8802 | 13.7012 | 20 | 39%
| OLD ROAN T1 |  | 4.0711 | -0.5755
| WANGO LA T1 |  | 3.8145 | 1.0754
BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | BEMROSE T1 | 11 | 3.9818 | -0.93824 | 19.2853 | 18.5375 | 18.5413 | 19.4859 | 20.1821 | 21.2015 | 37.5 | 39%
| CARR LA EAST T1 |  | 4.8597 | 0.6207
| LUCAS (FAZAKERLEY) T1 |  | 3.9139 | -0.78684
| NORRIS GREEN T1 |  | 1.6858 | -0.05785
| WEST DERBY T1 |  | 4.8339 | 0.53614
ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | ORB CL T1 | 11 | 2.5139 | 0.76832 | 8.9991 | 8.794 | 8.7885 | 9.1853 | 9.4432 | 9.8554 | 20 | 39%
| STONEBRIDGE LA T1 |  | 3.2137 | 0.082279
| STONEBRIDGE LA T2 |  | 3.2259 | 0.053595
FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | FAZAKERLEY HOSPITAL T1 | 11 | 3.5171 | 0.73441 | 13.6871 | 12.841 | 12.7062 | 12.9733 | 13.1475 | 13.5008 | 30 | 39%
| JACOBS T1 |  | 3.3881 | 0.73921
| JACOBS T2 |  | 3.2549 | -0.19386
| SEEDS LA T1 |  | 3.3821 | 0.70708
BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | BOOTLE GRID T1 | 11 | 2.3468 | -0.13515 | 18.6793 | 18.2285 | 18.2258 | 19.1482 | 19.8285 | 20.8398 | 37.5 | 39%
| KELLOGGS T1 |  | 2.3742 | -0.031541
| PACIFIC RD T1 |  | 2.4002 | -0.20752
| WASHINGTON ST T1 |  | 2.5844 | 0.95015
| WATERLOO T1 |  | 2.4356 | 0.46834
BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | BOOTLE GRID T2 | 11 | 3.3644 | -1.744 | 15.2821 | 14.7396 | 14.8248 | 15.6605 | 16.3428 | 17.2675 | 30 | 39%
| ORRELL MOUNT T1 |  | 3.3999 | -0.96024
| SCARISBRICK AVE T1 |  | 3.8 | 0.156
| TATTON RD T1 |  | 4.711 | 2.0934
MDHB FREEPORT T1 | MDHB FREEPORT T1 | 6.3 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
AINSDALE T1 / PINFOLD LA T1 | AINSDALE T1 | 6.6 | 3.243 | 0.011 | 6.315 | 6.1431 | 6.2462 | 6.771 | 7.3073 | 8.013 | 9.1 | 39%
| PINFOLD LA T1 |  | 3.072 | -0.02164
BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | BANASTRE RD T1 | 6.6 | 3.3299 | -0.7752 | 10.7675 | 10.3035 | 10.3287 | 10.9585 | 11.5112 | 12.2707 | 9.1 | 39% | Voltage uprating in construction, new firm capacity will be 20MVA.
| DOVER RD T1 |  | 3.6645 | 0.17484
| GRANTHAM CL T1 |  | 3.772 | 0.4449
IVY ST (SOUTHPORT) T1 / KENSINGTON RD T1 / MARKET ST T1 / SOUTHPORT T1 | IVY ST (SOUTHPORT) T1 | 11 | 3.852 | -0.949 | 15.0295 | 14.6266 | 14.6153 | 15.2541 | 15.7931 | 16.5517 | 30 | 39%
IVY ST (SOUTHPORT) T1 / KENSINGTON ROAD / MARKET ST T1 / SOUTHPORT T1 | KENSINGTON RD T1 | 11 | 3.8241 | 0.83119 | 15.0295 | 14.6266 | 14.6153 | 15.2541 | 15.7931 | 16.5517 | 0 | 37%
| MARKET ST T1 |  | 3.14 | -0.311
| SOUTHPORT T1 |  | 4.2119 | 0.208
LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | LORD ST T1 | 11 | 4.609 | 0.9179 | 17.6932 | 16.7396 | 17.0132 | 18.4891 | 20.1702 | 22.3778 | 30 | 39%
| MARSHSIDE T1 |  | 4.3173 | -0.74078
| MULLARDS BALMORAL DV T1 |  | 4.1175 | -0.71377
| SOUTHPORT T2 |  | 4.6467 | 0.22787
NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | NEVILL ST T1 | 11 | 3.5789 | 0.21551 | 10.235 | 10.0445 | 10.0254 | 10.4895 | 10.775 | 11.2475 | 20 | 39%
| OCEAN PLAZA T1 |  | 3.1251 | 0.14432
| YORK RD T1 |  | 3.5224 | 0.061374
ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | ACORNFIELD RD T1 | 11 | 2.9871 | 1.6239 | 14.7094 | 14.443 | 14.3812 | 14.915 | 15.1809 | 15.6643 | 30 | 39%
| DICKINSONS T1 |  | 3.6907 | 0.4424
| HAMMOND RD T1 |  | 3.8807 | 0.99092
| KODAK T1 |  | 3.7605 | 0.30913
KELCO T1 / NEWS INTERNATIONAL T1 / NEWS INTERNATIONAL T2 / PALCO T1 / SOUTHDENE T1 | KELCO T1 | 11 | 4.3543 | 1.4669 | 17.2167 | 16.8136 | 16.7351 | 17.3202 | 17.6068 | 18.1468 | 30 | 39% | PALCO Transformer on Open Standby
| NEWS INTERNATIONAL T1 |  | 3.7529 | -0.32757
| NEWS INTERNATIONAL T2 |  | 4.5446 | 2.4605
| PALCO T1 |  | 0 | 0
| SOUTHDENE T1 |  | 4.0349 | 0.34605
KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | KIRKBY CENTRAL T1 | 11 | 4.8515 | 0.95434 | 17.8507 | 16.579 | 16.5671 | 17.178 | 17.8252 | 18.9005 | 30 | 39%
| NORTHWOOD T1 |  | 4.6939 | -0.094586
| TOWER HILL (BANK LA) T1 |  | 2.73 | -0.6447
| WESTVALE T1 |  | 5.31 | 0.53246
OTIS ELEVATOR T1 / ST IVEL FOODS T1 | OTIS ELEVATOR T1 | 11 | 2.3422 | 1.223 | 4.8661 | 4.7791 | 4.7545 | 4.9243 | 5.0012 | 5.1453 | 10 | 39%
| ST IVEL FOODS T1 |  | 2.4713 | -0.50994
ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | ASH RD T1 | 11 | 3.1996 | 0.6635 | 15.7419 | 15.5002 | 15.4999 | 16.1187 | 16.5176 | 17.1253 | 20 | 39%
| KELLOGGS WREXHAM T1 |  | 3.3073 | 0.6463
| KELLOGGS WREXHAM T2 |  | 3.8581 | 10.5382
BERSHAM COLLIERY T1 | BERSHAM COLLIERY T1 | 11 | 3.7736 | 0.16663 | 3.7847 | 2.2897 | 2.2936 | 2.4336 | 2.547 | 2.719 | 4 | 39%
BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | BERSHAM RD T1 | 11 | 3.9793 | 0.089319 | 15.4941 | 15.0349 | 15.1145 | 15.9536 | 16.5822 | 17.5494 | 30 | 39%
| IND COOPE T1 |  | 3.8314 | 0.1435
| RHYD BROUGHTON LA T1 |  | 3.9819 | 1.276
| TUTTLE ST T1 |  | 3.7014 | -1.458
BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | BICC WREXHAM T1 | 11 | 4.623 | 1.5571 | 12.8416 | 12.5925 | 12.5448 | 12.9871 | 13.1876 | 13.5687 | 20 | 39%
| MARCHWIEL T1 |  | 4.171 | 1.2607
| WIE CENTRAL T1 |  | 3.6015 | 0.53761
CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | CHESTER ST (WREXHAM) T1 | 11 | 3.8179 | 0.49323 | 13.5107 | 13.0456 | 13.1491 | 13.9459 | 14.672 | 15.7376 | 30 | 39%
| EAGLES MEADOW T1 |  | 3.3743 | -0.55637
| RHOSNESNI T1 |  | 3.0796 | 0.18396
| WHITEGATE T1 |  | 3.2296 | -0.62387
CHOWLEY T1 / CHOWLEY T2 | CHOWLEY T1 | 11 | 3.0338 | -1.7097 | 6.6478 | 6.451 | 6.4949 | 6.9167 | 7.3283 | 7.8802 | 10 | 39% | Bad tags. Set to Last year.
| CHOWLEY T2 |  | 3.5943 | 2.22
COEDPOETH T1 / COEDPOETH T2 | COEDPOETH T1 | 11 | 2.5924 | -0.17336 | 5.4327 | 5.3342 | 5.4501 | 5.8706 | 6.3585 | 6.9928 | 10 | 39%
| COEDPOETH T2 |  | 2.8304 | -0.15432
DAVY WAY T1 / LLAY T1 | DAVY WAY T1 | 11 | 3.9676 | 0.43426 | 7.8316 | 7.6587 | 7.6566 | 7.9847 | 8.2134 | 8.5708 | 10 | 39%
| LLAY T1 |  | 3.6825 | 1.242
DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | DEESIDE ALUMINIUM T1 | 11 | 4.1033 | 0.47888 | 26.562 | 25.996 | 25.891 | 26.7505 | 27.1703 | 27.9632 | 30 | 39%
| DUNLOP PLASTICS T1 |  | 3.8569 | 1.2763
| FIRESTONE T1 |  | 4.3871 | 1.227
| TETRAPAK T1 |  | 3.9919 | 1.082
GWERSYLLT T1 | GWERSYLLT T1 | 11 | 5.2883 | -0.1665 | 5.291 | 5.3023 | 5.4535 | 5.9882 | 6.5469 | 7.2647 | 7.5 | 39%
MAELOR CREAMERY T1 | MAELOR CREAMERY T1 | 11 | 3.2997 | 0.661 | 3.3653 | 3.2464 | 3.2337 | 3.3448 | 3.4128 | 3.519 | 7.5 | 39%
PANDY T1 / PANDY T2 | PANDY T1 | 11 | 4.0329 | -0.23715 | 8.1227 | 7.5701 | 7.5302 | 7.8625 | 8.1413 | 8.5824 | 10 | 39%
| PANDY T2 |  | 4.081 | -0.14231
ROSSETT T1 | ROSSETT T1 | 11 | 2.9705 | 0.022672 | 3.21 | 4.1129 | 5.2545 | 6.7126 | 7.4356 | 8.3437 | 7.5 | 39%
TARPORLEY T1 | TARPORLEY T1 | 11 | 4.1224 | 0.1226 | 4.1242 | 4.0271 | 4.0888 | 4.3997 | 4.7414 | 5.1682 | 7.5 | 39%
BASCHURCH T1 | BASCHURCH T1 | 11 | 3.8679 | 0.53437 | 5.759 | 5.5422 | 5.5491 | 5.8382 | 6.1129 | 6.4947 | 7.5 | 39%
BRD T1 | BRD T1 | 11 | 5.097 | 0.49127 | 5.2598 | 5.1742 | 5.2209 | 5.597 | 5.9401 | 6.4022 | 7.5 | 39%
BUTTINGTON CROSS T1 | BUTTINGTON CROSS T1 | 11 | 4.4664 | 0.68149 | 4.5181 | 3.9235 | 3.9337 | 4.1136 | 4.2123 | 4.3919 | 7.5 | 39%
RAVEN SQUARE T1 | RAVEN SQUARE T1 | 11 | 6.2531 | 1.157 | 6.3602 | 6.1993 | 6.2491 | 6.66 | 7.009 | 7.5214 | 7.5 | 39%
WELSHPOOL T1 | WELSHPOOL T1 | 11 | 3.8899 | 0.32245 | 3.9032 | 3.8303 | 3.8605 | 4.0816 | 4.2891 | 4.5438 | 7.5 | 39%
CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | CADBURYS KRONOSPAN T1 | 11 | 3.0751 | 1.1162 | 6.2193 | 6.0857 | 6.1422 | 6.4834 | 6.7913 | 7.231 | 10 | 39%
| CADBURYS KRONOSPAN T2 |  | 2.8312 | 0.83176
CAERSWS T1 | CAERSWS T1 | 11 | 2.5967 | 0.3484 | 3.0929 | 3.0165 | 3.0549 | 3.2955 | 3.5498 | 3.8729 | 7.5 | 39%
MORDA T1 | MORDA T1 | 11 | 3.3277 | -0.18136 | 3.3327 | 3.3865 | 3.5094 | 3.8402 | 4.2732 | 4.7781 | 7.5 | 39%
CONEY GREEN T1 / OSWESTRY T2 / OSWESTRY T1 | CONEY GREEN T1 | 11 | 3.8801 | 0.76638 | 11.4147 | 10.5572 | 10.5345 | 10.871 | 11.1744 | 11.6954 | 20 | 39%
| OSWESTRY T1 |  | 3.6514 | -0.0087218
| OSWESTRY T2 |  | 3.8619 | -0.061514
CRIGGION RADIO STATION T1 | CRIGGION RADIO STATION T1 | 11 | 1.3608 | 0.87472 | 1.7665 | 1.757 | 1.7857 | 1.8849 | 1.9797 | 2.1024 | 4 | 39%
ELLESMERE T1 / MMB ELLESMERE T1 | ELLESMERE T1 | 11 | 3.2142 | 0.021354 | 7.2602 | 7.1431 | 7.2173 | 7.6932 | 8.125 | 8.7244 | 9 | 39%
| MMB ELLESMERE T1 |  | 3.4983 | 0.68526
EXPRESS FOODS T1 | EXPRESS FOODS T1 | 11 | -0.18418 | 0.17263 | 1.0882 | 1.4471 | 1.4607 | 1.5372 | 1.6047 | 1.6943 | 7.5 | 39%
FORDEN T1 | FORDEN T1 | 11 | 3.4676 | 0.14214 | 3.4705 | 3.5208 | 3.5464 | 3.7544 | 3.9789 | 4.264 | 4 | 39%
IFTON T1 / IFTON T2 | IFTON T1 | 11 | 2.982 | 1.096 | 5.9186 | 5.8303 | 5.89 | 6.3203 | 6.7373 | 7.2842 | 10 | 39%
| IFTON T2 |  | 2.9355 | -0.983
JOHNSTOWN T1 | JOHNSTOWN T1 | 11 | 5.1597 | 0.32615 | 6.2942 | 6.3352 | 6.4987 | 7.0361 | 7.5914 | 8.2877 | 7.5 | 39%
LEGACY LOCAL T1 | LEGACY LOCAL T1 | 11 | 2.2463 | -0.06109 | 2.2471 | 2.0758 | 2.0729 | 2.1686 | 2.3005 | 2.4899 | 7.5 | 39%
LIVERPOOL RD 33 T1 | LIVERPOOL RD 33 T1 | 11 | 3.9533 | 0.26127 | 3.9619 | 3.8527 | 3.9168 | 4.2101 | 4.4942 | 4.8898 | 11 | 39%
WHITCHURCH T1 | WHITCHURCH T1 | 11 | 5.0334 | 0.19697 | 5.0372 | 4.8422 | 4.853 | 5.1346 | 5.4061 | 5.7745 | 11 | 39%
YOCKINGS GATE T1 | YOCKINGS GATE T1 | 11 | 3.4186 | 0.069718 | 3.4193 | 3.4364 | 3.5388 | 3.8087 | 4.1243 | 4.4947 | 10 | 39%
LLANDDU QUARRY T1 | LLANDDU QUARRY T1 | 11 | 2.7055 | 0.67311 | 3.4125 | 3.2682 | 3.256 | 3.3992 | 3.5238 | 3.7069 | 4 | 39%
LLANDRINIO T1 | LLANDRINIO T1 | 11 | 2.562 | 0.1911 | 2.6782 | 2.6925 | 2.746 | 2.9635 | 3.189 | 3.4536 | 5.27 | 39%
LLANFAIR CAEREINION T1 | LLANFAIR CAEREINION T1 | 11 | 4.6725 | 0.3467 | 4.9561 | 4.9126 | 5.0254 | 5.4447 | 5.8897 | 6.4324 | 7.5 | 39%
LLANFYLLIN T1 / LLANFYLLIN T2 | LLANFYLLIN T1 | 11 | 2.4965 | -0.31128 | 5.145 | 4.9569 | 4.9969 | 5.434 | 5.836 | 6.3969 | 7.8 | 39%
| LLANFYLLIN T2 |  | 2.5725 | 0.76123
LLANGOLLEN T1 / LLANGOLLEN T2 | LLANGOLLEN T1 | 11 | 2.4408 | 0.41602 | 4.8149 | 4.6797 | 4.7226 | 5.091 | 5.448 | 5.9346 | 10 | 39%
| LLANGOLLEN T2 |  | 2.3721 | -0.27647
LLANIDLOES T1 / LLANIDLOES T2 | LLANIDLOES T1 | 11 | 1.7926 | 0.57516 | 4.2668 | 4.1741 | 4.2851 | 4.8497 | 5.3951 | 6.1376 | 5.73 | 39%
| LLANIDLOES T2 |  | 1.7044 | -0.35214
LLANSILIN T1 | LLANSILIN T1 | 11 | 3.3844 | 0.26769 | 3.4449 | 3.3843 | 3.4558 | 3.7589 | 4.0934 | 4.5072 | 7.5 | 39%
LLYNCLYS T1 | LLYNCLYS T1 | 11 | 3.9992 | 0.81018 | 4.0875 | 4.1809 | 4.2983 | 4.657 | 5.0797 | 5.5634 | 7.5 | 39%
MAES-Y-CLAWDD T1 | MAES-Y-CLAWDD T1 | 11 | 4.5267 | 0.73391 | 4.5861 | 4.4867 | 4.5064 | 4.7273 | 4.9257 | 5.1743 | 7.5 | 39%
MILFORD T1 | MILFORD T1 | 11 | 4.4741 | 0.0095708 | 4.4741 | 4.343 | 4.3946 | 4.6858 | 4.9669 | 5.3475 | 7.5 | 39%
MOCHDRE T1 | MOCHDRE T1 | 11 | 3.5762 | 0.68426 | 3.6411 | 3.5441 | 3.5454 | 3.6969 | 3.802 | 3.967 | 7.5 | 39%
MONSANTO T1 | MONSANTO T1 | 11 | 0.95022 | -0.1479 | 1.477 | 1.5144 | 1.5942 | 1.8486 | 2.0921 | 2.4114 | 7.5 | 39%
OVERTON T1 | OVERTON T1 | 11 | 3.5416 | 0.46937 | 3.5725 | 3.6062 | 3.7211 | 4.2858 | 4.7644 | 5.4168 | 7.5 | 39%
PREES T1 | PREES T1 | 11 | 5.166 | 0.8193 | 5.2306 | 4.9387 | 4.9386 | 5.1374 | 5.3736 | 5.6869 | 7.5 | 39%
RUABON T1 | RUABON T1 | 11 | 6.3105 | 0.10661 | 6.6837 | 6.5499 | 6.6465 | 7.0917 | 7.4816 | 8.0401 | 10 | 39%
SHAWBURY T1 | SHAWBURY T1 | 11 | 5.0832 | -0.15401 | 5.2405 | 5.227 | 5.297 | 5.6419 | 5.9867 | 6.3981 | 6.807 | 39%
WEM EAST T1 | WEM EAST T1 | 11 | 2.8475 | 0.37773 | 2.878 | 2.8088 | 2.8261 | 3.0101 | 3.1791 | 3.4148 | 7.5 | 39%
WEM T1 | WEM T1 | 11 | 4.6955 | 0.31471 | 4.7061 | 4.6259 | 4.7039 | 5.0208 | 5.3912 | 5.8317 | 7.5 | 39%
WEST FELTON T1 | WEST FELTON T1 | 11 | 1.5257 | 0.31759 | 2.9151 | 2.8651 | 2.8785 | 3.0305 | 3.1792 | 3.366 | 4 | 39%
ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | ATHOL ST T1 | 6.3 | 2.5024 | -0.054667 | 7.694 | 7.6238 | 7.6896 | 8.0779 | 8.4378 | 8.9071 | 17.4 | 39%
| CHISENHALE ST T1 |  | 2.3705 | -0.13323
| SANDHILLS LA T1 |  | 2.7987 | 0.77487
BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | BIBBYS T1 | 6.3 | 4.4621 | 1.753 | 11.6404 | 11.2555 | 11.2142 | 11.703 | 12.0254 | 12.5438 | 17.5 | 39%
| INLAND REVENUE OFFICES T1 |  | 3.7797 | 1.0046
| REGENT RD T1 |  | 3.104 | -0.15515
BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | BROOK ST T1 | 11 | 3.0538 | 0.56997 | 12.6202 | 12.3882 | 12.3638 | 12.8239 | 13.0928 | 13.5433 | 30 | 39%
| KINGSWAY TUNNEL T1 |  | 3.6853 | 3.1847
| NWWA SANDON DOCK T1 |  | 2.8251 | -1.9798
| NWWA SANDON DOCK T2 |  | 2.9469 | -0.11792
BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | BUCKINGHAM ST T1 | 6.3 | 3.1622 | 1.1752 | 8.6577 | 8.1945 | 8.0876 | 8.2414 | 8.2783 | 8.4347 | 17.5 | 39%
| EVERTON RD T1 |  | 2.4983 | -1.4461
| SUBURBAN RD T1 |  | 2.997 | 0.33793
CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | CLUBMOOR T1 | 6.3 | 2.2241 | -0.17934 | 7.2002 | 7.0715 | 7.0493 | 7.3168 | 7.4421 | 7.6775 | 17.5 | 39%
| DUNLOPS WALTON T1 |  | 3.1164 | 1.8598
| WALTON T2 |  | 1.8546 | -1.4126
CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | CLUBMOOR T2 | 6.3 | 3.7386 | 0.2724 | 10.7602 | 10.0753 | 9.93 | 10.1307 | 10.2088 | 10.4304 | 17.5 | 39%
| LISTER DV A T1 |  | 3.489 | -0.151
| SUBURBAN RD T2 |  | 3.5248 | 0.2898
DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | DELAMORE ST T1 | 6.3 | 4.1233 | -0.46028 | 12.4727 | 11.5711 | 11.4077 | 11.7398 | 11.981 | 12.4087 | 17.4 | 39%
| KIRKDALE T1 |  | 4.8081 | 1.9288
| WALTON T1 |  | 3.529 | -0.91466
EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | EVERTON BROW T1 | 6.3 | 3.9527 | 1.3326 | 10.7388 | 9.6868 | 9.4229 | 9.3642 | 9.2256 | 9.2255 | 17.5 | 39%
| GARDNERS ROW T1 |  | 3.249 | -1.1378
| SHEIL PK T1 |  | 3.5352 | 0.009974
MDHB CANADA DOCK | MDHB CANADA DOCK T1 | 6.3 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| MDHB CANADA DOCK T2 |  | - | -
NORTON SCRAP T1 / NORTON SCRAP T2 | NORTON SCRAP T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| NORTON SCRAP T2 |  | - | -
LITTLEWOODS T1 / PALL MALL T1 | LITTLEWOODS T1 | 6.3 | 2.5832 | 0.13238 | 4.7353 | 4.6795 | 4.717 | 4.9229 | 5.1405 | 5.4031 | 8.7 | 39%
| PALL MALL T1 |  | 2.1478 | 0.070459
BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | BOLTON ST T1 | 11 | 3.6702 | -0.179 | 14.8941 | 14.5291 | 14.4604 | 14.9559 | 15.1898 | 15.6506 | 20 | 39%
| GREEK ST T1 |  | 3.8875 | 0.82385
| HPO COPPERAS HILL T1 |  | 3.4529 | -1.0684
| OLDHAM PLACE T1 |  | 3.88 | 0.744
CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | CABLE ST T1 | 11 | 4.4329 | -0.3722 | 14.0259 | 13.6367 | 13.5489 | 13.9574 | 14.1278 | 14.4898 | 20 | 39%
| GRADWELL ST T2 |  | 4.7501 | 0.6702
| OLDHAM PLACE T2 |  | 4.811 | 0.647
CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | CABLE ST T2 | 11 | 3.349 | 1.3535 | 9.5402 | 9.5028 | 9.602 | 10.2241 | 10.6369 | 11.2 | 20 | 39%
| CROWN COURTS T1 |  | 2.9542 | -1.3685
| GRADWELL ST T1 |  | 3.2279 | 0.434
DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | DAILY POST & ECHO T1 | 6.3 | 1.9853 | 0.38219 | 3.9857 | 3.5468 | 3.427 | 3.4222 | 3.3026 | 3.2429 | 8.7 | 39%
| DAILY POST & ECHO T2 |  | 1.9209 | -1.1741
HARRINGTON ST T1 / PARADISE ST T1 | HARRINGTON ST T1 | 6.3 | 2.8989 | 1.017 | 5.1894 | 5.0577 | 5.4129 | 5.7648 | 5.8711 | 6.0493 | 8.7 | 39%
| PARADISE ST T1 |  | 2.2773 | -0.6456
HARRINGTON ST T2 / HIGHFIELD ST T1 | HARRINGTON ST T2 | 6.3 | 4.0469 | 1.7525 | 7.6516 | 4.0669 | 4.0487 | 4.184 | 4.2473 | 4.3731 | 8.7 | 39%
| HIGHFIELD ST T1 |  | 3.5194 | -0.61314
HARRINGTON ST T3 / LIME ST T1 | HARRINGTON ST T3 | 6.3 | 1.9453 | -0.60748 | 4.1521 | 3.7125 | 3.6086 | 3.5406 | 3.4451 | 3.3893 | 8.7 | 39%
| LIME ST T1 |  | 2.1994 | 0.85552
HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | HIGHFIELD ST T2 | 11 | 2.947 | -0.32035 | 9.0645 | 8.8964 | 8.9164 | 9.1409 | 9.2661 | 9.474 | 20 | 39%
| LIME ST T2 |  | 3.0326 | 0.512
| OLD HAYMARKET T1 |  | 3.0848 | -0.1746
MANN ISLAND T1 / MANN ISLAND T2 | MANN ISLAND T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| MANN ISLAND T2 |  | - | -
PADDINGTON PLACE T1 / PADDINGTON PLACE T2 | PADDINGTON PLACE T1 | 11 | - | - | - | 0.83336 | 0.8681 | 1.19 | 1.435 | 1.7742 | - | - | Demand data redacted
| PADDINGTON PLACE T2 |  | - | -
ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | ROYAL INSURANCE (NEW QUAY) T1 | 6.3 | 0.21584 | 0.013152 | 0.43078 | 0.53384 | 0.63304 | 0.77346 | 1.0192 | 1.2621 | 8.7 | 39%
| ROYAL INSURANCE (NEW QUAY) T2 |  | 0.21414 | 0.013037
ROYAL LIVERPOOL HOSP T1 / ROYAL LIVERPOOL HOSP T2 | ROYAL LIVERPOOL HOSP T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| ROYAL LIVERPOOL HOSP T2 |  | - | -
AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | AIGBURTH VALE T1 | 11 | 5.5214 | -0.30941 | 18.9652 | 17.919 | 17.8081 | 18.5595 | 19.1769 | 20.0889 | 37.5 | 39%
| IVY AVE T1 |  | 4.2503 | 0.73154
| MATHER AVE T1 |  | 0.69017 | 0.1384
| MOSSLEY HILL T1 |  | 3.7825 | -1.7972
| WAVERTREE T1 |  | 4.6473 | -0.4307
AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 | AIRPORT T1 | 11 | 3.0624 | -0.37186 | 10.2452 | 10.0995 | 10.1715 | 10.6995 | 11.1997 | 11.8454 | 30 | 39%
| ALDERWOOD AVE (CROYDE RD) T1 |  | 3.72 | -0.5047
| HAREFIELD RD T1 |  | 3.4119 | -0.144
ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | ALLERTON T1 | 11 | 2.7292 | -0.3306 | 14.2445 | 13.8308 | 13.7834 | 14.3096 | 14.6516 | 15.2036 | 37.5 | 39%
| ECP WEST-BANKS RD T1 |  | 2.9192 | 0.57972
| GARSTON T1 |  | 3.271 | 1.6075
| WEAVER IND EST T1 |  | 2.9772 | -0.41447
| YEW TREE RD T1 |  | 2.3465 | -1.2445
ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | ESTUARY COMMERCE PK T1 | 11 | 0 | 0 | 8.658 | 8.4877 | 8.4631 | 8.7677 | 8.9334 | 9.2332 | 30 | 39% | LEEWARD DR T2 and ESTUARY COMMERCE PK T1 out of service at time of group peak demand
| LEEWARD DR T1 |  | 0 | 0
| LEEWARD DR T2 |  | 2.8488 | 0.98735
| SPEKE HALL RD T1 |  | 3.0564 | 1.0343
| SPEKE SKY PK T1 |  | 2.5154 | -0.00844
ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | ALBERT DOCK T1 | 11 | 1.586 | 0.07222 | 6.5712 | 6.4264 | 6.4063 | 6.6359 | 6.7733 | 7.0087 | 30 | 39%
| KINGS DOCK T1 |  | 1.668 | 0.0152
| KINGS DOCK T2 |  | 1.674 | 0.01024
| WAPPING T1 |  | 1.642 | 0.02925
BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | BEAUMONT ST T1 | 11 | 5.4835 | 0.9126 | 20.8576 | 19.7103 | 20.0419 | 20.383 | 20.4523 | 21.3927 | 30 | 39%
| DINGLE VALE T1 |  | 5.2925 | 0.5077
| LARK LA T1 |  | 5.535 | 0.59671
| MDHB BRUNSWICK DOCK T1 |  | 4.5373 | -1.3957
ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | ARUNDEL T1 | 6.3 | 3.5422 | -0.0010533 | 10.1169 | 9.5191 | 9.4176 | 9.6974 | 9.8478 | 10.1608 | 17.5 | 39%
| GROVE PK T1 |  | 2.8757 | -0.70529
| WAVERTREE VALE T1 |  | 3.697 | 0.9096
BEECH ST T1 / LISTER DV A T2 | BEECH ST T1 | 6.3 | 2.0365 | 0 | 4.0661 | 3.8834 | 3.8481 | 3.978 | 4.0372 | 4.1612 | 8.7 | 39%
| LISTER DV B T2 |  | 2.017 | -0.3198
BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | BLUNDELL ST T1 | 11 | 3.0361 | -0.3441 | 9.3239 | 9.01 | 8.9527 | 9.1918 | 9.2793 | 9.5019 | 18.53 | 39%
| ROPEWALKS T1 |  | 3.015 | -0.18592
| ST JAMES T1 |  | 3.2723 | 0.43878
DINGLE T1 / GRANBY T1 / ST JAMES T2 | DINGLE T1 | 6.3 | 2.6306 | -1.0861 | 8.8148 | 5.1423 | 5.0933 | 5.2466 | 5.3267 | 5.481 | 17.5 | 39%
| GRANBY T1 |  | 3.1445 | -0.043409
| ST JAMES T2 |  | 3.0334 | 0.7969
EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | EDGE HILL T1 | 11 | 3.9544 | -1.1988 | 15.9915 | 15.6367 | 15.632 | 16.2202 | 16.653 | 17.3124 | 30 | 39%
| LIVERPOOL UNIVERSITY T1 |  | 3.9463 | 0.55222
| LIVERPOOL UNIVERSITY T2 |  | 4.0391 | 1.5485
| LIVERPOOL UNIVERSITY T3 |  | 4.0439 | -0.40212
EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | EDGE LA (TAPLEY PLACE) T1 | 11 | 4.267 | 0.4615 | 20.6312 | 18.9198 | 18.5602 | 18.7001 | 18.75 | 19.0103 | 37.5 | 39%
| LISTER DV B T3 |  | 4.462 | 0.4807
| MILL LA (WAVERTREE) T1 |  | 2.8333 | -0.93722
| PLESSEY (EDGE LA) T1 |  | 4.655 | 0.652
| STONEYCROFT T1 |  | 4.39 | 0.336
WAVERTREE BOULEVARD T1 / WAVERTREE BOULEVARD T2 | WAVERTREE BOULEVARD T1 | 11 | 1.8385 | -1.8588 | 5.5867 | 5.5806 | 5.6275 | 5.9319 | 6.1831 | 6.5122 | 7.5 | 39%
| WAVERTREE BOULEVARD T2 |  | -0.22728 | -3.4905
BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | BANGOR HOSP T1 | 11 | 2.978 | -0.41106 | 12.8731 | 12.5048 | 12.5332 | 13.1788 | 13.6826 | 14.4543 | 30 | 39%
| EITHINOG T1 |  | 3.0353 | 0.10034
| BANGOR UNIVERSITY T1 |  | 3.2364 | -0.0010001
| HIRAEL T1 |  | 3.6197 | 0.61842
MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | MINFFORDD T1 | 11 | 1.1506 | -0.40343 | 3.6007 | 3.5356 | 3.5847 | 3.8413 | 4.0902 | 4.4507 | 20 | 39%
| PARC BRYN CEGIN T1 |  | 1.2385 | 0.14458
| PARC BRYN CEGIN T2 |  | 1.2094 | 0.13243
BETHESDA T1 | BETHESDA T1 | 11 | 3.1297 | 0.1576 | 4.0204 | 4.2816 | 4.3242 | 4.6032 | 4.8838 | 5.2859 | 7.5 | 39%
CAERNARFON T1 | CAERNARFON T1 | 11 | 5.4201 | 0.3978 | 5.4347 | 5.322 | 5.3569 | 5.652 | 5.937 | 6.3121 | 7.5 | 39%
FERODO T1 | FERODO T1 | 11 | 2.4856 | 0.070273 | 2.5653 | 2.5778 | 2.6831 | 2.949 | 3.2383 | 3.6037 | 7.5 | 39%
LLANBERIS T1 | LLANBERIS T1 | 11 | 2.677 | 0.41815 | 3.4662 | 3.3675 | 3.398 | 3.653 | 3.8854 | 4.2193 | 5 | 39%
PARC MENAI T1 | PARC MENAI T1 | 11 | 1.4802 | 0.02178 | 1.4803 | 1.4843 | 1.5273 | 1.6391 | 1.7649 | 1.9213 | 7.5 | 39%
PEBLIC MILLS T1 | PEBLIC MILLS T1 | 11 | 1.083 | -0.05535 | 1.0844 | 1.131 | 1.1832 | 1.3117 | 1.587 | 1.7754 | 7.5 | 39%
PEN-Y-GROES T1 | PEN-Y-GROES T1 | 11 | 2.6884 | 0.10487 | 2.8262 | 2.8673 | 2.9381 | 3.2693 | 3.5929 | 4.0019 | 5.2 | 39%
ST HELENS RD T1 | ST HELENS RD T1 | 11 | 2.195 | 0.36639 | 4.1932 | 4.0993 | 4.1294 | 4.3893 | 4.6196 | 4.9567 | 7.5 | 39%
WAENFAWR T1 | WAENFAWR T1 | 11 | 2.9973 | 0.10794 | 3.0768 | 3.0495 | 3.128 | 3.4716 | 3.8511 | 4.3259 | 7.5 | 39%
BETWS-Y-COED T1 | BETWS-Y-COED T1 | 11 | 3.4403 | 0.01033 | 3.463 | 3.5642 | 3.716 | 4.2094 | 4.7448 | 5.3965 | 7.5 | 39%
COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | COLWYN BAY T1 | 11 | 2.276 | 0.73584 | 6.656 | 6.426 | 6.4236 | 6.7322 | 6.9528 | 7.2876 | 18 | 39%
| COLWYN BAY T2 |  | 2.2108 | -0.21147
| RHOS-ON-SEA T1 |  | 1.7636 | 1.7636
CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | CONWY T1 | 11 | 4.5443 | 0.97509 | 12.1018 | 11.6667 | 11.8455 | 12.8447 | 13.943 | 15.3846 | 27.32 | 39%
| DEGANWY T1 |  | 4.1102 | 1.1243
| LLANDUDNO JUNCTION T1 |  | 3.434 | -1.5303
DOLGARROG T1 / DOLGARROG T2 | DOLGARROG T1 | 11 | 3.9886 | 0.21371 | 4.3583 | 4.3726 | 4.4625 | 4.8284 | 5.2141 | 5.684 | 7.5 | 39%
| DOLGARROG T2 |  | 0.14331 | -0.028585
IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | IVY ST T1 | 11 | 4.0882 | -0.59395 | 11.8421 | 11.242 | 11.3349 | 12.1112 | 12.852 | 13.9113 | 20 | 39%
| LLYSFAEN RD T1 |  | 3.7162 | -0.27971
| OLD MILL T1 |  | 4.0377 | 0.90481
LLANDUDNO T1 / LLANDUDNO T2 | LLANDUDNO T1 | 11 | 2.915 | 0.08507 | 5.9897 | 5.6501 | 5.6637 | 5.9182 | 6.1873 | 6.5562 | 10 | 39%
| LLANDUDNO T2 |  | 3.0746 | -0.0481
LLANFAIRFECHAN T1 | LLANFAIRFECHAN T1 | 11 | 2.0517 | -0.08387 | 2.0535 | 2.0422 | 2.0975 | 2.3486 | 2.5922 | 2.9216 | 7.5 | 39%
LLANRWST T1 | LLANRWST T1 | 11 | 3.35 | 0.20366 | 3.4694 | 3.3133 | 3.3342 | 3.5747 | 3.8034 | 4.1297 | 7.5 | 39%
NANT-Y-GAMAR T1 | NANT-Y-GAMAR T1 | 11 | 4.7202 | -0.08395 | 4.7488 | 4.6454 | 4.6904 | 5.0336 | 5.3555 | 5.7756 | 7.5 | 39%
PENMAENMAWR T1 | PENMAENMAWR T1 | 11 | 2.303 | -0.22314 | 2.3138 | 2.3371 | 2.4342 | 2.7945 | 3.1538 | 3.6152 | 7.5 | 39%
REFORM ST T1 | REFORM ST T1 | 11 | 4.6401 | 0.30326 | 4.65 | 4.4486 | 4.4971 | 4.7709 | 4.9436 | 5.2144 | 7.5 | 39%
RHYD-Y-FOEL T1 | RHYD-Y-FOEL T1 | 11 | 1.8589 | 0.072869 | 2.5318 | 2.6269 | 2.734 | 3.0503 | 3.394 | 3.8071 | 7.5 | 39%
BRITISH OXYGEN T1 / WINDLEHURST T1 | BRITISH OXYGEN T1 | 6.6 | 2.9925 | 0.095006 | 6.1742 | 5.9077 | 5.9222 | 6.1502 | 6.366 | 6.6512 | 9.1 | 39%
| WINDLEHURST T1 |  | 3.1399 | 0.6225
CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | CARBORUNDUM T1 | 11 | 4.6451 | 1.6024 | 16.8051 | 16.265 | 16.3754 | 17.4616 | 18.5169 | 19.9415 | 30 | 39%
| HOUGHTONS LA T1 |  | 3.9312 | -0.46345
| RAINFORD T1 |  | 4.4807 | 1.1404
| WINDLEHURST T2 |  | 3.4725 | -1.0995
CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | CARLTON ST T1 | 6.6 | 3.5439 | 0.77745 | 9.7976 | 9.594 | 9.6055 | 10.0715 | 10.3835 | 10.8655 | 18.2 | 39%
| CARLTON ST T2 |  | 2.6878 | -0.17406
| CHALON WAY T2 |  | 3.5525 | -0.090268
CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | CHALON WAY T1 | 6.6 | 3.6303 | 0.4044 | 7.3577 | 7.1912 | 7.2142 | 7.6297 | 7.9694 | 8.4323 | 9.1 | 39% | TECHNOLOGY CAMPUS T1 recently under construction - not operating at time of group peak demand
| TECHNOLOGY CAMPUS T1 |  | 0 | 0
| WOODVILLE ST T1 |  | 3.7175 | -0.024225
PILKINGTONS PLATE | PILKINGTONS PLATE T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| PILKINGTONS PLATE T2 |  | - | -
DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | DESOTO RD T1 | 11 | 2.0643 | 0.17975 | 5.4039 | 5.2274 | 5.1944 | 5.3587 | 5.4365 | 5.5841 | 20 | 39%
| MERSEY BRIDGE T1 |  | 1.9195 | -0.81331
| PITT ST T1 |  | 1.2918 | -0.53675
APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | APPLETON T1 | 11 | 5.1889 | -0.3649 | 16.2003 | 15.6844 | 15.7667 | 16.6405 | 17.4716 | 18.6548 | 20 | 39%
| HORNSBRIDGE T1 |  | 5.4501 | 0.64101
| LUGSDALE T2 |  | 5.5414 | 0.52853
CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | CLOCKFACE T1 | 11 | 2.338 | -0.0497 | 12.8389 | 12.5822 | 12.6631 | 13.3775 | 13.999 | 14.8942 | 30 | 39%
| GEC ST HELENS T1 |  | 2.7211 | 0.36112
| HILLS MOSS T1 |  | 2.6285 | 0.13135
| NCB SUTTON MANOR T2 |  | 2.2 | -0.34152
DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | DITTON T1 | 11 | 4.7861 | 0.0118 | 17.1277 | 16.6723 | 16.7688 | 17.71 | 18.557 | 19.7794 | 30 | 39%
| GAVIN RD T1 |  | 4.2826 | -0.14462
| HOUGH GREEN T1 |  | 4.3899 | 0.060272
| RTZ T1 |  | 3.6651 | -0.29871
HOLT LA (WARRINGTON RD) T1 / PRESCOT GRID T1 / RAINHILL LOCAL T1 / WHISTON HOSP T1 | HOLT LA (WARRINGTON RD) T1 | 11 | 3.4927 | 0.3677 | 13.7017 | 18.1366 | 18.0602 | 18.6823 | 19.2504 | 20.2244 | 30 | 39%
| PRESCOT T1 |  | 3.161 | -0.73
| RAINHILL LOCAL T1 |  | 3.3868 | 0.4087
| WHISTON HOSP T1 |  | 3.4988 | 0.3512
LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | LUGSDALE T1 | 11 | 2.2936 | 0.2949 | 9.4133 | 9.1976 | 9.1652 | 9.5483 | 9.7045 | 10.0196 | 30 | 39%
| PILK SULLIVAN T1 |  | 2.6822 | 0.5572
| PILK SULLIVAN T2 |  | 2.5936 | 1.5073
| USAC T1 |  | 1.6335 | -0.38018
NWW SHELL GREEN T1 / NWW SHELL GREEN T2 | NWW SHELL GREEN T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| NWW SHELL GREEN T2 |  | - | -
PETER SPENCE T1 / PETER SPENCE T2 | PETER SPENCE T1 | 6.6 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| PETER SPENCE T2 |  | - | -
ALMATEX T1 / ST HELENS WWTW T1 / WATERY LA T2 | ALMATEX T1 | 6.6 | 3.888 | 0.32115 | 9.472 | 9.2038 | 9.2134 | 9.5575 | 9.8139 | 10.1948 | 18.2 | 39%
| ST HELENS WWTW T1 |  | 2.9128 | 0.68027
| WATERY LA T2 |  | 2.6468 | -0.3067
BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | BRITISH SIDAC T1 | 6.6 | 2.7238 | 0.63161 | 8.3719 | 8.2185 | 8.3302 | 8.8522 | 9.3798 | 10.1259 | 18.2 | 39% | ST HELENS LINKWAY under construction
| SHERDLEY RD T1 |  | 3.336 | 1.0637
| ST HELENS LINKWAY T1 |  | 0 | 6.068e-06
| WATERY LA T1 |  | 2.2667 | -0.82353
PILKINGTONS GREENGATE WRKS T1 / PILKINGTONS GREENGATE WRKS T2 | PILKINGTONS GREENGATE WRKS T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| PILKINGTONS GREENGATE WRKS T2 |  | - | -
PILKINGTONS HO T1 / SOMERFIELD DISTRIBUTION T1 / RAVENHEAD RETAIL PARK T1 | PILKINGTONS HO T1 | 11 | 3.9014 | -1.0303 | 12.6065 | 11.7133 | 11.5689 | 11.8517 | 12.0296 | 12.4144 | 20 | 39%
| RAVENHEAD RETAIL PK T1 |  | 4.033 | -0.13117
| SOMERFIELD DISTRIBUTION T1 |  | 4.6721 | 1.1836
BEDBURN DV T1 / BLUEBELL LA T1 / BROOKBRIDGE T1 / ECCLESTON T1 | BEDBURN DV T1 | 11 | 4.0498 | -0.86916 | 17.0655 | 16.5221 | 16.725 | 18.0804 | 19.557 | 21.5795 | 30 | 39%
| BLUEBELL LA T1 |  | 4.6541 | 0.82261
| BROOKBRIDGE T1 |  | 5.212 | 0.015252
| ECCLESTON T1 |  | 3.1433 | 0.49532
BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | BICC HUYTON QUARRY T1 | 11 | 2.9171 | 0.88497 | 8.1226 | 8.037 | 8.1927 | 8.8181 | 9.5091 | 10.4176 | 20 | 39%
| TARBOCK T1 |  | 2.641 | 0.023511
| WHISTON T1 |  | 2.5636 | -0.79264
BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | BROADGREEN T1 | 11 | 4.9364 | -0.5072 | 24.8884 | 23.6483 | 23.5073 | 24.4552 | 25.1354 | 26.2266 | 37.5 | 39%
| CROXTETH T1 |  | 4.4937 | -1.2367
| EAST PRESCOT RD (FINCH LA) T1 |  | 5.4071 | 0.71981
| KNOTTY ASH T1 |  | 5.1988 | 0.52592
| LEYFIELD RD T1 |  | 4.8512 | 0.24997
CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | CHILDWALL FIVEWAYS T1 | 11 | 4.4162 | -0.47577 | 23.5326 | 22.5505 | 22.5648 | 23.6247 | 24.5605 | 26.0054 | 37.5 | 39%
| CHILDWALL T1 |  | 6.0326 | 0.80651
| LYNDENE RD T1 |  | 4.4939 | 0.4867
| MIDDLEMASS HEY T1 |  | 4.1265 | -0.53164
| NAYLORS RD T1 |  | 4.4619 | -0.55487
HUYTON HEY RD T1 / WILSON RD T1 | HUYTON HEY RD T1 | 11 | 3.7695 | 0.84378 | 6.8949 | 6.6627 | 6.6976 | 7.1328 | 7.5435 | 8.1266 | 10 | 39%
| WILSON RD T1 |  | 3.1254 | -0.829
KNOWSLEY T1 / MARLED HEY T1 | KNOWSLEY T1 | 11 | 2.0571 | -0.17592 | 4.2556 | 4.0719 | 4.0517 | 4.249 | 4.3891 | 4.6019 | 10 | 39%
| MARLED HEY T1 |  | 2.1848 | -0.1639
CHIRON SHAW RD T1 / CHIRON SHAW RD T2 | CHIRON SHAW RD T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| CHIRON SHAW RD T2 |  | - | -
CONIX T1 / CONIX T2 / MEDEVA T1 | CONIX T1 | 11 | 2.364 | 0.45449 | 7.1561 | 7.0179 | 6.996 | 7.2287 | 7.3435 | 7.5513 | 20 | 39%
| CONIX T2 |  | 2.5051 | 3.2747
| MEDEVA T1 |  | 2.0922 | -2.0708
HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | HUNTS CROSS T1 | 11 | 4.4283 | 1.0628 | 16.652 | 16.0084 | 16.1634 | 17.1991 | 18.2084 | 19.6317 | 30 | 39%
| KENTON RD T1 |  | 4.0687 | -1.0682
| WOODEND AVE T1 |  | 4.2278 | 0.45287
| WOOLTON T1 |  | 3.9271 | -0.38041
ABERDYFI T1 | ABERDYFI T1 | 11 | 2.8548 | No good data | 2.8548 | 2.7752 | 2.805 | 3.0334 | 3.2513 | 3.5552 | 7.5 | 39%
ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | ABERYSTWYTH T1 | 11 | 3.8216 | 0.40252 | 18.5496 | 18.0585 | 18.1639 | 19.2577 | 20.2507 | 21.68 | 37.5 | 39%
| NORTH RD T1 |  | 4.0224 | 0.35549
| PARC-Y-LLYN T1 |  | 3.6537 | 0.10865
| PARC-Y-LLYN T2 |  | 3.1258 | -1.7521
| U C WALES T1 |  | 3.9236 | 1.1859
BOW ST T1 | BOW ST T1 | 11 | 4.7285 | 0.10236 | 4.7344 | 4.6396 | 4.7354 | 5.1241 | 5.5836 | 6.1349 | 7.5 | 39%
FAIRBOURNE T1 | FAIRBOURNE T1 | 11 | 2.1797 | -0.013786 | 2.1798 | 2.3011 | 2.4503 | 2.8513 | 3.2126 | 3.6767 | 7.5 | 39%
LLANILAR T1 | LLANILAR T1 | 11 | 1.711 | -0.036635 | 2.6013 | 2.3791 | 2.4394 | 2.6624 | 2.9199 | 3.2265 | 3.2 | 39%
MACHYNLLETH T1 | MACHYNLLETH T1 | 11 | 2.5268 | 0.033907 | 2.5352 | 2.5696 | 2.6675 | 2.9954 | 3.3433 | 3.7828 | 4 | 39%
RHYDLYDAN T2 | RHYDLYDAN T2 | 11 | 0.53423 | 0.09815 | 1.0508 | 1.0639 | 1.1169 | 1.2528 | 1.4394 | 1.6418 | 4 | 39%
TYWYN T1 | TYWYN T1 | 11 | 4.1962 | -0.021491 | 4.2145 | 4.2376 | 4.4101 | 5.0011 | 5.4137 | 6.0626 | 7.5 | 39%
ABERSOCH T1 | ABERSOCH T1 | 11 | 2.81 | 0.0955 | 2.8202 | 2.8852 | 3.0246 | 3.39 | 3.865 | 4.3996 | 4 | 39%
BALA T1 | BALA T1 | 11 | 3.3541 | 0.062907 | 3.4128 | 3.4195 | 3.5281 | 3.9466 | 4.4005 | 4.9649 | 7.5 | 39%
BARMOUTH T1 | BARMOUTH T1 | 11 | 2.2783 | 0.3182 | 2.433 | 2.4265 | 2.5147 | 2.7814 | 3.0932 | 3.4771 | 7.5 | 39%
BLAENAU FFESTINIOG T1 | BLAENAU FFESTINIOG T1 | 11 | 1.726 | -0.1087 | 2.1246 | 2.1826 | 2.1984 | 2.3246 | 2.4444 | 2.6259 | 4 | 39%
BLAENAU PLASTICS T1 / BLAENAU PLASTICS T2 | BLAENAU PLASTICS T1 | 11 | 1.057 | 0.59077 | 2.1489 | 2.2243 | 2.2977 | 2.5247 | 2.7598 | 3.0443 | - | - | Demand data redacted
| BLAENAU PLASTICS T2 |  | 1.0678 | -0.26975
BOTWNNOG T1 | BOTWNNOG T1 | 11 | 2.198 | 0.144 | 2.2496 | 2.2006 | 2.2319 | 2.4066 | 2.5916 | 2.8202 | 7.5 | 39%
BUTLINS T1 | BUTLINS T1 | 11 | 2.4758 | 0.15684 | 2.9116 | 2.81 | 2.7838 | 2.8754 | 2.917 | 3.0105 | 7.5 | 39%
CARMEL T1 | CARMEL T1 | 11 | 2.6942 | 0.17781 | 2.8871 | 2.7868 | 2.8416 | 3.0084 | 3.2495 | 3.543 | 4 | 39%
CEMMAES RD T1 | CEMMAES RD T1 | 11 | 2.4546 | 0.060499 | 2.4617 | 2.4411 | 2.5118 | 2.9021 | 3.2685 | 3.7349 | 4 | 39%
CORWEN T1 | CORWEN T1 | 11 | 3.7843 | 0.25423 | 3.8668 | 3.8271 | 3.8926 | 4.2587 | 4.6076 | 5.066 | 7.5 | 39%
CWM DYLI T1 | CWM DYLI T1 | 11 | 0.918 | -0.07485 | 0.92384 | 1.3158 | 1.3391 | 1.4743 | 1.5836 | 1.7439 | 4 | 39%
DOLGELLAU T1 | DOLGELLAU T1 | 11 | 3.948 | -0.164 | 4.0067 | 3.9795 | 4.0945 | 4.5834 | 5.0749 | 5.7149 | 7.5 | 39%
DYFFRYN ARDUDWY T1 | DYFFRYN ARDUDWY T1 | 11 | 2.1242 | 0.0678 | 2.1252 | 2.2017 | 2.2799 | 2.6357 | 2.9847 | 3.4142 | 7.5 | 39%
EDERN T1 | EDERN T1 | 11 | 3.0392 | 0.17143 | 3.0888 | 3.2142 | 3.3978 | 3.9123 | 4.4519 | 5.1198 | 4 | 39%
FOUR CROSSES T1 | FOUR CROSSES T1 | 11 | -4.6632 | 0.57738 | 2.3312 | 2.2978 | 2.3151 | 2.4597 | 2.5956 | 2.7648 | 4 | 39%
GLAN-YR-AFON T1 | GLAN-YR-AFON T1 | 11 | 0.7587 | 0.08467 | 2.2786 | 2.2267 | 2.2415 | 2.396 | 2.5269 | 2.7094 | 7.5 | 39%
HARLECH T1 | HARLECH T1 | 11 | 2.259 | 0.024486 | 2.2602 | 2.3553 | 2.4795 | 2.8785 | 3.209 | 3.6442 | 7.5 | 39%
LLANBEDROG T1 | LLANBEDROG T1 | 11 | 1.9939 | 0.054205 | 1.9946 | 2.0052 | 2.0665 | 2.3231 | 2.5816 | 2.9087 | 4 | 39%
LLANFROTHEN T1 | LLANFROTHEN T1 | 11 | 2.2902 | -0.08832 | 2.0535 | 2.1024 | 2.1832 | 2.5012 | 2.8346 | 3.2377 | 7.5 | 39%
MACHYNLLETH T2 | MACHYNLLETH T2 | 11 | 1.573 | -0.07272 | 1.5902 | 1.5889 | 1.6414 | 1.8549 | 2.0713 | 2.3457 | 4 | 39%
MAENTWROG T1 | MAENTWROG T1 | 11 | 1.5565 | -0.04475 | 1.5633 | 1.5981 | 1.6643 | 1.8689 | 2.0562 | 2.296 | 7.5 | 39%
MANOD T1 | MANOD T1 | 11 | 1.123 | 0.021699 | 1.1234 | 1.1796 | 1.2473 | 1.4486 | 1.6468 | 1.9006 | 4 | 39%
PORTHMADOG T1 / PORTHMADOG T2 | PORTHMADOG T1 | 11 | 2.1059 | -0.4062 | 4.2549 | 4.2042 | 4.3094 | 4.7672 | 5.2455 | 5.8725 | 10 | 39%
| PORTHMADOG T2 |  | 2.1481 | 0.4935
PWLLHELI T1 | PWLLHELI T1 | 11 | 3.5624 | 0.1274 | 3.5647 | 3.4341 | 3.4569 | 3.7247 | 3.9715 | 4.3254 | 7.5 | 39%
RHOSLAN T1 | RHOSLAN T1 | 11 | 3.2145 | 0.22821 | 3.2226 | 3.2516 | 3.3755 | 3.8106 | 4.3046 | 4.8899 | 7.5 | 39%
RIVALS T1 | RIVALS T1 | 11 | 1.3459 | -0.0087432 | 1.3459 | 1.428 | 1.5283 | 1.7517 | 2.0105 | 2.3079 | 4 | 39%
TRYWERYN T1 | TRYWERYN T1 | 11 | 1.1625 | 0.24065 | 1.6935 | 1.6342 | 1.637 | 1.754 | 1.8359 | 1.9675 | 4 | 39%
ALPOCO T1 | ALPOCO T1 | 11 | 2.1285 | 0.47798 | 2.1815 | 2.1508 | 2.1674 | 2.2949 | 2.4075 | 2.5545 | 7.5 | 39%
AMLWCH T1 / AMLWCH T2 | AMLWCH T1 | 11 | -0.000909 | -0.0003185 | 3.0892 | 3.1964 | 3.3392 | 3.7758 | 4.2648 | 4.8526 | 10 | 39% | AMLWCH T1 not operating at time of group peak demand
| AMLWCH T2 |  | 2.8813 | 0.0319
BEAUMARIS T1 / BEAUMARIS T2 | BEAUMARIS T1 | 11 | 1.827 | 0.029314 | 3.7336 | 3.7906 | 3.9303 | 4.3128 | 4.7608 | 5.2772 | 7.78 | 39%
| BEAUMARIS T2 |  | 1.9065 | -0.0048229
CAERGEILIOG T1 | CAERGEILIOG T1 | 11 | 3.6905 | -0.096895 | 3.6917 | 3.9254 | 4.0235 | 4.3935 | 4.8923 | 5.3737 | 7.5 | 39%
CEMAES BAY T1 | CEMAES BAY T1 | 11 | 1.4516 | -0.0594 | 1.6713 | 1.6985 | 1.7793 | 2.0013 | 2.2514 | 2.5398 | 4 | 39%
GAERWEN VIEW T1 | GAERWEN VIEW T1 | 11 | 1.669 | 0.33556 | 1.7024 | 1.7052 | 1.7247 | 1.8618 | 1.9702 | 2.1307 | 7.5 | 39%
LLAINGOCH T1 | LLAINGOCH T1 | 11 | 3.1347 | -0.028019 | 3.1348 | 3.0419 | 3.2084 | 3.5647 | 4.0293 | 4.6187 | 7.5 | 39%
HOLYHEAD T1 | HOLYHEAD T1 | 11 | 2.6352 | 0.21351 | 2.6438 | 2.6349 | 2.7072 | 2.9285 | 3.1945 | 3.5035 | 7.5 | 39%
LLANDDEUSANT T1 | LLANDDEUSANT T1 | 11 | 3.1201 | 0.16458 | 3.657 | 3.5925 | 3.6719 | 3.9323 | 4.2377 | 4.6037 | 7.5 | 39%
LLANDEGFAN T1 | LLANDEGFAN T1 | 11 | 2.2935 | -0.26732 | 2.425 | 2.3681 | 2.3964 | 2.5541 | 2.7391 | 2.967 | 7.5 | 39%
LLANDYFRYDOG T1 | LLANDYFRYDOG T1 | 11 | 2.18 | 0.065333 | 2.3027 | 2.2705 | 2.311 | 2.5299 | 2.7312 | 3.0112 | 7.5 | 39%
LLANFAELOG T1 | LLANFAELOG T1 | 11 | 2.6572 | 0.07392 | 2.6582 | 2.6172 | 2.636 | 2.7689 | 2.8883 | 3.0618 | 4 | 39%
LLANFAIR PG T1 | LLANFAIR PG T1 | 11 | 4.0534 | 0.17029 | 4.057 | 3.9578 | 4.0351 | 4.3665 | 4.7203 | 5.1776 | 7.5 | 39%
LLANGAFFO T1 | LLANGAFFO T1 | 11 | 3.6129 | 0.1252 | 3.615 | 3.583 | 3.6172 | 3.8395 | 4.0526 | 4.3567 | 7.5 | 39%
LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | LLANGEFNI IND EST T1 | 11 | 3.047 | 0.6002 | 6.3546 | 6.2058 | 6.1841 | 6.3984 | 6.5223 | 6.7365 | 10 | 39%
| LLANGEFNI IND EST T2 |  | 3.1718 | 0.706
LLANGEFNI T1 | LLANGEFNI T1 | 11 | 3.839 | 0.155 | 3.8593 | 3.8011 | 3.8489 | 4.1497 | 4.433 | 4.8226 | 7.5 | 39%
MONA T1 | MONA T1 | 11 | 0.65117 | -0.18469 | 1.7323 | 1.7386 | 1.7712 | 1.916 | 2.0606 | 2.2448 | 7.5 | 39%
PARC CYBI T1 / PARC CYBI T2 | PARC CYBI T1 | 11 | 1.4217 | 0.1091 | 2.8604 | 2.8617 | 2.9099 | 3.1432 | 3.3533 | 3.6206 | 10 | 39%
| PARC CYBI T2 |  | 1.4298 | 0.1156
PENTRAETH T1 | PENTRAETH T1 | 11 | 4.3385 | 0.009792 | 4.3471 | 4.2644 | 4.3079 | 4.6781 | 5.0019 | 5.4513 | 7.5 | 39%
RAF VALLEY T1 | RAF VALLEY T1 | 11 | 1.8817 | 0.096143 | 1.8841 | 1.9605 | 2.0461 | 2.3156 | 2.5962 | 2.9437 | - | - | Demand data redacted
VAUXHALLS | VAUXHALLS T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| VAUXHALLS T3 |  | - | -
| VAUXHALLS T4 |  | - | -
| VAUXHALLS T5 |  | - | -
BR STEELWORKS | BR STEELWORKS T1 | 6.6 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| BR STEELWORKS T2 |  | - | -
BRITSH GYPSUM T1 T2 T3 T4 | BRITSH GYPSUM T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| BRITSH GYPSUM T2 |  | - | -
| BRITSH GYPSUM T3 |  | - | -
| BRITSH GYPSUM T4 |  | - | -
YORKSHIRE IMPERIAL METALS | YORKSHIRE IMPERIAL METALS T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| YORKSHIRE IMPERIAL METALS T2 |  | - | -
FIBREGLASS | FIBREGLASS | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
BURTONHEAD ROAD (WATSON STREET T1 T2) | BURTONHEAD ROAD (WATSON STREET T1) | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| BURTONHEAD ROAD (WATSON STREET T2) |  | - | -
DISTA PRODUCTS | DISTA PRODUCTS T1 | 11 | - | - | - | 0 | 0 | 0 | 0 | 0 | - | - | Demand data redacted
| DISTA PRODUCTS T2 |  | - | -
| DISTA PRODUCTS T3 |  | - | -
| DISTA PRODUCTS T4 |  | - | -

## Table 3 - System Loads_EHV
TABLE 3 - LOAD INFORMATION
(1) Group Maximum Demand increased by measured distribution generation to provide true system demand.
Substations |  | Voltage Level | Transformer flows at group maximum demand - previous year (2022/2023) |  |  | Forecast Load Information |  |  |  |  | Group Firm Capacity | Minimum load scaling factor | Comments
[6 empty] | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028
S/S Group | S/S Name | kV | MW | MVAr | MVA(1) | MVA | MVA | MVA | MVA | MVA | MVA | %
ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 | 33 | 9.4559 | 4.3778 | 36.1457 | 37.1264 | 37.9794 | 39.3794 | 42.3949 | 46.4518 | 45.4 | 39%
| RHYDLYDAN GT1 |  | 0.453 | -4.22
| AINTREE GT1 |  | 25.6962 | -13.2055
| FORMBY GT2A |  | 23.9119 | 5.04
| LITHERLAND GT1B |  | 27.0998 | 6.3816
| AINTREE GT2 |  | 18.3421 | -7.2854
| FAZAKERLEY GT1 |  | 12.04 | 0.3804
| GILLMOSS GT2 |  | 20.66 | 4.674
AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | AMLWCH GT1 | 33 | 14.2844 | -0.30968 | 48.511 | 50.702 | 51.8156 | 53.5204 | 57.5723 | 62.8808 | 72.54 | 39%
| CAERGEILIOG GT1 |  | 13.3938 | -0.80216
| CAERGEILIOG GT2 |  | 13.6049 | -0.54764
BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 | 33 | 23.235 | 11.786 | 47.6351 | 48.9448 | 49.6531 | 51.1974 | 54.5864 | 59.0426 | 82.07 | 39%
| CAERNARFON GT2 |  | 18.565 | -2.6067
BOLD G4A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | BOLD G4A | 33 | 2.8782 | 0.12123 | 81.0816 | 86.3749 | 93.2181 | 94.1224 | 95.2354 | 97.2928 | 110.59 | 39% | WIDNES GT2 open standby for fault level control I 2021/22. Operating in 2022/23.
| PRESCOT GT1 |  | 16.2491 | -6.915
| WIDNES GT1 |  | 19.794 | 3.4268
| WIDNES GT2 |  | 15.6862 | 3.4365
BOOTLE GT1 / LITHERLAND GT1A | BOOTLE GT1 | 33 | 0.64708 | 3.8006 | 45.6447 | 45.4103 | 45.6105 | 46.7835 | 48.6148 | 51.2167 | 68.63 | 39% | Data issues with LITHERLAND GTs. Using last year's value.
| LITHERLAND GT1A |  | 1.8128 | 1.9886
BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A | 33 | 27.293 | 4.619 | 85.5909 | 82.7744 | 82.1765 | 82.3904 | 83.4695 | 85.7913 | 138.1 | 39%
| BURLINGTON ST GT1 |  | 29.626 | 0.257
| LISTER DV A GT2 |  | 28.118 | 4.846
BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | BROMBOROUGH GT2 | 33 | 12.918 | -3.488 | 81.4317 | 81.271 | 81.9306 | 84.4978 | 88.7339 | 94.7596 | 88.1 | 39% | HOOTON PK GT1A open standby for fault level control
| ELLESMERE PORT GT1 |  | 16.707 | 1.137
| HOOTON PK GT1A |  | 0 | 0
| HOOTON PK GT2A |  | 17.623 | 1.263
BROMBOROUGH GT3 / ROCK FERRY GT2 | BROMBOROUGH GT3 | 33 | 14.955 | -2.834 | 48.1264 | 48.716 | 49.431 | 51.2323 | 54.0118 | 57.84 | 71.42 | 39%
| ROCK FERRY GT2 |  | 14.504 | -3.18
BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 | 33 | 19.543 | 2.286 | 119.7005 | 119.4668 | 121.2515 | 124.516 | 129.5828 | 136.9577 | 154.7 | 39%
| LEGACY LOCAL GT1 |  | 19.192 | 2.173
| MARCHWIEL GT1 |  | 21.257 | 3.856
| MARCHWIEL GT2 |  | 20.909 | 3.291
| WREXHAM GT1 |  | 20.004 | 2.359
BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 | 33 | 15.205 | 0.47 | 60.5992 | 60.8258 | 61.4017 | 68.0329 | 71.4365 | 76.0688 | 81.99 | 39%
| HAWARDEN GT2 |  | 21.725 | 3.544
| HOLYWELL GT2 |  | 18 | 7.852
BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 | 33 | 25.784 | -2.788 | 81.3921 | 81.0264 | 81.387 | 82.542 | 84.3398 | 87.2217 | 139.03 | 39%
| LISTER DV B GT1 |  | 25.282 | 2.329
| PARADISE ST GT1 |  | 27.765 | 2.815
CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CASTLE CEMENT GT1 | 33 | 15.762 | 3.083 | 85.9921 | 86.6732 | 87.3264 | 90.1506 | 95.2945 | 102.3313 | 119.75 | 39% | SALTNEY G2B open standby for fault level control
| HAWARDEN GT1 |  | 16.221 | 2.643
| SALTNEY GT1 |  | 14.2675 | 2.5506
| SALTNEY G2B |  | -0.001812 | 0.002235
CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 | 33 | 33.673 | -3.208 | 107.2439 | 106.479 | 107.4072 | 119.173 | 121.2562 | 124.749 | 128.6 | 39% | SALTNEY G2A open standby for fault level control
| CRANE BANK GT1 |  | 35.393 | 2.052
| GUILDEN SUTTON GT1 |  | 34.554 | 1.861
| SALTNEY G2A |  | 0 | 0
COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 | 33 | 20.975 | -0.38956 | 63.4893 | 64.0173 | 65.0868 | 67.4846 | 72.3516 | 78.8286 | 92.5 | 39%
| COLWYN BAY GT2 |  | 19.1114 | -0.79018
| DOLGARROG GT2 |  | 14.367 | -1.7458
COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 | 33 | 17.8676 | 2.4645 | 119.0691 | 149.3979 | 157.8515 | 166.9356 | 174.0346 | 187.8916 | 197.4 | 39%
| CREWE GT1 |  | 16.72 | 1.287
| CREWE GT2A |  | 16.746 | -2.632
| CREWE GT4A |  | 16.6837 | -1.938
| RADWAY GREEN GT1 |  | 17.935 | 2.706
| RADWAY GREEN GT2 |  | 17.977 | 0.348
| WHITCHURCH GT2 |  | 12.8594 | -0.55205
DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | DEESIDE PK GRID GT1 | 33 | 9.76 | -0.492 | 37.991 | 39.7577 | 39.8419 | 45.5626 | 45.7366 | 50.765 | 51.66 | 39%
| SIXTH AVE GRID GT1 |  | 10.508 | 4.896
DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | DUTTON GT2 | 33 | 20.869 | 2.666 | 67.0755 | 82.2927 | 83.0227 | 85.1083 | 87.1647 | 90.5672 | 106.24 | 39%
| MOORE GT1 |  | 16.933 | -3.195
| PERCIVAL LA GT1 |  | 16.531 | 2.026
ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | ELLESMERE PORT GT2 | 33 | 12.367 | 2.002 | 46.1887 | 46.9435 | 47.5623 | 50.4394 | 53.8697 | 58.3431 | 100.57 | 39%
| INCE LOCAL GT1 |  | 15.252 | -3.197
| INCE LOCAL GT2 |  | 15.93 | 2.619
FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | FORMBY GT2B | 33 | 17.553 | -1.749 | 61.0052 | 60.4549 | 61.0836 | 62.9581 | 66.6105 | 71.5931 | 75 | 39%
| SOUTHPORT GT1 |  | 22.883 | -0.753
| SOUTHPORT GT2 |  | 20.231 | -0.956
FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 | 33 | 15.3492 | 0.13553 | 62.7383 | 66.7411 | 68.5938 | 71.9753 | 79.1376 | 88.2257 | 69.57 | 39%
| MAENTWROG GT1 |  | 4.879 | -2.85
| MAENTWROG GT2 |  | 4.6551 | -2.0055
GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | GARSTON GT2 | 33 | 18.03 | -0.73 | 55.3128 | 54.7396 | 54.7188 | 55.55 | 57.275 | 59.8326 | 108.25 | 39%
| SPEKE GT3 |  | 16.9634 | 0.21844
| WAVERTREE GT1A |  | 20.265 | -2.046
GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | GATEACRE GT1 | 33 | 31.356 | 0 | 87.185 | 86.0038 | 86.5673 | 88.8315 | 93.2899 | 99.7323 | 114.83 | 39% | KIRKBY GT3 not operating at time of group peak demand. KIRKBY GT3 tag stuck at likely time of peak, so last year's value is used.
| HUYTON GT1 |  | 25.286 | 0.73178
| KIRKBY GT3 |  | 0.0012956 | 0
| PRESCOT GT1A |  | 30.383 | -5.991
GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | GILLMOSS GT1 | 33 | 17.563 | 2.739 | 52.36 | 51.418 | 51.489 | 52.0674 | 53.2907 | 55.4398 | 90.2 | 39%
| KIRKBY GT2 |  | 14.6815 | 1.041
| SIMONSWOOD GT1 |  | 19.777 | 1.476
HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | HALEWOOD G1B | 33 | 0 | 0 | 26.29 | 27.8555 | 28.0905 | 28.4758 | 28.9292 | 30.0168 | 64.13 | 39% | HALEWOOD G1B and HALEWOOD G2B normally open (not operating at time of group peak demand)
| HALEWOOD G2B |  | 0 | 0
| HALEWOOD GT3 |  | 12.714 | -1.486
| SPEKE GT1A |  | 13.4044 | 4.4478
HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | HESWALL GT1 | 33 | 22.404 | -0.039 | 62.4954 | 63.2318 | 64.3792 | 66.8095 | 71.5142 | 77.779 | 86.9 | 39%
| HOYLAKE GT2 |  | 17.336 | -3.7
| PRENTON GRID GT3 |  | 22.5942 | -0.74674
HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 | 33 | 16.056 | 1.874 | 89.41 | 87.2504 | 88.2338 | 94.205 | 100.2562 | 108.3492 | 112.91 | 39%
| RHYL GT1 |  | 20.564 | 0.31057
| ST ASAPH GT2 |  | 15.4579 | 0.53114
| ST ASAPH GT4 |  | 14.6351 | 0.13921
LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 | 33 | 30.4616 | -4.1643 | 94.47 | 75.9567 | 75.4495 | 76.4126 | 77.6415 | 80.4548 | 138.4 | 39%
| SPARLING ST GT1 |  | 32.1797 | 0.53531
| WAVERTREE GT2 |  | 31.6275 | 0.88183
PRENTON GRID GT1 / ROCK FERRY GT1 | PRENTON GRID GT1 | 33 | 26.4928 | 0.60711 | 54.98 | 54.6943 | 55.4582 | 57.0934 | 60.7189 | 65.3731 | 74.42 | 39%
| ROCK FERRY GT1 |  | 28.465 | 0.8
WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | WALLASEY GT1 | 33 | 12.9363 | 0.33229 | 54.0206 | 52.0156 | 51.8645 | 52.8209 | 54.3425 | 56.82 | 94.98 | 39%
| WALLASEY GT2 |  | 14.3725 | 0.49784
| WOODSIDE GT2 |  | 12.962 | -4.607
BOLD G4B / RAVENHEAD G1A2 / ST HELENS GT2A | BOLD G4B | 33 | 0 | 0 | 25.9741 | 25.5231 | 25.5832 | 26.0311 | 26.9253 | 28.2819 | 64.5793 | 39% | BOLD G4B not operating at time of group MD
| RAVENHEAD G1A2 |  | -0.000801 | 0.001174
| ST HELENS GT2A |  | 17.06 | 1.8114
RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAVENHEAD G1A1 | 33 | 0 | 0 | 47.6426 | 47.4873 | 47.7314 | 48.96 | 51.2612 | 54.447 | 69.1112 | 39% | RAVENHEAD G1A1 not operating at time of group peak demand
| ST HELENS GT2B |  | 15.748 | -4.183
| WINDLE GT1 |  | 14.929 | 4.431
DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 | 33 | 30.9637 | 5.9153 | 92.6988 | 92.4589 | 93.6699 | 96.1364 | 100.2721 | 106.2196 | 102.9507 | 39%
| SANKEY BRIDGES GT1 |  | 27.029 | -9.9926
| WARRINGTON GT3 |  | 34.614 | -0.054
SANKEY BRIDGES GT3 / WARRINGTON GT5 | SANKEY BRIDGES GT3 | 33 | 12.0994 | -5.0507 | 59.8456 | 59.1277 | 59.3294 | 60.4173 | 62.8204 | 66.3433 | 75.3612 | 39%
| WARRINGTON GT5 |  | 12.955 | 0.436
ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 | 33 | 3.3219 | -2.222 | 55.167 | 55.4684 | 56.126 | 57.3607 | 60.6753 | 65.0122 | 85.36 | 39%
| ELWORTH GT2 |  | 3.8568 | 2.8502
| KNUTSFORD GT1 |  | 14.4585 | 1.0295
| KNUTSFORD GT2 |  | 14.0037 | 1.6192
HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 | 33 | 17.816 | -0.973 | 80.5574 | 81.8797 | 82.5096 | 84.9991 | 89.4495 | 95.6052 | 112.972 | 39%
| LOSTOCK GT2 |  | 18.3093 | 0.2108
| WINSFORD GT1 |  | 15.6917 | 1.0073
| WINSFORD GT2 |  | 13.3887 | 1.3901
LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 | 33 | 19.47 | 2.382 | 98.9966 | 100.2926 | 101.781 | 104.7237 | 111.491 | 120.5207 | 174.4 | 39%
| NEWTOWN GT2 |  | 6.78 | 4.036
| OSWESTRY GT8 |  | 26.8987 | 11.453
| WELSHPOOL GT1 |  | 8.6133 | 6.2769
OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 | 33 | 25.9707 | 8.0586 | 55.3471 | 56.568 | 57.0912 | 58.3379 | 61.734 | 66.1539 | 68.9 | 39%
| WHITCHURCH GT1 |  | 22.3995 | 4.9492