## GSP
Area | Grid Supply Point Name | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification
ENGLAND | AMERSHAM | 11.4/21.9 | 51.6652 | -0.65572 | SU93079712 | Shared Site | 0 | 31 | 129 | 48.6 | 275 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No |  | 400/132 | Green
ENGLAND | AXMINSTER | 11.26/21.9 | 50.7868 | -2.9216 | SY35139899 | Shared Site | 0 | 27.4 | 119.3346 | 213.6 | 5.5 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRIDConstrained Hotwiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating (NGET-RI-33539 Re-conductor the Fleet - Lovedean OHL circuits to increase capacity (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Partially Constrained | 132kV circuit reinforcement includes 0.3km circuit1 cable section as part of a Dual 132kV Cable. 3rd 132kV CCT between Axminster - Yeovil triggered. Yeovil BSP 2 x 60MVA transformers to be upgraded to 2 x 90MVA units. Completion date TBC. | 01/03/23 | Yes | Yes |  | 400/132 | Amber
ENGLAND | BOTLEY WOOD GSP | 11.09/40.0 | 50.8847 | -1.2327 | SU54070975 | 315 | 0 | 47.9107 | 209.8 | 193.1 | 13.9 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRIDConstrained Re-conductor the Fleet - Lovedean OHL circuits to increase capacity (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Unconstrained |  |  | No | Yes | Proximity to triggering SoW | 400/132 | Amber
ENGLAND | BRAMLEY (ANDO-THAT) | 10.15/NA* | 51.3374 | -1.0765 | SU64436022 | 274 | 0 | 72.409 | 244.5125 | 280.41 | 60 | 95 | Unconstrained |  |  | Constrained | Andover to be fed by Melksham, swapping Amesbury-Andover supplies. Ashford Hill compound - Thatcham 132kV reconfiguration scheme. | 01/06/21 | Yes | Yes | Moderate proximity to thermal rating for Bramley- Amesbury 132kV circt under FCO. No 132kV substation at Bramley just transformer feeder circuits (*). | 400/132 | Green
ENGLAND | BRAMLEY (BASI) | 13.28/NA* | 51.3374 | -1.0765 | SU64436022 | 255 | 52.6 | 60.85 | 196.9358 | 289.288 | 0 | 95 | Constrained |  |  | Constrained |  |  | Yes | Yes | No 132kV substation at Bramley just transformer feeder circuits(*). No reverse power headroom at supergrid transformer level. SOW required to be submitted to NG to confirm reverse power headroom | 400/132 | Red
ENGLAND | CHICKERELL GSP | 14.96/15.3 | 50.623 | -2.4888 | SY65528048 | 290 | 0 | 27.7 | 100.1768 | 121.6 | 10 (additional through SOW or headroom transfer) | 90 | Constrained | Latest update on Feb, 2023: Following the latest PP blulk submission result received from NG, a new 3rd SGT is to be triggered, associated with further 400kV reinforcement work requried. The expected completion date in after 2037. NATIONAL GRIDConstrained Hotwiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating (NGET-RI-33539) Re-conductor the Fleet - Lovedean OHL circuits to increase capacity (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Constrained | 3rd BSP Tx reinforcement triggered, to be completed by 2024; Reinforcement is triggered to take Redlands PSS off the meshed 33kV networks. A new 33kV circuit interconnecting Winterbourne Abbas and Yeovil BSP is proposed. |  | No | No | There is no 132kV network at Chickerell GSP, 3rd BSP Tx has been triggered. Further 33kV connection might trigger 4th BSP Tx, and transforming 132kV switchgears indoor due to space concern. | 400/132 | Red
ENGLAND | COWLEY | 14.20/31.5 | 51.7102 | -1.1906 | SP56020158 | 864 | 0 | 256.28 | 768.5417 | 1250.012 | 0(additional through SOW or headroom transfer) | 95 | Partially Constrained | Transmission works triggered by NG: Uprating of the Cowley - Walham / Cowley Minety 400kV circuit as well as the Bramley – Didcot 400kV circuits | 2027-11-01 | Unconstrained |  |  | Yes | Yes |  | 400/132 | Green
ENGLAND | EALING | 20.0/21.9 | 51.5018 | -0.29601 | TQ18377947 | 3x180 + 1x180 |  | 122 | 317.8 | 13.7 | 383.3 | 95 | Unconstrained |  |  | Constrained | EALING 66kV CB to be replaced to improve fault ratings | TBC | Not known | No |  | 275/66 | Red
ENGLAND | EAST CLAYDON | 10.52/TBC* | 51.9267 | -0.90926 | SP75102592 | Shared site | 0 | 10.92 | 56.036 | 193.611 | SOW to be submitted due to limited fault level headroom. | 95 | Partially Constrained | NG fault level reinforcements triggered following SoW | 2025-12-01 | Partially Constrained |  |  | Yes | No | Moderate proximity to thermal rating on 132kV circt Bicester North - East Claydon under FCO | 400/132 | Amber
ENGLAND | FAWLEY | 19.68/31.5 | 50.8207 | -1.3307 | SU47240256 | 240 | 0 | 127.8829 | 319 | 795.204 | 0 | 95 | Constrained | NATIONAL GRIDConstrained Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity. (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Constrained |  |  | Yes | No | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. ANM scheme in place on IOW to ease some of the 132kV constraints. Large scale 132kV reinforcement to be triggered to create more headroom for existing ANM scheme 3rd SGT energised, to be de-coupled with Nursling | 400/132 | Red
ENGLAND | FLEET BRAMLEY | 25.03/31.5 | 51.2499 | -0.8815 | SU78165068 | 2016 | 52.6 | 454.9055 | 1234.4353 | 1064.507 | GSP under SOW. Headroom TBC following response from NG | 95 | Constrained | NATIONAL GRIDConstrained Re-conductor the Bramley - Fleet OHL circuits to increase capacity (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Constrained |  |  | Yes | Yes | Near to thermal rating on part of MAID-WOKI 132kV circts. 132kV s/gear at Fleet full for f.level capacity.132kV upgrade rqd. thermal rating close on WOKHAM-BRACK-CAMB under SCO 132 kV switchgear at Fleet to be replaced with indoor GIS | 400/132 | Amber
ENGLAND | IVER 132KV | 20.0/20.0 | 51.5418 | -0.49771 | TQ04288361 | 720 | 99 | 378.7 | 720 | 286.04 | 776.7 | 95 | Unconstrained |  |  | Constrained | Iver 132kV CBs to be replaced to improve fault ratings | Q1 2027 in line with demand reinforcement | ModApp rqd | No |  | 400/132 | Red
ENGLAND | IVER 66KV | 15.92/40.0 | 51.5418 | -0.49771 | TQ04288361 | 299 | 0 | 123.2 | 299 | 0 | 375.9 | 95 | Unconstrained |  |  | Unconstrained |  |  | ModApp rqd | No | Moderate proximity to thermal rating for 66kV circuit Iver to Northolt under FCO | 275/66 | Green
ENGLAND | LALEHAM | 19.4/31.5 | 51.4246 | -0.46933 | TQ06527062 | 2x180 2x240 |  | 244.8 | 562.7 | 443.2 | 372 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No |  | 275/132 | Green
ENGLAND | LOVEDEAN | 14.70/25.0 | 50.917 | -1.0403 | SU67561350 | 876 | 0 | 200.95 | 667.3476 | 570.181 | 21.48 (additional through SOW or headroom transfer) | 95 | Constrained | NATIONAL GRIDConstrained Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity. (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | 31st October 2024 (Interim constraints prior to completion) | Partially Constrained |  |  | Yes | Yes | Moderate proximity to L-E fault level issue at 132kV switchgears. | 400/132 | Amber
ENGLAND | MANNINGTON GSP | 25/40 | 50.8465 | -1.8946 | SU07520522 | 960 | 31 | 387.1 | 1049 | 1069.309 | 0 | 95 | Constrained | Attributable Enabling Works (2023 Feb received) NGESO Project number: 102387-204878 • Extension of 400kV busbar for the installation of a new 240MVA, 400/132kV at Mannington 400kV substation Previous: NATIONAL GRIDConstrained Hotwiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating (NGET-RI-33539) Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. (NGET-RI-31671-2) Re-conductor the Bramley - Fleet OHL circuits to increase capacity. (NGET-RI-31671-1) Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. (NGET-RI-30752) | Dec 2036 for new SGT. Previous reinforcement work: 31st October 2024 (Interim constraints prior to completion) | Partially Constrained | Replacement of A205 CB, reinforcement of section of Mannington- Salisbury 132kV circt | 01/06/22 | Yes | Yes | Mannington GSP 132kV CBs reinforcement has been triggered. Any connection will pay 2nd comer charge. Timescale of the reinforcment 3 to 4 years. The 132kV circuit ring for Mannington GSP - Salisbury BSP - Shaftesbury BSP - POOL - LYTCHETT BSP - Mannington GSP has reached its thermal limit for reverse power flow (export capacity). Any more generation connection under the relevant network will trigger 132kV level major reinforcement if the new connetion cuases reverse power flow at 132kV level. | 400/132 | Amber
ENGLAND | MELKSHAM | 26.76/40 | 51.3919 | -2.1504 | ST89636588 | Shared site | 105.1 | 112.3 | 898.6 | 2198.5 | National Grid reinforcement required - 0MW available before completion of transmission reinforcement | 95 | Constrained | National Grid reinforcement works required to install a new SGT at Melksham, reconductor transmission line, estimated completion date Oct 2027 - 2029 | 2029-10-01 | Partially Constrained | Andover to be fed by Melksham, swapping Amesbury-Andover supplies. | 31/03/2023 | No | No | No spare bay at Melksham GSP for 132kV connections. Proximity to L-E fault level issue. N-2 & N-1 SGT capacity contraint | 400/132 | Red
ENGLAND | MINETY | 17.42/40.0 | 51.6075 | -2.0013 | SU00018985 | 885 | 118.9 | 179.4 | 659.3526 | 1028.431 | National Grid reinforcement required - 0MW available before completion of transmission reinforcement | 95 | Constrained | National Grid reinforcement works required to install a new SGT at Minety, estimated completion date Oct 2028 | 2028-10-01 | Partially Constrained |  |  | No | No | No spare bay at Minety GSP for 132kV connections. Future connections on Minety GSP will need ANM under N-2, due to NG SGT constraints. N-1 SGT capacity issue. | 400/132 | Red
ENGLAND | NORTH HYDE | 14.29/25.0 | 51.4992 | -0.41151 | TQ10367900 | 300 | 0 | 135.9 | 300 | 0 | 477.9 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No | None Known | 275/66 | Green
ENGLAND | NURSLING | 19.54/31.05 | 50.9409 | -1.488 | SU36071584 | 480 | 280 | 115.3136 | 620 | 663 | 0 | 95 | Constrained | 4th SGT triggered | 31st October 2031 | Partially Constrained |  |  | Yes | Yes | Proximity to L-E fault level issue. Constraints might be needed for when Fawley-Nursling GSPs are solidly coupled. No 132kV bay at Nursling GSP. Mod App required SoW required | 400/132 | Red
ENGLAND | WILLESDEN | 16.7/21.9 | 51.5349 | -0.25714 | TQ20988322 | 3 x 180 |  | 183.8 | 336.7 | 6.3 | 519 | 95 | Unconstrained |  |  | Unconstrained |  |  | Not known | No |  | 275/66 | Green
9
234

## BSP
Area | Bulk Supply Point Name | GSP Parent | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate Rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification
ENGLAND | ACTON LANE | WILLESDEN | 12.2/19.7 | 51.5343 | -0.25969 | TQ 20805 83142 | 4 x 40 | - | 14 | 39.2 | - | 74 | 50 | Constrained |  |  | Constrained | Andover-Amesbury reconfiguration. Switchgear reinforcement. |  | Yes | No | None known | 66/22 | Red
ENGLAND | ALDERSHOT | FLEET BRAMLEY | 17.22/25 | 51.2317 | -0.77077 | SU 85922 48779 | 228 | 0 | 29.9955 | 129.7628 | 4.317 | 65 |  | Constrained |  |  | Unconstrained | Switchgear-C reinforcement (FL results include new rating). | 01/03/2020 | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 132/33 | Red
ENGLAND | ALTON & FERNHURST | FLEET BRAMLEY | 18.04/17.5 | 51.1526 | -0.96149 | SU 72730 39772 | 200 | 45.97 | 17.56 | 75.6276 | 147.084 | 15 |  | Constrained |  |  | Constrained | Load blinder reinforcement. Switchgear-C reinforcement @ Fernhurst. Only Flexible headroom available on the 132 kV circuits from Fleet. | 01/06/2021 | Yes | Yes | Alton Fernhurst group to be split. 33kV circuit constraint at Alton BSP. Reinforcement triggered at Alton which will allow for space for connections and increased fault level headroom, but will have a 2030 completion date. Limited flexible headroom on the 132kV circuits from Alton/Fernhurst back to Fleet | 132/33 | Red
ENGLAND | AMESBURY | BRAMLEY (ANDO-THAT) | 10.20/25.0 | 51.1835 | -1.7747 | SU 15842 42724 | 90 | 0 | 14.34 | 56.1294 | 27.74 | 15 |  | Constrained |  |  | Constrained | Alton / Fernhurst split capital scheme and a new 132 kV switchboard to be installed at ALTO/FERN tee. | 01/12/2026 | No | No | limited by Ashfordhill-Andover 132kV circuit, totally full - only flexible export capacity available | 132/33 | Red
ENGLAND | ANDOVER | MELKSHAM | 14.58/17.5 | 51.2175 | -1.4955 | SU 35334 46598 | 180 | 0 | 16.0272 | 95.5205 | 112.566 | 0 | 95 | Constrained | a new SGT and reconductoring | 2027-10-01 | Constrained | Andover-Amesbury reconfiguration. New BSP transformer installation with CB reinforcement and 132kV switchyard conversion to indoor. | 31/03/2026 | No | No | Thermal constraint on upstream 132kV system with no headroom; There is no space for new 33kV CB connections; National Grid reinforcement works required for Melk SGT capacity constraints, estimated connection date for new applications is 2027. | 132/33 | Red
ENGLAND | ARNEWOOD | MANNINGTON GSP | 13.5/13.1 | 50.7746 | -1.6313 | SZ 26094 97294 | 60 | 0 | 11.5262 | 52.2467 | 17.919 | 0 |  | Constrained |  |  | Constrained | ARNEWOOD BSP 33kV CB reinforcement | 01/12/2023 | Yes | Yes | any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement | 132/33 | Red
ENGLAND | BASINGSTOKE T1A & T2A | BRAMLEY (BASI) | 13.49/17.5 | 51.2698 | -1.0678 | SU 65132 52710 | 78 | 52.63 | 17.74 | 68.222 | 37.95 | 27 |  | Constrained | Export loading on Bramley (Basingstoke) SGTs is at 100%. Modification application required to be submitted to National Grid for increased headroom. |  | Partially Constrained |  |  | No | No | No spare bay AND/OR space for extension. Fault level approaching limit at 33kV busbars | 132/32 | Red
ENGLAND | BASINGSTOKE T1B & T2B | BRAMLEY (BASI) | 13.90/17.5 | 51.2698 | -1.0678 | SU 65132 52711 | 90 | 25 | 16.4463 | 78.7106 | 79.358 | 35 |  | Constrained | Export loading on Bramley (Basingstoke) SGTs is at 100%. Modification application required to be submitted to National Grid for increased headroom. |  | Partially Constrained |  |  | No | No | No spare bay AND/OR space for extension. Fault level approaching limit at 33kV busbars | 132/33 | Red
ENGLAND | BASINGSTOKE T3 & T4 | BRAMLEY (BASI) | 11.16/17.5 | 51.2698 | -1.0678 | SU 65132 52712 | 90 | 0 | 12.611 | 66.0411 | 72.08 | 25 |  | Constrained | Export loading on Bramley (Basingstoke) SGTs is at 100%. Modification application required to be submitted to National Grid for increased headroom. |  | Partially Constrained |  |  | No | No | No spare bay AND/OR space for extension | 132/33 | Red
ENGLAND | BICESTER NORTH | EAST CLAYDON | 12.55/25 | 51.909 | -1.1333 | SP5972023735 | 90 | 39.105 | 11.2584 | 56.036 | 108.111 | 6.8 |  | Constrained |  |  | Constrained | 33kV circuit reinforcements between Bicester - Bicester North | 01/01/2025 | Yes | No | Constrained due to 132kV thermal limitations under FCO. | 132/33 | Red
ENGLAND | BOSTON MANOR | EALING | 15.2/25.0 | 51.4897 | -0.31558 | TQ 17043 78092 | 2 x 20/40 | - | 19.1 | 40.2 | 8.9 | 48 | 95 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 66/11 | Red
ENGLAND | BOTLEY WOOD | BOTLEY WOOD GSP | 14.86/25.0 | 50.8848 | -1.2327 | SU 54073 09759 | 90 | 0 | 10.2588 | 84.429 | 98.9 | 16 |  | Unconstrained |  |  | Unconstrained | Load blinder reinforcement |  | No | Yes | None known | 132/33 | Green
ENGLAND | BOURNEMOUTH | MANNINGTON GSP | 19.44/25.0 | 50.7315 | -1.9126 | SZ 06265 92437 | 150 | 0 | 36.4294 | 140.3466 | 14.92 | M86 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement | 132/33 | Amber
ENGLAND | BRACKNELL MAIN | FLEET BRAMLEY | 19.52/25.0 | 51.4173 | -0.7643 | SU 86026 69422 | 90 | 0 | 13.6031 | 67.2061 | 40 | 78 |  | Constrained |  |  | Constrained |  |  | Yes | Yes | Upstream thermal restrictions for SCO. Proximity to fault level when Bracknell is run solid. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP. | 132/33 | Red
ENGLAND | BRACKNELL RESERVE | FLEET BRAMLEY | 19.52/25.0 | 51.4173 | -0.7643 | SU 86026 69422 | 90 | 0 | 14.36 | 81.3201 | 3.71 | 73 |  | Constrained |  |  | Constrained |  |  | Yes | Yes | Upstream thermal restrictions for SCO. Proximity to fault level when Bracknell is run solid. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP. | 132/33 | Red
ENGLAND | BRIDGE ROAD | EALING | 12.7/18.4 | 51.469 | -0.34895 | TQ 14778 75741 | 3 x 20/40 | - | 16.2 | 54 | - | 92 | 95 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 66/11 | Red
ENGLAND | BURGHFIELD MAIN | FLEET BRAMLEY | 23.75/25.0 | 51.4293 | -1.0025 | SU 69442 70509 | 90 | 0 | 13.2683 | 67.9334 | 13.2 | 40 |  | Constrained |  |  | Unconstrained | 33kV switchboard replacement required |  | Yes | Yes | Moderate proximity to thermal rating on Reading to Burghfield 132kV circt under combined NG & SSE fault events. Fleet GSP 132kV switchgear saturated for fault level capacity. | 132/33 | Red
ENGLAND | BURGHFIELD RESERVE | FLEET BRAMLEY | 14.4/25.0 | 51.4293 | -1.0025 | SU 69442 70509 | 90 | 0 | 15.09 | 65.1843 | 80.35 | 58 |  | Constrained |  |  | Unconstrained | 33kV switchboard replacement required |  | Yes | Yes | Moderate proximity to thermal rating on Reading to Burghfield 132kV circt Fault level capacity saturated with a import-triggered reconfiguration on Burghfield BS Main and Reserve) | 132/33 | Red
ENGLAND | CAMBERLEY MAIN | FLEET BRAMLEY | 13.18/25.0 | 51.3279 | -0.75947 | SU 86530 59483 | 90 |  | 23.85 | 85.1784 | 0 | 85 |  | Constrained |  |  | Unconstrained | Switchgear-C reinforcement (FL results include new rating). | 01/03/2020 | Yes | Yes | Moderate upstream thermal restrictions for SCO. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 132/33 | Red
ENGLAND | CAMBERLEY RESERVE | FLEET BRAMLEY | 12.14/25.0 | 51.3279 | -0.75947 | SU 86530 59483 | 90 | 0 | 15.2721 | 70.155 | 22.45 | 80 |  | Constrained |  |  | Unconstrained | Switchgear-C reinforcement (FL results include new rating). | 01/03/2020 | Yes | Yes | Moderate upstream thermal restrictions for SCO. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 132/33 | Red
ENGLAND | CHALVEY | IVER 132KV | 22.32/25 | 51.505 | -0.60858 | SU 96669 79364 | 90 | 6 | 26 | 87.1 | 62.24 | 53.76 |  | Constrained |  |  | Unconstrained |  |  | No | No | None known | 132/33 | Green
ENGLAND | CHICHESTER & HUNSTON | LOVEDEAN | 17.06/25 | 50.8589 | -0.69023 | SU 92282 07416 | 270 | 11 | 38.54 | 182.22 | 225.37 | 0 |  | Constrained |  |  | Constrained | AVC &Load blinder and Switchgear-C reinforcement (FL results include new rating).The 75 MVA has already advised to reinforce to 90 MVA (2023).It will either requier a new BSP transformer or splitting the Chichester and Hunston. | 01/03/2025 | No | Yes | BSP transformers limitations under FCO. make fault rating reinforcement. | 132/33 | Red
ENGLAND | CHICKERELL | CHICKERELL GSP | 16.5/25 | 50.6233 | -2.4894 | SY 65479 80511 | 90 | 9 | 22.9428 | 100.1768 | 135.884 | 0 |  | Constraind | Latest update on Feb, 2023: Following the latest PP blulk submission result received from NG, a new 3rd SGT is to be triggered, associated with further 400kV reinforcement work requried. The expected completion date in after 2037. |  | Unconstrained | AVC and Load blinder reinforcement. Switchgear-C reinforcement (FL results include new rating). Will requier a third BSP transformer | 01/03/2022 | No | Yes | Close proximity to rating on short circt section. | 132/33 | Red
ENGLAND | CHIPPENHAM | MELKSHAM | 20.9/25 | 51.4674 | -2.1075 | ST 92629 74275 | 180 | 0 | 27.7776 | 111.8704 | 228.383 | 0 | 95 | Constrained | a new SGT and reconductoring | 2027-10-01 | Constrained | Switchgear-C, AVC, load blinder reinforcements. Malmesbury - Rodbourne Rail tee OHL reinforcement, and 3rd BSP transformer install, 33kV switchyard conversion to partial indoor | 01/06/2022 | No | No | Constrained due to BSP transformer limitation under FCO. National Grid reinforcement works required for Melksham SGT capacity constraints, estimated connection date for new applications is 2027. | 132/33 | Red
ENGLAND | CHRISTCHURCH | MANNINGTON GSP | 10.77/31.5 | 50.7379 | -1.7787 | SZ 15716 93165 | 90 | 0 | 17.0305 | 62.6142 | 121.0526 | 0 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement. BSP Transfomer rating limitation under N-1. | 132/33 | Amber
ENGLAND | CIPPENHAM | IVER 132KV | 14.6/25.0 | 51.5074 | -0.61431 | SU 96266 79634 | 90 | 0 | 16.2 | 55.5 | 0 | 106.2 |  | Constrained |  |  | Unconstrained |  |  | No | No | None known | 132/33 | Green
ENGLAND | CIRENCESTER | MINETY | 15.49/25 | 51.702 | -1.9623 | SP 02701 00368 | 90 | 28 | 10.36 | 64.6905 | 183.584 | 0 | 95 | Constrained | a new SGT | 2028-10-01 | Partially Constrained | AVC and Load blinder reinforcement, Minety - Cirencester 132kV circuit reinforcment | 01/06/2023 | No | Yes | Thermal constraint on BSP transformers. National Grid reinforcement works required for Minety SGT capacity constraints, estimated connection date for new applications is 2028 | 132/33 | Red
ENGLAND | COPLEY DENE | EALING | 14.7/13.1 | 51.5139 | -0.30889 | TQ 17445 80798 | 2 x 30/37.5 | - | 11.2 | 34.9 | - | 30 | 50 | Constrained |  |  | Constrained | EALING 66kV/22kV CB to be replaced to improve fault ratings / COPD PSS CB to be replaced to improved fault ratings | TBC | No | No |  | 66/11 | Red
ENGLAND | COWES & WOOTTON COMMON | FAWLEY | 20.34/25.0 | 50.7457 | -1.2853 | SZ 50519 94250 | 182 | 0 | 21.9529 | 121.7637 | 123.809 | 0 |  | Constrained | 132kV reinforcement to be triggered to create more headroom for ANM scheme |  | Constrained | 8x33kV CBs reinforcement at Cowes, Load blinder reinforcement at Wootton Common | 01/06/2024 | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. ANM scheme in place on IOW to ease some of the 132kV constraints. | 132/33 | Red
ENGLAND | COWLEY LOCAL MAIN | COWLEY | 13.18/25 | 51.7236 | -1.189 | SP 56113 03074 | 90 | 0 | 3.7376 | 58.0241 | 86.664 | 28.4 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 132/33 | Red
ENGLAND | COWLEY LOCAL RESERVE | COWLEY | 13.14/25.0 | 51.7236 | -1.189 | SP 56113 03074 | 90 | 0 | 17.7207 | 69.5302 | 65.709 | 71.6 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 132/33 | Green
ENGLAND | COXMOOR WOOD | FLEET BRAMLEY | 19.37/25.0 | 51.2512 | -0.87912 | SU 78324 50817 | 90 | 0 | 17.71 | 111.1732 | 89.91 | 15 |  | Constrained |  |  | Partially Constrained | Split of Coxmoor Wood-Pyestock BSP groups. | 01/03/2021 | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP. No fault level headroom at Coxmoor Wood, reinforcement required | 132/33 | Red
ENGLAND | DENHAM | IVER 132KV | 20.81/25 | 51.5782 | -0.53251 | TQ 01785 87618 | 90 | 20 | 26.8 | 77.9 | 50.9 | 65.9 |  | Constrained |  |  | Unconstrained |  |  | No | No | None known | 132/22 | Green
ENGLAND | DRAYTON | COWLEY | 23.23/25 | 51.6312 | -1.3269 | SU 46684 92706 | 180 | 18.95 | 29.8609 | 137.338 | 223.558 | 20 |  | Constrained | 2x 132kV cct reinforcements between Cowley - Drayton. An ANM scheme has also been triggered at those circuits. | 2024-11-01 | Constrained | AVC and load blinder reinforcements. 33kV CB reinforcements. | 01/05/2023 | No | No | Upstream thermal restrictions under FCO. | 132/33 | Red
ENGLAND | EALING (D) | EALING | 12.3/13.1 | 51.5018 | -0.296 | TQ 18371 79475 | 2 x 40, 1 x 20/45 | - | 21.5 | 64.5 | 1.9 | 60 | 50 | Constrained |  |  | Constrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 66/22 | Red
ENGLAND | EALING (E) | EALING | 16.1/25.0 | 51.5018 | -0.296 | TQ 18371 79475 | 3 x 20 | - | 16.8 | 49.8 | - | 36 | 50 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 66/11 | Red
ENGLAND | EAST BEDFONT A | LALEHAM | 14.7/25.0 | 51.4531 | -0.44141 | TQ 08394 73826 | 2 x 60 | - | 32.4 | 74.8 | 7 | 82 | 95 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 132/22 | Green
ENGLAND | EAST BEDFONT B | LALEHAM | 11.9/25.0 | 51.4531 | -0.44141 | TQ 08394 73826 | 1 x 20 1 x 20/40 | - | 10.7 | 31.8 | - | 29 | 95 | Unconstrained |  |  | Unconstrained | 132/11kV transformer to be upgraded at EBED B. | TBC | Yes | No | None known | 132/11 | Green
ENGLAND | FAREHAM MAIN | LOVEDEAN | 15.43/25 | 50.8331 | -1.1986 | SU 56534 04031 | 90 | 0 | 21.61 | 90.0165 | 111.821 | 14 |  | Partially Constrained |  |  | Partially Constrained | Fareham-C switchgear upgrade (FL results include new rating) | 01/03/2023 | No | Yes | None known | 132/33 | Amber
ENGLAND | FAREHAM RESERVE | LOVEDEAN | 13.10/25 | 50.8331 | -1.1986 | SU 56534 04031 | 60 | 0 | 9.2373 | 72.8082 | 48.06 | 10 |  | Partially Constrained |  |  | Partially Constrained | Fareham-C switchgear upgrade (FL results include new rating) | 01/03/2023 | No | Yes | None known | 132/33 | Amber
ENGLAND | FAWLEY NORTH | FAWLEY | 15.32/25.0 | 50.8385 | -1.3746 | SU 44135 04515 | 133 | 0 | 61.1107 | 96.0259 | 0 | 0 |  | Constrained | 132kV reinforcement to be triggered to create more headroom for ANM scheme |  | Constrained |  |  | No | Yes | This isConstrained due to GSP wide distribution constraints (SSEN-NG). | 132/11 | Red
ENGLAND | FAWLEY SOUTH | FAWLEY | 5.32/17.5 | 50.8368 | -1.3568 | SU 45387 04335 | 38.5 | 0 | 13.0907 | 22.0982 | 0 | 0 |  | Constrained | 132kV reinforcement to be triggered to create more headroom for ANM scheme |  | Constrained |  |  | No | Yes | This isConstrained due to GSP wide distribution constraints (SSEN-NG). | 132/11 | Red
ENGLAND | FROME | MELKSHAM | 19.92/25.0 | 51.231 | -2.305 | ST 78803 48019 | 180 | 105.1 | 27.57 | 100.859 | 133.3 | 10 | 95 | Partially Constrained | a new SGT and reconductoring | 2027-10-01 | Constrained | AVC & Load Blinder. Frome-C switchgear reinforcement (Fl results include new rating), 132kV busbar, 3rd 90MVA transformer, 132kV Melksham - Frome cct2 reinforcement | 31/03/2026 | No | No | Estimated delivery time for BSP transformer reinforcement at Frome is 2026/2027; NG reinf works required for Melk SGT capacity,conn date is 2027. | 132/33 | Amber
ENGLAND | GALILEO | MINETY | 19.35/25 | 51.5524 | -1.8486 | SU 10596 83733 | 45 | 0 | 6.9654 | 27.4648 | 10 | 0 | 95 | Constrained | a new SGT | 2028-10-01 | Partially Constrained |  |  | No | Yes | Thermal constraint on 132kV circuits to Minety with no remaining headroom. NG reinf works required for Minety SGT capacity constraints, estimated connection date for new applications is 2028 | 132/11 | Red
ENGLAND | GREENFORD | WILLESDEN | 11.1/20.0 | 51.5414 | -0.34763 | TQ 14688 83790 | 2 x 30/60 | - | 18.4 | 46.7 | 1 | 48 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | HAVANT | LOVEDEAN | 18.10/25 | 50.8467 | -0.9982 | SU 70625 05720 | 90 | 0 | 18.8843 | 96.5077 | 69.468 | 36 |  | Partially Constrained |  |  | Partially Constrained | Havant AVC reinforcement, Havant-C switchgear reainforcement (FL results include new rating). | 01/07/2022 | No | Yes | None known | 132/33 | Green
ENGLAND | HAYES | NORTH HYDE | 15.96/17.5 | 51.5042 | -0.42345 | TQ 09519 79541 | 60 | 0 | 13.5345 | 48.9308 | 0 | 74.6 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | HEADINGTON | COWLEY | 16.21/17.5 | 51.7693 | -1.2123 | SP 54454 08145 | 90 | 0 | 4.424 | 51.6858 | 76.264 | 11 |  | Constrained |  |  | Constrained | Reconfiguration of Headington-Bicester North BSP groups. |  | No | No | Upstream thermal restrictions under FCO. Proximity to fault rating. | 132/33 | Red
ENGLAND | HIGH WYCOMBE | COWLEY | 12.13/25.0 | 51.6222 | -0.77685 | SU 84773 92191 | 90 | 0 | 28.4179 | 99.8874 | 26.538 | 21 |  | Constrained |  |  | Constrained |  |  | No | No | Upstream thermal restrictions under FCO. | 132/33 | Green
ENGLAND | IRONBRIDGE | EALING | 13.0/25.0 | 51.5089 | -0.35546 | TQ 14226 80171 | 2 x 20/40 | - | 13 | 35.7 | 1.1 | 50 | 95 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 66/11 | Red
ENGLAND | LANGLEY | FAWLEY | 16.1/25.0 | 50.8102 | -1.3601 | SU 45185 01376 | 58 | 0 | 5.8894 | 24.665 | 19.83 | 0 |  | Constrained | 132kV reinforcement to be triggered to create more headroom for ANM scheme |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 132/33 | Red
ENGLAND | LONGFORD | IVER 132KV | 16.58/25 | 51.4802 | -0.50506 | TQ 03910 76751 | 90 | 0 | 25.7 | 49.8 | 45.7 | 70 |  | Constrained |  |  | Unconstrained |  |  | No | No | Future connections would trigger AVC reinforcement | 132/33 | Green
ENGLAND | LOUDWATER | AMERSHAM | 14.71/18.4 | 51.6128 | -0.69231 | SU 90644 91247 | 90 | 0 | 13.2564 | 98.7472 | 56.5 | 46.7 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 132/33 | Green
ENGLAND | LYNES COMMON | FAWLEY | 13.61/17.5 | 50.8467 | -1.3792 | SU 43804 05423 | 30 | 0 | 1.1861 | 1.9224 | 0 | 0 |  | Constrained | 132kV reinforcement to be triggered to create more headroom for ANM scheme |  | Constrained |  |  | No | Yes | This isConstrained due to GSP wide distribution constraints (SSEN-NG). | 132/11 | Red
ENGLAND | LYTCHETT | MANNINGTON GSP | 11.08/25.0 | 50.7475 | -2.0326 | SY 97796 94214 | 90 | 0 | 16.01 | 84.6068 | 155.7895 | 0 |  | Constrained | existing 2 x 90MVA BSP transformers are to be upgraded to 120MVA transformers. |  | Constrained | Update protection settings. Adding more than 5MVA Generator at 33kv level triggers BSP Tx reinforcement. | 01/08/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1. | 132/33 | Red
ENGLAND | MAIDENHEAD | FLEET BRAMLEY | 16.63/17.5 | 51.5112 | -0.75361 | SU 86592 79883 | 90 | 0 | 22.02 | 74.9914 | 0.218 | 5 |  | Constrained |  |  | Constrained |  |  | Yes | Yes | Prox to fault rating. Prox to thermal rating on short cable section of Maidenhead. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinf required at Fleet GSP | 132/33 | Red
ENGLAND | MANNINGTON | MANNINGTON GSP | 11.68/13.1 | 50.8465 | -1.8945 | SU 07523 05221 | 120 | 0 | 18.5317 | 90.1279 | 120.917 | 0 |  | Constrained |  |  | Constrained | Reinf 33kV isolators on the Mannington/Mill Lane, AVC reinforcement. | 01/12/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1 | 132/33 | Red
ENGLAND | NETLEY COMMON | BOTLEY WOOD GSP | 12.25/25 | 50.9055 | -1.325 | SU 47559 12003 | 90 | 0 | 33.47 | 113.2781 | 44.3 | 65 |  | Unconstrained |  |  | Partially Constrained | AVC & load blinder reinforcement,C switchgear reinforcement (FL Results include new rating), 3rd BSP transformer | 2024 | No | Yes | Proximity to make fault rating | 132/33 | Amber
ENGLAND | NORRINGTON | MELKSHAM | 24.6/31.5 | 51.3838 | -2.1699 | ST 88273 64983 | 270 | 77.5 | 46.78 | 188.4412 | 255.2 | 5 | 95 | Constrained | a new SGT and reconductoring | 2027-10-01 | Constrained | NNORR-CORS 33kV cable upgrade. New 132/33kV transformer and 33kV CB reinforcement. | 01/12/2023 | No | No | No capacity left on Norrington BSP transformers for generation connections; fault level is approaching the limit of CB break rating; NG reinforcement works required for Melk SGT capacity constraints, est connection date for new applications is 2027. | 132/33 | Red
ENGLAND | NORTH HYDE (D) | NORTH HYDE | 7.78/18.4 | 51.4992 | -0.41141 | TQ 10367 79001 | 45 | 0 | 9.1818 | 42.0224 | 0 | 49.9 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/22 | Green
ENGLAND | NORTH HYDE (E) | NORTH HYDE | 11.06/13.1 | 51.4992 | -0.41141 | TQ 10367 79001 | 76 | 0 | 12.3842 | 60.8915 | 0 | 54.1 |  | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | OXFORD | COWLEY | 13.48/25.0 | 51.7503 | -1.2763 | SP 50054 05983 | 90 | 0 | 26.42 | 79.9526 | 77.779 | 8 |  | Constrained | 132kV reinforcements at one of the Oxford - Cowley 132kV cct's | 2023-11-01 | Constrained |  |  | No | No | Upstream thermal restrictions under FCO. | 132/33 | Amber
ENGLAND | PERIVALE | WILLESDEN | 13.8/25.0 | 51.5332 | -0.30675 | TQ 17544 82947 | 2 x 20/40 | - | 14.2 | 36.2 | - | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No |  | 66/11 | Green
ENGLAND | POOLE PS (HAMWORTHY) | MANNINGTON GSP | 13.89/25.0 | 50.7167 | -1.9985 | SZ 00203 90789 | 60 | 0 | 8.8203 | 29.9627 | 3.4 | 0 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement | 132/33 | Amber
ENGLAND | PORTSMOUTH | LOVEDEAN | 16.1/25.0 | 50.7933 | -1.1018 | SZ 63405 99685 | 90 | 0 | 24.6641 | 101.3414 | 21.465 | 89 |  | Partially Constrained |  |  | Partially Constrained |  |  | No | Yes | None known | 132/33 | Green
ENGLAND | PYESTOCK | FLEET BRAMLEY | 19.81/25.0 | 51.2841 | -0.81213 | SU 82940 54553 | 90 | 0 | 18.27 | 52.9403 | 0 | 85 |  | Constrained |  |  | Partially Constrained | Split of Coxmoor Wood-Pyestock BSP groups. | 01/03/2021 | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 132/33 | Amber
ENGLAND | READING | FLEET BRAMLEY | 18.28/17.5 | 51.4588 | -0.92704 | SU 74642 73856 | 228 | 0 | 41.9618 | 142.5513 | 47.48 | 240 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 132/33 | Red
ENGLAND | READING TOWN | FLEET BRAMLEY | 13.25/17.5 | 51.4615 | -0.97105 | SU 71580 74111 | 9 | 0 | 14.8104 | 64.147 | 0.649 | 85.5 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 132/33 | Red
ENGLAND | REDHILL | MANNINGTON GSP | 19.19/25 | 50.765 | -1.8797 | SZ 08581 96162 | 90 | 0 | 15.52 | 66.6735 | 116.981 | 0 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement | 132/33 | Amber
ENGLAND | ROWNHAMS | NURSLING | 19.08/25 | 50.9499 | -1.4723 | SU 37168 16854 | 90 | 0 | 27.35 | 105.9 | 111 | 30 |  | Constrained |  |  | Constrained | Rownhams-C switchgear reinforcement (FL Results include new rating), Directional Relay Reinforcement | 2025 | Yes | Yes | No spare bay AND/OR space for extension | 132/33 | Red
ENGLAND | SALISBURY | MANNINGTON GSP | 20.5/25.0 | 51.0818 | -1.8436 | SU 11049 31395 | 105 | 0 | 24.95 | 106.8829 | 88 | 0 |  | Constrained |  |  | Constrained | Update protection settings. Adding more than 5MVA Generator at 33kv level triggers BSP Tx reinforcement |  | Yes | Yes | BSP Transfomer rating limitation under N-1,any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement. | 132/33 | Red
ENGLAND | SHAFTESBURY | MANNINGTON GSP | 16.1/25.0 | 51.0133 | -2.2089 | ST 85442 23791 | 90 | 0 | 15.1881 | 78.4723 | 121.094 | 0 |  | Constrained |  |  | Constrained | AVC reinforcement | 01/12/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1,any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement. 3rd BSP Tx reinforcement to be triggered. Update protection settings. | 132/33 | Red
ENGLAND | SLOUGH | IVER 132KV | 24.23/31.5 | 51.5266 | -0.62371 | SU 95574 81752 | 270 | 0 | 31.5 | 98.6 | 118 | 183.5 |  | Constrained |  |  | Unconstrained | Fault Level Reinforcement triggered. |  | No | No | Constrained cable route out of BSP | 132/33 | Green
ENGLAND | SLOUGH SOUTH | IVER 132KV | 11.93/17.5 | 51.5234 | -0.62556 | SU 95452 81391 | 270 | 0 | 76.8 | 144.1 | 0 | 183.5 |  | Constrained |  |  | Unconstrained |  |  | No | No | Space constraint within switchroom | 132/33 | Green
ENGLAND | SOUTHAMPTON MAIN | NURSLING | 11.01/13.1 | 50.906 | -1.4122 | SU 41425 11999 | 90 | 0 | 12.0546 | 58.3 | 1.73 | 61.6 |  | Constrained |  |  | Constrained | AVC upgrade needed |  | Yes | Yes | AVC reinforcement to be triggered | 132/33 | Red
ENGLAND | SOUTHAMPTON RESERVE | NURSLING | 11.09/17.5 | 50.906 | -1.4122 | SU 41425 11999 | 60 | 0 | 14.4285 | 78.1 | 11.08 | 82.1 |  | Constrained |  |  | Constrained | AVC upgrade needed |  | Yes | Yes | AVC reinforcement to be triggered | 132/33 | Red
ENGLAND | SOUTHFIELD ROAD | EALING | 9.8/13.1 | 51.5038 | -0.26477 | TQ 20533 79746 | 2 x 20/40 | - | 12.2 | 44.7 | - | 32 | 50 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 66/11 | Red
ENGLAND | STAINES | LALEHAM | 16.1/31.5 | 51.4386 | -0.49671 | TQ 04585 72135 | 2 x 90, 2 x 120 | - | 79.8 | 204.7 | 140.4 | 140 | 95 | Unconstrained |  |  | Partially Constrained |  |  | Yes | No | Restrictions on STAINES C2 BSP. | 132/33 | Amber
ENGLAND | STRATTON MAIN | MINETY | 21.95/31.5 | 51.5973 | -1.7556 | SU 17028 88748 | 90 | 98.2 | 18.29 | 82.8308 | 90.1 | 20 | 95 | Partially Constrained | a new SGT | 2028-10-01 | Partially Constrained | auto-close scheme to run Stratton solid under N-1, 33kV and 11kV CB upgrades | 31/03/2024 | No | Yes | Constrained space at Stratton 33kV switchyear for new 33kV CB connection; NG reinforcement works required for Minety SGT capacity constraints, est conn date for new applications is 2028 | 132/33 | Red
ENGLAND | STRATTON RESERVE | MINETY | 21.95/31.5 | 51.5973 | -1.7556 | SU 17028 88748 | 60 | 19 | 13.55 | 61.5785 | 52.261 | 0 | 95 | Constrained | a new SGT | 2028-10-01 | Partially Constrained | Load blinder reinforcement, auto-close scheme to run Stratton solid under N-1, 33kV and 11kV CB upgrades | 31/03/2024 | No | Yes | Thermal constraint on 132kV circuits to Minety with no remaining headroom. National Grid reinforcement works required for Minety SGT capacity, est connection date for new applications is 2028 | 132/33 | Red
ENGLAND | SWINDON | MINETY | 16.78/25 | 51.5823 | -1.8218 | SU 12447 87062 | 90 | 6.75 | 16.78 | 93.0696 | 103.298 | 10 | 95 | Partially Constrained | a new SGT | 2028-10-01 | Partially Constrained | 33kV circuit breaker reinforcement |  | No | Yes | Constrained by BSP transformer capacity. National Grid reinforcement works required for Minety SGT capacity constraints, estimated connection date for new applications is 2028 | 132/33 | Amber
ENGLAND | THATCHAM | BRAMLEY (ANDO-THAT) | 19.06/25 | 51.3945 | -1.2421 | SU 52824 66435 | 195 | 0 | 45.3888 | 173.3562 | 88.43 | 80 |  | Constrained |  |  | Partially Constrained | Limitation to reverse power headroom is Bramley SGT capacity. Fault level capacity approaching limit. Reinforcement required |  | No | No | No spare bay AND/OR space for extension. Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 132/33 | Red
ENGLAND | TOOTHILL | MINETY | 19.55/25 | 51.5542 | -1.8111 | SU 13191 83945 | 180 | 0 | 15.12 | 108.9394 | 108.27 | 0 | 95 | Constrained | a new SGT | 2028-10-01 | Constrained | Load blinder reinforcement, 33kV CB upgrade, 132/33kV transformer upgrade with new 132kV switchroom. | 31/03/2024 | No | Yes | Thermal constraint on upstream 132kV system with no remaining headroom.National Grid reinf works required for Melksham SGT capacity constraints, est connection date for new applications is 2028 | 132/33 | Red
ENGLAND | UPTON | IVER 132KV | 14.58/25 | 51.505 | -0.54851 | TQ 00838 79445 | 76 | 0 | 13.7 | 40.9 | 9.2 | 80.5 |  | Constrained |  |  | Unconstrained |  |  | No | No | None known | 132/22 | Green
ENGLAND | VELMORE | NURSLING | 18.8/25.0 | 50.9708 | -1.391 | SU 42855 19215 | 126 | 0 | 25.58 | 108 | 99.55 | 40 |  | Constrained |  |  | Constrained | 3rd BSP Tx reinforcement, cct reinforcement between Velmore and Hedge End | 01/06/2024 | Yes | Yes |  | 132/33 | Red
ENGLAND | VICARAGE FARM ROAD | NORTH HYDE | 12.58/13.1 | 51.4757 | -0.38356 | TQ 12358 76435 | 38 | 0 | 7.1747 | 30.4971 | 0 | 0.7 |  | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to fault rating | 66/11 | Amber
ENGLAND | WAREHAM | MANNINGTON GSP | 12.9/13.1 | 50.6956 | -2.121 | SY 91548 88451 | 30 | 0 | 7.79 | 30.337 | 48.09 | 0 |  | Constrained |  |  | Constrained | AVC reinforcement .Update protection settings. Adding more than 5MVA Generator at 33kv level triggers BSP Tx reinforcement | 01/12/2021 | Yes | Yes | BSP Transfomer rating limitation under N-1. Any new connection will pay 2nd comer of Mann GSP 132kV CBs reinforcement. Adding more than 5MVA Generator at 33kv level triggers BSP Tx reinforcement. | 132/33 | Red
ENGLAND | WEST GRAFTON | MELKSHAM | 12.48/17.5 | 51.3315 | -1.6526 | SU 24302 59215 | 45 | 0 | 6.72 | 31.3396 | 47.9 | 0 | 95 | Constrained | a new SGT and reconductoring | 2027-10-01 | Constrained |  |  | No | No | Thermal constraint on upstream 132kV system with no remaining headroom.Reinforcement works required for Melksham SGT capacity constraints, est connection date for new applications is 2027. | 132/33 | Red
ENGLAND | WINCHESTER | NURSLING | 15.58/25.0 | 51.0376 | -1.3601 | SU 44965 26671 | 90 | 0 | 19.89 | 106.6 | 166.15 | 5 |  | Constrained |  |  | Constrained | Limited headroom due to BSP transformer, and upstream 132kV circuits constraints |  | Yes | Yes |  | 132/33 | Red
ENGLAND | WINFRITH HEATH | MANNINGTON GSP | 15.68/17.5 | 50.6782 | -2.2738 | SY 80748 86538 | 30 | 0 | 1.535 | 7.594 | 21.87 | 0 |  | Constrained |  |  | Constrained | Update protection settings. | 01/10/2021 | Yes | Yes | any new connection will pay 2nd comer of Mannington GSP 132kV CBs reinforcement. Update protection settings. Adding more than 5MVA Generator at the BSP triggers upstream 132kv OHL reinforcement | 132/11 | Red
ENGLAND | WITNEY & YARNTON | COWLEY | 14.15/31.5 | 51.772 | -1.4854 | SP 35605 08274 | 90 | 23.95 | 23.42 | 84.1222 | 276.55 | 2 |  | Constrained | 132kV reinforcements at the Yarnton - Headington tee 132kV cct's. An ANM scheme has also been triggered at those cct's. | 2023-07-01 | Constrained | Load blinder and AVC reinforcements at Yarnton. 132/33kV Tx reinforcements at Yarnton. | 01/05/2023 | No | No | None known | 132/33 | Red
ENGLAND | WOKINGHAM | FLEET BRAMLEY | 12.31/25.0 | 51.4024 | -0.85724 | SU 79589 67665 | 90 | 0 | 6.92 | 40.067 | 77 | 20 |  | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP. Limited transformer reverse power capacity on Wokingham BSP | 132/33 | Red
ENGLAND | WYMERING & FORT WIDLEY | LOVEDEAN | 13.82/25.0 | 50.8449 | -1.0789 | SU 64948 05441 | 60 | 0 | 7.2725 | 28.9638 | 88.66 | 88 |  | Partially Constrained |  |  | Partially Constrained | Wymering AVC reinforcement | 01/03/2021 | No | Yes | None known | 132/33 | Green
ENGLAND | YEOVIL | AXMINSTER | 17.05/25.0 | 50.9499 | -2.6052 | ST 57586 16894 | 90 | 0 | 24.5253 | 114.2996 | 100.95 | 4 |  | Constrained |  |  | Constrained | Update DOC setting for RPF, AVC upgrade | 01/03/2021 | Yes | Yes | Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO, 29km of 132kV Axminster-Yeovil OHL has reached the thermal rating. There are currently 2 x 132kV circuits (mainly OHL) between Axminster GSP - Yeovil BSP. The 3rd 32km+ circuit (cable) is to be installed to improve the security of the network (in case of N-2 losing 2 x existing 132kV circuit). Mod App to NG is ongoing and might add more uncertainty. Estimated timespan is for at least 5 - 6 years. | 132/33 | Red
7223.348

## PS
Area | Primary Substation Name | GSP Parent | BSP Parent | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate Rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification
ENGLAND | ALDERNEY | MANNINGTON GSP | BOURNEMOUTH | 13.05/13.1 | 50.7559 | -1.9408 | SZ 04270 95141 | 24 | 0 | 3.3934 | 19.5797 | 9.27 | 19 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Proximity to fault rating. | 33/11 | Red
ENGLAND | ALDERSHOT | FLEET BRAMLEY | ALDERSHOT | 17.18/25.0 | 51.2322 | -0.76998 | SU 85976 48834 | 19.5 | 0 | 2.9721 | 13.3549 | 2.4 | 19 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinf required at Fleet GSP. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinf required at Fleet GSP | 33/11 | Red
ENGLAND | ALDERTON | MELKSHAM | CHIPPENHAM | 3.23/13.1 | 51.5552 | -2.2234 | ST 84609 84059 | 3 | 0 | 0.64887 | 3.3083 | 0 | 0.15 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 | 33/11 | Red
ENGLAND | ALRESFORD | FLEET BRAMLEY | ALTON & FERNHURST | 6.42/13.1 | 51.0888 | -1.1492 | SU 59684 32511 | 13 | 0 | 2.62 | 12.0165 | 0 | 20 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | 33kV circuit reinforcement is required for any new connection. Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | ALTON LOCAL | FLEET BRAMLEY | ALTON & FERNHURST | 10.04/13.1 | 51.1511 | -0.96576 | SU 72434 39606 | 37.5 | 0 | 7.13 | 29.4668 | 0.25 | 5 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | ANDOVER | MELKSHAM | ANDOVER | 8.78/25.0 | 51.2179 | -1.4968 | SU 35240 46643 | 30 | 0 | 2.1643 | 8.5253 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with no remaining headroom. NG reinf works required for Melksham SGT capacity constraints, estimated connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | ANDOVER EAST | MELKSHAM | ANDOVER | 8.61/13.1 | 51.2158 | -1.458 | SU 37953 46433 | 30 | 0 | 5.3985 | 19.2974 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with no remaining headroom. NG reinf works required for Melksham SGT capacity constraints, estimated connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | ANDOVER TOWN | MELKSHAM | ANDOVER | 8.91/16.0 | 51.2038 | -1.4831 | SU 36207 45078 | 10 | 0 | 2.0513 | 8.2155 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with no remaining headroom. NG reinf works required for Melksham SGT capacity constraints, estimated connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | ARBORFIELD | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | 4.34/13.1 | 51.3859 | -0.90996 | SU 75949 65766 | 18 | 0 | 1.5127 | 0 | 2.44 | 17 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | No | Connections might not possible prior to Bramley Green-Arborfield reconfiguration. Rein required at Arborfield and the 33kV circuits from Little Hungerford to accommodate connection. Voltage Issues. | 33/11 | Amber
ENGLAND | ARGYLE ROAD | LOVEDEAN | CHICHESTER & HUNSTON | 10.63/13.1 | 50.7845 | -0.67939 | SZ 93193 99152 | 30 | 0 | 3.22 | 16.3476 | 0 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Green
ENGLAND | ARNCOTT | COWLEY | HEADINGTON | 9.24/13.1 | 51.8581 | -1.1196 | SP 60730 18095 | 15 | 0 | 1.9501 | 13.8261 | 12.2 | 1 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Voltage & thermal upstream limitations. | 33/11 | Red
ENGLAND | ASCOT | FLEET BRAMLEY | BRACKNELL MAIN | 7.91/25.0 | 51.4113 | -0.6841 | SU 91615 68855 | 30 | 0 | 5.2309 | 2.7495 | 0 | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP 33kV CBs close to fault rating | 33/11 | Red
ENGLAND | ASHLING ROAD | LOVEDEAN | CHICHESTER & HUNSTON | 10.93/13.1 | 50.854 | -0.80682 | SU 84085 06737 | 26 | 0 | 5.4537 | 23.5505 | 1.9 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | ASHTON PARK | MELKSHAM | NORRINGTON | 9.58/13.1 | 51.3186 | -2.1859 | ST 87141 57741 | 23.5 | 0 | 3.6445 | 21.0681 | 4.175 | 8 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constraimed by the 33kV circuits between Norrington and Ashton Park; In addtion, there is no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | AVON RUBBER | MELKSHAM | NORRINGTON | 8.98/13.1 | 51.3772 | -2.1388 | ST 90435 64246 | 7.5 | 0 | 0.46047 | 8.4465 | 0.14 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | BAGSHOT | FLEET BRAMLEY | BRACKNELL RESERVE | 6.88/20.0 | 51.3635 | -0.69255 | SU 91122 63523 | 24 | 0 | 3.5604 | 14.6388 | 0 | 28 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP 33kV CBs close to fault rating | 33/11 | Red
ENGLAND | BALL HILL | BRAMLEY (ANDO-THAT) | THATCHAM | 5.88/13.1 | 51.3658 | -1.3921 | SU 42417 63142 | 15 | 0 | 1.1288 | 7.1688 | 0 | 16 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Red
ENGLAND | BARTON STACEY | MELKSHAM | ANDOVER | 4.67/7.9 | 51.1822 | -1.3994 | SU 42075 42720 | 6 | 0 | 1.4791 | 6.4159 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with no remaining headroom. NG reinf works required for Melksham SGT capacity constraints, estimated connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | BASINGSTOKE | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | 11.15/13.1 | 51.2698 | -1.0674 | SU 65155 52705 | 30 | 0 | 3.97 | 17.5526 | 12.75 | 18 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Red
ENGLAND | BASSETT | NURSLING | VELMORE | 11.06/13.1 | 50.9415 | -1.4008 | SU 42193 15958 | 30 | 0 | 2.442 | 16.7924 | 0.231 | 33 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | BATH ROAD EAST | NORTH HYDE | NORTH HYDE (D) | 5.43/13.1 | 51.4804 | -0.43035 | TQ 09097 76885 | 13 | 0 | 2.2652 | 12.2234 | 0 | 15 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
ENGLAND | BATH ROAD WEST | IVER 132KV | LONGFORD | 13.57/13.1 | 51.4804 | -0.47763 | TQ 05814 76820 | 25.1 | 0 | 6.227 | 16.53 | 0 | 18.8 | 50 | Unconstrained |  |  | Constrained |  |  | No | No | Proximity to fault level | 33/11 | Red
ENGLAND | BEACONSFIELD (END B/B) | IVER 132KV | UPTON | 3.39/25.0 | 51.612 | -0.64865 | SU 93668 91219 | 6.5 | 0 | 1 | 4.9 | 0 | 4.25 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to Primary transformers limitations under FCO. | 22/6.6 | Red
ENGLAND | BEACONSFIELD (MIDDLE B/B) | IVER 132KV | DENHAM | 9.17/25.0 | 51.612 | -0.64865 | SU 93668 91219 | 12.9 | 0 | 3.17 | 11.67 | 0 | 9.6 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
ENGLAND | BEENHAM | BRAMLEY (ANDO-THAT) | THATCHAM | 6.52/13.1 | 51.4173 | -1.1644 | SU 58204 69025 | 13 | 0 | 1.3293 | 6.8129 | 1.9 | 7.5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Red
ENGLAND | BEMERTON | MANNINGTON GSP | SALISBURY | 8.42/20.0 | 51.0803 | -1.836 | SU 11583 31233 | 30 | 0 | 3.7555 | 15.0277 | 0 | 0 | 50 | Constrained |  |  | Unconstrained | Bemerton-C switchgear reinforcement | 01/06/21 | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Green
ENGLAND | BERINSFIELD | COWLEY | Cowley Local (2 x 45) | 7.76/20.0 | 51.655 | -1.1575 | SU 58382 95467 | 24 | 0 | 0.84134 | 12.9945 | 19.82 | 19 | 50 | Constrained | ANM scheme triggered upstream by accepted generation |  | Unconstrained |  |  | Yes | No | ANM installed to avoid upstream 33kV thermal issues under FCO. | 33/11 | Red
ENGLAND | BEVOIS VALLEY | NURSLING | Southampton (2 x 60) | 8.3/25.0 | 50.9166 | -1.3947 | SU 42648 13187 | 22.9 | 0 | 3.1824 | 14.5218 | 1.175 | 24 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/6.6 | Green
ENGLAND | BICESTER | EAST CLAYDON | BICESTER NORTH | 11.86/16.0 | 51.8934 | -1.153 | SP 58381 21988 | 60 | 0 | 4.5935 | 24.4978 | 33.511 | 2 | 50 | Constrained |  |  | Constrained |  |  | No | No | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | BILLINGSHURST | LOVEDEAN | CHICHESTER & HUNSTON | 2.91/20.0 | 51.026 | -0.45704 | TQ 08305 26315 | 10 | 0 | 1.5607 | 9.524 | 0 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | BILSHAM | LOVEDEAN | CHICHESTER & HUNSTON | 10.88/13.1 | 50.8057 | -0.61956 | SU 97366 01594 | 30 | 0 | 3.5818 | 17.4718 | 42.172 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | BINSTEAD | FAWLEY | COWES & WOOTTON COMMON | 8.06/13.1 | 50.7195 | -1.2023 | SZ 56409 91399 | 15 | 0 | 1.2018 | 5.9004 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | BIRDHAM | LOVEDEAN | CHICHESTER & HUNSTON | 7.46/13.1 | 50.7886 | -0.83856 | SZ 81965 99422 | 10 | 0 | 2.6652 | 11.8424 | 0 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | BISHOPS WALTHAM | BOTLEY WOOD GSP | NETLEY COMMON | 7.42/20.0 | 50.9468 | -1.1944 | SU 56691 16683 | 24 | 0 | 3.2655 | 16.8712 | 7.5 | 19 | 50 | Partially Constrained |  |  | Unconstrained |  |  | Yes | Yes | 33kV upstream restriction on Netley Common to Bishops Waltham 33kV circts | 33/11 | Amber
ENGLAND | BISHOPSTOKE | NURSLING | VELMORE | 8.78/13.1 | 50.9638 | -1.3398 | SU 46463 18472 | 13 | 0 | 1.3082 | 5.5202 | 7.6 | 14 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | BITTERNE | BOTLEY WOOD GSP | NETLEY COMMON | 8.24/25.0 | 50.9154 | -1.3596 | SU 45116 13082 | 13 | 0 | 2.3446 | 10.4926 | 0 | 14 | 50 | Partially Constrained |  |  | Unconstrained |  |  | Yes | Yes | Proximity to voltage issues. | 33/6.6 | Amber
ENGLAND | BLACK BOURTON | MINETY | Stratton (2 x 60) | 5.65/25.0 | 51.7324 | -1.5909 | SP 28349 03818 | 10 | 0 | 1.0822 | 6.1408 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | BLANDFORD | MANNINGTON GSP | LYTCHETT | 6.22/20.0 | 50.8492 | -2.1603 | ST 88810 05536 | 30.7 | 0 | 3.975 | 16.2387 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
ENGLAND | BLEDINGTON | COWLEY | WITNEY & YARNTON | 3.03/25.0 | 51.9012 | -1.6287 | SP 25641 22580 | 5 | 0 | 1.2498 | 4.7714 | 0.188 | 3 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | No | Moderate proximity to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | BORDON | FLEET BRAMLEY | ALTON & FERNHURST | 9.13/13.1 | 51.1108 | -0.82635 | SU 82256 35269 | 26 | 0 | 4.09 | 23.7987 | 0 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | BOSCOMBE DOWN | BRAMLEY (ANDO-THAT) | AMESBURY | 10.09/13.1 | 51.1684 | -1.7556 | SU 17186 41044 | 30 | 0 | 5.9565 | 20.6855 | 14 | 22 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. Upstream 132kV capacity for export is circa 15MVA flexible | 33/11 | Red
ENGLAND | BOSCOMBE EAST | MANNINGTON GSP | CHRISTCHURCH | 10.11/13.1 | 50.7315 | -1.8365 | SZ 11636 92447 | 26.5 | 0 | 3.5592 | 12.8399 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | BOURNE VALLEY | MANNINGTON GSP | BOURNEMOUTH | 8.96/13.1 | 50.7313 | -1.9134 | SZ 06207 92415 | 30 | 0 | 5.4246 | 24.535 | 0 | 35 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | BOURTON | MANNINGTON GSP | SHAFTESBURY | 6.61/20.0 | 51.0712 | -2.3245 | ST 77363 30262 | 13 | 0 | 1.5 | 8.8406 | 1.5 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | BOVINGTON | MANNINGTON GSP | WAREHAM | 6.97/13.1 | 50.6899 | -2.2288 | SY 83933 87831 | 9.8 | 0 | 1.36 | 5.432 | 5 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | BOWERDEAN | AMERSHAM | LOUDWATER | 10.27/13.1 | 51.6369 | -0.73389 | SU 87718 93880 | 20 | 0 | 4.5089 | 22.2 | 0 | 24.5089 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | BRACKNELL | FLEET BRAMLEY | BRACKNELL MAIN | 13.82/20.0 | 51.4171 | -0.7636 | SU 86075 69397 | 76 | 0 | 12.0438 | 44.6216 | 0 | 85 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP 33kV CBs close to fault rating | 33/11 | Red
ENGLAND | BRADFORD-ON-AVON | MELKSHAM | NORRINGTON | 8.06/25.0 | 51.3438 | -2.2704 | ST 81260 60564 | 21.8 | 0 | 4.0482 | 12.4253 | 0.125 | 8 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | BRAMLEY GREEN | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | 6.05/25.0 | 51.3217 | -1.0337 | SU 67431 58511 | 15 | 0 | 1.0729 | 5.0448 | 15.76 | 16 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | No | Voltage issues following Arborfield switchover to Reading BSP; and 33kV circuit from Basingstoke to Bramley Green is full for export capacity | 33/11 | Red
ENGLAND | BRANDON ROAD | LOVEDEAN | PORTSMOUTH | 8.55/25.0 | 50.784 | -1.0834 | SZ 64712 98665 | 26 | 0 | 4.161 | 18.0336 | 0 | 30 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | BRAYWICK ROAD | FLEET BRAMLEY | MAIDENHEAD | 9.96/13.1 | 51.5185 | -0.72033 | SU 88887 80726 | 30 | 0 | 6.227 | 21.6535 | 0.075 | 17 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP Constrained on the 132kV circuits for export | 33/11 | Red
ENGLAND | BRENTFORD | EALING | EALING (D) | 11.2/25.0 | 51.4912 | -0.30665 | TQ 17659 78277 | 4 x 10/13 | - | 13.5 | 38.9 | - | 28 | 50 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 2022-11-22 | Red
ENGLAND | BROCKHAMPTON | LOVEDEAN | HAVANT | 12.26/25 | 50.8476 | -0.99473 | SU 70868 05828 | 30 | 0 | 3.7851 | 16.4424 | 16.62 | 18 | 50 | Unconstrained |  |  | Unconstrained | Switchgear -E reinforcement due to make issue (FL results include new rating). | 01/03/22 | Yes | Yes |  | 33/11 | Green
ENGLAND | BROCKHURST | LOVEDEAN | Fareham T1A T2A (90MVAs) | 9.47/13.1 | 50.8151 | -1.1585 | SU 59381 02061 | 30 | 0 | 4.9688 | 22.4676 | 0 | 26 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | BROMHAM | MELKSHAM | NORRINGTON | 2.71/13.1 | 51.393 | -2.0205 | ST 98670 65994 | 5 | 0 | 0.4256 | 2.3762 | 0.4 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations under FCO. also no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | BROOK STREET | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | 9.81/13.1 | 51.2657 | -1.0915 | SU 63480 52228 | 30 | 0 | 3.2269 | 13.7676 | 0 | 33 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | BRUTON | MELKSHAM | FROME | 3/25.0 | 51.1148 | -2.4429 | ST 69094 35148 | 8 | 0 | 1.1584 | 5.2632 | 1.362 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | BURFORD | COWLEY | WITNEY & YARNTON | 5.84/13.1 | 51.8108 | -1.629 | SP 25671 12529 | 6.5 | 0 | 0.85963 | 4.3982 | 0 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections | 33/11 | Red
ENGLAND | BUSHEY | MANNINGTON GSP | WAREHAM | 2.49/13.1 | 50.6515 | -2.0343 | SY 97671 83532 | 3.5 | 0 | 0.35932 | 1.6113 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | BUTTS ASH | FAWLEY | LANGLEY | 11.21/25.0 | 50.85 | -1.4059 | SU 41923 05772 | 23 | 0 | 4.0141 | 16.2685 | 11.5 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | CALNE | MELKSHAM | CHIPPENHAM | 11.73/13.1 | 51.4515 | -1.9939 | SU 00521 72497 | 21 | 0 | 1.6027 | 15.285 | 12.5 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 and fault level constraints | 33/11 | Red
ENGLAND | CAMBERLEY | FLEET BRAMLEY | CAMBERLEY MAIN | 13.67/25.0 | 51.3276 | -0.75871 | SU 86584 59452 | 80 | 0 | 8.8523 | 25.8617 | 0 | 85 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | CANAL BANK 11KV | WILLESDEN | CANAL BANK 11KV | 15.9/25.0 | 51.5337 | -0.25795 | TQ 20927 83082 | 2 x 30/60 | - | 23.4 | 60 | - | 80 | 95 | Unconstrained |  |  | Partially Constrained |  |  | No | No | None known | 22/6.6 | Amber
ENGLAND | CANAL BANK 6.6KV | WILLESDEN | ACTON LANE | 12.3/13.1 | 51.5337 | -0.25795 | TQ 20927 83082 | 3 x 11.5 | - | 1.6 | 9.1 | - | 13 | 50 | Constrained |  |  | Constrained | To be made redundant and supseded by CANB 11kV |  | No | No | Not applicable | 66/11 | Red
ENGLAND | CARTERTON | COWLEY | WITNEY & YARNTON | 8.91/13.1 | 51.7684 | -1.5919 | SP 28261 07823 | 30 | 0 | 4.93 | 18.9177 | 0 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections. | 33/11 | Red
ENGLAND | CASTLE CARY | AXMINSTER | YEOVIL | 5.67/25.0 | 51.0776 | -2.5076 | ST 64534 31039 | 15 | 7.5 | 1.1708 | 6.2599 | 5.27 | 7 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to upstream 33kV circts restrictions. There is no reverse power capacity at the Yeovil BSP, 33kV circuit thermal limitation. | 33/11 | Red
ENGLAND | CAUSEWAY | LALEHAM | STAINES | 14.4/25.0 | 51.4348 | -0.52304 | TQ 02763 71680 | 2 x 15/30, 1 x 12/24 | - | 12.1 | 33.7 | 14.1 | 25 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Amber
ENGLAND | CAVERSHAM | FLEET BRAMLEY | READING TOWN | 8.5/13.1 | 51.4762 | -0.9717 | SU 71512 75747 | 30 | 0 | 2.7457 | 13.225 | 0 | 6 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Voltage level constraints on the 33kV network Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | CENTRAL | MANNINGTON GSP | BOURNEMOUTH | 10.22/13.1 | 50.7269 | -1.8555 | SZ 10293 91931 | 30 | 0 | 6.0367 | 26.8072 | 5.4 | 31 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Green
ENGLAND | CENTRAL BRIDGE | NURSLING | Southampton (2 x 60) | 10.27/25.0 | 50.8992 | -1.3957 | SU 42591 11255 | 40 | 0 | 4.163 | 19.3416 | 0.1455 | 44 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | CERNE ABBAS | CHICKERELL GSP | CHICKERELL | 1.32/13.1 | 50.8079 | -2.4819 | ST 66140 01039 | 2.6 | 0 | 0.24007 | 1.7635 | 0 | 3 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Constrained due to Primary transformers limitations.There is no reverse power capacity at the Chickerell BSP | 33/11 | Red
ENGLAND | CHALVEY | IVER 132KV | CHALVEY | 13.71/25.0 | 51.505 | -0.60858 | SU 96669 79364 | 76 | 6 | 13.44 | 40.7 | 8.8 | 42.6 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | CHANDLERS FORD | NURSLING | VELMORE | 8.41/25.0 | 50.9917 | -1.3817 | SU 43494 21552 | 30 | 0 | 2.9598 | 13.1131 | 0 | 32 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | CHAPEL | NURSLING | Southampton (2 x 60) | 13.6/25.0 | 50.9057 | -1.392 | SU 42849 11983 | 15 | 0 | 2.6666 | 11.7175 | 0 | 17 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | None known | 33/6.6 | Green
ENGLAND | CHARLBURY | COWLEY | WITNEY & YARNTON | 6.39/13.1 | 51.8628 | -1.4781 | SP 36034 18376 | 15 | 0 | 1.2 | 5.7181 | 4.378 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections | 33/11 | Red
ENGLAND | CHARMINSTER | CHICKERELL GSP | CHICKERELL | 5.95/25.0 | 50.7374 | -2.4646 | SY 67309 93186 | 12 | 0 | 2.1491 | 8.2825 | 0 | 14 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | CHICHESTER | LOVEDEAN | CHICHESTER & HUNSTON | 13.12/25.0 | 50.859 | -0.69142 | SU 92198 07420 | 23 | 0 | 3.27 | 18.7349 | 16.35 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | CHICKERELL | CHICKERELL GSP | CHICKERELL | 9.48/25.0 | 50.6233 | -2.4894 | SY 65479 80511 | 14.8 | 0 | 0.48257 | 9.4875 | 4.769 | 10 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | CHILTON CANTELO | AXMINSTER | YEOVIL | 7.83/20.0 | 50.9924 | -2.6011 | ST 57910 21616 | 9.75 | 0 | 2.4383 | 8.3433 | 0 | 12 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to upstream 33kV circts restrictions.There is no reverse power capacity at the Yeovil BSP,33kV circuit thermal limitation. | 33/11 | Red
ENGLAND | CHINEHAM | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | 9.01/25.0 | 51.2977 | -1.0676 | SU 65105 55805 | 30 | 0 | 3.0308 | 16.0248 | 1.368 | 32 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | CHIPPING NORTON | COWLEY | WITNEY & YARNTON | 5.53/25.0 | 51.9388 | -1.5449 | SP 31382 26792 | 15 | 0 | 3.4751 | 9.7818 | 0.05 | 3 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained due to upstream thermal and voltage issues. | 33/11 | Red
ENGLAND | CHISBRIDGE | COWLEY | HIGH WYCOMBE | 6.32/13.1 | 51.5955 | -0.84321 | SU 80226 89155 | 9.8 | 0 | 2.0303 | 5.7892 | 0 | 1 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections. Upstream Voltage & thermal issues. | 33/11 | Red
ENGLAND | CHISLEDON | MINETY | TOOTHILL | 7.23/25.0 | 51.518 | -1.7291 | SU 18894 79934 | 15 | 0 | 1.0974 | 4.2246 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | CHOBHAM | FLEET BRAMLEY | BRACKNELL RESERVE | 6.6/25.0 | 51.3598 | -0.60575 | SU 97173 63223 | 14.3 | 0 | 2.1094 | 11.4903 | 0 | 11 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP 33kV CBs close to fault rating | 33/11 | Red
ENGLAND | CHOLSEY | COWLEY | DRAYTON | 5.75/13.1 | 51.5581 | -1.1616 | SU 58223 84685 | 15 | 0 | 1.3489 | 6.2208 | 0.3 | 7 | 50 | Constrained | 33kV reinforcements between Milton - Drayton |  | Unconstrained |  |  | Yes | No | Constrained due to 33kV circts limitations under FCO. | 33/11 | Red
ENGLAND | CHRISTCHURCH | MANNINGTON GSP | CHRISTCHURCH | 8.87/20.0 | 50.7377 | -1.7789 | SZ 15698 93141 | 39 | 0 | 5.8584 | 23.0048 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | CHURCH ROAD | LALEHAM | EAST BEDFONT A | 7.5/13.1 | 51.4344 | -0.46469 | TQ 06820 71722 | 2 x 12.5 | - | 3.2 | 14 | - | 9 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 2022-11-22 | Green
ENGLAND | CIRENCESTER TOWN | MINETY | CIRENCESTER | 10.43/13.1 | 51.7062 | -1.9614 | SP 02761 00827 | 21 | 0 | 3.8089 | 21.154 | 1.526 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on BSP transformers and upstream 132kV feeders | 33/11 | Red
ENGLAND | CLARENCE ROAD | IVER 132KV | CIPPENHAM | 12.21/25.0 | 51.4807 | -0.62394 | SU 95654 76652 | 45 | 0 | 8.0498 | 31.8963 | 0 | 30.6 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | COCKLEBURY | MELKSHAM | CHIPPENHAM | 12.86/13.1 | 51.4639 | -2.1101 | ST 92447 73890 | 35.5 | 0 | 4.7211 | 16.3493 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 | 33/11 | Red
ENGLAND | CODFORD | MELKSHAM | FROME | 3.66/25.0 | 51.1553 | -2.039 | ST 97372 39559 | 5 | 0 | 1.6731 | 3.5068 | 2 | 0 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | No | Constrained due to 33kV CROC - CODF cct thermal and voltage limitations. plus the thermal constraint on the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | COKES LANE | IVER 132KV | DENHAM | 10.94/13.1 | 51.6674 | -0.56644 | SU 99240 97483 | 16.2 | 0 | 0.92097 | 8.3029 | 0 | 9 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
ENGLAND | COLLEGE PARK | LOVEDEAN | WYMERING & FORT WIDLEY | 9.05/13.1 | 50.82 | -1.0659 | SU 65893 02686 | 13 | 0 | 2.0957 | 10.4527 | 0 | 15 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | CORDWALLIS | FLEET BRAMLEY | MAIDENHEAD | 9.27/13.1 | 51.5287 | -0.72872 | SU 88285 81857 | 30 | 0 | 6.5539 | 21.5432 | 0 | 17 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP Constrained on the 132kV circuits for export | 33/11 | Red
ENGLAND | CORFE MULLEN | MANNINGTON GSP | LYTCHETT | 8.55/13.1 | 50.7642 | -2.0215 | SY 98583 96071 | 30 | 0 | 2.6543 | 13.1185 | 1.15 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | CORSHAM | MELKSHAM | NORRINGTON | 8.1/13.1 | 51.4251 | -2.1917 | ST 86766 69583 | 10 | 0 | 2.6303 | 9.9177 | 2 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | COTTISFORD | EAST CLAYDON | BICESTER NORTH | 2.29/13.1 | 51.9755 | -1.1422 | SP 59021 31128 | 2.5 | 0 | 0.25079 | 3.3105 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | No | No | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | COURAGES | FLEET BRAMLEY | BURGHFIELD MAIN | 10.43/13.1 | 51.4207 | -0.98046 | SU 70990 69570 | 26.5 | 0 | 4.9131 | 15.0087 | 5.7 | 25 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | COVE | FLEET BRAMLEY | CAMBERLEY RESERVE | 7.61/13.1 | 51.2962 | -0.77632 | SU 85415 55937 | 24 | 0 | 2.9578 | 10.0124 | 0 | 26 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | COWES POWER STATION | FAWLEY | COWES & WOOTTON COMMON | 9.42/13.1 | 50.7464 | -1.2851 | SZ 50535 94332 | 30 | 0 | 4.2795 | 21.3071 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | COWLEY LOCAL | COWLEY | Cowley Local (2 x 90) | 11.14/25.0 | 51.7236 | -1.189 | SP 56113 03074 | 30 | 0 | 6.7559 | 26.7218 | 0.709 | 35 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | COXMOOR WOOD | FLEET BRAMLEY | COXMOOR WOOD | 4.99/16.0 | 51.2508 | -0.87983 | SU 78275 50779 | 9.5 | 0 | 1.829 | 7.6789 | 0 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Limited headroom at BSP circa 15MVA | 33/11 | Amber
ENGLAND | CREEKMOOR | MANNINGTON GSP | LYTCHETT | 10.94/13.1 | 50.7467 | -1.9935 | SZ 00552 94121 | 26 | 0 | 3.5583 | 15.8743 | 1.024 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | CRICKLADE | MINETY | CIRENCESTER | 6.21/20.0 | 51.6382 | -1.8656 | SU 09400 93270 | 15 | 0 | 1.8412 | 10.9176 | 0 | 0 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | thermal constraint on 33kV system, BSP transformers and upstream 132kV feeders. | 33/11 | Red
ENGLAND | CROCKERTON | MELKSHAM | FROME | 7.25/13.1 | 51.1894 | -2.1769 | ST 87736 43371 | 14 | 0 | 2.9645 | 11.7461 | 1 | 8 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Constrained by the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | CROOKHAM | FLEET BRAMLEY | COXMOOR WOOD | 11.05/25.0 | 51.2739 | -0.83014 | SU 81702 53403 | 24 | 0 | 2.1948 | 12.5813 | 0 | 24 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | No headroom on the 132kV circuit from Bramley to Andover which feeds Amesbury BSP cause constraint for this Primary for new connctions. | 33/11 | Green
ENGLAND | CROWTHORNE | FLEET BRAMLEY | CAMBERLEY MAIN | 10.96/25.0 | 51.372 | -0.78788 | SU 84470 64352 | 30 | 0 | 5.3414 | 22.6698 | 0 | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | DEAN GARDENS | EALING | EALING (D) | 4.2/13.1 | 51.5102 | -0.32198 | TQ 16546 80368 | 1 x 10/12.5 | - | 0.6 | 5.7 | 0.2 | 7 | 50 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 2022-11-22 | Red
ENGLAND | DEDDINGTON | COWLEY | WITNEY & YARNTON | 3.87/13.1 | 51.9694 | -1.3212 | SP 46729 30325 | 4 | 0 | 0.86864 | 4.3857 | 0.05 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal and voltage issues. | 33/11 | Red
ENGLAND | DENHAM AVENUE | IVER 132KV | DENHAM | 12.50/13.1 | 51.5686 | -0.50431 | TQ 03761 86587 | 13 | 0 | 3.48 | 1.03 | 0 | 10 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | Moderate proximity to fault rating | 22/6.6 | Amber
ENGLAND | DEVIZES | MELKSHAM | NORRINGTON | 8.83/13.1 | 51.348 | -1.9999 | SU 00106 60986 | 21 | 0 | 7.0416 | 23.3608 | 1.468 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | 33kV system voltage and thermal constraints on the Norrington - Devizes 33kV ccts; no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | DORCAN SOUTH | MINETY | TOOTHILL | 6.80/13.1 | 51.5504 | -1.7232 | SU 19288 83540 | 22 | 0 | 3.4692 | 14.1064 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | DORCHESTER | CHICKERELL GSP | CHICKERELL | 8.33/13.0 | 50.7124 | -2.4388 | SY 69113 90401 | 21 | 0 | 4.8781 | 18.0432 | 1.995 | 3 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Upstream 33kV circts restrictions under FCO. Potential Voltage issue for new connections.There is no reverse power capacity at the Chickerell BSP | 33/11 | Red
ENGLAND | DOWN GRANGE | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | 9.30/13.1 | 51.248 | -1.1188 | SU 61604 50238 | 30 | 0 | 4.4037 | 21.897 | 0 | 18 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | DRAKES WAY | MINETY | Stratton (2 x 90) | 8.22/13.1 | 51.5694 | -1.7576 | SU 16899 85647 | 15 | 0 | 1.5052 | 7.3993 | 0 | 7 | 50 | Unconstrained |  |  | Unconstrained | 33kV CB reinforcement | 2024-03-31 | Yes | No | None known | 33/11 | Green
ENGLAND | DUNBRIDGE | NURSLING | WINCHESTER | 5.15/13.1 | 51.0347 | -1.5519 | SU 31520 26244 | 9.8 | 0 | 1.8843 | 7.2255 | 0.044 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Proximity to voltage issues. | 33/11 | Amber
ENGLAND | EAST HOWE | MANNINGTON GSP | REDHILL | 10.33/13.1 | 50.7556 | -1.9051 | SZ 06789 95116 | 30 | 0 | 4.6322 | 22.8924 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Green
ENGLAND | EASTERTON | MELKSHAM | NORRINGTON | 6.45/13.1 | 51.2917 | -1.9789 | SU 01568 54730 | 15 | 0 | 1.7472 | 9.3866 | 0.23 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | 33kV system voltage and thermal constraints on the Norrington - Devizes 33kV ccts; no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | EASTHAMPSTEAD | FLEET BRAMLEY | BRACKNELL RESERVE | 8.97/25.0 | 51.3972 | -0.76309 | SU 86148 67194 | 30 | 0 | 4.7008 | 18.9554 | 0 | 30 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP 33kV CBs close to fault rating | 33/11 | Amber
ENGLAND | EASTLEIGH NORTH | NURSLING | VELMORE | 10.92/16.0 | 50.9683 | -1.3545 | SU 45426 18958 | 40 | 0 | 7.105 | 31.7281 | 3.92 | 43 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | EASTNEY | LOVEDEAN | PORTSMOUTH | 8.87/13.1 | 50.7871 | -1.06 | SZ 66357 99040 | 20 | 0 | 1.7791 | 8.1831 | 0 | 21 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | EGHAM | LALEHAM | STAINES | 10.1/20.0 | 51.4326 | -0.54804 | TQ 01030 71404 | 2 x 15/30 | - | 9.2 | 27.1 | - | 36 | 95 | Partially Constrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Amber
ENGLAND | ELECTRIC HOUSE | MANNINGTON GSP | BOURNEMOUTH | 11.84/13.1 | 50.722 | -1.8773 | SZ 08757 91379 | 26 | 0 | 4.5105 | 16.0283 | 0.25 | 31 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | ELMS ROAD | FLEET BRAMLEY | WOKINGHAM | 10.11/25.0 | 51.41 | -0.83594 | SU 81057 68532 | 30 | 0 | 4.542 | 21.1396 | 45.4 | 34 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP approaching transformer reverse power capacity. | 33/11 | Amber
ENGLAND | EMSWORTH | LOVEDEAN | HAVANT | 8.14/25.0 | 50.847 | -0.93802 | SU 74861 05807 | 13 | 0 | 2.5149 | 11.1645 | 0.865 | 14 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | ENFORD | BRAMLEY (ANDO-THAT) | AMESBURY | 4.05/25.0 | 51.2644 | -1.8046 | SU 13728 51712 | 8 | 0 | 0.38104 | 3.1502 | 0 | 8 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations. Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. Upstream 132kV capacity for export is circa 15MVA flexible | 33/11 | Red
ENGLAND | EYNSHAM | COWLEY | WITNEY & YARNTON | 6.82/25.0 | 51.7895 | -1.3891 | SP 42236 10266 | 24 | 0 | 3.975 | 12.3356 | 1 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited expansion space for CB connections | 33/11 | Red
ENGLAND | FAIRFORD | MINETY | CIRENCESTER | 7.59/25.0 | 51.7036 | -1.7928 | SP 14418 00559 | 15 | 0 | 2.0119 | 9.0908 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on BSP transformers and upstream 132kV feeders | 33/11 | Red
ENGLAND | FARINGDON | MINETY | Stratton (2 x 60) | 6.12/25.0 | 51.6524 | -1.5848 | SU 28819 94924 | 10.5 | 5.07 | 2.8045 | 12.5285 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | FARLINGTON | LOVEDEAN | WYMERING & FORT WIDLEY | 11.23/13.1 | 50.8392 | -1.0442 | SU 67400 04843 | 26 | 0 | 1.9017 | 10.9216 | 0 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | FARNBOROUGH | FLEET BRAMLEY | CAMBERLEY RESERVE | 7.18/13.1 | 51.2777 | -0.73396 | SU 88404 53930 | 30 | 0 | 3.942 | 15.7868 | 0 | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | FARNHAM | FLEET BRAMLEY | ALDERSHOT | 10.43/13.1 | 51.2179 | -0.79125 | SU 84517 47217 | 22 | 0 | 3.8829 | 20.0338 | 0 | 20 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | FARNHAM ROYAL | IVER 132KV | SLOUGH | 13.25/25.0 | 51.5364 | -0.62308 | SU 95597 82844 | 48 | 0 | 7.06 | 27.79 | 12 | 19 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | FELTHAM | LALEHAM | EAST BEDFONT A | 12.1/13.1 | 51.4435 | -0.40959 | TQ 10628 72811 | 3 x 12.5 | - | 3.7 | 11.2 | - | 16 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
ENGLAND | FERNDOWN | MANNINGTON GSP | MANNINGTON | 11.38/13.0 | 50.8057 | -1.9078 | SU 06593 00685 | 45 | 0 | 5.5328 | 24.0056 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | FIVE OAKS | FLEET BRAMLEY | ALTON & FERNHURST | 8.54/13.1 | 51.0502 | -0.42283 | TQ 10647 29057 | 15 | 0 | 1.88 | 9.9253 | 11.4 | 5 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP. Voltage issues. Fault level reinforcement required at Fernhurst 33 kV | 33/11 | Red
ENGLAND | FLACKWELL HEATH | AMERSHAM | LOUDWATER | 11.45/13.1 | 51.5954 | -0.69247 | SU 90667 89318 | 26.7 | 0 | 1.9282 | 12.01 | 1.4 | 27.2282 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | FLETCHWOOD | NURSLING | ROWNHAMS | 7.7/25.0 | 50.9078 | -1.5206 | SU 33800 12142 | 30 | 0 | 4.4658 | 17.6428 | 0 | 31 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | FORDINGBRIDGE | MANNINGTON GSP | MANNINGTON | 6.41/13.1 | 50.939 | -1.8011 | SU 14069 15523 | 15 | 0 | 1.5594 | 7.0552 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | No spare bay.BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | FRATTON PARK | LOVEDEAN | PORTSMOUTH | 11.20/13.1 | 50.7974 | -1.0629 | SU 66139 00180 | 34 | 0 | 5.9886 | 24.5865 | 0 | 40 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | FRENCHAY ROAD | COWLEY | OXFORD (Osney) | 10.28/13.1 | 51.7707 | -1.2706 | SP 50426 08256 | 19.5 | 0 | 2.8548 | 10.4708 | 0 | 11 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | FRESHWATER | FAWLEY | COWES & WOOTTON COMMON | 6.3/25.0 | 50.6813 | -1.5155 | SZ 34325 86965 | 15 | 0 | 1.42 | 6.5788 | 0.45 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | FRIMLEY | FLEET BRAMLEY | CAMBERLEY RESERVE | 7.79/12.5 | 51.3138 | -0.74242 | SU 87745 57942 | 30 | 0 | 4.7762 | 24.4059 | 1.4 | 33 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Green
ENGLAND | FROME | MELKSHAM | FROME | 11.48/25 | 51.2312 | -2.3043 | ST 78850 48051 | 46 | 0 | 7.4804 | 28.7827 | 2.72 | 10 | 50 | Unconstrained |  |  | Unconstrained | 11kV CB reinforcement | T232 | Yes | No | Constrained by the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | FRYERS LANE | COWLEY | HIGH WYCOMBE | 11.8/13.1 | 51.6373 | -0.7741 | SU 84935 93873 | 26 | 0 | 2.8693 | 14.971 | 0 | 21 | 50 | Unconstrained |  |  | Unconstrained |  | CB reinforcement | Yes | No | None known | 33/11 | Green
ENGLAND | FULSCOT | COWLEY | DRAYTON | 10.73/13.1 | 51.6018 | -1.2158 | SU 54413 89511 | 21 | 0 | 2.91 | 16.3733 | 7.56 | 7 | 50 | Constrained | 33kV reinforcements between Milton - Drayton |  | Unconstrained |  |  | Yes | No | Constrained due to 33kV circts limitations under FCO. | 33/11 | Red
ENGLAND | FYFIELD | COWLEY | WITNEY & YARNTON | 4.83/25.0 | 51.6931 | -1.3901 | SU 42256 99551 | 15 | 0 | 2.0576 | 9.5202 | 0 | 3 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | GABLE HEAD | LOVEDEAN | HAVANT | 8.4/13.1 | 50.7942 | -0.97692 | SZ 72204 99904 | 30 | 0 | 2.5379 | 12.7308 | 0.24 | 32 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | GAMBLE ROAD | LOVEDEAN | WYMERING & FORT WIDLEY | 9.34/25.0 | 50.8119 | -1.082 | SU 64771 01769 | 30 | 0 | 5.1669 | 19.0092 | 0.8 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | GERRARDS CROSS | IVER 132KV | DENHAM | 13.10/25.0 | 51.5817 | -0.55855 | SU 99973 87964 | 15.2 | 0 | 3.9 | 14.5 | 0 | 11.5 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
ENGLAND | GILLINGHAM | MANNINGTON GSP | SHAFTESBURY | 6.53/25.0 | 51.0309 | -2.2839 | ST 80185 25765 | 30 | 0 | 1.2193 | 7.4361 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | GODALMING | FLEET BRAMLEY | ALDERSHOT | 6.91/13.1 | 51.1904 | -0.61702 | SU 96743 44375 | 30 | 0 | 4.5973 | 19.7005 | 0 | 30 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinf required at Fleet GSP. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinf required at Fleet GSP | 33/11 | Red
ENGLAND | GOLDSMITHS | WILLESDEN | ACTON LANE | 12.1/13.1 | 51.5128 | -0.25642 | TQ 21089 80758 | 2 x 11.5 | - | 3 | 12.2 | - | 9 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | CB fault ratings close to the limit | 22/6.6 | Amber
ENGLAND | GORDON ROAD | NURSLING | WINCHESTER | 8.05/25.0 | 51.0672 | -1.3132 | SU 48217 29991 | 30 | 0 | 5.6979 | 23.8982 | 0 | 0 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | GORING | FLEET BRAMLEY | BURGHFIELD RESERVE | 6.63/25.0 | 51.5417 | -1.1318 | SU 60305 82895 | 15 | 0 | 2.0363 | 6.0249 | 0 | 8 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | GRASSINGHAM ROAD | IVER 132KV | DENHAM | 12.41/13.1 | 51.6088 | -0.55492 | TQ 00165 90988 | 26 | 0 | 4.2616 | 13.2 | 0 | 17.3 | 50 | Unconstrained |  |  | Constrained |  |  | No | No | Moderate proximity to fault rating. | 22/6.6 | Amber
ENGLAND | GREENFORD | WILLESDEN | GREENFORD | 11.1/20.0 | 51.5413 | -0.34753 | TQ 14695 83785 | 2 x 30/60 | - | 18.4 | 46.7 | 1 | 49 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | GREENHAM COMMON | BRAMLEY (ANDO-THAT) | THATCHAM | 8.29/25.0 | 51.3762 | -1.284 | SU 49935 64365 | 24 | 0 | 2.7281 | 6.5633 | 0 | 26 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Green
ENGLAND | GREETHAM STREET | LOVEDEAN | PORTSMOUTH | 9.05/13.1 | 50.7976 | -1.0869 | SU 64445 00178 | 30 | 0 | 3.4624 | 12.9502 | 0.2 | 33 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | GROVE | COWLEY | DRAYTON | 7.23/13.1 | 51.604 | -1.4308 | SU 39515 89611 | 15 | 0 | 5.1002 | 21.0773 | 0 | 7 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. Upstream thermal issues. | 33/11 | Red
ENGLAND | GUSSAGE ST MICHAEL | MANNINGTON GSP | SHAFTESBURY | 2.42/16.0 | 50.9022 | -2.0207 | ST 98638 11417 | 3 | 0 | 0.27435 | 1.5737 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | HAMBLE | BOTLEY WOOD GSP | NETLEY COMMON | 10.62/20.0 | 50.8767 | -1.3281 | SU 47370 08794 | 30 | 7.6 | 5.8013 | 15.9992 | 12.2 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | HAMWORTHY | MANNINGTON GSP | POOLE PS (HAMWORTHY) | 8.4/13.1 | 50.7168 | -1.9999 | SZ 00104 90800 | 22.9 | 0 | 4.0335 | 16.6297 | 0 | 0 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | HAREFIELD | IVER 132KV | DENHAM | 9.34/25.0 | 51.6103 | -0.49948 | TQ 04001 91227 | 10 | 0 | 1.2961 | 4.9 | 0 | 6.3 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
ENGLAND | HARESTOCK | NURSLING | WINCHESTER | 7.31/25.0 | 51.0792 | -1.346 | SU 45908 31300 | 24.3 | 0 | 4.4749 | 16.976 | 0.47 | 0 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | HARVARD LANE | EALING | EALING (D) | 9.0/13.1 | 51.4885 | -0.27273 | TQ 20021 78030 | 2 x 10/12,5 1 x 12/24 | - | 10.6 | 26.4 | 1.6 | 19 | 50 | Constrained |  |  | Unconstrained | EALING 66kV/22kV CB to be replaced to improve fault ratings | TBC | No | No |  | 2022-11-22 | Red
ENGLAND | HASLEMERE | FLEET BRAMLEY | ALTON & FERNHURST | 8.96/25.0 | 51.0778 | -0.72663 | SU 89300 31710 | 21.4 | 0 | 4.6334 | 19.1519 | 0 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | HASLINGBOURNE | FLEET BRAMLEY | ALTON & FERNHURST | 2.86/25.0 | 50.9735 | -0.60289 | SU 98188 20276 | 13 | 0 | 1.5663 | 7.5892 | 0 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP. Voltage issues. Fault level reinforcement required at Fernhurst 33 kV | 33/11 | Red
ENGLAND | HAWKERIDGE | MELKSHAM | FROME | 13.41/25.0 | 51.2762 | -2.196 | ST 86422 53026 | 15 | 18.3 | 3.2618 | 13.337 | 15.34 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | 33kV system thermal constraint on the TROW - HAWK - WBUR - WBUC ring network; plus the thermal constraint on the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | HAWLEY | FLEET BRAMLEY | COXMOOR WOOD | 3.77/13.1 | 51.3118 | -0.7679 | SU 85973 57691 | 23 | 0 | 2.4681 | 12.335 | 0 | 25 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Limited headroom at BSP circa 15MVA | 33/11 | Amber
ENGLAND | HEADINGTON | COWLEY | HEADINGTON | 13.81/25.0 | 51.7688 | -1.2125 | SP 54440 08085 | 40 | 0 | 4.3743 | 17.2973 | 3.6 | 11 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | HEDGE END | NURSLING | VELMORE | 6.3/20.0 | 50.9385 | -1.3035 | SU 49035 15685 | 14.2 | 0 | 1.9509 | 12.3069 | 0 | 16 | 50 | Unconstrained |  |  | Unconstrained | Split Hedge End-Bishops Waltham | 30/01/20 | Yes | Yes | None known | 33/11 | Green
ENGLAND | HENLEY | FLEET BRAMLEY | READING | 7.94/25.0 | 51.5356 | -0.90465 | SU 76070 82422 | 30 | 0 | 4.2867 | 16.748 | 0 | 34 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | HENSTRIDGE | AXMINSTER | YEOVIL | 3.92/25.0 | 50.9721 | -2.3905 | ST 72676 19263 | 24 | 0 | 0.81262 | 10.6807 | 4.23 | 20 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | HERRIARD | FLEET BRAMLEY | ALTON & FERNHURST | 4.88/16.0 | 51.2001 | -1.0457 | SU 66770 44972 | 7.5 | 0 | 0.27 | 1.5245 | 7.4 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | 33kV circuit reinforcement is required for any new connection. Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | HIGH WYCOMBE | COWLEY | HIGH WYCOMBE | 9.01/13.1 | 51.6223 | -0.77742 | SU 84733 92200 | 30 | 0 | 6.0192 | 21.2399 | 1.07 | 21 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | HIGH WYCOMBE TOWN | COWLEY | HIGH WYCOMBE | 13.18/13.1 | 51.629 | -0.75454 | SU 86304 92972 | 46.3 | 0 | 5.687 | 27.0851 | 0 | 21 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Proximity to fault rating | 33/11 | Red
ENGLAND | HILLINGDON | IVER 66KV |  | 13.14/25.0 | 51.5341 | -0.45196 | TQ 07470 82827 | 40 | 0 | 9.401 | 34.8147 | 0 | 50 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | HILSEA | LOVEDEAN | WYMERING & FORT WIDLEY | 8.56/13.1 | 50.83 | -1.0586 | SU 66394 03806 | 30 | 0 | 2.6597 | 14.2038 | 0.327 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | HINCHESLEA | MANNINGTON GSP | ARNEWOOD | 7.06/13.1 | 50.8029 | -1.6068 | SU 27805 00447 | 15 | 0 | 1.7985 | 6.7151 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | HINDHEAD | FLEET BRAMLEY | ALDERSHOT | 5.74/20.0 | 51.1208 | -0.73501 | SU 88631 36479 | 21 | 0 | 2.7435 | 13.1218 | 0 | 16.8 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | 33kV circuit rating is 16.8MVA in summer. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Green
ENGLAND | HINTON MARTELL | MANNINGTON GSP | MANNINGTON | 2.64/7.9 | 50.8538 | -1.9914 | SU 00702 06030 | 4 | 0 | 0.32865 | 1.9367 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | HITCHES LANE | FLEET BRAMLEY | COXMOOR WOOD | 8.55/13.1 | 51.2865 | -0.86196 | SU 79461 54769 | 40 | 0 | 5.0281 | 22.4292 | 4.26 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Limited headroom at BSP circa 15MVA | 33/11 | Red
ENGLAND | HOEFORD | LOVEDEAN | Fareham T1A T2A (90MVAs) | 10.07/13.1 | 50.8365 | -1.1798 | SU 57855 04433 | 19.5 | 0 | 3.93 | 17.2255 | 0.5 | 23 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | HOLES BAY | MANNINGTON GSP | LYTCHETT | 9.86/25.0 | 50.7272 | -1.9911 | SZ 00725 91955 | 30 | 0 | 1.0526 | 20.5573 | 7.87 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | HOLWELL | MELKSHAM | FROME | 7.12/25.0 | 51.2002 | -2.3994 | ST 72191 44633 | 15 | 0 | 1.3717 | 10.5683 | 1 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | 33kV system thermal constraint on the TROW - HAWK - WBUR - WBUC ring network; plus the thermal constraint on the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | HOMINGTON | MANNINGTON GSP | SALISBURY | 3.97/25.0 | 51.0336 | -1.8339 | SU 11742 26037 | 15 | 0 | 1.5607 | 5.4085 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | HOOK | FLEET BRAMLEY | COXMOOR WOOD | 8.61/25.0 | 51.2785 | -0.96049 | SU 72602 53780 | 30 | 0 | 3.4071 | 14.0442 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fault level at Burghfield BSP is at it's limit. Reinforcement required to uprate the 33kV switchboard at Burghfield. | 33/11 | Green
ENGLAND | HOPE AND ANCHOR | LALEHAM | EAST BEDFONT A | 7.7/13.1 | 51.4363 | -0.37988 | TQ 12710 72057 | 1 x 12.5 | - | 0.5 | 2.6 | - | 7 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
ENGLAND | HORNDEAN | LOVEDEAN | HAVANT | 4.95/13.1 | 50.9104 | -1.0019 | SU 70271 12802 | 30 | 0 | 3.1135 | 22.1944 | 8 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | HOUGHTON | NURSLING | WINCHESTER | 3.42/25.0 | 51.084 | -1.5191 | SU 33784 31741 | 9.8 | 0 | 1.5546 | 6.8872 | 5 | 0 | 50 | Partially Constrained |  |  | Unconstrained |  |  | Yes | Yes | Proximity to voltage issues. | 33/11 | Amber
ENGLAND | HOUNDMILLS | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | 9.72/25.0 | 51.2717 | -1.1099 | SU 62187 52886 | 40 | 0 | 6.2795 | 17.644 | 2.5 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level at Burghfield BSP is at it's limit. Reinforcement required to uprate the 33kV switchboard at Burghfield. | 33/11 | Green
ENGLAND | HUNGERFORD | BRAMLEY (ANDO-THAT) | THATCHAM | 5.83/13.1 | 51.4186 | -1.5115 | SU 34066 68957 | 13 | 0 | 1.71 | 9.0354 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Fault level at Burghfield BSP is at it's limit. Reinforcement required to uprate the 33kV switchboard at Burghfield. | 33/11 | Red
ENGLAND | HUNSTON | LOVEDEAN | CHICHESTER & HUNSTON | 12.08/25.0 | 50.8167 | -0.76711 | SU 86949 02632 | 30 | 0 | 4.7999 | 28.8788 | 12 | 5.36 | 50 | Constrained |  |  | Partially Constrained | AVC Upgrade | 01/09/22 | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | HURSTBOURNE TARRANT | MELKSHAM | ANDOVER | 4.2/25.0 | 51.2701 | -1.4368 | SU 39384 52476 | 5 | 0 | 1.1431 | 5.4589 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with no remaining headroom. NG reinforcement works required for Melk SGT capacity constraints, estimated connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | JAYS CLOSE | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | 14.08/20.0 | 51.2466 | -1.098 | SU 63055 50105 | 40 | 0 | 7.9012 | 30.973 | 4 | 37 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | KENNINGTON | COWLEY | Cowley Local (2 x 45) | 4.30/13.1 | 51.7061 | -1.2361 | SP 52881 01094 | 6 | 0 | 0.72862 | 6.7733 | 0.4 | 6 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. | 33/11 | Red
ENGLAND | KENTWOOD HILL | FLEET BRAMLEY | BURGHFIELD MAIN | 10.71/16.0 | 51.4614 | -1.0355 | SU 67102 74048 | 21.9 | 0 | 4.2234 | 19.3328 | 0 | 28 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | KIDDINGTON | COWLEY | WITNEY & YARNTON | 6.2/13.1 | 51.9156 | -1.371 | SP 43362 24301 | 24 | 0 | 2.293 | 10.9434 | 0.179 | 3 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream voltage constraints. | 33/11 | Red
ENGLAND | KIDMORE END | FLEET BRAMLEY | READING | 3.7/25.0 | 51.4985 | -0.99366 | SU 69953 78205 | 14.2 | 0 | 1.5394 | 8.0603 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | KINGS RIDE | FLEET BRAMLEY | CAMBERLEY MAIN | 10.43/13.1 | 51.3461 | -0.74432 | SU 87551 61530 | 24 | 0 | 3.1653 | 14.15 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | KINGSCLERE | BRAMLEY (ANDO-THAT) | THATCHAM | 6.75/25.0 | 51.331 | -1.2553 | SU 51982 59358 | 9.8 | 0 | 1.4937 | 6.1205 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Red
ENGLAND | KINTBURY | BRAMLEY (ANDO-THAT) | THATCHAM | 5.9/13.1 | 51.4021 | -1.4601 | SU 37657 67143 | 10 | 0 | 0.95934 | 5.7601 | 0.2 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Red
ENGLAND | KNOWL HILL | FLEET BRAMLEY | MAIDENHEAD | 5.55/25.0 | 51.5048 | -0.80771 | SU 82849 79105 | 6.5 | 0 | 0.64015 | 4.1495 | 0 | 0 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP Constrained on the 132kV circuits for export | 33/11 | Amber
ENGLAND | LABURNUM ROAD | FLEET BRAMLEY | ALDERSHOT | 12.25/25.0 | 51.247 | -0.769 | SU 86017 50475 | 36.3 | 0 | 6.1886 | 25.1512 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | 3x33kV circuit ratings are 16.8MVA in summer. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | LAMBOURN | BRAMLEY (ANDO-THAT) | THATCHAM | 5.7/25.0 | 51.5019 | -1.5219 | SU 33280 78217 | 9.8 | 0 | 1.4338 | 7.9867 | 0 | 11 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Amber
ENGLAND | LANGLEY | FAWLEY | LANGLEY | 9.66/25 | 50.8106 | -1.3604 | SU 45158 01418 | 15 | 0 | 2.0586 | 9.0683 | 8.33 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | LANGLEY COURT | FLEET BRAMLEY | ALTON & FERNHURST | 7.89/25.0 | 51.0552 | -0.84786 | SU 80847 29056 | 24 | 0 | 2.36 | 10.0048 | 0.217 | 5 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP. Voltage issues. Fault level reinforcement required at Fernhurst 33 kV | 33/11 | Amber
ENGLAND | LARKHILL | AXMINSTER | YEOVIL | 9.57/25.0 | 50.9498 | -2.6608 | ST 53677 16914 | 23 | 0 | 2.4833 | 12.8291 | 0 | 25 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | LEAFIELD | COWLEY | WITNEY & YARNTON | 6.15/13.1 | 51.8352 | -1.5619 | SP 30282 15270 | 6.5 | 0 | 0.85469 | 4.4058 | 0 | 3 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream voltage constraints. | 33/11 | Red
ENGLAND | LEAMINGTON PARK | WILLESDEN | ACTON LANE | 12.3/13.1 | 51.5199 | -0.26407 | TQ 20539 81536 | 2 x 10 | - | 4.2 | 16.2 | - | 9 | 50 | Unconstrained |  |  | Unconstrained | To be upgraded but still limited by the CB at ACTL BSP | TBC | No | No | None known | 22/6.6 | Green
ENGLAND | LECHLADE | MINETY | Stratton (2 x 60) | 5.5/13.1 | 51.7028 | -1.682 | SP 22074 00496 | 7.5 | 0 | 1.1128 | 7.4738 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | LECKHAMPSTEAD | BRAMLEY (ANDO-THAT) | THATCHAM | 4.52/13.1 | 51.496 | -1.3681 | SU 43962 77635 | 6.5 | 0 | 2.1643 | 4.8117 | 0 | 7 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Amber
ENGLAND | LEE-ON-SOLENT | LOVEDEAN | Fareham T1B T2B (1x90, 1x60MVA) | 7.74/13.1 | 50.7994 | -1.1946 | SU 56858 00293 | 24 | 0 | 2.8166 | 13.7867 | 0 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | LEIGH PARK | LOVEDEAN | HAVANT | 13.0/25 | 50.8659 | -0.9762 | SU 72144 07875 | 30.5 | 0 | 4.3614 | 20.5177 | 3.743 | 31 | 50 | Unconstrained |  |  | Unconstrained | Switchgear -E reinforcement (Completed. FL results include new rating). |  | Yes | Yes | Proximity to fault rating | 33/11 | Green
ENGLAND | LITTLE HUNGERFORD | FLEET BRAMLEY | READING | 14.40/17.5 | 51.4422 | -0.91693 | SU 75372 72019 | 42 | 0 | 8.4134 | 25.652 | 4.08 | 35 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | LITTLE MARLOW | COWLEY | HIGH WYCOMBE | 7.78/20.0 | 51.5824 | -0.75967 | SU 86037 87794 | 30 | 0 | 5.0496 | 17.6616 | 0 | 21 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | LORDSHILL | NURSLING | ROWNHAMS | 11.64/13.1 | 50.9426 | -1.4499 | SU 38746 16055 | 30 | 0 | 2.7797 | 14.6934 | 0 | 28 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | LOVE LANE | BRAMLEY (ANDO-THAT) | THATCHAM | 8.85/25.0 | 51.4135 | -1.3208 | SU 47334 68495 | 40 | 0 | 6.4929 | 21.0047 | 0 | 46 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Amber
ENGLAND | LOVELACE ROAD | COWLEY | WITNEY & YARNTON | 4.74/13.1 | 51.7898 | -1.2708 | SP 50395 10376 | 12 | 0 | 1.1169 | 5.8241 | 0 | 3 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Single security Primary. | 33/11 | Red
ENGLAND | LYMINGTON | MANNINGTON GSP | ARNEWOOD | 9.28/13.1 | 50.7704 | -1.5515 | SZ 31720 96856 | 30 | 0 | 3.8605 | 17.9821 | 2.17 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | LYNEHAM | MELKSHAM | CHIPPENHAM | 7.41/13.1 | 51.5232 | -2.0108 | ST 99348 80481 | 7.5 | 0 | 2.6269 | 11.6671 | 2.75 | 1 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 | 33/11 | Red
ENGLAND | MAIDEN NEWTON | CHICKERELL GSP | CHICKERELL | 6.49/25.0 | 50.7779 | -2.5809 | SY 59138 97747 | 10 | 0 | 0.042652 | 10.6758 | 3.71 | 14 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | MAIDENHEAD | FLEET BRAMLEY | MAIDENHEAD | 13/13.1 | 51.5105 | -0.75517 | SU 86485 79800 | 45 | 0 | 1.1288 | 10.221 | 0 | 17.14 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP Constrained on the 132kV circuits for export | 33/11 | Amber
ENGLAND | MALMESBURY | MELKSHAM | CHIPPENHAM | 7.29/13.1 | 51.5862 | -2.1127 | ST 92288 87493 | 10 | 0 | 5.7003 | 28.301 | 1.079 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 plus local voltage constraint. | 33/11 | Red
ENGLAND | MANCHESTER ROAD | MINETY | SWINDON | 11.66/13.1 | 51.5648 | -1.7813 | SU 15254 85130 | 37 | 0 | 3.822 | 10.4628 | 0 | 10 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained by BSP transformer capacity, National Grid reinforcement works required at Minety with an expected completion in 2025-2027 and fault level constraints at primary | 33/11 | Amber
ENGLAND | MANNINGTON | MANNINGTON GSP | MANNINGTON | 8.17/13.1 | 50.8468 | -1.8935 | SU 07592 05256 | 15 | 0 | 7.0904 | 28.7694 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | MARKET | LOVEDEAN | CHICHESTER & HUNSTON | 10.71/13.1 | 50.8357 | -0.77329 | SU 86479 04732 | 20 | 0 | 1.3861 | 7.8703 | 0 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | MARLBOROUGH SOUTH | MELKSHAM | WEST GRAFTON | 4.49/25.0 | 51.4131 | -1.724 | SU 19293 68264 | 15 | 0 | 2.9652 | 15.1135 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
ENGLAND | MAYBUSH | NURSLING | ROWNHAMS | 13.21/25 | 50.9325 | -1.4546 | SU 38426 14930 | 26 | 0 | 3.8714 | 11.8763 | 2 | 28 | 50 | Unconstrained |  |  | Unconstrained | Maybush-E switchgear reinforcement | 01/03/21 | Yes | Yes | None known | 33/11 | Green
ENGLAND | MELKSHAM TOWN | MELKSHAM | NORRINGTON | 13.24/25 | 51.3758 | -2.1426 | ST 90170 64096 | 30 | 10 | 3.6213 | 15.8712 | 8.829 | 15 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | No | no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | MEYRICK ROAD | LOVEDEAN | HAVANT | 8.45/25.0 | 50.8534 | -0.99487 | SU 70849 06469 | 25.4 | 0 | 5.2502 | 23.9869 | 0 | 29 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | MIDDLE WALLOP | MELKSHAM | ANDOVER | 4.37/13.1 | 51.1598 | -1.5583 | SU 30984 40155 | 7 | 0 | 4.1914 | 18.4193 | 4.8 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Wide constraints on 33kV, 132kV systems and BSP capacity. | 33/11 | Red
ENGLAND | MIDHURST | FLEET BRAMLEY | ALTON & FERNHURST | 8.38/13.1 | 50.9687 | -0.74632 | SU 88127 19555 | 30 | 0 | 0.84642 | 4.6059 | 5 | 19 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP. Voltage issues. Fault level reinforcement required at Fernhurst 33 kV | 33/11 | Amber
ENGLAND | MILBORNE PORT | AXMINSTER | YEOVIL | 2.49/13.1 | 50.9762 | -2.4582 | ST 67929 19741 | 3.5 | 0 | 3.4022 | 12.9511 | 4 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations.There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | MILFORD | FLEET BRAMLEY | ALDERSHOT | 6.43/20.0 | 51.1786 | -0.64633 | SU 94719 43018 | 24 | 0 | 0.58417 | 3.126 | 0.177 | 26 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | MILFORD-ON-SEA | MANNINGTON GSP | ARNEWOOD | 7.28/25.0 | 50.7391 | -1.601 | SZ 28252 93347 | 13 | 0 | 3.6092 | 12.5604 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | No spare bay. | 33/11 | Red
ENGLAND | MILL LANE | MANNINGTON GSP | MANNINGTON | 8.88/13.1 | 50.85 | -1.7927 | SU 14691 05633 | 22.9 | 0 | 1.89 | 9.5849 | 8.6 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | MILTON | COWLEY | DRAYTON | 15.49/16.0 | 51.6251 | -1.2792 | SU 49992 92060 | 46.4 | 0 | 4.6572 | 20.1904 | 6.837 | 7 | 50 | Constrained | 33kV reinforcements between Milton - Drayton |  | Unconstrained |  |  | Yes | No | Upstream thermal constraints. | 33/11 | Green
ENGLAND | MINCHINGTON | MANNINGTON GSP | SHAFTESBURY | 2.53/12.0 | 50.9301 | -2.056 | ST 96164 14520 | 5 | 0 | 9.7638 | 39.283 | 0 | 0 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | MINETY VILLAGE | MINETY | CIRENCESTER | 6.38/13.1 | 51.6262 | -1.9776 | SU 01647 91932 | 15 | 0 | 0.42327 | 3.0176 | 3.158 | 0 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | voltage constraint on 33kV system, thermal constraint on BSP transformers and upstream 132kV feeders | 33/11 | Red
ENGLAND | MORTIMER | FLEET BRAMLEY | BURGHFIELD RESERVE | 5.32/13.1 | 51.3726 | -1.1073 | SU 62236 64103 | 15 | 0 | 1.069 | 4.291 | 0 | 11 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | Circa 7MW export headroom on 33kV circuits upstream. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | MVEE | FLEET BRAMLEY | BRACKNELL RESERVE | 8.01/13.1 | 51.3841 | -0.5914 | SU 98120 65945 | 30 | 0 | 1.6918 | 8.9453 | 0 | 30 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP 33kV CBs close to fault rating | 33/11 | Amber
ENGLAND | NETHERHAMPTON | MANNINGTON GSP | SALISBURY | 8.1/13.1 | 51.0611 | -1.8233 | SU 12478 29102 | 13 | 0 | 0.67063 | 3.929 | 9.8 | 0 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | NETLEY COMMON 11KV | BOTLEY WOOD GSP | NETLEY COMMON | 12.25/13.1 | 50.9057 | -1.3242 | SU 47615 12025 | 30 | 0 | 7.3373 | 28.4297 | 0 | 34.6 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | NEW MILTON | MANNINGTON GSP | ARNEWOOD | 9.26/13.1 | 50.7536 | -1.6746 | SZ 23049 94942 | 30 | 0 | 6.0351 | 20.271 | 2.749 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | No spare bay. | 33/11 | Red
ENGLAND | NEW STREET | MANNINGTON GSP | MANNINGTON | 4.11/25.0 | 50.8417 | -1.785 | SU 15233 04713 | 5 | 0 | 0.40725 | 1.802 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | NEWPORT | FAWLEY | COWES & WOOTTON COMMON | 11.22/13.1 | 50.7034 | -1.2923 | SZ 50076 89544 | 38 | 0 | 6.2606 | 29.9817 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. ANM scheme in place on IOW to ease some of the 132kV constraints. 11kV CBs reinforcement will be required. | 33/11 | Red
ENGLAND | NORMANDY | FLEET BRAMLEY | ALDERSHOT | 2.61/16.0 | 51.2676 | -0.66519 | SU 93221 52894 | 2.5 | 0 | 0.51239 | 2.6619 | 0 | 3 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | NORTH BADDESLEY | NURSLING | ROWNHAMS | 10.55/13.1 | 50.9833 | -1.4589 | SU 38080 20568 | 19.5 | 0 | 4.2002 | 15.7888 | 0 | 23 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | NORTH FAREHAM | LOVEDEAN | Fareham T1A T2A (90MVAs) | 7.5/13.1 | 50.8636 | -1.1996 | SU 56427 07430 | 15.2 | 0 | 1.4373 | 15.282 | 0 | 17 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | NORTH FELTHAM | LALEHAM | EAST BEDFONT A | 10.0/25.0 | 51.462 | -0.40378 | TQ 10987 74875 | 1 x 12.5 2 x 11.5 | - | 9 | 23.5 | 2.3 | 17 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 2022-11-22 | Green
ENGLAND | NORTH HINKSEY | COWLEY | OXFORD (Osney) | 7.11/25.0 | 51.7362 | -1.297 | SP 48645 04403 | 9.8 | 0 | 1.4327 | 7.05 | 1.3 | 9 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | No spare bay. | 33/11 | Red
ENGLAND | NORTHLEACH | MINETY | CIRENCESTER | 5.78/25.0 | 51.8268 | -1.8482 | SP 10557 14251 | 10 | 0 | 1.5851 | 6.592 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on BSP transformers and upstream 132kV feeders | 33/11 | Red
ENGLAND | NORTHOLT | IVER 66KV |  | 11.84/13.1 | 51.537 | -0.39304 | TQ 11550 83230 | 38 | 0 | 7.291 | 28.2427 | 0 | 44 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | NORTHUMBERLAND AVENUE | FLEET BRAMLEY | READING | 12.83/25.0 | 51.4342 | -0.96265 | SU 72207 71092 | 25 | 0 | 4.5725 | 17.4193 | 3 | 27 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | NUFFIELD | COWLEY | HIGH WYCOMBE | 3.47/25.0 | 51.5758 | -1.0154 | SU 68329 86784 | 7 | 0 | 0.96022 | 5.0385 | 0 | 1 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream Voltage & thermal issues. | 33/11 | Red
ENGLAND | OAKRIDGE | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | 7.94/13.1 | 51.2786 | -1.091 | SU 63496 53664 | 30 | 0 | 2.6292 | 10.119 | 0 | 32 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | OLD ROAD | COWLEY | HEADINGTON | 10.83/13.1 | 51.7538 | -1.2007 | SP 55274 06426 | 30 | 0 | 5.5366 | 16.8533 | 0.344 | 11 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | OSNEY | COWLEY | OXFORD (Osney) | 9.26/13.1 | 51.7496 | -1.275 | SP 50148 05901 | 30 | 0 | 5.31 | 24.0474 | 0.504 | 11 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | OVERTON | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | 9.58/13.1 | 51.255 | -1.2554 | SU 52061 50913 | 16 | 0 | 1.046 | 14.6827 | 11.6 | 6 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | PADWORTH | FLEET BRAMLEY | BURGHFIELD RESERVE | 3.65/13.1 | 51.3901 | -1.1068 | SU 62243 66052 | 5 | 0 | 0.48142 | 3.3781 | 0 | 5 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | PANGBOURNE | FLEET BRAMLEY | BURGHFIELD RESERVE | 8.51/25.0 | 51.4808 | -1.0948 | SU 62960 76144 | 30 | 0 | 1.9776 | 11.316 | 0 | 20 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Green
ENGLAND | PARK GATE | BOTLEY WOOD GSP | BOTLEY WOOD | 8.27/13.1 | 50.8716 | -1.2713 | SU 51369 08259 | 30 | 0 | 4.8897 | 21.8539 | 0 | 27 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PARK HOUSE | BRAMLEY (ANDO-THAT) | AMESBURY | 4.3/25.0 | 51.1928 | -1.6703 | SU 23138 43780 | 4 | 0 | 0.1829 | 3.302 | 0 | 4 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations. Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. Upstream 132kV capacity for export is circa 15MVA flexible | 33/11 | Red
ENGLAND | PARK NORTH | MINETY | Stratton (2 x 90) | 9.27/13.1 | 51.5595 | -1.741 | SU 18052 84542 | 30 | 0 | 4.8778 | 19.4529 | 1 | 15 | 50 | Partially Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PARK ROYAL | WILLESDEN | ACTON LANE | 12.1/13.1 | 51.5261 | -0.26963 | TQ 20137 82215 | 2 x 11.5 | - | 2.5 | 10.2 | - | 8 | 50 | Unconstrained |  |  | Partially Constrained |  |  | No | No | CB fault ratings close to the limit | 22/6.6 | Amber
ENGLAND | PARKSTONE NORTH | MANNINGTON GSP | BOURNEMOUTH | 9.58/13.1 | 50.7297 | -1.9557 | SZ 03222 92233 | 29.8 | 0 | 5.4421 | 24.561 | 0 | 35 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PARKSTONE SOUTH | MANNINGTON GSP | BOURNEMOUTH | 11.38/25.0 | 50.7082 | -1.9339 | SZ 04762 89848 | 30 | 0 | 2.4539 | 9.378 | 0 | 32 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PEACOCK FARM | FLEET BRAMLEY | WOKINGHAM | 7.36/25.0 | 51.4111 | -0.78253 | SU 84770 68709 | 15 | 0 | 1.2559 | 7.0238 | 31.6 | 16 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP approaching transformer reverse power capacity. | 33/11 | Green
ENGLAND | PERIVALE | WILLESDEN | PERIVALE | 13.8/25.0 | 51.5332 | -0.30675 | TQ 17544 82947 | 2 x 20/40 | - | 14.2 | 36.2 | - | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | PETERSFIELD | FLEET BRAMLEY | ALTON & FERNHURST | 6.02/13.1 | 51.0054 | -0.94422 | SU 74173 23420 | 30 | 0 | 5.3462 | 21.1769 | 0.25 | 5 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP. Voltage issues. Fault level reinforcement required at Fernhurst 33 kV | 33/11 | Red
ENGLAND | PETERSFIELD AVENUE | IVER 132KV | CHALVEY | 18.63/25.0 | 51.513 | -0.5876 | SU 98108 80286 | 42 | 0 | 12.89 | 37.9 | 3.94 | 30 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | PETERSFINGER | MANNINGTON GSP | SALISBURY | 6.61/13.1 | 51.0631 | -1.7786 | SU 15608 29334 | 14 | 0 | 2.3891 | 13.4211 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | PEWSEY | BRAMLEY (ANDO-THAT) | AMESBURY | 2.84/25.0 | 51.3322 | -1.7902 | SU 14710 59252 | 17 | 0 | 1.3396 | 9.5413 | 0 | 17 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Connections might not be possible prior to Andover-Amesbury reconfiguration scheme. Upstream 132kV capacity for export is circa 15MVA flexible | 33/11 | Amber
ENGLAND | PIDDLETRENTHIDE | CHICKERELL GSP | CHICKERELL | 5.37/13.1 | 50.7971 | -2.4246 | SY 70169 99809 | 5 | 0 | 0.31066 | 3.3656 | 0 | 6 | 50 | Constrained |  |  | Partially Constrained |  |  | No | Yes | Moderate proximity to Primary transformers limitations.There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | PINGEWOOD | FLEET BRAMLEY | READING | 6.1/25.0 | 51.4099 | -1.0131 | SU 68735 68336 | 14.3 | 0 | 1.4632 | 7.9179 | 0 | 15 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | PLAISTOW | FLEET BRAMLEY | ALTON & FERNHURST | 3.39/20.0 | 51.0569 | -0.54497 | TQ 02071 29626 | 4.85 | 0 | 0.98974 | 7.2908 | 0.322 | 10 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP. Voltage issues. Fault level reinforcement required at Fernhurst 33 kV | 33/11 | Red
ENGLAND | PLESSEY | MINETY | Stratton (2 x 90) | 8.58/20.0 | 51.5791 | -1.765 | SU 16381 86720 | 15 | 0 | 2.7435 | 10.9633 | 0 | 7 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PLESSEY TITCHFIELD | LOVEDEAN | Fareham T1A T2A (90MVAs) | 8.07/12.5 | 50.8594 | -1.2428 | SU 53390 06922 | 30 | 0 | 3.9508 | 14.6982 | 0 | 16 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | POOLE (HILL STREET) | MANNINGTON GSP | POOLE PS (HAMWORTHY) | 12.6/13.1 | 50.715 | -1.9859 | SZ 01091 90595 | 23 | 0 | 4.0118 | 13.9036 | 3.4 | 0 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | Yes | Proximity to fault rating | 33/11 | Red
ENGLAND | PORTCHESTER | LOVEDEAN | WYMERING & FORT WIDLEY | 11.14/13.1 | 50.8464 | -1.1201 | SU 62043 05575 | 19.5 | 0 | 4.3118 | 15.3926 | 3.5 | 18 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PORTLAND | CHICKERELL GSP | CHICKERELL | 8.70/13.1 | 50.5644 | -2.4488 | SY 68307 73941 | 18.1 | 0 | 2.8349 | 11.8874 | 2.4 | 18 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | PORTSMOUTH | LOVEDEAN | PORTSMOUTH | 11.35/25.0 | 50.7933 | -1.1018 | SZ 63405 99685 | 40 | 0 | 3.1978 | 12.329 | 1.25 | 23 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PORTWAY | MELKSHAM | ANDOVER | 10.33/13.1 | 51.2122 | -1.5089 | SU 34402 46001 | 26 | 0 | 1.5969 | 17.387 | 12.326 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with noheadroom. NG reinforcement works required for Melksham SGT capacity constraints, estimated connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | POYLE | IVER 132KV | LONGFORD | 10.99/25.0 | 51.4695 | -0.51239 | TQ 03425 75555 | 25.7 | 0 | 4.923 | 20.76 | 0 | 17.8 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | PRESSED STEEL SWINDON | MINETY | Stratton (2 x 90) | 12.91/31.5 | 51.5759 | -1.7566 | SU 16963 86368 | 10 | 0 | 1.8237 | 9.0937 | 0 | 5 | 50 | Unconstrained |  |  | Unconstrained | 11kV CB reinforcement | 2024-03-31 | Yes | Yes | None known | 33/11 | Red
ENGLAND | PRESTON CANDOVER | FLEET BRAMLEY | ALTON & FERNHURST | 7.28/25.0 | 51.1662 | -1.1307 | SU 60879 41131 | 15 | 0 | 1.06 | 4.965 | 20 | 0 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | 33kV circuit reinforcement is required for any new connection. Limited flexible headroom on the 132 kV circuits from Fleet. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV fault level reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | PUDDLETOWN | CHICKERELL GSP | CHICKERELL | 4.49/13.1 | 50.7544 | -2.3667 | SY 74226 95039 | 6.3 | 0 | 0.46296 | 2.5868 | 0 | 6 | 50 | Constrained |  |  | Partially Constrained |  |  | No | Yes | Moderate proximity to Primary transformers limitations.There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | PULHAM | AXMINSTER | YEOVIL | 4.4/13.1 | 50.8838 | -2.4054 | ST 71579 09451 | 5 | 0 | 0.9765 | 5.208 | 0 | 7 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | PURBROOK | LOVEDEAN | WYMERING & FORT WIDLEY | 8.22/13.1 | 50.866 | -1.0486 | SU 67047 07819 | 13 | 0 | 1.19 | 7.1624 | 0 | 15 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | PYESTOCK 33/11 | FLEET BRAMLEY | PYESTOCK | 10.2/20.0 | 51.2841 | -0.81213 | SU 82940 54553 | 24 | 0 | 0.9145 | 8.448 | 0 | 0 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | QUARRY ROAD | MINETY | TOOTHILL | 12.82/31.5 | 51.5491 | -1.7803 | SU 15334 83380 | 20 | 0 | 3.6082 | 14.8261 | 1.8 | 0 | 50 | Constrained |  |  | Constrained | 11kV CB reinforcement | 2023-03-31 | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | QUEENSMEAD | FLEET BRAMLEY | CAMBERLEY RESERVE | 7.82/13.1 | 51.2936 | -0.75277 | SU 87062 55683 | 13 | 0 | 1.8315 | 8.4661 | 0 | 14 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | RAMSBURY | MELKSHAM | WEST GRAFTON | 3.84/13.1 | 51.4473 | -1.6074 | SU 27380 72108 | 8 | 0 | 0.85469 | 4.5061 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
ENGLAND | READING | FLEET BRAMLEY | READING | 14.75/20.0 | 51.4582 | -0.92779 | SU 74591 73788 | 55 | 0 | 9.5839 | 30.7446 | 1.14 | 65 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | READING TOWN | FLEET BRAMLEY | READING TOWN | 8.40/13.1 | 51.4616 | -0.97163 | SU 71540 74122 | 60 | 0 | 7.6589 | 32.0978 | 0.5 | 68 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | REDHILL | MANNINGTON GSP | REDHILL | 8.5/25.0 | 50.7649 | -1.8807 | SZ 08512 96149 | 39 | 0 | 2.951 | 21.8339 | 8.71 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | REDLANDS | CHICKERELL GSP | CHICKERELL | 9.36/13.1 | 50.6396 | -2.4662 | SY 67131 82321 | 15 | 0 | 2.3777 | 11.309 | 0 | 17 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | REDLYNCH | MANNINGTON GSP | SALISBURY | 3.90/13.1 | 50.9843 | -1.7297 | SU 19073 20576 | 9 | 0 | 1.44 | 7.5426 | 7.6 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | REGENTS PARK | NURSLING | Southampton (2 x 90) | 8.78/13.1 | 50.9156 | -1.4428 | SU 39267 13050 | 30 | 0 | 3.2443 | 16.0258 | 1.2 | 32 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | RISSINGTON | COWLEY | WITNEY & YARNTON | 3.07/16.0 | 51.8743 | -1.7222 | SP 19225 19563 | 10.3 | 0 | 1.2955 | 5.9414 | 0 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. Upstream voltage issues. | 33/11 | Red
ENGLAND | RIVERSIDE | BRAMLEY (ANDO-THAT) | THATCHAM | 12.11/20.0 | 51.4017 | -1.3136 | SU 47846 67187 | 22.9 | 0 | 2.4874 | 12.6529 | 0 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Amber
ENGLAND | ROCKBOURNE | MANNINGTON GSP | MANNINGTON | 1.39/16.0 | 50.9596 | -1.836 | SU 11617 17810 | 2 | 0 | 0.31257 | 1.9803 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | ROMSEY | NURSLING | ROWNHAMS | 8.37/13.1 | 50.9883 | -1.4872 | SU 36092 21110 | 21 | 0 | 3.3001 | 16.4942 | 0 | 7.1 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to 33kV circts limitations under FCO. | 33/11 | Green
ENGLAND | ROSE GREEN | LOVEDEAN | CHICHESTER & HUNSTON | 11.07/13.1 | 50.7866 | -0.72499 | SZ 89974 99335 | 20 | 0 | 2.15 | 13.2669 | 8.045 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | ROSE HILL | COWLEY | Cowley Local (2 x 90) | 10.95/13.1 | 51.7234 | -1.2249 | SP 53637 03027 | 26 | 0 | 3.4474 | 15.9116 | 0.8 | 29 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | ROWDEN | MELKSHAM | CHIPPENHAM | 8.93/13.1 | 51.4524 | -2.1337 | ST 90805 72608 | 23 | 0 | 3.6088 | 21.3908 | 0 | 1 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 | 33/11 | Red
ENGLAND | ROWNER PARK | LOVEDEAN | Fareham T1B T2B (1x90, 1x60MVA) | 8.92/13.1 | 50.8037 | -1.178 | SU 58018 00782 | 30 | 0 | 2.3984 | 8.5597 | 0 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | RYDE | FAWLEY | COWES & WOOTTON COMMON | 7.93/13.1 | 50.7243 | -1.1577 | SZ 59554 91973 | 30 | 0 | 4.3955 | 18.425 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | SALISBURY CENTRAL | MANNINGTON GSP | SALISBURY | 13.4/17.5 | 51.0735 | -1.7985 | SU 14215 30481 | 40 | 0 | 7.6208 | 24.7181 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | SANDHURST | FLEET BRAMLEY | CAMBERLEY MAIN | 7.22/13.1 | 51.3413 | -0.80122 | SU 83597 60930 | 30 | 0 | 5.0496 | 21.2545 | 0.2 | 29 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | SANDOWN | FAWLEY | COWES & WOOTTON COMMON | 7.71/13.1 | 50.6621 | -1.1542 | SZ 59877 85052 | 15 | 0 | 3.0036 | 12.2416 | 1.98 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | SELSEY | LOVEDEAN | CHICHESTER & HUNSTON | 6.93/20.0 | 50.7419 | -0.78725 | SZ 85667 94289 | 11.9 | 0 | 2.53 | 9.8924 | 0 | 9 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | SHAFTESBURY | MANNINGTON GSP | SHAFTESBURY | 9.5/16.0 | 51.0091 | -2.2066 | ST 85605 23325 | 13 | 0 | 2.7559 | 11.9403 | 0.317 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | SHALFLEET | FAWLEY | COWES & WOOTTON COMMON | 7.36/25.0 | 50.696 | -1.4233 | SZ 40828 88643 | 15 | 0 | 1.1584 | 7.6178 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | SHANKLIN | FAWLEY | COWES & WOOTTON COMMON | 7.17/13.1 | 50.634 | -1.1839 | SZ 57809 81912 | 30 | 0 | 1.8219 | 12.0461 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | SHERBORNE | AXMINSTER | YEOVIL | 7.55/13.1 | 50.9618 | -2.5143 | ST 63978 18163 | 10 | 0 | 2.2721 | 8.097 | 0 | 7 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Limited expansion space for CB connections,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | SHIPTON OLIFFE | MINETY | CIRENCESTER | 2.89/13.1 | 51.8705 | -1.945 | SP 03884 19102 | 3 | 0 | 0.68 | 4.1708 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on BSP transformers and upstream 132kV feeders | 33/11 | Red
ENGLAND | SHIRLEY | NURSLING | Southampton (2 x 90) | 8.35/25.0 | 50.9224 | -1.4325 | SU 39988 13808 | 30 | 0 | 3.8287 | 16.1392 | 0 | 33 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | SHRIVENHAM | MINETY | Stratton (2 x 60) | 6.99/13.1 | 51.5895 | -1.6581 | SU 23782 87902 | 15 | 0 | 1.7604 | 6.5985 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | SHROTON | MANNINGTON GSP | SHAFTESBURY | 6.83/25.0 | 50.9222 | -2.2097 | ST 85356 13659 | 24 | 0 | 1.99 | 10.5216 | 6.6 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | SIDNEY ROAD | LALEHAM | STAINES | 9.8/13.1 | 51.4353 | -0.50379 | TQ 04100 71760 | 2 x 15/30 | - | 2.8 | 14.1 | 1.3 | 17 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Amber
ENGLAND | SILKSTEAD | NURSLING | ROWNHAMS | 5.3/13.1 | 51.0187 | -1.3658 | SU 44578 24565 | 13 | 0 | 1.6544 | 7.6761 | 2.07 | 12 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | SILVER STREET | FLEET BRAMLEY | READING | 12.22/13.1 | 51.4498 | -0.96589 | SU 71957 72821 | 26.6 | 0 | 3.8714 | 18.3567 | 7 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate proximity to fault rating. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | SOMERFORD | MANNINGTON GSP | CHRISTCHURCH | 11.62/13.1 | 50.7416 | -1.7426 | SZ 18262 93590 | 26 | 0 | 4.9906 | 18.9909 | 1 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | SOUTH BERSTED | LOVEDEAN | CHICHESTER & HUNSTON | 11.42/16.0 | 50.7983 | -0.66719 | SU 94025 00705 | 20 | 0 | 3.3862 | 21.1985 | 10.453 | 2 | 50 | Constrained |  |  | Unconstrained | 11kV switchgear rating is just above the Fault level at HV. |  | Yes | Yes | There is no reverse power capacity at the BSB and new generations will requier new BSP Transformer, AVC reinfocement, 33kV switchgear reinforcement at Chichester BSP | 33/11 | Amber
ENGLAND | SOUTHBOURNE | MANNINGTON GSP | CHRISTCHURCH | 11.74/25.0 | 50.7281 | -1.8092 | SZ 13563 92074 | 19.5 | 0 | 2.5911 | 11.8411 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | SOUTHCOTE | FLEET BRAMLEY | BURGHFIELD RESERVE | 11.45/16.0 | 51.4368 | -1.0202 | SU 68199 71325 | 19.5 | 0 | 1.9722 | 9.2832 | 0.21 | 21 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | SPARKFORD | AXMINSTER | YEOVIL | 6.88/13.1 | 51.0275 | -2.5608 | ST 60767 25496 | 5 | 0 | 0.59877 | 4.3067 | 0.2 | 7 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | SPRING QUARRY WEST | MELKSHAM | NORRINGTON | 10.46/13.1 | 51.4173 | -2.2262 | ST 84368 68717 | 30 | 0 | 0.93817 | 9.7452 | 12 | 15 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | SPRINGFIELD ROAD | NORTH HYDE | NORTH HYDE (D) | 11.21/13.1 | 51.5135 | -0.39589 | TQ 11409 80620 | 27.4 | 0 | 4.2909 | 19.4038 | 0 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/6.6 | Green
ENGLAND | ST CROSS | NURSLING | WINCHESTER | 10.24/13.1 | 51.0508 | -1.3268 | SU 47287 28156 | 26 | 0 | 4.2886 | 16.2159 | 0.234 | 0 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | ST EBBES | COWLEY | OXFORD (Osney) | 10.39/25.0 | 51.748 | -1.2589 | SP 51259 05741 | 30 | 0 | 4.5877 | 18.6748 | 0.7 | 11 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | ST JOHNS | BRAMLEY (ANDO-THAT) | THATCHAM | 10.52/13.1 | 51.3944 | -1.3242 | SU 47113 66363 | 25.3 | 0 | 4.5115 | 20.9073 | 0 | 25 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Red
ENGLAND | STANDLAKE | COWLEY | WITNEY & YARNTON | 4.93/13.1 | 51.7185 | -1.438 | SP 38923 02349 | 6.5 | 0 | 0.47853 | 6.7466 | 2 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to Primary transformers limitations under FCO. Upstream thermal issues. | 33/11 | Red
ENGLAND | STANTON FITZWARREN | MINETY | Stratton (2 x 60) | 9.15/25.0 | 51.6174 | -1.7474 | SU 17585 90987 | 14 | 0 | 2.5931 | 12.4931 | 7.5 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | STANWELL | LALEHAM | STAINES | 9.0/13.1 | 51.444 | -0.47612 | TQ 06003 72766 | 2 x 15/30 | - | 3.3 | 10.4 | - | 18 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Amber
ENGLAND | STAPLEFORD | MANNINGTON GSP | SALISBURY | 6.3/13.1 | 51.1329 | -1.9032 | SU 06871 37078 | 13 | 0 | 2.1559 | 7.0289 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | STOKENCHURCH | COWLEY | HIGH WYCOMBE | 6.53/20.0 | 51.6427 | -0.88684 | SU 77124 94355 | 9.8 | 0 | 2.0119 | 8.9368 | 0 | 1 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream voltage & thermal constraints. | 33/11 | Red
ENGLAND | STRATTON | MINETY | Stratton (2 x 60) | 10.94/25.0 | 51.5981 | -1.756 | SU 16998 88837 | 30 | 0 | 3.9071 | 14.5376 | 6.1 | 0 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | SUNBURY CROSS | LALEHAM | STAINES | 10.2/25.0 | 51.4183 | -0.41873 | TQ 10053 69996 | 2 x 15/30, 1 x 28 | - | 13.4 | 40.9 | 15.4 | 28 | 50 | Partially Constrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Amber
ENGLAND | SUNGARD | LALEHAM | EAST BEDFONT A | 7.0/25.0 | 51.4687 | -0.39868 | TQ 11325 75625 | 2 x 12/24 | - | 5.3 | 7 | - | 29 | 95 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 2022-11-22 | Green
ENGLAND | SUNNINGHILL | FLEET BRAMLEY | BRACKNELL RESERVE | 7.52/13.1 | 51.3997 | -0.65364 | SU 93757 67606 | 24 | 0 | 2.8959 | 12.9812 | 0 | 27 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | BSP 33kV CBs close to fault rating | 33/6.6 | Green
ENGLAND | SUTTON BENGER | MELKSHAM | CHIPPENHAM | 6.81/13.1 | 51.5193 | -2.0966 | ST 93394 80051 | 15 | 0 | 1.0517 | 11.7722 | 0.914 | 0 | 50 | Constrained |  |  | Constrained | Transformer upgrade | 2021-12-01 | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 | 33/11 | Red
ENGLAND | SUTTON LANE | IVER 132KV | UPTON | 8.35/25.0 | 51.4971 | -0.52936 | TQ 02185 78595 | 24 | 0 | 2.9 | 11.7 | 8.8 | 6.1 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
ENGLAND | SWANAGE | MANNINGTON GSP | WAREHAM | 5.29/25.0 | 50.6134 | -1.973 | SZ 02010 79296 | 13 | 0 | 2.5667 | 9.8191 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | SWINDON | MINETY | SWINDON | 10.45/13.1 | 51.5814 | -1.8217 | SU 12449 86967 | 60 | 0 | 8.0529 | 34.6753 | 5.66 | 10 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained by BSP transformer capacity, National Grid reinforcement works required at Minety with an expected completion in 2025-2027 and fault level constraints at primary | 33/11 | Amber
ENGLAND | TADLEY | BRAMLEY (ANDO-THAT) | THATCHAM | 7.61/25.0 | 51.3606 | -1.1719 | SU 57753 62717 | 15.2 | 0 | 1.7833 | 8.2197 | 0.3 | 0 | 50 | Unconstrained |  |  | Constrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Red
ENGLAND | TAPLOW | IVER 132KV | SLOUGH | 9.82/25.0 | 51.5226 | -0.67937 | SU 91721 81234 | 23 | 0 | 4.44 | 13.94 | 0 | 16 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | TARRANT RUSHTON | MANNINGTON GSP | SHAFTESBURY | 4.55/25.0 | 50.8652 | -2.0794 | ST 94510 07307 | 4 | 0 | 1.0212 | 3.7997 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | TEFFONT | MANNINGTON GSP | SALISBURY | 3.05/13.1 | 51.0783 | -2.0037 | ST 99837 30994 | 4.5 | 0 | 0.81 | 5.0099 | 0 | 0 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate proximity to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | TEMPLE FARM | FLEET BRAMLEY | MAIDENHEAD | 2.72/25.0 | 51.5475 | -0.78743 | SU 84178 83872 | 4 | 0 | 0.74254 | 2.7262 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Voltage issues with the 33kV upstream network Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP Constrained on the 132kV circuits for export | 33/11 | Red
ENGLAND | TETBURY | MELKSHAM | CHIPPENHAM | 6.22/13.1 | 51.6397 | -2.1501 | ST 89708 93444 | 7.5 | 0 | 1.4896 | 6.3052 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 | 33/11 | Red
ENGLAND | THATCHAM | BRAMLEY (ANDO-THAT) | THATCHAM | 14.81/25.0 | 51.3948 | -1.2431 | SU 52758 66466 | 30 | 0 | 5.9498 | 31.4558 | 11.3 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Red
ENGLAND | THE GREEN | NORTH HYDE | NORTH HYDE (D) | 9.16/13.1 | 51.5033 | -0.38177 | TQ 12414 79503 | 12 | 0 | 2.0258 | 10.4467 | 0 | 14 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 22/6.6 | Red
ENGLAND | THE MALL | FLEET BRAMLEY | READING TOWN | 9.61/13.1 | 51.4541 | -0.97498 | SU 71319 73293 | 26.5 | 0 | 3.658 | 18.3947 | 0.149 | 30 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | THEALE | FLEET BRAMLEY | BURGHFIELD RESERVE | 7.58/20.0 | 51.4344 | -1.0698 | SU 64755 71015 | 24 | 0 | 2.0607 | 8.898 | 0.31 | 20 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | THRUXTON | MELKSHAM | ANDOVER | 5.17/13.1 | 51.2095 | -1.5843 | SU 29134 45674 | 5 | 0 | 1.1 | 5.2473 | 18.95 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with no headroom. National Grid reinforcement works required for Melk SGT capacity constraints, est connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | TIDWORTH | MELKSHAM | WEST GRAFTON | 4.28/25.0 | 51.245 | -1.6563 | SU 24088 49593 | 14 | 0 | 2.7679 | 9.598 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
ENGLAND | TISBURY | MANNINGTON GSP | SHAFTESBURY | 4.95/25.0 | 51.0614 | -2.095 | ST 93438 29127 | 9.12 | 0 | 1.0364 | 5.4488 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | TITCHFIELD | LOVEDEAN | Fareham T1A T2A (90MVAs) | 10.01/13.1 | 50.8483 | -1.2328 | SU 54104 05695 | 15 | 0 | 2.1835 | 10.0365 | 0.321 | 17 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | TONGHAM | FLEET BRAMLEY | ALDERSHOT | 9.82/16.0 | 51.2377 | -0.7364 | SU 88310 49487 | 30 | 0 | 2.9071 | 15.4316 | 1.74 | 20 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Voltage issues with the 33kV upstream network. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | TOOTHILL | MINETY | TOOTHILL | 14.75/18.4 | 51.5546 | -1.8108 | SU 13215 83986 | 60 | 0 | 4.2178 | 23.9307 | 2.058 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | TOTTON | NURSLING | ROWNHAMS | 10.84/13.1 | 50.9192 | -1.4916 | SU 35835 13428 | 24.5 | 0 | 3.9781 | 15.078 | 2 | 26 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | TOWNHILL PARK | BOTLEY WOOD GSP | NETLEY COMMON | 8.45/13.1 | 50.9307 | -1.3588 | SU 45156 14783 | 30 | 0 | 4.2295 | 20.0906 | 0 | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | TRADING ESTATE | MINETY | SWINDON | 10.83/25.0 | 51.5715 | -1.8068 | SU 13490 85868 | 21.6 | 0 | 1.7436 | 11.0649 | 2.57 | 10 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Constrained by BSP transformer capacity, National Grid reinforcement works required at Minety with an expected completion in 2025-2027. | 33/11 | Amber
ENGLAND | TRASH GREEN | FLEET BRAMLEY | BURGHFIELD RESERVE | 7.84/16.0 | 51.4139 | -1.0487 | SU 66254 68745 | 15 | 0 | 1.9305 | 11.9684 | 1.7 | 15 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Circa 7MW export headroom on 33kV circuits upstream. Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | TROWBRIDGE TOWN | MELKSHAM | NORRINGTON | 11.16/13.1 | 51.3212 | -2.2214 | ST 84668 58036 | 26 | 0 | 4.413 | 18.4995 | 2.5 | 8 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | no fault level headroom at Norrington 33kV for new gen connections | 33/11 | Red
ENGLAND | TWYFORD | FLEET BRAMLEY | READING | 6.67/13.1 | 51.4806 | -0.87198 | SU 78430 76339 | 15 | 0 | 2.6527 | 13.2487 | 0.1 | 17 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Red
ENGLAND | UNION STREET | COWLEY | Cowley Local (2 x 90) | 9.84/25.0 | 51.7489 | -1.2356 | SP 52865 05849 | 30 | 0 | 3.6275 | 15.0916 | 0 | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | UPPER HEYFORD | EAST CLAYDON | BICESTER NORTH | 8.1/13.1 | 51.9271 | -1.2488 | SP 51750 25667 | 15 | 0 | 2.1949 | 12.719 | 5.82 | 2 | 50 | Constrained |  |  | Constrained |  |  | No | No | Constrained due to upstream thermal limitations. Limited expansion space for CB connections. | 33/11 | Red
ENGLAND | UPTON | IVER 132KV | UPTON | 10.40/13.1 | 51.5049 | -0.54906 | TQ 00800 79434 | 26 | 0 | 5.5 | 22.8 | 0.4 | 18.1 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 22/11 | Green
ENGLAND | UXBRIDGE | IVER 66KV |  | 10.33/20.0 | 51.5405 | -0.4876 | TQ 04984 83484 | 72.8 | 0 | 11.55 | 45.5495 | 0 | 84 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | VELMORE | NURSLING | VELMORE | 8.94/18.4 | 50.9707 | -1.3899 | SU 42935 19205 | 30 | 0 | 7.4158 | 24.4158 | 1.5 | 36 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | VENTNOR | FAWLEY | COWES & WOOTTON COMMON | 9.41/16.0 | 50.5977 | -1.208 | SZ 56148 77857 | 30 | 0 | 1.8698 | 10.1419 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | No | Yes | Highly meshed GSP with several 132kV constraints for combined SSEN & NG SGT outages. A 3rd SGT has been triggered by SSEN (ModApp). ANM scheme in place on IOW to ease some of the 132kV constraints. | 33/11 | Red
ENGLAND | VERWOOD | MANNINGTON GSP | MANNINGTON | 6.79/13.1 | 50.8915 | -1.8917 | SU 07716 10226 | 13 | 0 | 2.0861 | 10.7664 | 5 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | 33kV upstream restrictions. No spare bay. | 33/11 | Red
ENGLAND | WALLINGFORD | COWLEY | Cowley Local (2 x 45) | 7.61/13.1 | 51.601 | -1.1373 | SU 59847 89486 | 19.5 | 0 | 2.39 | 16.0187 | 4.494 | 18 | 50 | Constrained | ANM scheme triggered upstream by accepted generation |  | Unconstrained |  |  | Yes | No | ANM installed to avoid upstream 33kV thermal issues under FCO. | 33/11 | Red
ENGLAND | WANTAGE | COWLEY | DRAYTON | 9.40/13.1 | 51.5921 | -1.4054 | SU 41290 88304 | 19.5 | 0 | 2.39 | 14.3779 | 0.05 | 7 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream thermal constraints. | 33/11 | Amber
ENGLAND | WAREHAM TOWN | MANNINGTON GSP | WAREHAM | 7.54/13.1 | 50.6868 | -2.1141 | SY 92036 87463 | 13.9 | 0 | 2.6048 | 11.3887 | 0.1 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to upstream thermal limitations. | 33/11 | Red
ENGLAND | WARFIELD | FLEET BRAMLEY | BRACKNELL MAIN | 8.44/13.1 | 51.4348 | -0.75039 | SU 86960 71382 | 22.1 | 0 | 5.4508 | 22.161 | 0 | 4 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | 33kV circuits at capacity for export BSP 33kV CBs close to fault rating | 33/11 | Red
ENGLAND | WARMINSTER | MELKSHAM | FROME | 7.74/16.0 | 51.2 | -2.217 | ST 84936 44551 | 15 | 0 | 1.8698 | 8.4771 | 0 | P371 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | Constrained by the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | WATERLOOVILLE | LOVEDEAN | WYMERING & FORT WIDLEY | 10.61/13.1 | 50.879 | -1.035 | SU 67988 09282 | 45 | 0 | 5.6144 | 22.205 | 0.05 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | WATLINGTON | COWLEY | HIGH WYCOMBE | 5.72/25.0 | 51.6431 | -1.0027 | SU 69106 94287 | 9.8 | 0 | 1.4191 | 6.3776 | 17 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream voltage & thermal constraints. | 33/11 | Red
ENGLAND | WELL END | AMERSHAM | LOUDWATER | 8.68/13.1 | 51.5835 | -0.72393 | SU 88511 87957 | 24 | 0 | 5.68 | 21.7 | 7.2 | 22.48 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | WEST END | LOVEDEAN | Fareham T1A T2A (90MVAs) | 11.7/13.1 | 50.852 | -1.1886 | SU 57216 06147 | 30 | 0 | 3.3377 | 12.4382 | 0 | 26 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | WEST GRAFTON VILLAGE | MELKSHAM | WEST GRAFTON | 7.52/13.1 | 51.3411 | -1.6477 | SU 24639 60279 | 7.5 | 0 | 1.0064 | 6.1736 | 0.18 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Constrained by 132kV system capacity. | 33/11 | Red
ENGLAND | WEST HENDFORD | AXMINSTER | YEOVIL | 12.38/13.1 | 50.9367 | -2.6418 | ST 55000 15442 | 30 | 0 | 5.3578 | 19.2441 | 6.08 | 7 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO. Moderate proximity to fault rating,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | WEST STOUR | MANNINGTON GSP | SHAFTESBURY | 6.4/13.1 | 50.9973 | -2.3192 | ST 77699 22040 | 9.8 | 0 | 0.92891 | 5.2395 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | WESTBOURNE | MANNINGTON GSP | BOURNEMOUTH | 9.54/13.1 | 50.7229 | -1.8931 | SZ 07642 91485 | 30 | 0 | 3.8635 | 15.791 | 0 | 34 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | WESTBURY | MELKSHAM | FROME | 10.00/13.1 | 51.2628 | -2.1783 | ST 87654 51530 | 30 | 0 | 2.5393 | 14.9613 | 4.76 | 0 | 50 | Constrained |  |  | Unconstrained | 33kV Frome - Westbury circuit reinforcement | 2024-03-31 | Yes | No | 33kV system thermal constraint on the TROW - HAWK - WBUR - WBUC ring network; plus the thermal constraint on the Melksham - Frome 132kV cct1 and cct2 and Frome BSP TX | 33/11 | Red
ENGLAND | WESTBURY CEMENT | MELKSHAM | FROME | 8.8/31.5 | 51.272 | -2.1722 | ST 88084 52553 | 4 | 0 | 1.2559 | 13.9317 | 0 | 0 | 50 | Constrained |  |  | Unconstrained | 33kV CB reinforcement | 2024-03-31 | Yes | No | Private network | 33/11 | Red
ENGLAND | WESTERN ESPLANADE | NURSLING | Southampton (2 x 90) | 8.8/31.5 | 50.9061 | -1.4095 | SU 41618 12009 | 60 | 0 | 6.8917 | 33.1963 | 0.36 | 69 | 50 | Unconstrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate proximity to fault rating. | 33/11 | Amber
ENGLAND | WESTON | BOTLEY WOOD GSP | NETLEY COMMON | 10.81/13.1 | 50.8869 | -1.3587 | SU 45207 09912 | 26 | 0 | 1.7985 | 11.5416 | 2.6 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | WEYMOUTH | CHICKERELL GSP | CHICKERELL | 12.73/20.0 | 50.6107 | -2.4615 | SY 67443 79096 | 30 | 0 | 5.7937 | 23.7292 | 3.02 | 23 | 50 | Constrained |  |  | Unconstrained |  |  | No | Yes | There is no reverse power capacity at the Chickerell BSP | 33/11 | Amber
ENGLAND | WHEATLEY | COWLEY | HEADINGTON | 8.9/16.0 | 51.7438 | -1.1211 | SP 60777 05379 | 15 | 0 | 2.0931 | 8.0267 | 7.12 | 11 | 50 | Unconstrained | Reinforcement of the 33/11kV Tx's and adjacent 33kV cct's under Ofgem Green Recovery funding |  | Constrained | Reinforcement of the 33/11kV Tx's and adjcent 33kV cct's under Ofgem Green Recovery funding | 2025-09-01 | Yes | No | Limited space for extension. | 33/11 | Green
ENGLAND | WHITCHURCH | MELKSHAM | ANDOVER | 4.47/13.1 | 51.2335 | -1.3436 | SU 45924 48466 | 5 | 0 | 0.72576 | 4.8463 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Thermal constraint on upstream 132kV system with no headroom. National Grid reinforcement works required for Melk SGT capacity constraints, est connection date for new applications is 2025-2027. | 33/11 | Red
ENGLAND | WHITELEY | BOTLEY WOOD GSP | BOTLEY WOOD | 8.52/25.0 | 50.8762 | -1.249 | SU 52936 08794 | 30 | 0 | 6.0075 | 23.9603 | 0 | 27 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | WHITEWAY | MINETY | CIRENCESTER | 7.83/13.1 | 51.7262 | -1.9713 | SP 02076 03059 | 30 | 0 | 4.027 | 23.6229 | 0 | 0 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | thermal constraint on BSP transformers and upstream 132kV feeders | 33/11 | Red
ENGLAND | WHITLEY WOOD | FLEET BRAMLEY | BURGHFIELD MAIN | 8.65/13.1 | 51.4213 | -0.95424 | SU 72812 69667 | 30 | 0 | 1.9656 | 7.5613 | 0 | 30 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | WILSON ROAD | FLEET BRAMLEY | BURGHFIELD MAIN | 11.35/25.0 | 51.4545 | -1.005 | SU 69235 73304 | 27.6 | 0 | 3.9994 | 15.7538 | 0 | 30 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Fleet GSP 132kV switchgear saturated for fault level capacity. 132kV reinforcement required at Fleet GSP | 33/11 | Amber
ENGLAND | WIMBORNE | MANNINGTON GSP | MANNINGTON | 8.46/13.1 | 50.7995 | -1.9728 | SZ 02014 99989 | 19.5 | 0 | 3.7118 | 18.6866 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | WIMBORNE ST GILES | MANNINGTON GSP | MANNINGTON | 2.85/12.0 | 50.9136 | -1.9583 | SU 03028 12678 | 1.5 | 0 | 0.19361 | 1.0824 | 0 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Constrained due to Primary transformers limitations under FCO. | 33/11 | Red
ENGLAND | WINCANTON | MANNINGTON GSP | SHAFTESBURY | 6.62/25.0 | 51.0488 | -2.411 | ST 71286 27802 | 15 | 0 | 1.67 | 8.1054 | 14.9 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | WINDRUSH PARK | COWLEY | WITNEY & YARNTON | 8.46/16.0 | 51.7855 | -1.5177 | SP 33366 09758 | 30 | 0 | 3.2676 | 12.8995 | 0.83 | 3 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Upstream Voltage & thermal constraints. | 33/11 | Red
ENGLAND | WINSMORE LANE | COWLEY | DRAYTON | 10.25/13.1 | 51.6694 | -1.2854 | SU 49513 96982 | 26 | 0 | 4.3237 | 16.818 | 0.001 | 7 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | WINTERBORNE KINGSTON | MANNINGTON GSP | LYTCHETT | 6.1/13.1 | 50.7826 | -2.2194 | SY 84631 98138 | 9.8 | 0 | 1.4041 | 6.5204 | 0 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | BSP Transformer rating under N-1 | 33/11 | Red
ENGLAND | WITNEY TOWN | COWLEY | WITNEY & YARNTON | 11.62/13.1 | 51.7841 | -1.4818 | SP 35844 09625 | 24 | 0 | 4.623 | 20.3794 | 0 | 3 | 50 | Constrained |  |  | Unconstrained | Reinforcement of the 33/11kV Tx's under Ofgem Green Recovery funding | 2023-04-01 | Yes | No | None known | 33/11 | Amber
ENGLAND | WOKINGHAM | FLEET BRAMLEY | WOKINGHAM | 7.98/25.0 | 51.4024 | -0.85724 | SU 79589 67665 | 30 | 0 | 2.2558 | 9.8504 | 0 | 0 | 50 | constrained |  |  | Unconstrained |  |  | Yes | Yes | Voltage issues with the 33kV upstream network | 33/11 | Green
ENGLAND | WOODCOTE | FLEET BRAMLEY | BURGHFIELD RESERVE | 3.67/16.0 | 51.5299 | -1.0727 | SU 64425 81624 | 5 | 0 | 1.0593 | 3.649 | 0 | 6 | 50 | Unconstrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate proximity to Primary transformers limitations. | 33/11 | Amber
ENGLAND | WOODMILL LANE | NURSLING | Southampton (2 x 90) | 11.48/25.0 | 50.937 | -1.379 | SU 43733 15470 | 24 | 0 | 2.3344 | 9.2575 | 0 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/6.6 | Green
ENGLAND | WOODSTOCK | COWLEY | WITNEY & YARNTON | 7.81/13.1 | 51.854 | -1.351 | SP 44795 17462 | 15 | 0 | 1.8398 | 8.7735 | 5.510.171 | 3 | 50 | Constrained |  |  | Constrained |  |  | Yes | No | Limited space for extension. | 33/11 | Red
ENGLAND | WOOLSTON | BOTLEY WOOD GSP | NETLEY COMMON | 7.45/20.0 | 50.899 | -1.3736 | SU 44145 11242 | 16.9 | 0 | 4.0604 | 13.8474 | 0 | 21 | 50 | Partially Constrained |  |  | Unconstrained |  |  | Yes | Yes | Proximity to voltage issues. | 33/6.6 | Amber
ENGLAND | WOOTTON BASSETT | MINETY | SWINDON | 14.31/25.0 | 51.529 | -1.892 | SU 07587 81123 | 24 | 0 | 1.4768 | 12.0728 | 23 | 0 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | 33kV system thermal constraint with no remaining headroom | 33/11 | Red
ENGLAND | WOOTTON ROAD | COWLEY | OXFORD (Osney) | 6.63/25.0 | 51.681 | -1.2892 | SU 49244 98269 | 18.2 | 0 | 2.8502 | 13.4853 | 0.24 | 11 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | No | None known | 33/11 | Green
ENGLAND | WRECCLESHAM | FLEET BRAMLEY | COXMOOR WOOD | 7.64/25.0 | 51.1921 | -0.82662 | SU 82093 44312 | 30 | 0 | 2.7801 | 14.5967 | 20 | 12 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | Yes | Limited headroom at BSP circa 15MVA | 33/11 | Amber
ENGLAND | WROUGHTON | MINETY | TOOTHILL | 10.67/13.1 | 51.5323 | -1.7931 | SU 14446 81504 | 24 | 0 | 1.4861 | 9.6605 | 4 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | thermal constraint on Minety - Galileo 132kV cct | 33/11 | Red
ENGLAND | WYCOMBE MARSH | AMERSHAM | LOUDWATER | 8.0/25.0 | 51.6185 | -0.72193 | SU 88582 91845 | 17.3 | 0 | 2.33 | 11.1 | 0 | 19.63 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 33/11 | Green
ENGLAND | WYMERING | LOVEDEAN | WYMERING & FORT WIDLEY | 9.58/20.0 | 50.8443 | -1.0785 | SU 64974 05375 | 60 | 0 | 13.0238 | 38.4573 | 4.135 | 25 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | None known | 33/11 | Green
ENGLAND | YARNTON | COWLEY | WITNEY & YARNTON | 11.33/25.0 | 51.8055 | -1.3012 | SP 48277 12108 | 40 | 0 | 4.9261 | 24.5346 | 5 | 3 | 50 | Unconstrained |  |  | Unconstrained | AVC upgrade at Yarnton 33/11kV Tx's | 2022-08-01 | Yes | No | None known | 33/11 | Green
ENGLAND | YATTENDON | BRAMLEY (ANDO-THAT) | THATCHAM | 5.99/12.0 | 51.4652 | -1.2284 | SU 53699 74307 | 13 | 0 | 2.4996 | 10.6286 | 0 | 15 | 50 | Constrained |  |  | Unconstrained |  |  | Yes | No | Fault level reinforcement required at Thatcham 33kV. Approaching 100% loading on 132kV circuits from Bramley to Thatcham on import | 33/11 | Amber
ENGLAND | YATTON KEYNELL | MELKSHAM | CHIPPENHAM | 9.06/13.1 | 51.4808 | -2.1843 | ST 87300 75782 | 15 | 0 | 0.96981 | 7.2333 | 0 | 0 | 50 | Constrained |  |  | Constrained | 33/11kV transformer reinforcement | 2022-12-31 | Yes | No | Constrained due to upstream thermal limitations on Chippenham BSP TX under N-1 | 33/11 | Red
ENGLAND | YEOVIL | AXMINSTER | YEOVIL | 13.18/25 | 50.9494 | -2.6037 | ST 57690 16833 | 20 | 0 | 3.5024 | 14.0913 | 10 | 7 | 50 | Constrained |  |  | Unconstrained | Yeovil-E switchgear reinforcement (completed - FL results include new rating). |  | Yes | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | YETMINSTER | AXMINSTER | YEOVIL | 8.06/25.0 | 50.89 | -2.5659 | ST 60294 10206 | 7.5 | 0 | 1.5748 | 8.0192 | 0.8 | 7 | 50 | Constrained |  |  | Partially Constrained |  |  | Yes | Yes | Moderate Proximity to thermal rating on short section of 132kV circt Axminster-Yeovil under FCO,There is no reverse power capacity at the Yeovil BSP | 33/11 | Red
ENGLAND | YIEWSLEY | IVER 66KV |  | 10.53/13.1 | 51.5177 | -0.47885 | TQ 05643 80961 | 60 | 0 | 7.93 | 39.4861 | 0 | 68 | 50 | Unconstrained |  |  | Unconstrained |  |  | No | No | None known | 66/11 | Green
ENGLAND | ZETLAND ROAD | LOVEDEAN | Fareham T1B T2B (1x90, 1x60MVA) | 10.17/13.1 | 50.7968 | -1.1416 | SU 60592 00043 | 26 | 0 | 4.256 | 17.3315 | 0 | 24 | 50 | Unconstrained |  |  | Unconstrained |  |  | Yes | Yes | Partialy constraint due to limited reverse power capacity | 33/11 | Amber
ENGLAND | WINTON | MANNINGTON GSP | REDHILL | 12.65/13.1 | 50.7439 | -1.8689 | SZ 09349 93822 | 26 | 0 | 6.4929 | 23.0771 | 5.061 | 0 | 50 | Constrained |  |  | Constrained |  |  | Yes | Yes | Proximity to fault rating | 33/11 | Amber

## Contracted Generation
Area | Project Name | GSP Parent | BSP Parent | PS Parent | Technology Type | Voltage (kV) | Status | Contracted Capacity (MVA)
ENGLAND | ALDERNEY PROJECT_315 |  |  | ALDERNEY | LANDFILL GAS | 11kV | CONNECTED | 7.5
ENGLAND | ALDERNEY PROJECT_316 |  |  | ALDERNEY | NATURAL GAS | 11kV | CONNECTED | 1.4
ENGLAND | ALDERNEY PROJECT_853 |  |  | ALDERNEY | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.3
ENGLAND | ALDERNEY PROJECT_854 |  |  | ALDERNEY | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.07
ENGLAND | ALDERSHOT PROJECT_179 |  |  | ALDERSHOT | LANDFILL GAS | 11kV | CONNECTED | 2.4
ENGLAND | ALTON & FERNHURST PROJECT_184 |  | ALTON & FERNHURST |  | NATURAL GAS | 33kV | CONNECTED | 15
ENGLAND | ALTON & FERNHURST PROJECT_195 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | ALTON & FERNHURST PROJECT_196 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.92
ENGLAND | ALTON & FERNHURST PROJECT_202 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | ALTON & FERNHURST PROJECT_203 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.3
ENGLAND | ALTON & FERNHURST PROJECT_211 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | ALTON & FERNHURST PROJECT_602 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 9.975
ENGLAND | ALTON & FERNHURST PROJECT_815 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
ENGLAND | ALTON & FERNHURST PROJECT_842 |  | ALTON & FERNHURST |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 21.05
ENGLAND | ALTON LOCAL PROJECT_197 |  |  | ALTON LOCAL | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.25
ENGLAND | AMESBURY PROJECT_410 |  | AMESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.64
ENGLAND | AMESBURY PROJECT_412 |  | AMESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.6
ENGLAND | AMESBURY PROJECT_446 |  | AMESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
ENGLAND | ANDOVER PROJECT_52 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | ANDOVER PROJECT_53 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14.31
ENGLAND | ANDOVER PROJECT_59 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 33.68
ENGLAND | ANDOVER PROJECT_60 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
ENGLAND | ANDOVER PROJECT_762 |  | ANDOVER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15
ENGLAND | ARBORFIELD PROJECT_34 |  |  | ARBORFIELD | LANDFILL GAS | 11kV | CONNECTED | 1
ENGLAND | ARBORFIELD PROJECT_35 |  |  | ARBORFIELD | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.44
ENGLAND | ARNCOTT PROJECT_102 |  |  | ARNCOTT | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
ENGLAND | ARNCOTT PROJECT_124 |  |  | ARNCOTT | GAS TURBINE | 11kV | ACCEPTED | 5
ENGLAND | ARNEWOOD PROJECT_754 |  | ARNEWOOD |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 13
ENGLAND | ASHFORD COMMON PROJECT_263 |  |  | ASHTON PARK | DIESEL | 22kV | CONNECTED | 6
ENGLAND | ASHLING ROAD PROJECT_296 |  |  | ASHLING ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
ENGLAND | ASHLING ROAD PROJECT_689 |  |  | ASHLING ROAD | CHP - GAS TURBINE | 11kV | CONNECTED | 1.8
ENGLAND | ASHTON PARK PROJECT_443 |  |  | ASHTON PARK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ENGLAND | ASHTON PARK PROJECT_713 |  |  | ASHTON PARK | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.175
ENGLAND | AVON RUBBER PROJECT_458 |  |  | AVON RUBBER | PV AND BATTERY | 11kV | ACCEPTED | 0.14
ENGLAND | AXMINSTER PROJECT_18 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 35
ENGLAND | AXMINSTER PROJECT_19 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 35
ENGLAND | AXMINSTER PROJECT_25 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 30
ENGLAND | BASINGSTOKE PROJECT_36 |  |  | BASINGSTOKE | WASTE TO ENERGY | 11kV | CONNECTED | 12
ENGLAND | BASINGSTOKE PROJECT_37 |  |  | BASINGSTOKE | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.75
ENGLAND | BASINGSTOKE T1A & T2A PROJECT_41 |  | BASINGSTOKE T1A & T2A |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
ENGLAND | BASINGSTOKE T1A & T2A PROJECT_42 |  | BASINGSTOKE T1A & T2A |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3
ENGLAND | BASINGSTOKE T1A & T2A PROJECT_559 |  | BASINGSTOKE T1A & T2A |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 14.2
ENGLAND | BASINGSTOKE T1B & T2B PROJECT_44 |  | BASINGSTOKE T1B & T2B |  | GAS TURBINE | 33kV | CONNECTED | 16
ENGLAND | BASINGSTOKE T1B & T2B PROJECT_603 |  | BASINGSTOKE T1B & T2B |  | BATTERY | 33kV | ACCEPTED | 25
ENGLAND | BASINGSTOKE T1B & T2B PROJECT_834 |  | BASINGSTOKE T1B & T2B |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 7.16
ENGLAND | BASINGSTOKE T3 & T4 PROJECT_47 |  | BASINGSTOKE T3 & T4 |  | BATTERY | 33kV | ACCEPTED | 20
ENGLAND | BASINGSTOKE T3 & T4 PROJECT_654 |  | BASINGSTOKE T3 & T4 |  | PV & BATTERY | 33kV | ACCEPTED | 31.58
ENGLAND | BASINGSTOKE T3 & T4 PROJECT_819 |  | BASINGSTOKE T3 & T4 |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18
ENGLAND | BASSETT PROJECT_719 |  |  | BASSETT | LANDFILL GAS | 11kV | ACCEPTED | 0.21
ENGLAND | BASSETT PROJECT_728 |  |  | BASSETT | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.021
ENGLAND | BEENHAM PROJECT_54 |  |  | BEENHAM | LANDFILL GAS | 11kV | CONNECTED | 1.9
ENGLAND | BERINSFIELD PROJECT_100 |  |  | BERINSFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
ENGLAND | BERINSFIELD PROJECT_109 |  |  | BERINSFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.14
ENGLAND | BERINSFIELD PROJECT_789 |  |  | BERINSFIELD | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 13.68
ENGLAND | BEVOIS VALLEY PROJECT_532 |  |  | BEVOIS VALLEY | CHP - GAS TURBINE | 6.6kV | CONNECTED | 1
ENGLAND | BEVOIS VALLEY PROJECT_722 |  |  | BEVOIS VALLEY | CHP - GAS TURBINE | 11kV | CONNECTED | 0.175
ENGLAND | BICESTER NORTH PROJECT_137 |  |  | BICESTER | GAS TURBINE | 11kV | ACCEPTED | 5.29
ENGLAND | BICESTER NORTH PROJECT_568 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 44
ENGLAND | BICESTER NORTH PROJECT_638 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.499
ENGLAND | BICESTER NORTH PROJECT_87 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | BICESTER NORTH PROJECT_90 |  | BICESTER NORTH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17.16
ENGLAND | BICESTER PROJECT_111 |  |  | BICESTER | CHP - GAS TURBINE | 11kV | CONNECTED | 3.169
ENGLAND | BICESTER PROJECT_117 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.899
ENGLAND | BICESTER PROJECT_625 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.023
ENGLAND | BICESTER PROJECT_648 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
ENGLAND | BICESTER PROJECT_651 |  |  | BICESTER | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
ENGLAND | BICESTER PROJECT_97 |  |  | BICESTER | WASTE TO ENERGY | 33kV | CONNECTED | 26
ENGLAND | BILSHAM PROJECT_291 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
ENGLAND | BILSHAM PROJECT_293 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
ENGLAND | BILSHAM PROJECT_294 |  |  | BILSHAM | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.772
ENGLAND | BILSHAM PROJECT_302 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.2
ENGLAND | BILSHAM PROJECT_708 |  |  | BILSHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 15
ENGLAND | BILSHAM PROJECT_798 |  |  | BILSHAM | CHP - GAS TURBINE | 11kV | ACCEPTED | 7.2
ENGLAND | BINSTEAD PROJECT_175 |  |  | BINSTEAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.85
ENGLAND | BISHOPS WALTHAM PROJECT_27 |  |  | BISHOPS WALTHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | BISHOPS WALTHAM PROJECT_686 |  |  | BISHOPS WALTHAM | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
ENGLAND | BISHOPSTOKE PROJECT_788 |  |  | BISHOPSTOKE | GAS TURBINE | 11kV | ACCEPTED | 7.6
ENGLAND | BLANDFORD PROJECT_397 |  |  | BLANDFORD | GAS | 11kV | ACCEPTED | 0
ENGLAND | BLANDFORD PROJECT_398 |  |  | BLANDFORD | DIESEL | 11kV | ACCEPTED | 0
ENGLAND | BLEDINGTON PROJECT_110 |  |  | BLEDINGTON | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.188
ENGLAND | BOSCOMBE DOWN PROJECT_441 |  |  | BOSCOMBE DOWN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 10
ENGLAND | BOSCOMBE DOWN PROJECT_454 |  |  | BOSCOMBE DOWN | DIESEL | 11kV | CONNECTED | 4
ENGLAND | BOSTON MANOR PROJECT_133 |  | BOSTON MANOR |  | OTHER SYNCHRONOUS | 11kV | CONNECTED | 7.5
ENGLAND | BOSTON MANOR PROJECT_135 |  | BOSTON MANOR |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 1
ENGLAND | BOTLEY WOOD GSP PROJECT_838 | BOTLEY WOOD GSP |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 49.9
ENGLAND | BOTLEY WOOD PROJECT_29 |  | BOTLEY WOOD |  | LANDFILL GAS | 33kV | ACCEPTED | 14
ENGLAND | BOTLEY WOOD PROJECT_30 |  | BOTLEY WOOD |  | DIESEL | 33kV | CONNECTED | 20
ENGLAND | BOTLEY WOOD PROJECT_558 |  | BOTLEY WOOD |  | BATTERY | 33kV | ACCEPTED | 49.9
ENGLAND | BOTLEY WOOD PROJECT_814 |  | BOTLEY WOOD |  | BATTERY | 33kV | ACCEPTED | 15
ENGLAND | BOURTON PROJECT_335 |  |  | BOURTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
ENGLAND | BOVINGTON PROJECT_396 |  |  | BOVINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | BRACKNELL MAIN PROJECT_212 |  | BRACKNELL MAIN |  | DIESEL | 33kV | CONNECTED | 20
ENGLAND | BRACKNELL MAIN PROJECT_217 |  | BRACKNELL MAIN |  | GAS TURBINE | 33kV | CONNECTED | 20
ENGLAND | BRADFORD-ON-AVON PROJECT_597 |  |  | BRADFORD-ON-AVON | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.125
ENGLAND | BRAMLEY (ANDO-THAT) PROJECT_560 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 40
ENGLAND | BRAMLEY (ANDO-THAT) PROJECT_599 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15.79
ENGLAND | BRAMLEY (ANDO-THAT) PROJECT_600 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 21.05
ENGLAND | BRAMLEY (ANDO-THAT) PROJECT_763 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 40
ENGLAND | BRAMLEY (ANDO-THAT) PROJECT_816 | BRAMLEY (ANDO-THAT) |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 47.4
ENGLAND | BRAMLEY (BASI) PROJECT_601 | BRAMLEY (BASI) |  |  | BATTERY | 132kV | ACCEPTED | 99.9
ENGLAND | BRAMLEY GREEN PROJECT_843 |  |  | BRAMLEY GREEN | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15.79
ENGLAND | BRAYWICK ROAD PROJECT_224 |  |  | BRAYWICK ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.075
ENGLAND | BROCKHAMPTON PROJECT_276 |  |  | BROCKHAMPTON | CHP - GAS TURBINE | 11kV | CONNECTED | 3.3
ENGLAND | BROCKHAMPTON PROJECT_282 |  |  | BROCKHAMPTON | NATURAL GAS | 11kV | CONNECTED | 5
ENGLAND | BROCKHAMPTON PROJECT_314 |  |  | BROCKHAMPTON | CHP - GAS TURBINE | 11kV | ACCEPTED | 5.32
ENGLAND | BROCKHAMPTON PROJECT_667 |  |  | BROCKHAMPTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
ENGLAND | BROCKHAMPTON PROJECT_687 |  |  | BROCKHAMPTON | CHP - GAS TURBINE | 11kV | CONNECTED | 3
ENGLAND | BROMHAM PROJECT_452 |  |  | BROMHAM | GAS TURBINE | 11kV | CONNECTED | 0.4
ENGLAND | BRUTON PROJECT_449 |  |  | BRUTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.202
ENGLAND | BRUTON PROJECT_738 |  |  | BRUTON | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.16
ENGLAND | BURGHFIELD MAIN PROJECT_765 |  | BURGHFIELD MAIN |  | GAS TURBINE | 11kV | ACCEPTED | 7.5
ENGLAND | BURGHFIELD RESERVE PROJECT_189 |  | BURGHFIELD RESERVE |  | NATURAL GAS | 33kV | CONNECTED | 47.5
ENGLAND | BURGHFIELD RESERVE PROJECT_200 |  | BURGHFIELD RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | BURGHFIELD RESERVE PROJECT_833 |  | BURGHFIELD RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12.63
ENGLAND | BUTTS ASH PROJECT_149 |  |  | BUTTS ASH | LANDFILL GAS | 11kV | CONNECTED | 11.5
ENGLAND | CALNE PROJECT_405 |  |  | CALNE | LANDFILL GAS | 11kV | CONNECTED | 2.5
ENGLAND | CALNE PROJECT_406 |  |  | CALNE | LANDFILL GAS | 11kV | CONNECTED | 2.5
ENGLAND | CALNE PROJECT_461 |  |  | CALNE | GAS TURBINE | 11kV | ACCEPTED | 7.5
ENGLAND | CAMBERLEY PROJECT_235 |  |  | CAMBERLEY | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
ENGLAND | CAMBERLEY RESERVE PROJECT_817 |  | CAMBERLEY RESERVE |  | GAS TURBINE | 33kV | ACCEPTED | 21.05
ENGLAND | CANAL BANK PROJECT_555 |  |  | CANAL BANK 11KV | CHP - GAS TURBINE | 11kV | CONNECTED | 2.77
ENGLAND | CANAL BANK PROJECT_557 |  |  | CANAL BANK 11KV | GAS TURBINE | 11kV | ACCEPTED | 2.2
ENGLAND | CASTLE CARY PROJECT_12 |  |  | CASTLE CARY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.32
ENGLAND | CASTLE CARY PROJECT_4 |  |  | CASTLE CARY | LANDFILL GAS | 11kV | CONNECTED | 3.8
ENGLAND | CASTLE CARY PROJECT_812 |  |  | CASTLE CARY | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.15
ENGLAND | CAUSEWAY PROJECT_262 |  |  | CAUSEWAY | LANDFILL GAS | 11kV | CONNECTED | 3.5
ENGLAND | CAUSEWAY PROJECT_266 |  |  | CAUSEWAY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.6
ENGLAND | CENTRAL BRIDGE PROJECT_848 |  |  | CENTRAL BRIDGE | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1455
ENGLAND | CENTRAL PROJECT_331 |  |  | CENTRAL | CHP - GAS TURBINE | 11kV | DISCONNECTED | 5.4
ENGLAND | CHALVEY PROJECT_251 |  |  | CHALVEY | LANDFILL GAS | 11kV | CONNECTED | 2.5
ENGLAND | CHALVEY PROJECT_576 |  | CHALVEY |  | BATTERY | 33kV | ACCEPTED | 49.5
ENGLAND | CHALVEY PROJECT_606 |  |  | CHALVEY | BATTERY | 11kV | ACCEPTED | 6.3
ENGLAND | CHARLBURY PROJECT_108 |  |  | CHARLBURY | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 4.3
ENGLAND | CHARLBURY PROJECT_621 |  |  | CHARLBURY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.078
ENGLAND | CHICHESTER & HUNSTON PROJECT_283 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | CHICHESTER & HUNSTON PROJECT_285 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6
ENGLAND | CHICHESTER & HUNSTON PROJECT_290 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | CHICHESTER & HUNSTON PROJECT_292 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
ENGLAND | CHICHESTER & HUNSTON PROJECT_295 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
ENGLAND | CHICHESTER & HUNSTON PROJECT_298 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | CHICHESTER & HUNSTON PROJECT_301 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
ENGLAND | CHICHESTER & HUNSTON PROJECT_303 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
ENGLAND | CHICHESTER & HUNSTON PROJECT_308 |  | CHICHESTER & HUNSTON |  | PV & BATTERY | 33kV | CONNECTED | 7
ENGLAND | CHICHESTER & HUNSTON PROJECT_581 |  | CHICHESTER & HUNSTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15
ENGLAND | CHICHESTER & HUNSTON PROJECT_677 |  | CHICHESTER & HUNSTON |  | BATTERY | 33kV | CONNECTED | 7
ENGLAND | CHICHESTER & HUNSTON PROJECT_755 |  | CHICHESTER & HUNSTON |  | WASTE TO ENERGY | 33kV | ACCEPTED | 30
ENGLAND | CHICHESTER PROJECT_272 |  |  | CHICHESTER | NATURAL GAS | 11kV | CONNECTED | 8.6
ENGLAND | CHICHESTER PROJECT_273 |  |  | CHICHESTER | LANDFILL GAS | 11kV | CONNECTED | 3.75
ENGLAND | CHICHESTER PROJECT_305 |  |  | CHICHESTER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ENGLAND | CHICKERELL PROJECT_661 |  |  | CHICKERELL | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
ENGLAND | CHICKERELL PROJECT_67 |  | CHICKERELL |  | NATURAL GAS | 33kV | CONNECTED | 47.8
ENGLAND | CHICKERELL PROJECT_670 |  | CHICKERELL |  | WASTE TO ENERGY | 33kV | ACCEPTED | 15.2
ENGLAND | CHICKERELL PROJECT_692 |  |  | CHICKERELL | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.7
ENGLAND | CHICKERELL PROJECT_695 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.2
ENGLAND | CHICKERELL PROJECT_72 |  | CHICKERELL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
ENGLAND | CHICKERELL PROJECT_73 |  | CHICKERELL |  | ANAEROBIC DIGESTER | 33kV | CONNECTED | 1.3
ENGLAND | CHICKERELL PROJECT_76 |  | CHICKERELL |  | BATTERY | 33kV | ACCEPTED | 10
ENGLAND | CHICKERELL PROJECT_77 |  | CHICKERELL |  | BATTERY | 33kV | ACCEPTED | 5
ENGLAND | CHICKERELL PROJECT_771 |  | CHICKERELL |  | PV & BATTERY | 33kV | ACCEPTED | 20
ENGLAND | CHICKERELL PROJECT_772 |  | CHICKERELL |  | PV & BATTERY | 33kV | ACCEPTED | 10
ENGLAND | CHILTON CANTELLO PROJECT_5 |  |  | CHILTON CANTELO | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | CHILTON CANTELO PROJECT_795 |  |  | CHILTON CANTELO | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 7.2
ENGLAND | CHINEHAM PROJECT_45 |  |  | CHINEHAM | CHP - GAS TURBINE | 11kV | CONNECTED | 1.368
ENGLAND | CHIPPENHAM PROJECT_399 |  | CHIPPENHAM |  | NATURAL GAS | 33kV | CONNECTED | 12
ENGLAND | CHIPPENHAM PROJECT_401 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | CHIPPENHAM PROJECT_402 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
ENGLAND | CHIPPENHAM PROJECT_408 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.5
ENGLAND | CHIPPENHAM PROJECT_409 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
ENGLAND | CHIPPENHAM PROJECT_414 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.1
ENGLAND | CHIPPENHAM PROJECT_421 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11
ENGLAND | CHIPPENHAM PROJECT_422 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
ENGLAND | CHIPPENHAM PROJECT_426 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
ENGLAND | CHIPPENHAM PROJECT_464 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 40
ENGLAND | CHIPPENHAM PROJECT_584 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42
ENGLAND | CHIPPENHAM PROJECT_595 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42.11
ENGLAND | CHIPPENHAM PROJECT_786 |  | CHIPPENHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10.53
ENGLAND | CHIPPING NORTON PROJECT_613 |  |  | CHIPPING NORTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ENGLAND | CHOLSEY PROJECT_619 |  |  | CHOLSEY | LANDFILL GAS | 11kV | CONNECTED | 0.05
ENGLAND | CHOLSEY PROJECT_623 |  |  | CHOLSEY | LANDFILL GAS | 11kV | CONNECTED | 0.25
ENGLAND | CHRISTCHURCH PROJECT_330 |  | CHRISTCHURCH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.5
ENGLAND | CHRISTCHURCH PROJECT_355 |  | CHRISTCHURCH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | CHRISTCHURCH PROJECT_368 |  | CHRISTCHURCH |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3
ENGLAND | CHRISTCHURCH PROJECT_824 |  | CHRISTCHURCH |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 40
ENGLAND | CIRENCESTER PROJECT_480 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | CIRENCESTER PROJECT_481 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
ENGLAND | CIRENCESTER PROJECT_482 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.7
ENGLAND | CIRENCESTER PROJECT_523 |  | CIRENCESTER |  | PV AND BATTERY | 33kV | ACCEPTED | 10.53
ENGLAND | CIRENCESTER PROJECT_524 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 75
ENGLAND | CIRENCESTER PROJECT_588 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10
ENGLAND | CIRENCESTER PROJECT_658 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 24.2
ENGLAND | CIRENCESTER PROJECT_739 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 13.68
ENGLAND | CIRENCESTER PROJECT_774 |  | CIRENCESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15.79
ENGLAND | CIRENCESTER TOWN PROJECT_505 |  |  | CIRENCESTER TOWN | PV & BATTERY | 11kV | ACCEPTED | 1
ENGLAND | CIRENCESTER TOWN PROJECT_746 |  |  | CIRENCESTER TOWN | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.526
ENGLAND | CODFORD PROJECT_418 |  |  | CODFORD | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2
ENGLAND | CODFORD PROJECT_775 |  |  | CODFORD | DIESEL | 0.4kV | ACCEPTED | 0
ENGLAND | CORFE MULLEN PROJECT_317 |  |  | CORFE MULLEN | LANDFILL GAS | 11kV | CONNECTED | 1.15
ENGLAND | CORSHAM PROJECT_416 |  |  | CORSHAM | OTHER SYNCHRONOUS | 11kV | CONNECTED | 2
ENGLAND | COURAGES PROJECT_187 |  |  | COURAGES | WIND FARM | 11kV | CONNECTED | 2.2
ENGLAND | COURAGES PROJECT_193 |  |  | COURAGES | DIESEL | 11kV | ACCEPTED | 1.5
ENGLAND | COURAGES PROJECT_218 |  |  | COURAGES | DIESEL | 11kV | ACCEPTED | 2
ENGLAND | COWES & WOOTTON COMMON PROJECT_146 |  | COWES & WOOTTON COMMON |  | NATURAL GAS | 33kV | CONNECTED | 33
ENGLAND | COWES & WOOTTON COMMON PROJECT_152 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.8
ENGLAND | COWES & WOOTTON COMMON PROJECT_153 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | COWES & WOOTTON COMMON PROJECT_154 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | COWES & WOOTTON COMMON PROJECT_159 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | COWES & WOOTTON COMMON PROJECT_165 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.1
ENGLAND | COWES & WOOTTON COMMON PROJECT_730 |  | COWES & WOOTTON COMMON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.003
ENGLAND | COWES & WOOTTON COMMON PROJECT_855 |  | COWES & WOOTTON COMMON |  | TIDAL | 33kV | ACCEPTED | 19.836
ENGLAND | COWES PROJECT_164 |  |  | COWES POWER STATION | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
ENGLAND | COWLEY LOCAL MAIN PROJECT_129 |  | COWLEY LOCAL MAIN |  | BATTERY | 33kV | ACCEPTED | 11
ENGLAND | COWLEY LOCAL MAIN PROJECT_779 |  | COWLEY LOCAL MAIN |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 50
ENGLAND | COWLEY LOCAL PROJECT_118 |  |  | COWLEY LOCAL | DIESEL | 11kV | CONNECTED | 0.56
ENGLAND | COWLEY LOCAL PROJECT_620 |  |  | COWLEY LOCAL | OTHER SYNCHRONOUS | 11kV | CONNECTED | 0.149
ENGLAND | COWLEY LOCAL RESERVE PROJECT_586 |  | COWLEY LOCAL RESERVE |  | PV & BATTERY | 33kV | ACCEPTED | 50
ENGLAND | COWLEY LOCAL RESERVE PROJECT_98 |  | COWLEY LOCAL RESERVE |  | GAS TURBINE | 33kV | CONNECTED | 12
ENGLAND | COWLEY PROJECT_128 | COWLEY |  |  | GAS TURBINE | 132kV | ACCEPTED | 99.99
ENGLAND | COWLEY PROJECT_567 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 50
ENGLAND | COWLEY PROJECT_633 | COWLEY |  |  | DIESEL | 11kV | CONNECTED | 2.01
ENGLAND | COWLEY PROJECT_640 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.1
ENGLAND | COWLEY PROJECT_644 | COWLEY |  |  | WIND FARM | 11kV | CONNECTED | 0.014
ENGLAND | COWLEY PROJECT_646 | COWLEY |  |  | DIESEL | 11kV | ACCEPTED | 0.001
ENGLAND | COWLEY PROJECT_781 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 52.53
ENGLAND | COWLEY PROJECT_80 | COWLEY |  |  | GAS TURBINE | 132kV | CONNECTED | 100
ENGLAND | COWLEY PROJECT_811 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 3.178
ENGLAND | COWLEY PROJECT_813 | COWLEY |  |  | BATTERY | 132kV | ACCEPTED | 52.58
ENGLAND | COWLEY PROJECT_839 | COWLEY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 49.9
ENGLAND | COXMOOR WOOD PROJECT_205 |  | COXMOOR WOOD |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.3
ENGLAND | COXMOOR WOOD PROJECT_213 |  | COXMOOR WOOD |  | NATURAL GAS | 33kV | CONNECTED | 16
ENGLAND | COXMOOR WOOD PROJECT_214 |  | COXMOOR WOOD |  | NATURAL GAS | 33kV | CONNECTED | 16
ENGLAND | COXMOOR WOOD PROJECT_229 |  | COXMOOR WOOD |  | PV & BATTERY | 33kV | CONNECTED | 6.2
ENGLAND | COXMOOR WOOD PROJECT_836 |  | COXMOOR WOOD |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 23.15
ENGLAND | CREEKMOOR PROJECT_359 |  |  | CREEKMOOR | WASTE TO ENERGY | 11kV | CONNECTED | 1.024
ENGLAND | CROCKERTON PROJECT_415 |  |  | CROCKERTON | STEAM TURBINE | 11kV | CONNECTED | 1
ENGLAND | DEDDINGTON PROJECT_650 |  |  | DEDDINGTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.05
ENGLAND | DENHAM PROJECT_255 |  | DENHAM |  | BATTERY | 22kV | ACCEPTED | 20
ENGLAND | DENHAM PROJECT_259 |  | DENHAM |  | GAS TURBINE | 22kV | ACCEPTED | 20
ENGLAND | DEVIZES PROJECT_429 |  |  | DEVIZES | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
ENGLAND | DEVIZES PROJECT_598 |  |  | DEVIZES | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.068
ENGLAND | DEVIZES PROJECT_810 |  |  | DEVIZES | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1
ENGLAND | DORCHESTER PROJECT_671 |  |  | DORCHESTER | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
ENGLAND | DORCHESTER PROJECT_68 |  |  | DORCHESTER | NATURAL GAS | 11kV | CONNECTED | 1.44
ENGLAND | DORCHESTER PROJECT_710 |  |  | DORCHESTER | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.36
ENGLAND | DORCHESTER PROJECT_74 |  |  | DORCHESTER | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.095
ENGLAND | DORCHESTER PROJECT_75 |  |  | DORCHESTER | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.1
ENGLAND | DRAYTON PROJECT_101 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 21.25
ENGLAND | DRAYTON PROJECT_734 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
ENGLAND | DRAYTON PROJECT_735 |  | DRAYTON |  | GAS TURBINE | 33kV | ACCEPTED | 18
ENGLAND | DRAYTON PROJECT_778 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 25.26
ENGLAND | DRAYTON PROJECT_805 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 40
ENGLAND | DRAYTON PROJECT_86 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | DRAYTON PROJECT_89 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14.1
ENGLAND | DRAYTON PROJECT_95 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 35
ENGLAND | DRAYTON PROJECT_96 |  | DRAYTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.2
ENGLAND | DUNBRIDGE PROJECT_591 |  |  | DUNBRIDGE | PV & BATTERY | 0.4kV | ACCEPTED | 0.044
ENGLAND | EAST CLAYDON PROJECT_587 | EAST CLAYDON |  |  | BATTERY | 132kV | ACCEPTED | 40
ENGLAND | EAST CLAYDON PROJECT_743 | EAST CLAYDON |  |  | PV & BATTERY | 132kV | ACCEPTED | 45.5
ENGLAND | EASTERTON PROJECT_837 |  |  | EASTERTON | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.23
ENGLAND | EASTLEIGH NORTH PROJECT_528 |  |  | EASTLEIGH NORTH | LANDFILL GAS | 11kV | CONNECTED | 2.92
ENGLAND | EASTLEIGH NORTH PROJECT_542 |  |  | EASTLEIGH NORTH | OTHER SYNCHRONOUS | 0.4kV | CONNECTED | 1
ENGLAND | ELECTRIC HOUSE PROJECT_374 |  |  | ELECTRIC HOUSE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
ENGLAND | ELMS ROAD PROJECT_846 |  |  | ELMS ROAD | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 45.4
ENGLAND | EMSWORTH PROJECT_665 |  |  | EMSWORTH | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
ENGLAND | EMSWORTH PROJECT_690 |  |  | EMSWORTH | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.065
ENGLAND | EYNSHAM PROJECT_92 |  |  | EYNSHAM | DIESEL | 11kV | CONNECTED | 1
ENGLAND | FAREHAM MAIN PROJECT_306 |  | FAREHAM MAIN |  | DIESEL | 33kV | CONNECTED | 20
ENGLAND | FAREHAM MAIN PROJECT_313 |  | FAREHAM MAIN |  | BATTERY | 33kV | ACCEPTED | 40
ENGLAND | FAREHAM MAIN PROJECT_699 |  | FAREHAM MAIN |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0
ENGLAND | FAREHAM MAIN PROJECT_741 |  | FAREHAM MAIN |  | BATTERY | 33kV | ACCEPTED | 20
ENGLAND | FAREHAM PROJECT_286 |  | FAREHAM MAIN |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17.5
ENGLAND | FAREHAM RESERVE PROJECT_668 |  | FAREHAM RESERVE |  | CHP - GAS TURBINE | 33kV | ACCEPTED | 30.56
ENGLAND | FARNHAM ROYAL PROJECT_246 |  |  | FARNHAM ROYAL | WASTE TO ENERGY | 11kV | CONNECTED | 12
ENGLAND | FAWLEY PROJECT_150 | FAWLEY |  |  | GAS TURBINE | 132kV | CONNECTED | 76.565
ENGLAND | FAWLEY PROJECT_155 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 140
ENGLAND | FAWLEY PROJECT_156 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 145
ENGLAND | FAWLEY PROJECT_157 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 145
ENGLAND | FAWLEY PROJECT_158 | FAWLEY |  |  | OIL | 132kV | CONNECTED | 145
ENGLAND | FIVE OAKS PROJECT_180 |  |  | FIVE OAKS | NATURAL GAS | 11kV | CONNECTED | 6.4
ENGLAND | FIVE OAKS PROJECT_181 |  |  | FIVE OAKS | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | FLACKWELL HEATH PROJECT_1 |  |  | FLACKWELL HEATH | LANDFILL GAS | 11kV | CONNECTED | 1.4
ENGLAND | FLEET BRAMLEY PROJECT_231 | FLEET BRAMLEY |  |  | BATTERY | 132kV | ACCEPTED | 99.9
ENGLAND | FLEET BRAMLEY PROJECT_242 | FLEET BRAMLEY |  |  | GAS TURBINE | 132kV | ACCEPTED | 99.9
ENGLAND | FLEET BRAMLEY PROJECT_652 | FLEET BRAMLEY |  |  | PV & BATTERY | 132kV | ACCEPTED | 49.9
ENGLAND | FLEET BRAMLEY PROJECT_764 | FLEET BRAMLEY |  |  | BATTERY | 33kV | ACCEPTED | 31.6
ENGLAND | FLEET BRAMLEY PROJECT_807 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 46.316
ENGLAND | FLEET BRAMLEY PROJECT_818 | FLEET BRAMLEY |  |  | BATTERY | 132kV | ACCEPTED | 105.263
ENGLAND | FLEET BRAMLEY PROJECT_844 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 132kV | CONNECTED | 105.26
ENGLAND | FRATTON PARK PROJECT_700 |  |  | FRATTON PARK | CHP - GAS TURBINE | 11kV | CONNECTED | 0
ENGLAND | FRESHWATER PROJECT_171 |  |  | FRESHWATER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
ENGLAND | FRESHWATER PROJECT_172 |  |  | FRESHWATER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
ENGLAND | FRIMLEY PROJECT_190 |  |  | FRIMLEY | LANDFILL GAS | 11kV | CONNECTED | 1.4
ENGLAND | FROME PROJECT_413 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.5
ENGLAND | FROME PROJECT_420 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
ENGLAND | FROME PROJECT_423 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.5
ENGLAND | FROME PROJECT_433 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | FROME PROJECT_434 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7
ENGLAND | FROME PROJECT_435 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.16
ENGLAND | FROME PROJECT_442 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | FROME PROJECT_448 |  |  | FROME | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
ENGLAND | FROME PROJECT_456 |  | FROME |  | BATTERY | 33kV | ACCEPTED | 0.8
ENGLAND | FROME PROJECT_457 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.35
ENGLAND | FROME PROJECT_459 |  | FROME |  | WASTE TO ENERGY | 33kV | ACCEPTED | 28.8
ENGLAND | FROME PROJECT_460 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
ENGLAND | FROME PROJECT_465 |  | FROME |  | BATTERY | 33kV | ACCEPTED | 7
ENGLAND | FROME PROJECT_594 |  |  | FROME | GAS TURBINE | 11kV | ACCEPTED | 2.67
ENGLAND | FROME PROJECT_733 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10.53
ENGLAND | FROME PROJECT_736 |  | FROME |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12.63
ENGLAND | FULSCOT PROJECT_131 |  |  | FULSCOT | LANDFILL GAS | 11kV | ACCEPTED | 7.56
ENGLAND | GABLE HEAD PROJECT_711 |  |  | GABLE HEAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
ENGLAND | GALILEO PROJECT_511 |  | GALILEO |  | BATTERY | 11kV | ACCEPTED | 10
ENGLAND | GAMBLE ROAD PROJECT_666 |  |  | GAMBLE ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.8
ENGLAND | GREEN PARK PROJECT_188 |  |  | GREENFORD | NATURAL GAS | 11kV | CONNECTED | 3
ENGLAND | GREENFORD PROJECT_556 |  |  | GREENFORD | NATURAL GAS | 11kV | CONNECTED | 1
ENGLAND | GREETHAM STREET PROJECT_678 |  |  | GREETHAM STREET | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
ENGLAND | GREETHAM STREET PROJECT_679 |  |  | GREETHAM STREET | CHP - GAS TURBINE | 11kV | CONNECTED | 0.05
ENGLAND | GREETHAM STREET PROJECT_702 |  |  | GREETHAM STREET | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.12
ENGLAND | HAMBLE PROJECT_33 |  |  | HAMBLE | BATTERY | 11kV | ACCEPTED | 5
ENGLAND | HAMBLE PROJECT_585 |  |  | HAMBLE | LANDFILL GAS | 11kV | ACCEPTED | 7.2
ENGLAND | HARESTOCK PROJECT_716 |  |  | HARESTOCK | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.42
ENGLAND | HARESTOCK PROJECT_726 |  |  | HARESTOCK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ENGLAND | HARVARD LANE PROJECT_136 |  |  | HARVARD LANE | GAS TURBINE | 11kV | CONNECTED | 1.6
ENGLAND | HAVANT PROJECT_300 |  | HAVANT |  | DIESEL | 33kV | CONNECTED | 20
ENGLAND | HAVANT PROJECT_309 |  | HAVANT |  | CHP - GAS TURBINE | 33kV | CONNECTED | 20
ENGLAND | HAWKERIDGE PROJECT_450 |  |  | HAWKERIDGE | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.08
ENGLAND | HAWKERIDGE PROJECT_451 |  |  | HAWKERIDGE | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1
ENGLAND | HAWKERIDGE PROJECT_578 |  |  | HAWKERIDGE | NATURAL GAS | 11kV | ACCEPTED | 7.56
ENGLAND | HAWKERIDGE PROJECT_593 |  |  | HAWKERIDGE | GAS TURBINE | 11kV | ACCEPTED | 7.6
ENGLAND | HEADINGTON PROJECT_103 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
ENGLAND | HEADINGTON PROJECT_132 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 13
ENGLAND | HEADINGTON PROJECT_582 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18
ENGLAND | HEADINGTON PROJECT_93 |  |  | HEADINGTON | CHP - GAS TURBINE | 11kV | CONNECTED | 3.6
ENGLAND | HEADINGTON PROJECT_94 |  | HEADINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | HENSTRIDGE PROJECT_11 |  |  | HENSTRIDGE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.13
ENGLAND | HENSTRIDGE PROJECT_13 |  |  | HENSTRIDGE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.1
ENGLAND | HERRIARD PROJECT_182 |  |  | HERRIARD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | HERRIARD PROJECT_216 |  |  | HERRIARD | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.4
ENGLAND | HIGH WYCOMBE PROJECT_628 |  |  | HIGH WYCOMBE | CHP - GAS TURBINE | 11kV | CONNECTED | 0.07
ENGLAND | HIGH WYCOMBE PROJECT_749 |  | HIGH WYCOMBE |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 8.468
ENGLAND | HIGH WYCOMBE PROJECT_84 |  |  | HIGH WYCOMBE | LANDFILL GAS | 11kV | CONNECTED | 1
ENGLAND | HILSEA INCINERATOR PROJECT_278 |  |  | HILSEA | WASTE TO ENERGY | 33kV | CONNECTED | 20
ENGLAND | HILSEA PROJECT_660 |  |  | HILSEA | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
ENGLAND | HILSEA PROJECT_683 |  |  | HILSEA | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.108
ENGLAND | HILSEA PROJECT_684 |  |  | HILSEA | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.069
ENGLAND | HITCHES LANE PROJECT_199 |  |  | HITCHES LANE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.26
ENGLAND | HOEFORD PROJECT_669 |  |  | HOEFORD | CHP - GAS TURBINE | 0.4kV | ACCEPTED | 0.5
ENGLAND | HOEFORD PROJECT_796 |  |  | HOEFORD | CHP - GAS TURBINE | 11kV | ACCEPTED | 7
ENGLAND | HOLES BAY PROJECT_373 |  |  | HOLES BAY | BATTERY | 11kV | ACCEPTED | 7.5
ENGLAND | HOLES BAY PROJECT_385 |  |  | HOLES BAY | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.37
ENGLAND | HOLWELL PROJECT_436 |  |  | HOLWELL | WIND FARM | 11kV | CONNECTED | 0.5
ENGLAND | HOLWELL PROJECT_437 |  |  | HOLWELL | WIND FARM | 11kV | CONNECTED | 0.5
ENGLAND | HOLWELL PROJECT_752 |  |  | HOLWELL | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.842
ENGLAND | HOMINGTON PROJECT_827 |  |  | HOMINGTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 9
ENGLAND | HORNDEAN PROJECT_289 |  |  | HORNDEAN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ENGLAND | HORNDEAN PROJECT_709 |  |  | HORNDEAN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ENGLAND | HOUGHTON PROJECT_758 |  |  | HOUGHTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 5
ENGLAND | HOUNDMILLS PROJECT_38 |  |  | HOUNDMILLS | NATURAL GAS | 11kV | CONNECTED | 1.3
ENGLAND | HOUNDMILLS PROJECT_40 |  |  | HOUNDMILLS | DIESEL | 11kV | CONNECTED | 1.2
ENGLAND | HUNSTON PROJECT_281 |  |  | HUNSTON | DIESEL | 11kV | CONNECTED | 2
ENGLAND | HUNSTON PROJECT_312 |  |  | HUNSTON | BATTERY | 11kV | ACCEPTED | 10
ENGLAND | HUNSTON PROJECT_688 |  |  | HUNSTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.035
ENGLAND | HUNSTON PROJECT_694 |  |  | HUNSTON | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
ENGLAND | HUNSTON PROJECT_705 |  |  | HUNSTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.8
ENGLAND | HUNSTON PROJECT_707 |  |  | HUNSTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.5
ENGLAND | IRONBRIDGE PROJECT_134 |  | IRONBRIDGE |  | DIESEL | 11kV | CONNECTED | 1.012
ENGLAND | JAYS CLOSE PROJECT_46 |  |  | JAYS CLOSE | DIESEL | 11kV | CONNECTED | 4
ENGLAND | KENNINGTON PROJECT_622 |  |  | KENNINGTON | SMALL HYDRO | 11kV | CONNECTED | 0.4
ENGLAND | KIDDINGTON PROJECT_624 |  |  | KIDDINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.179
ENGLAND | KINTBURY PROJECT_56 |  |  | KINTBURY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
ENGLAND | LANGLEY COURT PROJECT_608 |  |  | LANGLEY COURT | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.217
ENGLAND | LANGLEY PROJECT_161 |  |  | LANGLEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | LANGLEY PROJECT_170 |  |  | LANGLEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3
ENGLAND | LANGLEY PROJECT_715 |  |  | LANGLEY | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.33
ENGLAND | LEIGH PARK PROJECT_277 |  |  | LEIGH PARK | LANDFILL GAS | 11kV | CONNECTED | 3.5
ENGLAND | LEIGH PARK PROJECT_697 |  |  | LEIGH PARK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.243
ENGLAND | LONGFORD PROJECT_245 |  | LONGFORD |  | WASTE TO ENERGY | 33kV | CONNECTED | 45.7
ENGLAND | LOUDWATER PROJECT_2 |  | LOUDWATER |  | BATTERY | 33kV | ACCEPTED | 40
ENGLAND | LYMINGTON PROJECT_361 |  |  | LYMINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
ENGLAND | LYMINGTON PROJECT_372 |  |  | LYMINGTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.17
ENGLAND | LYNEHAM PROJECT_407 |  |  | LYNEHAM | DIESEL | 11kV | CONNECTED | 2.75
ENGLAND | LYTCHETT PROJECT_338 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.3
ENGLAND | LYTCHETT PROJECT_339 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.2
ENGLAND | LYTCHETT PROJECT_340 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | LYTCHETT PROJECT_343 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.8
ENGLAND | LYTCHETT PROJECT_346 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.36
ENGLAND | LYTCHETT PROJECT_360 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | LYTCHETT PROJECT_395 |  | LYTCHETT |  | BATTERY | 33kV | ACCEPTED | 25
ENGLAND | LYTCHETT PROJECT_583 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12
ENGLAND | LYTCHETT PROJECT_822 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 32
ENGLAND | LYTCHETT PROJECT_825 |  | LYTCHETT |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12
ENGLAND | MAIDENHEAD PROJECT_206 |  | MAIDENHEAD |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 0.143
ENGLAND | MALMESBURY PROJECT_455 |  |  | MALMESBURY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.5
ENGLAND | MALMESBURY PROJECT_803 |  |  | MALMESBURY | GAS TURBINE | 11kV | ACCEPTED | 0.579
ENGLAND | MANNINGTON GSP PROJECT_322 | MANNINGTON GSP |  |  | NATURAL GAS | 132kV | CONNECTED | 9.5
ENGLAND | MANNINGTON GSP PROJECT_389 | MANNINGTON GSP |  |  | BATTERY | 132kV | ACCEPTED | 49.5
ENGLAND | MANNINGTON GSP PROJECT_391 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 132kV | ACCEPTED | 40
ENGLAND | MANNINGTON GSP PROJECT_574 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 49.99
ENGLAND | MANNINGTON GSP PROJECT_575 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 29.4
ENGLAND | MANNINGTON GSP PROJECT_823 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
ENGLAND | MANNINGTON GSP PROJECT_851 | MANNINGTON GSP |  |  | BATTERY | 132kV | ACCEPTED | 52.1
ENGLAND | MANNINGTON GSP PROJECT_856 | MANNINGTON GSP |  |  | BATTERY | 132kV | ACCEPTED | 99.9
ENGLAND | MANNINGTON PROJECT_319 |  | MANNINGTON |  | LANDFILL GAS | 33kV | CONNECTED | 3.16
ENGLAND | MANNINGTON PROJECT_341 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.025
ENGLAND | MANNINGTON PROJECT_342 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11.2
ENGLAND | MANNINGTON PROJECT_347 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11
ENGLAND | MANNINGTON PROJECT_348 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 16
ENGLAND | MANNINGTON PROJECT_356 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.032
ENGLAND | MANNINGTON PROJECT_386 |  | MANNINGTON |  | BATTERY | 33kV | ACCEPTED | 49.9
ENGLAND | MANNINGTON PROJECT_393 |  | MANNINGTON |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 33kV | ACCEPTED | 8
ENGLAND | MAYBUSH PROJECT_526 |  |  | MAYBUSH | NATURAL GAS | 11kV | CONNECTED | 2
ENGLAND | MELKSHAM PROJECT_439 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 132kV | CONNECTED | 41.2
ENGLAND | MELKSHAM PROJECT_453 | MELKSHAM |  |  | BATTERY | 132kV | ACCEPTED | 105.2
ENGLAND | MELKSHAM PROJECT_463 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 52.53
ENGLAND | MELKSHAM PROJECT_753 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 52.63
ENGLAND | MELKSHAM PROJECT_770 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 105.26
ENGLAND | MELKSHAM TOWN PROJECT_417 |  |  | MELKSHAM TOWN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
ENGLAND | MELKSHAM TOWN PROJECT_468 |  |  | MELKSHAM TOWN | GAS TURBINE | 11kV | ACCEPTED | 7.2
ENGLAND | MELKSHAM TOWN PROJECT_802 |  |  | MELKSHAM TOWN | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.126
ENGLAND | MIDDLE WALLOP PROJECT_55 |  |  | MIDDLE WALLOP | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.4
ENGLAND | MIDDLE WALLOP PROJECT_61 |  |  | MIDDLE WALLOP | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.4
ENGLAND | MIDHURST PROJECT_185 |  |  | MIDHURST | NATURAL GAS | 11kV | CONNECTED | 5
ENGLAND | MILBORNE PORT PROJECT_20 |  |  | MILBORNE PORT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ENGLAND | MILFORD PROJECT_198 |  |  | MILFORD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.177
ENGLAND | MILL LANE PROJECT_318 |  |  | MILL LANE | LANDFILL GAS | 11kV | CONNECTED | 1
ENGLAND | MILL LANE PROJECT_571 |  |  | MILL LANE | LANDFILL GAS | 11kV | ACCEPTED | 7.6
ENGLAND | MILTON PROJECT_612 |  |  | MILTON | LANDFILL GAS | 11kV | CONNECTED | 0.45
ENGLAND | MILTON PROJECT_626 |  |  | MILTON | SMALL HYDRO | 11kV | CONNECTED | 0.406
ENGLAND | MILTON PROJECT_645 |  |  | MILTON | DIESEL | 11kV | CONNECTED | 1
ENGLAND | MILTON PROJECT_649 |  |  | MILTON | DIESEL | 11kV | ACCEPTED | 0.001
ENGLAND | MILTON PROJECT_809 |  |  | MILTON | DIESEL | 11kV | ACCEPTED | 0
ENGLAND | MILTON PROJECT_81 |  |  | MILTON | DIESEL | 11kV | CONNECTED | 3.3
ENGLAND | MILTON PROJECT_91 |  |  | MILTON | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1.68
ENGLAND | MINETY PROJECT_496 | MINETY |  |  | PHOTOVOLTAIC PLANT | 132kV | CONNECTED | 49.9
ENGLAND | MINETY PROJECT_499 | MINETY |  |  | BATTERY | 132kV | ACCEPTED | 105.2
ENGLAND | MINETY PROJECT_506 | MINETY |  |  | BATTERY | 132kV | ACCEPTED | 157.58
ENGLAND | MINETY PROJECT_510 | MINETY |  |  | BATTERY | 132kV | ACCEPTED | 52.53
ENGLAND | MINETY PROJECT_518 | MINETY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 52.53
ENGLAND | MINETY PROJECT_737 | MINETY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 31.58
ENGLAND | MINETY PROJECT_769 | MINETY |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 31.58
ENGLAND | MINETY VILLAGE PROJECT_748 |  |  | MINETY VILLAGE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 3.158
ENGLAND | MINETY VILLAGE PROJECT_806 |  |  | MINETY VILLAGE | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0
ENGLAND | MVEE PROJECT_186 |  |  | MVEE | LANDFILL GAS | 11kV | CONNECTED | 1.33
ENGLAND | MVEE PROJECT_194 |  |  | MVEE | ANAEROBIC DIGESTER | 11kV | CONNECTED | 2.38
ENGLAND | NETHERHAMPTON PROJECT_828 |  |  | NETHERHAMPTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 9.8
ENGLAND | NETLEY COMMON PROJECT_28 |  | NETLEY COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
ENGLAND | NETLEY COMMON PROJECT_31 |  | NETLEY COMMON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | NEW MILTON PROJECT_332 |  |  | NEW MILTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
ENGLAND | NEW MILTON PROJECT_378 |  |  | NEW MILTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ENGLAND | NEW MILTON PROJECT_757 |  |  | NEW MILTON | GAS TURBINE | 11kV | ACCEPTED | 0.999
ENGLAND | NEWPORT PROJECT_147 |  |  | NEWPORT | LANDFILL GAS | 11kV | CONNECTED | 1.2
ENGLAND | NEWPORT PROJECT_148 |  |  | NEWPORT | NATURAL GAS | 11kV | CONNECTED | 2.5
ENGLAND | NEWPORT PROJECT_169 |  |  | NEWPORT | NATURAL GAS | 11kV | CONNECTED | 0.65
ENGLAND | NEWPORT PROJECT_173 |  |  | NEWPORT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
ENGLAND | NEWPORT PROJECT_174 |  |  | NEWPORT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
ENGLAND | NEWPORT PROJECT_177 |  |  | NEWPORT | NATURAL GAS | 11kV | CONNECTED | 0.5
ENGLAND | NEWPORT PROJECT_725 |  |  | NEWPORT | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.05
ENGLAND | NORRINGTON PROJECT_400 |  | NORRINGTON |  | NATURAL GAS | 33kV | CONNECTED | 5.45
ENGLAND | NORRINGTON PROJECT_403 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
ENGLAND | NORRINGTON PROJECT_419 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | NORRINGTON PROJECT_424 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
ENGLAND | NORRINGTON PROJECT_425 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14
ENGLAND | NORRINGTON PROJECT_428 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.16
ENGLAND | NORRINGTON PROJECT_430 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | NORRINGTON PROJECT_431 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 13
ENGLAND | NORRINGTON PROJECT_432 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | NORRINGTON PROJECT_438 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 20
ENGLAND | NORRINGTON PROJECT_440 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.21
ENGLAND | NORRINGTON PROJECT_447 |  | NORRINGTON |  | CHP - GAS TURBINE | 33kV | CONNECTED | 0.5
ENGLAND | NORRINGTON PROJECT_466 |  | NORRINGTON |  | BATTERY | 33kV | ACCEPTED | 20
ENGLAND | NORRINGTON PROJECT_469 |  | NORRINGTON |  | NATURAL GAS | 33kV | CONNECTED | 16
ENGLAND | NORRINGTON PROJECT_579 |  | NORRINGTON |  | PV & BATTERY | 33kV | ACCEPTED | 20
ENGLAND | NORRINGTON PROJECT_760 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 24.21
ENGLAND | NORRINGTON PROJECT_785 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10.53
ENGLAND | NORRINGTON PROJECT_804 |  | NORRINGTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42.11
ENGLAND | NORRINGTON PROJECT_831 |  | NORRINGTON |  | BATTERY | 33kV | ACCEPTED | 21.05
ENGLAND | NORTH HINKSEY PROJECT_618 |  |  | NORTH HINKSEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.3
ENGLAND | NORTHUMBERLAND AVENUE PROJECT_191 |  |  | NORTHUMBERLAND AVENUE | LANDFILL GAS | 11kV | CONNECTED | 3
ENGLAND | NURSLING PROJECT_534 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 132kV | CONNECTED | 50
ENGLAND | NURSLING PROJECT_536 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 40
ENGLAND | NURSLING PROJECT_776 | NURSLING |  |  | BATTERY | 132kV | ACCEPTED | 54.348
ENGLAND | NURSLING PROJECT_791 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 32
ENGLAND | OLD ROAD PROJECT_635 |  |  | OLD ROAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.344
ENGLAND | OSNEY PROJECT_636 |  |  | OSNEY | DIESEL | 11kV | CONNECTED | 0.504
ENGLAND | OVERTON PROJECT_39 |  |  | OVERTON | NATURAL GAS | 11kV | CONNECTED | 7.2
ENGLAND | OVERTON PROJECT_43 |  |  | OVERTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.2
ENGLAND | OVERTON PROJECT_605 |  |  | OVERTON | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.2
ENGLAND | OXFORD PROJECT_634 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.21
ENGLAND | OXFORD PROJECT_642 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
ENGLAND | OXFORD PROJECT_643 |  | OXFORD |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.02
ENGLAND | OXFORD PROJECT_767 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 52.5
ENGLAND | OXFORD PROJECT_782 |  | OXFORD |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 22.105
ENGLAND | PARK NORTH PROJECT_519 |  |  | PARK NORTH | CHP - SPARK IGNITION | 11kV | ACCEPTED | 1
ENGLAND | PEACOCK FARM PROJECT_832 |  |  | PEACOCK FARM | BATTERY | 33kV | ACCEPTED | 31.6
ENGLAND | PETERSFIELD AVENUE PROJECT_243 |  |  | PETERSFIELD AVENUE | NATURAL GAS | 11kV | CONNECTED | 1.94
ENGLAND | PETERSFIELD AVENUE PROJECT_564 |  |  | PETERSFIELD AVENUE | CHP - GAS TURBINE | 11kV | ACCEPTED | 2
ENGLAND | PETERSFIELD PROJECT_204 |  |  | PETERSFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.25
ENGLAND | PLAISTOW PROJECT_655 |  |  | PLAISTOW | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.322
ENGLAND | POOLE (HILL STREET) PROJECT_379 |  |  | POOLE (HILL STREET) | CHP - GAS TURBINE | 11kV | ACCEPTED | 0
ENGLAND | POOLE (HILL STREET) PROJECT_390 |  |  | POOLE (HILL STREET) | DIESEL | 11kV | ACCEPTED | 3.4
ENGLAND | PORTCHESTER PROJECT_279 |  |  | PORTCHESTER | LANDFILL GAS | 11kV | CONNECTED | 3.5
ENGLAND | PORTLAND PROJECT_69 |  |  | PORTLAND | DIESEL | 11kV | CONNECTED | 2.4
ENGLAND | PORTSMOUTH PROJECT_288 |  |  | PORTSMOUTH | OTHER SYNCHRONOUS | 33kV | CONNECTED | 1
ENGLAND | PORTSMOUTH PROJECT_675 |  |  | PORTSMOUTH | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
ENGLAND | PORTSMOUTH PROJECT_680 |  | PORTSMOUTH |  | CHP - GAS TURBINE | 11kV | CONNECTED | 0.015
ENGLAND | PORTSMOUTH PROJECT_701 |  |  | PORTSMOUTH | CHP - GAS TURBINE | 33kV | CONNECTED | 0
ENGLAND | PORTWAY PROJECT_51 |  |  | PORTWAY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.3
ENGLAND | PORTWAY PROJECT_64 |  |  | PORTWAY | DIESEL | 11kV | CONNECTED | 1.76
ENGLAND | PORTWAY PROJECT_768 |  |  | PORTWAY | GAS TURBINE | 11kV | ACCEPTED | 4.266
ENGLAND | PRESTON CANDOVER PROJECT_609 |  |  | PRESTON CANDOVER | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
ENGLAND | QUARRY ROAD PROJECT_509 |  |  | QUARRY ROAD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 1.8
ENGLAND | READING PROJECT_201 |  | READING |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.08
ENGLAND | READING PROJECT_226 |  |  | READING | SMALL HYDRO | 11kV | ACCEPTED | 0.1
ENGLAND | READING PROJECT_227 |  |  | READING | DIESEL | 11kV | ACCEPTED | 0.44
ENGLAND | READING PROJECT_228 |  |  | READING | DIESEL | 11kV | ACCEPTED | 0.6
ENGLAND | READING PROJECT_230 |  | READING |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 11
ENGLAND | READING PROJECT_841 |  | READING |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
ENGLAND | READING TOWN PROJECT_208 |  |  | READING TOWN | ANAEROBIC DIGESTER | 11kV | CONNECTED | 0.5
ENGLAND | REDHILL PROJECT_324 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 20.31
ENGLAND | REDHILL PROJECT_352 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 24.8
ENGLAND | REDHILL PROJECT_353 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.9
ENGLAND | REDHILL PROJECT_354 |  | REDHILL |  | ANAEROBIC DIGESTER | 33kV | ACCEPTED | 5
ENGLAND | REDHILL PROJECT_363 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.5
ENGLAND | REDHILL PROJECT_364 |  |  | REDHILL | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4.9
ENGLAND | REDHILL PROJECT_365 |  |  | REDHILL | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.81
ENGLAND | REDHILL PROJECT_387 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 3.7
ENGLAND | REDHILL PROJECT_829 |  | REDHILL |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 40
ENGLAND | REDLYNCH PROJECT_327 |  |  | REDLYNCH | LANDFILL GAS | 11kV | CONNECTED | 0.6
ENGLAND | REDLYNCH PROJECT_328 |  |  | REDLYNCH | LANDFILL GAS | 11kV | CONNECTED | 1
ENGLAND | REDLYNCH PROJECT_337 |  |  | REDLYNCH | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6
ENGLAND | REGENTS PARK PROJECT_530 |  |  | REGENTS PARK | WASTE TO ENERGY | 11kV | CONNECTED | 1.2
ENGLAND | ROSE GREEN PROJECT_274 |  |  | ROSE GREEN | DIESEL | 11kV | CONNECTED | 5
ENGLAND | ROSE GREEN PROJECT_275 |  |  | ROSE GREEN | LANDFILL GAS | 11kV | CONNECTED | 3.045
ENGLAND | ROSE HILL PROJECT_641 |  |  | ROSE HILL | CHP - GAS TURBINE | 11kV | CONNECTED | 0.8
ENGLAND | ROWNHAMS PROJECT_535 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | ROWNHAMS PROJECT_537 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.32
ENGLAND | ROWNHAMS PROJECT_538 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.99
ENGLAND | ROWNHAMS PROJECT_544 |  | ROWNHAMS |  | BATTERY | 33kV | ACCEPTED | 10
ENGLAND | ROWNHAMS PROJECT_545 |  | ROWNHAMS |  | OTHER SYNCHRONOUS | 33kV | ACCEPTED | 20
ENGLAND | ROWNHAMS PROJECT_551 |  | ROWNHAMS |  | NATURAL GAS | 33kV | CONNECTED | 20
ENGLAND | ROWNHAMS PROJECT_745 |  | ROWNHAMS |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 6.8
ENGLAND | ROWNHAMS PROJECT_792 |  | ROWNHAMS |  | BATTERY | 33kV | ACCEPTED | 52.105
ENGLAND | RYDE PROJECT_151 |  |  | RYDE | NATURAL GAS | 11kV | CONNECTED | 1.25
ENGLAND | SALISBURY PROJECT_325 |  | SALISBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9.25
ENGLAND | SALISBURY PROJECT_572 |  | SALISBURY |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12.5
ENGLAND | SANDOWN PROJECT_176 |  |  | SANDOWN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.98
ENGLAND | SHAFTESBURY PROJECT_323 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.6
ENGLAND | SHAFTESBURY PROJECT_326 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12
ENGLAND | SHAFTESBURY PROJECT_349 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
ENGLAND | SHAFTESBURY PROJECT_357 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
ENGLAND | SHAFTESBURY PROJECT_358 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4
ENGLAND | SHAFTESBURY PROJECT_366 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.5
ENGLAND | SHAFTESBURY PROJECT_367 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 4.125
ENGLAND | SHAFTESBURY PROJECT_370 |  |  | SHAFTESBURY | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.08
ENGLAND | SHAFTESBURY PROJECT_377 |  | SHAFTESBURY |  | BATTERY | 33kV | ACCEPTED | 20
ENGLAND | SHAFTESBURY PROJECT_384 |  |  | SHAFTESBURY | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.237
ENGLAND | SHAFTESBURY PROJECT_756 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 21.052
ENGLAND | SHAFTESBURY PROJECT_820 |  | SHAFTESBURY |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 14.5
ENGLAND | SHALFLEET PROJECT_162 |  |  | SHALFLEET | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
ENGLAND | SHALFLEET PROJECT_718 |  |  | SHALFLEET | WIND FARM | 11kV | ACCEPTED | 0.25
ENGLAND | SHANKLIN PROJECT_163 |  |  | SHANKLIN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2.8
ENGLAND | SHROTON PROJECT_334 |  |  | SHROTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 6.6
ENGLAND | SIDNEY ROAD PROJECT_264 |  |  | SIDNEY ROAD | NATURAL GAS | 11kV | CONNECTED | 1.3
ENGLAND | SILKSTEAD PROJECT_548 |  |  | SILKSTEAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.5
ENGLAND | SILKSTEAD PROJECT_717 |  |  | SILKSTEAD | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.37
ENGLAND | SILKSTEAD PROJECT_720 |  |  | SILKSTEAD | OTHER SYNCHRONOUS | 11kV | ACCEPTED | 0.2
ENGLAND | SILVER STREET PROJECT_192 |  |  | SILVER STREET | DIESEL | 11kV | ACCEPTED | 7
ENGLAND | SLOUGH PROJECT_247 |  | SLOUGH |  | OTHER SYNCHRONOUS | 33kV | CONNECTED | 60
ENGLAND | SLOUGH PROJECT_260 |  | SLOUGH |  | STEAM TURBINE | 33kV | ACCEPTED | 46
ENGLAND | SOMERFORD PROJECT_375 |  |  | SOMERFORD | OTHER SYNCHRONOUS | 11kV | CONNECTED | 1
ENGLAND | SOUTH BERSTED PROJECT_672 |  |  | SOUTH BERSTED | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
ENGLAND | SOUTH BERSTED PROJECT_696 |  |  | SOUTH BERSTED | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.313
ENGLAND | SOUTH BERSTED PROJECT_797 |  |  | SOUTH BERSTED | CHP - GAS TURBINE | 11kV | ACCEPTED | 10.14
ENGLAND | SOUTHAMPTON RESERVE PROJECT_525 |  | SOUTHAMPTON RESERVE |  | GEOTHERMAL | 33kV | CONNECTED | 7
ENGLAND | SOUTHAMPTON RESERVE PROJECT_546 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 0.81
ENGLAND | SOUTHAMPTON RESERVE PROJECT_714 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 1.9
ENGLAND | SOUTHAMPTON RESERVE PROJECT_723 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
ENGLAND | SOUTHAMPTON RESERVE PROJECT_727 |  | SOUTHAMPTON RESERVE |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.037
ENGLAND | SOUTHAMPTON RESERVE PROJECT_729 |  | SOUTHAMPTON RESERVE |  | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.015
ENGLAND | SOUTHCOTE PROJECT_221 |  |  | SOUTHCOTE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.21
ENGLAND | SPARKFORD PROJECT_14 |  |  | SPARKFORD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.2
ENGLAND | SPRING QUARRY WEST PROJECT_445 |  |  | SPRING QUARRY WEST | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 7
ENGLAND | SPRING QUARRY WEST PROJECT_467 |  |  | SPRING QUARRY WEST | GAS TURBINE | 11kV | ACCEPTED | 5
ENGLAND | ST CROSS PROJECT_724 |  |  | ST CROSS | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.064
ENGLAND | ST CROSS PROJECT_847 |  |  | ST CROSS | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1684
ENGLAND | ST EBBES PROJECT_631 |  |  | ST EBBES | DIESEL | 11kV | CONNECTED | 0.2
ENGLAND | ST EBBES PROJECT_632 |  |  | ST EBBES | DIESEL | 11kV | CONNECTED | 0.5
ENGLAND | STAINES PROJECT_269 |  | STAINES |  | BATTERY | 33kV | ACCEPTED | 49
ENGLAND | STAINES PROJECT_271 |  | STAINES |  | BATTERY | 33kV | ACCEPTED | 49
ENGLAND | STAINES PROJECT_562 |  | STAINES |  | BATTERY | 33kV | ACCEPTED | 49.9
ENGLAND | STANDLAKE PROJECT_85 |  |  | STANDLAKE | LANDFILL GAS | 11kV | CONNECTED | 2
ENGLAND | STANTON FITZWARREN PROJECT_491 |  |  | STANTON FITZWARREN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 4
ENGLAND | STANTON FITZWARREN PROJECT_492 |  |  | STANTON FITZWARREN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 3.5
ENGLAND | STRATTON MAIN PROJECT_487 |  | STRATTON MAIN |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 28.6
ENGLAND | STRATTON MAIN PROJECT_488 |  | STRATTON MAIN |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 22.6
ENGLAND | STRATTON MAIN PROJECT_503 |  | STRATTON MAIN |  | BATTERY | 33kV | ACCEPTED | 20
ENGLAND | STRATTON PROJECT_497 |  |  | STRATTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.71
ENGLAND | STRATTON PROJECT_498 |  |  | STRATTON | DIESEL | 11kV | CONNECTED | 2
ENGLAND | STRATTON PROJECT_514 |  |  | STRATTON | BATTERY | 11kV | ACCEPTED | 1.36
ENGLAND | STRATTON PROJECT_590 |  |  | STRATTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.526
ENGLAND | STRATTON PROJECT_750 |  |  | STRATTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.505
ENGLAND | STRATTON RESERVE PROJECT_471 |  | STRATTON RESERVE |  | WIND FARM | 33kV | CONNECTED | 6.5
ENGLAND | STRATTON RESERVE PROJECT_477 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | STRATTON RESERVE PROJECT_478 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | STRATTON RESERVE PROJECT_486 |  | STRATTON RESERVE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9
ENGLAND | STRATTON RESERVE PROJECT_773 |  | STRATTON RESERVE |  | BATTERY | 33kV | ACCEPTED | 3.16
ENGLAND | SUNBURY CROSS PROJECT_265 |  |  | SUNBURY CROSS | OTHER SYNCHRONOUS | 11kV | CONNECTED | 10
ENGLAND | SUNBURY CROSS PROJECT_267 |  |  | SUNBURY CROSS | WASTE TO ENERGY | 11kV | ACCEPTED | 3.7
ENGLAND | SUNBURY CROSS PROJECT_268 |  |  | SUNBURY CROSS | CHP - GAS TURBINE | 11kV | ACCEPTED | 1.7
ENGLAND | SUTTON BENGER PROJECT_589 |  |  | SUTTON BENGER | BATTERY | 11kV | ACCEPTED | 0.914
ENGLAND | SUTTON LANE PROJECT_248 |  |  | SUTTON LANE | CHP - GAS TURBINE | 11kV | CONNECTED | 4.5
ENGLAND | SUTTON LANE PROJECT_249 |  |  | SUTTON LANE | WASTE TO ENERGY | 11kV | CONNECTED | 1.5
ENGLAND | SUTTON LANE PROJECT_250 |  |  | SUTTON LANE | LANDFILL GAS | 11kV | CONNECTED | 2.8
ENGLAND | SWINDON PROJECT_470 |  | SWINDON |  | LANDFILL GAS | 33kV | CONNECTED | 5
ENGLAND | SWINDON PROJECT_479 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 15
ENGLAND | SWINDON PROJECT_484 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8
ENGLAND | SWINDON PROJECT_485 |  |  | SWINDON | DIESEL | 11kV | CONNECTED | 1.781
ENGLAND | SWINDON PROJECT_493 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5
ENGLAND | SWINDON PROJECT_502 |  | SWINDON |  | DIESEL | 33kV | CONNECTED | 6
ENGLAND | SWINDON PROJECT_507 |  |  | SWINDON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2.5
ENGLAND | SWINDON PROJECT_512 |  |  | SWINDON | BATTERY | 11kV | ACCEPTED | 1.2
ENGLAND | SWINDON PROJECT_517 |  | SWINDON |  | BATTERY | 33kV | ACCEPTED | 12
ENGLAND | SWINDON PROJECT_657 |  |  | SWINDON | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.163
ENGLAND | SWINDON PROJECT_783 |  | SWINDON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 20
ENGLAND | SWINDON PROJECT_801 |  |  | SWINDON | BATTERY | 0.4kV | ACCEPTED | 0.084
ENGLAND | TADLEY PROJECT_62 |  |  | TADLEY | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.3
ENGLAND | THATCHAM PROJECT_49 |  |  | THATCHAM | NATURAL GAS | 11kV | CONNECTED | 9.6
ENGLAND | THATCHAM PROJECT_50 |  |  | THATCHAM | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
ENGLAND | THATCHAM PROJECT_57 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 14
ENGLAND | THATCHAM PROJECT_58 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 16
ENGLAND | THATCHAM PROJECT_65 |  | THATCHAM |  | GAS TURBINE | 33kV | ACCEPTED | 20.53
ENGLAND | THATCHAM PROJECT_835 |  | THATCHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 24.2
ENGLAND | THE MALL PROJECT_209 |  |  | THE MALL | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.149
ENGLAND | THEALE PROJECT_219 |  |  | THEALE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.25
ENGLAND | THEALE PROJECT_220 |  |  | THEALE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.06
ENGLAND | THRUXTON PROJECT_747 |  |  | THRUXTON | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18.95
ENGLAND | TITCHFIELD PROJECT_698 |  |  | TITCHFIELD | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.15
ENGLAND | TITCHFIELD PROJECT_712 |  |  | TITCHFIELD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.171
ENGLAND | TONGHAM PROJECT_178 |  |  | TONGHAM | LANDFILL GAS | 11kV | CONNECTED | 1.33
ENGLAND | TONGHAM PROJECT_215 |  |  | TONGHAM | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.41
ENGLAND | TOOTHILL PROJECT_472 |  |  | TOOTHILL | LANDFILL GAS | 11kV | CONNECTED | 2
ENGLAND | TOOTHILL PROJECT_489 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 48.51
ENGLAND | TOOTHILL PROJECT_490 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.2
ENGLAND | TOOTHILL PROJECT_495 |  | TOOTHILL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.76
ENGLAND | TOOTHILL PROJECT_508 |  | TOOTHILL |  | BATTERY | 33kV | ACCEPTED | 31.58
ENGLAND | TOOTHILL PROJECT_656 |  |  | TOOTHILL | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.058
ENGLAND | TOOTHILL PROJECT_740 |  |  | TOOTHILL | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.12
ENGLAND | TOOTHILL PROJECT_751 |  | TOOTHILL |  | BATTERY | 33kV | ACCEPTED | 5.26
ENGLAND | TOTTON PROJECT_549 |  |  | TOTTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 2
ENGLAND | TRADING ESTATE PROJECT_473 |  |  | TRADING ESTATE | DIESEL | 11kV | CONNECTED | 0.42
ENGLAND | TRADING ESTATE PROJECT_504 |  |  | TRADING ESTATE | CHP - SPARK IGNITION | 11kV | CONNECTED | 2.15
ENGLAND | TRASH GREEN PROJECT_207 |  |  | TRASH GREEN | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.7
ENGLAND | TROWBRIDGE TOWN PROJECT_444 |  |  | TROWBRIDGE TOWN | DIESEL | 11kV | CONNECTED | 2.5
ENGLAND | TWYFORD PROJECT_225 |  |  | TWYFORD | CHP - GAS TURBINE | 11kV | ACCEPTED | 0.1
ENGLAND | UPPER HEYFORD PROJECT_116 |  |  | UPPER HEYFORD | LANDFILL GAS | 11kV | CONNECTED | 1.57
ENGLAND | UPPER HEYFORD PROJECT_119 |  |  | UPPER HEYFORD | LANDFILL GAS | 11kV | ACCEPTED | 1
ENGLAND | UPPER HEYFORD PROJECT_83 |  |  | UPPER HEYFORD | LANDFILL GAS | 11kV | CONNECTED | 3.25
ENGLAND | UPTON PROJECT_253 |  |  | UPTON | GAS TURBINE | 11kV | ACCEPTED | 0.4
ENGLAND | VELMORE PROJECT_529 |  |  | VELMORE | DIESEL | 11kV | CONNECTED | 1.5
ENGLAND | VELMORE PROJECT_531 |  | VELMORE |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6.3
ENGLAND | VELMORE PROJECT_539 |  | VELMORE |  | DIESEL | 33kV | ACCEPTED | 20
ENGLAND | VELMORE PROJECT_852 |  | VELMORE |  | BATTERY | 33kV | ACCEPTED | 60
ENGLAND | VERWOOD PROJECT_394 |  |  | VERWOOD | GAS | 11kV | ACCEPTED | 5
ENGLAND | WALLINGFORD PROJECT_121 |  |  | WALLINGFORD | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
ENGLAND | WALLINGFORD PROJECT_610 |  |  | WALLINGFORD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.684
ENGLAND | WALLINGFORD PROJECT_614 |  |  | WALLINGFORD | LANDFILL GAS | 11kV | CONNECTED | 2.4
ENGLAND | WALLINGFORD PROJECT_99 |  |  | WALLINGFORD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 1.36
ENGLAND | WANTAGE PROJECT_616 |  |  | WANTAGE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ENGLAND | WAREHAM PROJECT_321 |  | WAREHAM |  | LANDFILL GAS | 33kV | CONNECTED | 3.23
ENGLAND | WAREHAM PROJECT_329 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 6
ENGLAND | WAREHAM PROJECT_345 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 9
ENGLAND | WAREHAM PROJECT_350 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 3.96
ENGLAND | WAREHAM PROJECT_351 |  | WAREHAM |  | LANDFILL GAS | 33kV | ACCEPTED | 20.8
ENGLAND | WAREHAM PROJECT_573 |  | WAREHAM |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 0
ENGLAND | WAREHAM PROJECT_830 |  | WAREHAM |  | GAS TURBINE | 132kV | ACCEPTED | 0
ENGLAND | WAREHAM TOWN PROJECT_376 |  |  | WAREHAM TOWN | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.1
ENGLAND | WATERLOOVILLE PROJECT_681 |  |  | WATERLOOVILLE | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.05
ENGLAND | WATLINGTON PROJECT_104 |  |  | WATLINGTON | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 17
ENGLAND | WELL END PROJECT_3 |  |  | WELL END | BATTERY | 11kV | ACCEPTED | 7.2
ENGLAND | WEST GRAFTON PROJECT_411 |  | WEST GRAFTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.64
ENGLAND | WEST GRAFTON PROJECT_784 |  | WEST GRAFTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42.1
ENGLAND | WEST GRAFTON VILLAGE PROJECT_427 |  |  | WEST GRAFTON VILLAGE | PHOTOVOLTAIC PLANT | 0.4kV | CONNECTED | 0.18
ENGLAND | WEST HENDFORD PROJECT_794 |  |  | WEST HENDFORD | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 6.08
ENGLAND | WESTBURY PROJECT_404 |  |  | WESTBURY | LANDFILL GAS | 11kV | CONNECTED | 4.76
ENGLAND | WESTERN ESPLANADE PROJECT_682 |  |  | WESTERN ESPLANADE | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.18
ENGLAND | WESTERN ESPLANADE PROJECT_721 |  |  | WESTERN ESPLANADE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.18
ENGLAND | WESTON PROJECT_26 |  |  | WESTON | LANDFILL GAS | 11kV | CONNECTED | 2.6
ENGLAND | WEYMOUTH PROJECT_70 |  |  | WEYMOUTH | NATURAL GAS | 11kV | CONNECTED | 3.02
ENGLAND | WHEATLEY PROJECT_570 |  |  | WHEATLEY | NATURAL GAS | 11kV | ACCEPTED | 7.12
ENGLAND | WINCANTON PROJECT_336 |  |  | WINCANTON | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | WINCANTON PROJECT_821 |  |  | WINCANTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 9.9
ENGLAND | WINCHESTER PROJECT_541 |  | WINCHESTER |  | OTHER SYNCHRONOUS | 33kV | ACCEPTED | 20
ENGLAND | WINCHESTER PROJECT_577 |  | WINCHESTER |  | BATTERY | 33kV | ACCEPTED | 10
ENGLAND | WINCHESTER PROJECT_759 |  | WINCHESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 26.32
ENGLAND | WINCHESTER PROJECT_787 |  | WINCHESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 15.79
ENGLAND | WINCHESTER PROJECT_793 |  | WINCHESTER |  | BATTERY | 33kV | ACCEPTED | 55
ENGLAND | WINCHESTER PROJECT_849 |  | WINCHESTER |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 33.3
ENGLAND | WINDRUSH PARK PROJECT_637 |  |  | WINDRUSH PARK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.03
ENGLAND | WINDRUSH PARK PROJECT_840 |  |  | WINDRUSH PARK | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.8
ENGLAND | WINSMORE LANE PROJECT_647 |  |  | WINSMORE LANE | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.001
ENGLAND | WINTON PROJECT_320 |  |  | WINTON | DIESEL | 11kV | CONNECTED | 5.061
ENGLAND | WITNEY & YARNTON PROJECT_105 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 11.85
ENGLAND | WITNEY & YARNTON PROJECT_106 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 12.5
ENGLAND | WITNEY & YARNTON PROJECT_107 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10
ENGLAND | WITNEY & YARNTON PROJECT_113 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.95
ENGLAND | WITNEY & YARNTON PROJECT_565 |  | WITNEY & YARNTON |  | PV & BATTERY | 33kV | ACCEPTED | 13.5
ENGLAND | WITNEY & YARNTON PROJECT_566 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 21.5
ENGLAND | WITNEY & YARNTON PROJECT_592 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 18
ENGLAND | WITNEY & YARNTON PROJECT_617 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ENGLAND | WITNEY & YARNTON PROJECT_627 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.05
ENGLAND | WITNEY & YARNTON PROJECT_629 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.015
ENGLAND | WITNEY & YARNTON PROJECT_630 |  | WITNEY & YARNTON |  | CHP - GAS TURBINE | 11kV | CONNECTED | 1
ENGLAND | WITNEY & YARNTON PROJECT_742 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 5
ENGLAND | WITNEY & YARNTON PROJECT_780 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 49.9
ENGLAND | WITNEY & YARNTON PROJECT_790 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 6
ENGLAND | WITNEY & YARNTON PROJECT_800 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 33
ENGLAND | WITNEY & YARNTON PROJECT_845 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 35
ENGLAND | WITNEY & YARNTON PROJECT_88 |  | WITNEY & YARNTON |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 35
ENGLAND | WOODMILL LANE PROJECT_850 |  |  | WOODMILL LANE | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.171
ENGLAND | WOODSTOCK PROJECT_611 |  |  | WOODSTOCK | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.51
ENGLAND | WOODSTOCK PROJECT_766 |  |  | WOODSTOCK | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 5
ENGLAND | WOOTTON BASSETT PROJECT_474 |  |  | WOOTTON BASSETT | WASTE TO ENERGY | 11kV | CONNECTED | 2
ENGLAND | WOOTTON BASSETT PROJECT_475 |  |  | WOOTTON BASSETT | LANDFILL GAS | 11kV | CONNECTED | 2
ENGLAND | WOOTTON BASSETT PROJECT_483 |  |  | WOOTTON BASSETT | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 5
ENGLAND | WOOTTON BASSETT PROJECT_522 |  |  | WOOTTON BASSETT | LANDFILL GAS | 11kV | ACCEPTED | 6.5
ENGLAND | WOOTTON BASSETT PROJECT_659 |  |  | WOOTTON BASSETT | GAS TURBINE | 11kV | ACCEPTED | 7.5
ENGLAND | WOOTTON ROAD PROJECT_615 |  |  | WOOTTON ROAD | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.24
ENGLAND | WRECCLESHAM PROJECT_232 |  |  | WRECCLESHAM | BATTERY | 33kV | ACCEPTED | 20
ENGLAND | WROUGHTON PROJECT_500 |  |  | WROUGHTON | LANDFILL GAS | 11kV | CONNECTED | 2
ENGLAND | WROUGHTON PROJECT_501 |  |  | WROUGHTON | LANDFILL GAS | 11kV | CONNECTED | 2
ENGLAND | WYMERING & FORT WIDLEY PROJECT_307 |  | WYMERING & FORT WIDLEY |  | DIESEL | 33kV | CONNECTED | 19.85
ENGLAND | WYMERING & FORT WIDLEY PROJECT_310 |  | WYMERING & FORT WIDLEY |  | LANDFILL GAS | 33kV | ACCEPTED | 20
ENGLAND | WYMERING PROJECT_280 |  |  | WYMERING | CHP - GAS TURBINE | 11kV | CONNECTED | 4
ENGLAND | WYMERING PROJECT_673 |  |  | WYMERING | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0
ENGLAND | WYMERING PROJECT_674 |  |  | WYMERING | CHP - GAS TURBINE | 11kV | CONNECTED | 0.135
ENGLAND | YARNTON PROJECT_808 |  |  | YARNTON | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 5
ENGLAND | YEOVIL PROJECT_10 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 4.13
ENGLAND | YEOVIL PROJECT_21 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 9
ENGLAND | YEOVIL PROJECT_22 |  | YEOVIL |  | CHP - GAS TURBINE | 33kV | ACCEPTED | 15
ENGLAND | YEOVIL PROJECT_23 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 7.6
ENGLAND | YEOVIL PROJECT_6 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 10.59
ENGLAND | YEOVIL PROJECT_7 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 8.8
ENGLAND | YEOVIL PROJECT_8 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 5.55
ENGLAND | YEOVIL PROJECT_9 |  | YEOVIL |  | PHOTOVOLTAIC PLANT | 33kV | CONNECTED | 7.5
ENGLAND | YETMINSTER PROJECT_15 |  |  | YETMINSTER | DIESEL | 11kV | CONNECTED | 0.4
ENGLAND | YETMINSTER PROJECT_16 |  |  | YETMINSTER | CHP - GAS TURBINE | 11kV | CONNECTED | 0.25
ENGLAND | YETMINSTER PROJECT_17 |  |  | YETMINSTER | PHOTOVOLTAIC PLANT | 11kV | CONNECTED | 0.15
ENGLAND | MELKSHAM PROJECT _1 | MELKSHAM |  |  | BATTERY | 132kV | ACCEPTED | 49.9
ENGLAND | COWLEY PROJECT_128 | COWLEY |  |  | OTHER | 132kV | ACCEPTED | 99.8
ENGLAND | MANNINGTON_PROJECT_1 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.082
ENGLAND | NURSLING_PROJECT_1 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.16
ENGLAND | NURSLING_PROJECT_2 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.11
ENGLAND | MANNINGTON_PROJECT_2 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.248
ENGLAND | MANNINGTON_PROJECT_3 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.6
ENGLAND | AXMINSTER_PROJECT_1 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.59
ENGLAND | MANNINGTON_PROJECT_4 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 0.4kV | ACCEPTED | 0.1
ENGLAND | AXMINSTER_PROJECT_2 | AXMINSTER |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 35
ENGLAND | MANNINGTON_PROJECT_5 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 18.81
ENGLAND | CHICKERELL_PROJECT_1 | CHICKERELL GSP |  |  | BATTERY | 33kV | ACCEPTED | 49
ENGLAND | NURSLING_PROJECT_3 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 100
ENGLAND | LALEHAM_PROJECT_1 | LALEHAM |  |  | BATTERY | 132kV | ACCEPTED | 50
ENGLAND | LALEHAM_PROJECT_2 | LALEHAM |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 28.5
ENGLAND | MANNINGTON_PROJECT_6 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 50.53
ENGLAND | MANNINGTON_PROJECT_7 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 16
ENGLAND | MANNINGTON_PROJECT_8 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 132kV | ACCEPTED | 20
ENGLAND | MANNINGTON_PROJECT_9 | MANNINGTON GSP |  |  | BATTERY | 33kV | ACCEPTED | 9
ENGLAND | MANNINGTON_PROJECT_10 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 12.63
ENGLAND | MANNINGTON_PROJECT_11 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 10.32
ENGLAND | MANNINGTON_PROJECT_12 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 9.47
ENGLAND | MANNINGTON_PROJECT_13 | MANNINGTON GSP |  |  | GAS | 11kV | ACCEPTED | 5.34
ENGLAND | MANNINGTON_PROJECT_14 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 33kV | ACCEPTED | 21.05
ENGLAND | MANNINGTON_PROJECT_15 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 33kV | ACCEPTED | 33.68
ENGLAND | MANNINGTON_PROJECT_16 | MANNINGTON GSP |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 42.11
ENGLAND | NURSLING_PROJECT_792 |  |  |  | PHOTOVOLTAIC PLANT + BATTERY STORAGE | 132kV | ACCEPTED | 105.26
ENGLAND | MANNINGTON_PROJECT_17 |  |  |  | BATTERY | 132kV | ACCEPTED | 49.9
ENGLAND | MANNINGTON_PROJECT_18 |  |  |  | BATTERY | 132kV | ACCEPTED | 99.9
ENGLAND | AXMINSTER_PROJECT_3 |  |  |  | BATTERY | 132kV | ACCEPTED | 60
ENGLAND | MINETY_PROJECT_100 | MINETY |  |  | BATTERY | 132kV | ACCEPTED | 50
ENGLAND | NURSLING_PROJECT_100 | NURSLING |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.44
ENGLAND | MELKSHAM_PROJECT_100 | MELKSHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.59
ENGLAND | CHICKERELL GSP_PROJECT_100 | CHICKERELL GSP |  |  | BATTERY | 132kV | ACCEPTED | 49.9
ENGLAND | BRAMLEY_PROJECT_100 | BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.2
ENGLAND | BRAMLEY_PROJECT_100 | BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 0.132
ENGLAND | LALEHAM_PROJECT_100 | LALEHAM |  |  | PHOTOVOLTAIC PLANT | 11kV | ACCEPTED | 2
ENGLAND | FLEET BRAMLEY_PROJECT_100 | FLEET BRAMLEY |  |  | PHOTOVOLTAIC PLANT | 33kV | ACCEPTED | 0.1
ENGLAND | IVER 66KV_PROJECT_100 | IVER 66KV |  |  | BATTERY | 132kV | ACCEPTED | 50
ENGLAND | LALEHAM_PROJECT_100 | LALEHAM |  |  | BATTERY | 132KV | ACCEPTED | 99.9
ENGLAND | COWLEY_PROJECT_100 | COWLEY

## Quoted Jobs
Area | Project Name | GSP Parent | BSP Parent | PS Parent | Technology Type | Capacity (MVA) | Quotation Expiry Date | Contestable Costs | Non-Contestable Costs | Reinforcement Works
ENGLAND |  | AMERSHAM |  |  | BATTERY | 99 | 2023-03-21 | 3160824.12 | 1226183.27 | 58704.32
ENGLAND |  | AXMINSTER |  |  | PHOTOVOLTAIC | 0.29 | 2023-05-09 | 2762.12 | 2762.12 | 0
ENGLAND |  | AXMINSTER |  |  | BATTERY | 49.9 | 2023-03-01 | 15197506.47 | 8422775.3 | 0
ENGLAND |  | BOTLEY WOOD |  |  | OTHER | 27 | 2023-03-09 | 5399534.88 | 631187.38 | 33829.71
ENGLAND |  | BOTLEY WOOD |  |  | PHOTOVOLTAIC | 0.99 | 2023-03-05 | 22094.49 | 22094.49 | 0
ENGLAND |  | BOTLEY WOOD |  |  | PHOTOVOLTAIC | 0.96 | 2023-05-03 | 125547.63 | 36,021.08 | 8571.86
ENGLAND |  | BRAMLEY |  |  | OTHER | 0.7 | 2023-05-09 | 670 | 670 | 0
ENGLAND |  | BRAMLEY |  |  | CHP | 0.774 | 2023-03-12 | 129375.85 | 16891.01 | 0
ENGLAND |  | BRAMLEY |  |  | PHOTOVOLTAIC | 20 | 2023-05-17 | 5597319.97 | 354797.57 | 0
ENGLAND |  | BRAMLEY |  |  | PHOTOVOLTAIC | 0.264 | 2023-04-20 | £1364.00 | £1364.00 | £1364.00
ENGLAND |  | BRAMLEY |  |  | BATTERY | 38 | 2023-05-09 | 3226191.45 | 1071593.72 | 0
ENGLAND |  | CHICKERELL |  |  | PHOTOVOLTAIC | 0.13 | 2023-05-08 | 7030.61 | 7030.61 | 0
ENGLAND |  | CHICKERELL |  |  | BATTERY | 45 | 2023-03-08 | 31935057.73 | 2046471.73 | 0
ENGLAND |  | COWLEY |  |  | PHOTOVOLTAIC | 1 | 2023-04-26 | 98652.67 | 98652.67 | 0
ENGLAND |  | COWLEY |  |  | OTHER | 7.6 | 2023-05-22 | 579372.67 | 579372.67 | 0
ENGLAND |  | COWLEY |  |  | PHOTOVOLTAIC | 7.7 | 2023-02-21 | 6089805.13 | 35474.95 | 2472154.71
ENGLAND |  | COWLEY |  |  | PHOTOVOLTAIC | 20 | 2023-04-17 | 0 | 320707.27 | 0
ENGLAND |  | COWLEY |  |  | BATTERY | 49.9 | 2023-05-04 | 11259268.54 | 5997076.28 | 0
ENGLAND |  | COWLEY |  |  | PHOTOVOLTAIC | 72 | 2023-03-01 | 3511174.66 | 1914128.21 | 0
ENGLAND |  | COWLEY |  |  | BATTERY | 99.9 | 2023-03-21 | 7130867.17 | 1234476.32 | 0
ENGLAND |  | COWLEY |  |  | BATTERY | 100 | 2023-02-01 | 27226577.88 | 1919881.27 | 0
ENGLAND |  | DIDCOT |  |  | BATTERY | 40 | 2023-04-12 | 8914847.93 | 2364235.72 | 0
ENGLAND |  | EAST CLAYDON |  |  | PHOTOVOLTAIC | 0.5 | 2023-02-20 | 4706917.24 | 1477222.63 | 21281.79
ENGLAND |  | EAST CLAYDON |  |  | PHOTOVOLTAIC | 0.72 | 2023-03-22 | 1664 | 1664 | 0
ENGLAND |  | FAWLEY |  |  | CHP | 32.162 | 2023-02-07 | NA | 32242 | 0
ENGLAND |  | FAWLEY |  |  | BATTERY | 49.9 | 2023-05-01 | 37951806.44 | 773384.37 | 0
ENGLAND |  | FAWLEY |  |  | PHOTOVOLTAIC | 15 | 2023-05-24 | 16367 | 16367 | 0
ENGLAND |  | FLEET |  |  | PHOTOVOLTAIC | 0.11 | 2023-04-20 | 8381.56 | 8381.56 | 0
ENGLAND |  | FLEET |  |  | PHOTOVOLTAIC | 6 | 2023-05-10 | 2775722.88 | 260201.61 | 9624.67
ENGLAND |  | FLEET |  |  | PHOTOVOLTAIC | 20 | 2023-04-24 | 2377648.59 | 1504265.43 | 722137.09
ENGLAND |  | FLEET |  |  | PHOTOVOLTAIC | 80 | 2023-03-20 | 5610825.88 | 2444379.91 | 0
ENGLAND |  | FLEET |  |  | BATTERY | 99.9 | 2023-03-22 | 23650483.36 | 2667903.39 | 0
ENGLAND |  | FLEET |  |  | PHOTOVOLTAIC | 26 | 2023-05-07 | 2558948.94 | 1437720.64 | 1948463.12
ENGLAND |  | FLEET BRAMLEY |  |  | PHOTOVOLTAIC | 0 | 2023-02-09 | 1144499.53 | 1144499.53 | 0
ENGLAND |  | FLEET BRAMLEY |  |  | PHOTOVOLTAIC | 0.3 | 2023-04-13 | 0 | 2215.95 | 0
ENGLAND |  | FLEET BRAMLEY |  |  | OTHER | 1.7 | 2023-11-01 | 2681467.64 | 1402437.19 | 99347.21
ENGLAND |  | FLEET BRAMLEY |  |  | BATTERY | 8 | 2023-04-05 | 2485066 | 1621518.59 | 9098
ENGLAND |  | FLEET BRAMLEY |  |  | OTHER | 17 | 2023-05-04 | 8243682.95 | 3197844.49 | 0
ENGLAND |  | FLEET BRAMLEY |  |  | OTHER | 19.27 | 2023-04-06 | 184434.18 | 120703.89 | 1342
ENGLAND |  | FLEET BRAMLEY |  |  | OTHER | 20 | 2023-05-01 | 2088023.37 | 493560.14 | 327347.67
ENGLAND |  | FLEET BRAMLEY |  |  | PHOTOVOLTAIC | 60 |  | 0 | 0 | 0
ENGLAND |  | FLEET BRAMLEY |  |  | BATTERY | 150 | 1900-03-30
ENGLAND |  | FLEET BRAMLEY |  |  | BATTERY | 170 | 2023-04-05 | 10317874.02 | 1480446.42 | 2067
ENGLAND |  | FLEET |  |  | OTHER | 17 | 2023-03-15 | 11650917.75 | 1348629.97 | 99347.21
ENGLAND |  | FLEET BRAMLEY |  |  | OTHER | 0.3 | 2023-05-10 | 6006567.14 | 2750995.25 | 0
ENGLAND |  | FLEET BRAMLEY |  |  | PHOTOVOLTAIC | 17 | 2023-03-23 | 10118907.6 | 1338211.34 | 99347.21
ENGLAND |  | FLEET BRAMLEY |  |  | PHOTOVOLTAIC | 17 | 2023-04-23 | 5724469.23 | 1348624.97 | 100024.41
ENGLAND |  | IVER |  |  | Phototvoltaic | 0.2 | 2023-04-20 | 370 | 370 | 0
ENGLAND |  | IVER |  |  | PHOTOVOLTAIC | 52.63 | 2023-02-15 | 15328724.98 | 2277561.57 | 0
ENGLAND |  | IVER |  |  | OTHER | 49.9 | 2023-02-06 | 4159610.06 | 2336211.77 | 5484982.69
ENGLAND |  | IVER 66KV |  |  | PHOTOVOLTAIC | 0.15 | 2023-04-17 | 370 | 370 | 0
ENGLAND |  | LOVEDEAN |  |  | OTHER | 21.05 | 2023-05-03 | 625471.72 | 625471.72 | 35475.34
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 0.7 | 2023-04-10 | 1664 | 1664 | £1364.00
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 0.89 | 2023-04-13 | £1237.84 | £670.00 | £360.00
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 1.73 | 2023-05-23 | 297054.01 | 218508.3 | 0
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 20 | 2023-02-08 | 3634191.29 | 400386.06 | 11038.79
ENGLAND |  | LOVEDEAN |  |  | OTHER | 22 | 2023-02-22 | 1860369.57 | 1000887.17 | 12164.54
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 32.39 | 2023-02-23 | n.a | 9558.47 | 1364
ENGLAND |  | LOVEDEAN |  |  | BATTERY | 49.2 | 2023-04-27 | 6635020.02 | 2571900.61 | 617543.8
ENGLAND |  | LOVEDEAN |  |  | OTHER | 49.9 | 2023-03-22 | 2817693.58 | 1207537.61 | 626815.9
ENGLAND |  | LOVEDEAN |  |  | OTHER | 49.9 | 2023-04-13 | 2776359.5 | 1205465.61 | 626815.9
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 49.9 | 2023-03-20 | 5629496.1 | 1126016.77 | 0
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 49.9 | 2023-03-20 | 4963527.94 | 1126016.77 | 0
ENGLAND |  | LOVEDEAN |  |  | BATTERY | 50.7 | 2023-05-15 | 246110.88 | 176298.67 | 1364
ENGLAND |  | LOVEDEAN |  |  | PHOTOVOLTAIC | 0kW | 2023-04-16 | 370 | 370 | 0
ENGLAND |  | Lovedean |  |  | PHOTOVOLTAIC | 0kW | 2023-05-24 | 670 | 670 | 0
ENGLAND |  | Lovedean |  |  | BATTERY | 35 | 2023-05-10 | 10360460.54 | 831012.91 | 13408.64
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 0.06 | 2023-02-20 | 0 | 2800 | 0
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 0.09 | 2023-03-20 | 100632.09 | 10229.18 | 0
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 0.12 | 2023-03-14 | 1029.36 | 1029.36 | 0
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 0.18 | 2023-03-05 | 67917.55 | 37258.55 | 0
ENGLAND |  | Mannington |  |  | OTHER | 0.2 | 2022-04-05 | 16479.37 | 8027.54 | 11110.91
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 0.2 | 2023-04-13 | 185 | 185 | 0
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 0.2 | 2023-04-16 | 185 | 185 | 0
ENGLAND |  | Mannington |  |  | OTHER | 1.93 | 2023-03-19 | 366813.53 | 120703.89 | 0
ENGLAND |  | Mannington |  |  | OTHER | 12 | 2023-04-19 | 1477582.72 | 1477582.72 | 0
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 20.6 | 2023-03-20 | 4047343.74 | 1339451.5 | 0
ENGLAND |  | Mannington |  |  | OTHER | 25 | 2023-05-16 | 21376716.92 | 1183465.72 | 0
ENGLAND |  | Mannington |  |  | BATTERY | 35 | 2023-05-08 | 27426517.98 | 1245395.21 | 0
ENGLAND |  | Mannington |  |  | PHOTOVOLTAIC | 49.5 | 2023-03-08 | 9160767.01 | 1330599.54 | 0
ENGLAND |  | Mannington |  |  | BATTERY | 99.9 | 2023-03-22 | 8794606.49 | 1245400.21 | 0
ENGLAND |  | Mannington GSP |  |  | OTHER | 0 | 2023-03-12 | 0 | 2072 | 0
ENGLAND |  | MELKSHAM |  |  | PHOTOVOLTAIC | 7.7 | 2023-02-21 | 6089805.13 | 35474.96 | 2472154.71
ENGLAND |  | Melksham |  |  | PHOTOVOLTAIC | 8 | 2023-04-06 | 2412131.89 | 1546429.12 | 0
ENGLAND |  | Melksham |  |  | OTHER | 10 | 2023-04-16 | 1937598.64 | 828517.56 | 0
ENGLAND |  | Melksham |  |  | PHOTOVOLTAIC | 47.5 | 2023-04-10 | 9615707.3 | 2430834.03 | 0
ENGLAND |  | Melksham |  |  | BATTERY | 100 | 2023-05-02 | 42221706.1 | 1296414.12 | 0
ENGLAND |  | Minety |  |  | PHOTOVOLTAIC | 0 | 2023-03-19 | 189108.38 | 189108.38 | 0
ENGLAND |  | Minety |  |  | OTHER | 0.6 | 2023-04-25 | 180649.87 | 95726.28 | 0
ENGLAND |  | Minety |  |  | BATTERY | 99.9 | 2023-04-10 | 4901162.13 | 1323613.52 | 0
ENGLAND |  | Minety |  |  | PHOTOVOLTAIC | 18 | 2023-02-28 | 3698554.05 | 495532.72 | 10923902.08
ENGLAND |  | NORTH HYDE |  |  | PHOTOVOLTAIC | 0.14 | 2023-05-16 | 13253.63 | 13253.63 | 0
ENGLAND |  | Nursling |  |  | PHOTOVOLTAIC | 0.24 | 2023-04-16 | 2739.18 | 370 | 0
ENGLAND |  | Nursling |  |  | OTHER | 1.93 | 2023-05-02 | 234702.03 | 138190.18 | 49293.92
ENGLAND |  | Nursling |  |  | PHOTOVOLTAIC | 15.2 | 2023-03-22 | 3422765.27 | 811121.23 | 0
ENGLAND |  | Nursling |  |  | PHOTOVOLTAIC | 21.84 | 2023-02-15 | 1783987.26 | 552959.02 | 0
ENGLAND |  | Nursling |  |  | BATTERY | 49.9 | 2023-02-20 | 19769038.95 | 1953695.77 | 0
ENGLAND |  | WILLESDEN |  |  | PHOTOVOLTAIC | 0.069 | 2023-03-08 | 0 | 0 | 0
ENGLAND |  | WILLESDEN |  |  | PHOTOVOLTAIC | 0.9 | 2023-03-13 | 0 | 0 | 0
ENGLAND |  | WILLESDEN |  |  | BATTERY | 40 | 2023-05-09 | 55250 | 54462 | 0