## GSP
Area | Grid Supply Point Name | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification
Shetland | Shetland | 5.31 / 17.5 | 59.898088 | -1.3045615 | HU39011276 | 30 | 0 | 9.585 | 43.3 | 111.163 | 0 | 100 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 | Red

## BSP
Area | Bulk Supply Point Name | GSP Parent | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate Rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification

## PS
Area | Primary Substation Name | GSP Parent | BSP Parent | Break Fault Level vs Rating (kA) | Location Latitude | Location Longitude | Location Grid Ref | Nameplate Rating (MVA) | Sum of quoted generation (MVA) | Minimum Load (MW) | Maximum Load (MW) | Contracted Generation (MVA) | Available Headroom Capacity (MVA) | Reverse Powerflow Capability (%) | Upstream status | Transmission Works | Transmission reinforcement date | Downstream status | Distribution Works | Distribution reinforcement date | SoW needed? | Part of SWAN? | Other constraints | Voltage (kV) | Site Classification
Shetland | Brae | Shetland |  | 3.03 / 18.4 | 60.4016 | -1.3478 | HU3604068816 | 5.0 | 0 | 1.2 | 3.1545 | 0.2 | 6 | 100 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Firth | Shetland |  | 2.97 / 13.1 | 60.4489 | -1.2027 | HU4396874166 | 5.0 | 0 | 0.39836 | 1.5379 | 0 | 2.8984 | 50 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Gremista | Shetland |  | NA | 60.1666 | -1.1645 | HU4646842756 | 48 | 0 | 4.3 | 20.3 | 7.18 | 21.12 | 50 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Gutcher | Shetland |  | 1.58 / 13.1 | 60.6759 | -1.0036 | HU5453899599 | 4 | 0 | 0.086085 | 0.88156 | 0.545 | 1.5411 | 50 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Mid Yell | Shetland |  | 2.21 / 13.1 | 60.6035 | -1.1221 | HU4817291442 | 5 | 0 | 0.11277 | 0.67105 | 0 | 5.1128 | 100 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Scalloway | Shetland |  | 3.53 / 13.1 | 60.1392 | -1.2565 | HU4139939639 | 8 | 0 | 0.92008 | 4.4271 | 0 | 8.9201 | 100 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Setter Sandwick | Shetland |  | NA | 60.0162 | -1.229 | HU4308625957 | 4.0 | 0 | 0.59698 | 2.7273 | 0 | 2.597 | 50 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Sumburgh | Shetland |  | 1.54 / 18.4 | 59.898 | -1.3047 | HU3900512755 | 4 | 0 | 0.39166 | 2.3441 | 0 | 4.3917 | 100 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Tumblin | Shetland |  | 2.24 / 12.5 | 60.2631 | -1.3993 | HU3334053363 | 5 | 0 | 0.5 | 2.27 | 0 | 3 | 50 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Unst | Shetland |  | 1.27 / 20 | 60.7985 | -0.82632 | HP6398113411 | 4 | 0 | 0.34795 | 1.618 | 0 | 2.348 | 50 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red
Shetland | Voe | Shetland |  | 3.37 / 13.1 | 60.3496 | -1.2557 | HU4117663079 | 8 | 0 | 0.73241 | 3.3653 | 0 | 8.7324 | 100 | Constrained |  |  | Constrained |  |  | No | No | None Known | 33 / 11 | Red

## Contracted Generation
Area | Project Name | GSP Parent | BSP Parent | PS Parent | Technology Type | Voltage (kV) | Status | Contracted Capacity (MVA) | Expected Connection Date
Shetland | Shetland Project 01 | Shetland |  |  | CHP | 33kV | Connected | 18
Shetland | Shetland Project 02 | Shetland |  |  | Wind | 33kV | Connected | 1.98
Shetland | Shetland Project 03 |  |  | Gremista | Wind | 11kV | Connected | 1.7
Shetland | Shetland Project 04 |  |  | Gutcher | Wind | LV | Connected | 0.5
Shetland | Shetland Project 05 | Shetland |  |  | Tidal | 33kV | Connected | 0.045
Shetland | Shetland Project 06 |  |  | Gremista | Wind | 11kV | Connected | 4.5
Shetland | Shetland Project 07 |  |  | Gutcher | Wind | LV | Connected | 3
Shetland | Shetland Project 08 |  |  | Brae | Tidal | 11kV | Connected | 0.5
Shetland | Shetland Project 09 | Shetland |  |  | Wind | LV | Connected | 0.2
Shetland | Shetland Project 10 | Shetland |  |  | Diesel | 33kV | Connected | 28
Shetland | Shetland Project 11 | Shetland |  |  | Diesel | 33kV | Connected | 37
Shetland | Shetland Project 12 | Shetland |  |  | Other | 33kV | Contracted | 5.838 | January 2022
Shetland | Shetland Project 13 | Shetland |  |  | Other | 33kV | Connected | 0
Shetland | Shetland Project 14 | Shetland |  |  | Wind | 33kV | Contracted | 9.9 | March 2024
Shetland | Shetland Project 15 | Shetland |  |  | Wind | 33kV | Contracted | 0.9 | September 2024
Shetland | Shetland Project 16 | Shetland |  |  | Wind | 33kV | Contracted | 2.3 | September 2024
Shetland | Shetland Project 17 | Shetland |  |  | PV | 33kV | Contracted | 5 | December 2024

## Quoted Jobs
Area | Project Name | GSP Parent | BSP Parent | PS Parent | Technology Type | Capacity (MVA) | Quotation Expiry Date | Contestable Costs | Non-Contestable Costs | Reinforcement Works
Shetland | Shetland Quoted Job 1 | Shetland |  |  | Wind | 5 | December 2022 | 1323585.69 | 47844.18 | 0